## 2021 Inspection Report Data
# | Inspection Report | Date Inspection Report Received | Date of Inspection | Report Item Number | Brief Description of Defect | Defect Severity | Defect Status | Corrective Action | Defect Corrected Date
1 | MJ-PGE-034 | 2021-01-27 | 2021-01-12 | 1.1 | 1106 - No lightning arresters in Surge District 2 per PG&E’s specs | Category 2 – Moderate: 12 months or scheduled in WMP update (other) | Closed by OEIS | Install lightning arresters | 2021-03-30
1 | MJ-PGE-034 | 2021-01-27 | 2021-01-12 | 1.2 | 1106 - Table 2: Basic Minimum Allowable Clearance of Wires from Other Wires at Crossings, in Midspans and at Supports | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | None required | N/A
1 | MJ-PGE-034 | 2021-01-27 | 2021-01-12 | 7 | 1106 - Table 2: Basic Minimum Allowable Clearance of Wires from Other Wires at Crossings, in Midspans and at Supports | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | None required | N/A
2 | MJ-PGE-035 | 2021-01-28 | 2021-01-21 | 3 | 1106 - Table 2: Basic Minimum Allowable Clearance of Wires from Other Wires at Crossings, in Midspans and at Supports | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | None required | N/A
2 | MJ-PGE-035 | 2021-01-28 | 2021-01-21 | 4 | 1106 - Table 2: Basic Minimum Allowable Clearance of Wires from Other Wires at Crossings, in Midspans and at Supports | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | None required | N/A
3 | QP-PGE-005 | 2021-02-01 | 2021-01-21 | 15 | 426 - Failure to follow utility standards, manual, or best practices (GO95 Rule 31.1) in HFTD | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjust guy wire contact with vegetation | 2021-02-11
4 | MJ-PGE-036 | 2021-02-16 | 2021-02-04 | 1 | 500.5 - Utility does not collaborate with local and State environmental regulatory bodies to plan and execute vegetation management practices that mitigate negative environmental impacts. | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | None required | N/A
4 | MJ-PGE-036 | 2021-02-16 | 2021-02-04 | 2 | 500.5 - Utility does not collaborate with local and State environmental regulatory bodies to plan and execute vegetation management practices that mitigate negative environmental impacts. | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | None required | N/A
5 | AS-PGE-044 | 2021-02-18 | 2021-01-12 | 10 | 318 - Supply conductor, conductor taps, feeder taps not covered or insulated. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjusted rotated dead end conductor cover to proper configuration. | 2022-02-14
6 | EM-PGE-001 | 2021-03-01 | 2021-02-23 | 2 | 419.1 - Ground wire broken or uncovered in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Repair exposed ground wire | 2021-03-02
6 | EM-PGE-001 | 2021-03-01 | 2021-02-23 | 7 | 500.5 - Utility does not collaborate with local and State environmental regulatory bodies to plan and execute vegetation management practices that mitigate negative environmental impacts. | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | Remove tree(s) | 2021-03-15
7 | MJ-PGE-037 | 2021-03-02 | 2021-02-17 | 4 | 702.1 - Wildfire-related data and algorithms are not disclosed | Category 2 – Moderate: 3-6 months (in HFTD Tier 2) | Closed by OEIS | None required | N/A
7 | MJ-PGE-037 | 2021-03-02 | 2021-02-17 | 5 | PRC 4292 - This defect will not be listed as such until further confirmation from the utility. It's listed as a defect for tracking purposes (refer to the comments section for more info). purposes. (refer to the comments section for more info). | Category 2 – Moderate: 3-6 months (in HFTD Tier 2) | Closed by OEIS | None required | N/A
8 | QP-PGE-008 | 2021-03-02 | 2021-02-22 | 7 | 522.1 - Energized circuit of 750 volts or less shows strain or evidence of abrasion from vegetation contact in HFTD | Category 2 – Moderate: 12 months or scheduled in WMP update (other) | Closed by OEIS | Trim vegetation | 2021-03-12
8 | QP-PGE-008 | 2021-03-02 | 2021-02-22 | 12 | 426.1 - Failure to follow utility standards, manual, or best practices (GO95 Rule 31.1) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Install HVS | 2021-03-12
8 | QP-PGE-008 | 2021-03-02 | 2021-02-22 | 13 | 423.1 - Guy wire loose (loose guy wires do not provide necessary mechanical support) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjust guy wire | 2021-03-12
8 | QP-PGE-008 | 2021-03-02 | 2021-02-22 | 17 | 423.1 - Guy wire loose (loose guy wires do not provide necessary mechanical support) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjust guy wire | 2021-03-12
8 | QP-PGE-008 | 2021-03-02 | 2021-02-22 | 18 | 423.1 - Guy wire loose (loose guy wires do not provide necessary mechanical support) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjust guy wire | 2021-03-12
8 | QP-PGE-008 | 2021-03-02 | 2021-02-22 | 20 | 426.1 - Failure to follow utility standards, manual, or best practices (GO95 Rule 31.1) in HFTD. | Category 2 – Moderate: 12 months or scheduled in WMP update (other) | Closed by OEIS | Replace Pole | 2021-08-26
8 | QP-PGE-008 | 2021-03-02 | 2021-02-22 | 21 | 426.1 - Failure to follow utility standards, manual, or best practices (GO95 Rule 31.1) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Install HVS | 2021-03-12
9 | QP-PGE-009 | 2021-03-02 | 2021-02-23 | 1 | 423.1 - Guy wire loose (loose guy wires do not provide necessary mechanical support) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjust guy wire | 2021-03-12
9 | QP-PGE-009 | 2021-03-02 | 2021-02-23 | 3 | 423.1 - Guy wire loose (loose guy wires do not provide necessary mechanical support) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjust guy wire | 2021-03-12
9 | QP-PGE-009 | 2021-03-02 | 2021-02-23 | 4 | 419.1 - Ground wire broken or uncovered in HFTD. | Category 2 – Moderate: 12 months or scheduled in WMP update (other) | Closed by OEIS | Repair exposed ground wire | 2021-03-12
9 | QP-PGE-009 | 2021-03-02 | 2021-02-23 | 7 | 423.1 - Guy wire loose (loose guy wires do not provide necessary mechanical support) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjust guy wire | 2021-03-12
10 | IG-PGE-008 | 2021-03-03 | 2021-02-23 | 4 | 521.1 - Vegetation violates minimum clearance standard (Rule 35, Case 14) in HFTD or PRC 4292 and PRC 4293 | Category 1 – Severe: Immediate Resolution (3 Days) | Closed by OEIS | None required | N/A
11 | AS-PGE-045 | 2021-03-18 | 2021-03-16 | 2.1 | 416.1- GO95 Table 2 violation: i.e. Insufficient clearance between wires in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Uncover buried anchor heads | 2021-03-29
11 | AS-PGE-045 | 2021-03-18 | 2021-03-16 | 2.2 | 416.1 - GO95 Table 2 violation: i.e. Insufficient clearance between wires in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjust clearance issue between guy wire and communication line | 2021-05-06
11 | AS-PGE-045 | 2021-03-18 | 2021-03-16 | 3 | 416.1 - GO95 Table 2 violation: i.e. Insufficient clearance between wires in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjust clearance issue between guy wire and communication line | 2021-05-04
11 | AS-PGE-045 | 2021-03-18 | 2021-03-16 | 4 | 426.1 - Failure to follow utility standards, manual, or best practices (GO95 Rule 31.1) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Replace HVS | 2021-03-29
12 | ELZ_PGE_2021_1 | 2021-03-23 | 2021-03-17 | 2 | 520.1 - Failure to meet EVM requirements per wildfire mitigation plan and GO95 Rule 35, Appendix E | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | None required | N/A
12 | ELZ_PGE_2021_1 | 2021-03-23 | 2021-03-17 | 3 | 520.1 - Failure to meet EVM requirements per wildfire mitigation plan and GO95 Rule 35, Appendix E | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | None required | N/A
12 | ELZ_PGE_2021_1 | 2021-03-23 | 2021-03-17 | 5 | 520.1 - Failure to meet EVM requirements per wildfire mitigation plan and GO95 Rule 35, Appendix E | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | None required | N/A
12 | ELZ_PGE_2021_1 | 2021-03-23 | 2021-03-17 | 6 | 520.1 - Failure to meet EVM requirements per wildfire mitigation plan and GO95 Rule 35, Appendix E | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | None required | N/A
12 | ELZ_PGE_2021_1 | 2021-03-23 | 2021-03-17 | 7 | 523.1 - Presence of Hazard tree or branch, i.e. dead, decaying tree or branch overhanging (GO 95 Rule 35) in HFTD. | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | Tree will be reassessed during routine inspection in the spring of 2021 | 2021-06-10
12 | ELZ_PGE_2021_1 | 2021-03-23 | 2021-03-17 | 10 | 421.1 - Pole Condition unhealthy: Leaning more than 10 degrees or shows significant decay in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | None required | N/A
12 | ELZ_PGE_2021_1 | 2021-03-23 | 2021-03-17 | 11 | 520.1 - Failure to meet EVM requirements per wildfire mitigation plan and GO95 Rule 35, Appendix E | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | None required | N/A
12 | ELZ_PGE_2021_1 | 2021-03-23 | 2021-03-17 | 12 | 520.1 - Failure to meet EVM requirements per wildfire mitigation plan and GO95 Rule 35, Appendix E | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | None required | N/A
12 | ELZ_PGE_2021_1 | 2021-03-23 | 2021-03-17 | 13 | 520.1 - Failure to meet EVM requirements per wildfire mitigation plan and GO95 Rule 35, Appendix E | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | None required | N/A
13 | IAG_PGE_2021_9 | 2021-03-23 | 2021-03-12 | 4 | 521.1 - Vegetation violates minimum clearance standard (Rule 35, Case 14) in HFTD or PRC 4292 and PRC 4293 | Category 1 – Severe: Immediate Resolution (3 Days) | Closed by OEIS | Remove tree branch from line | 2021-03-24
13 | IAG_PGE_2021_9 | 2021-03-23 | 2021-03-12 | 9 | 423.1 - Guy wire loose (loose guy wires do not provide necessary mechanical support) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Removed down guy, eliminated angle, and installed tangent crossarm | 2021-03-31
14 | QAP-PGE-2021-011 | 2021-03-26 | 2021-03-17 | 15 | 522.1 - Energized circuit of 750 volts or less shows strain or evidence of abrasion from vegetation contact in HFTD | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Trim vegetation around service | 2021-04-19
15 | SS7_PGE_2021_002 | 2021-04-05 | 2021-03-25 | 2 | 426.1 - Failure to follow utility standards, manual, or best practices (GO95 Rule 31.1) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Replace HVS | 2021-10-28
15 | SS7_PGE_2021_002 | 2021-04-05 | 2021-03-25 | 3 | 426.1 - Failure to follow utility standards, manual, or best practices (GO95 Rule 31.1) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Replace HVS | 2021-10-28
16 | SS7_PGE_2021_003 | 2021-04-05 | 2021-03-25 | 5 | 523.1 - Presence of Hazard tree or branch, i.e. dead, decaying tree or branch overhanging (GO 95 Rule 35) in HFTD. | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | Send TPN | 2021-04-15
16 | SS7_PGE_2021_003 | 2021-04-05 | 2021-03-25 | 8 | 521.1 - Vegetation violates minimum clearance standard (Rule 35, Case 14) in HFTD or PRC 4292 and PRC 4293 | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | Remove tree branch from line | 2021-04-07
16 | SS7_PGE_2021_003 | 2021-04-05 | 2021-03-25 | 10 | 423.1 - Guy wire loose (loose guy wires do not provide necessary mechanical support) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Send TPN | 2021-04-15
17 | SS7_PGE_2021_004 | 2021-04-05 | 2021-03-26 | 1 | 424.1 - Anchors supporting wooden pole not visible or buried under vegetation in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Adjust guy anchor clearance | 2021-07-01
18 | QAP_PGE_2021_012 | 2021-04-05 | 2021-03-31 | 1 | 426.1 - Failure to follow utility standards, manual, or best practices (GO95 Rule 31.1) in HFTD. | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Replace HVS | 2021-06-30
18 | QAP_PGE_2021_012 | 2021-04-05 | 2021-03-31 | 6 | 524.1 - Vegetation contacting guy wire above the guy insulator in HFTD | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Trim vegetation contact | 2021-04-07
18 | QAP_PGE_2021_012 | 2021-04-05 | 2021-03-31 | 8 | 524.1 - Vegetation contacting guy wire above the guy insulator in HFTD | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | None required | 2021-05-10
18 | QAP_PGE_2021_012 | 2021-04-05 | 2021-03-31 | 12 | 524.1 - Vegetation contacting guy wire above the guy insulator in HFTD | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Remove vegetation contact above guy insulator | 2021-07-28
18 | QAP_PGE_2021_012 | 2021-04-05 | 2021-03-31 | 13 | 524.1 - Vegetation contacting guy wire above the guy insulator in HFTD | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Remove vegetation contact above guy insulator | 2021-08-26
18 | QAP_PGE_2021_012 | 2021-04-05 | 2021-03-31 | 14 | 419.1 - Ground wire broken or uncovered in HFTD. | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | Repair exposed ground wire | 2021-04-07
18 | QAP_PGE_2021_012 | 2021-04-05 | 2021-03-31 | 17 | 416.1 - GO95 Table 2 violation: i.e. Insufficient clearance between wires in HFTD. | Category 2 – Moderate: 1-2 months (in HFTD Tier 3) | Closed by OEIS | None required | 2021-05-10
19 | QAP_PGE_2021_013 | 2021-04-07 | 2021-04-01 | 13 | 524.1 - Vegetation contacting guy wire above the guy insulator in HFTD | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Remove vegetation contacting guy wire | 2021-05-18
19 | QAP_PGE_2021_013 | 2021-04-07 | 2021-04-01 | 23 | 524.1 - Vegetation contacting guy wire above the guy insulator in HFTD | Category 3 – Minor: 12 months or resolution schedule included in WMP update | Closed by OEIS | Remove vegetation contacting guy wire | 2021-04-21
20 | MJ4_PGE_2021_040 | 2021-04-09 | 2021-04-05 | 10 | 305.3 - Utility does not inspect, repair or replace or reinforce distribution poles that is consistent with plan. distribution poles that is consistent with plan. | Category 2 – Moderate: 3-6 months (in HFTD Tier 2) | Closed by OEIS | None required | N/A