## Quarterly Submission Guide
| Yes | No | <-- for dropdowns
Wildfire Safety Division Attachment 2.3
Wildifire Mitigation Plan Quarterly report - non-spatial data template
Resolution WSD-011 Attachment 2.3
Instructions for use |  |  |  | Relevant options for mitigations table: Table 12
1 | Fill out the tan cells (color represented here) starting with the cell below (D17: Utility). The Utility name will populate the Table tabs to follow. Date modified will vary by table.
2 | Cells will only accept valid entries. For most cells, this is positive numbers
3 | For each Table tab, after a modification is made, denote the date of the change in cell C4 for each Table tab. |  |  |  | Initiative categories | WMP Maturity model Categories | Driver options
4 | Some columns have an additional header in row 5 to serve as clarification for several columns. With the exception of projected data, row 5 will be highlighted in blue (color represented here) |  |  |  | Vegetation inspection | Risk Assessment & Mapping | 1. Ignitions | Contact with vegetation
5 | Some required metrics are future projections. For these, row 5, above the projections will be highlighted light green (color represented here) |  |  |  | Vegetation management project | Situational Awareness & Forecasting |  | Other contact with object
| In future submissions, report updated projected numbers if / when projections have changed, and report actuals once the quarter / year has passed. |  |  |  | Asset inspection | Grid Design & System Hardening |  | Equipment failure
6 | For data required annually rather than quarterly (see Tables 7.3 - 10), report for entire year even if part of the year is projected. Once year has passed, update cell with actuals |  |  |  | Grid hardening | Asset Management & Inspections |  | Wire-to-wire contact
7 | Some tables will have additional instructions provided in a Notes box located in cells D2 - D4 |  |  |  | Other | Vegetation Management & Inspections |  | Contamination
| Notes will explain terms, signal where projections are required, and provide other useful information. |  |  |  |  | Grid Operations & Operating Protocols |  | Vandalism / Theft
8 | For the initial quarterly submission, utilities are required to submit data on annual metrics for 2015 - 2020, which should represent the most updated data from the 2020 WMP for years 2015-2019 |  |  |  |  | Data Governance | 2. PSPS | PSPS - for sectionalization, etc.
* | Do not add or manipulate the template for any of the tabs |  |  |  |  | Resource Allocation Methodology
Emergency Planning & Preparedness
Update the below table to establish which year, quarter of the WMP cycle this submission this represents. | [5 empty] | Stakeholder Cooperation & Community Engagement
Utility |  | Bear Valley Electric Service, Inc.
First year of 3-year WMP cycle |  | 2020
Submission year |  | 2021
Submission quarter |  | Q4
Date Modified |  | 2022-01-24

## Table 1
Utility | Bear Valley Electric Service, Inc. | Notes:
Table No. | 1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2022-01-17
Note: These columns are placeholders for future QR submissions.
Table 1: Recent performance on progress metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Progress metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Grid condition findings from inspection - Distribution lines in HFTD | 1.a. | Number of circuit miles inspected from patrol inspections in HFTD - Distribution lines | 210.81 | 210.81 | 210.81 | 210.81 | 210.81 | 85.02 | 0.66 | 78.5 | 70.83 | 84.18 | 0.66 | 277.44 | 97.83 |  |  |  |  | # circuit miles
| 1.b. | Number of circuit miles inspected from detailed inspections in HFTD - Distribution lines | NA | NA | NA | NA | 118.61 | 36.92 | 0 | 8.91 | 0 | 0 | 0 | 52.06 | 2.84 |  |  |  |  | # circuit miles | 2019 values account for months June - December 2019 to align with prior record-keeping practices of June - May for WMP metric tracking periods.
| 1.c. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Distribution lines | NA | NA | NA | NA | 12 | 0 | 0 | 264.98 | 233.51 | 0 | 0 | 289.56 | 0 |  |  |  |  | # circuit miles | 2019 values account for months June - December 2019 to align with prior record-keeping practices of June - May for WMP metric tracking periods.
| 1.d. | Level 1 findings in HFTD for patrol inspections - Distribution lines | NA | NA | 0 | 2 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # findings
| 1.e. | Level 1 findings in HFTD for detailed inspections - Distribution lines | NA | NA | 0 | 4 | 3 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # findings
| 1.f. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | NA | NA | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # findings
| 1.g. | Level 2 findings in HFTD for patrol inspections - Distribution lines | NA | NA | 0 | 127 | 14 | 40 | 5 | 0 | 0 | 0 | 0 | 2 | 1 |  |  |  |  | # findings
| 1.h. | Level 2 findings in HFTD for detailed inspections - Distribution lines | NA | NA | 0 | 307 | 248 | 14 | 1 | 38 | 0 | 1 | 0 | 3 | 0 |  |  |  |  | # findings
| 1.i. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | NA | NA | 0 | 127 | 14 | 0 | 0 | 0 | 39 | 0 | 0 | 12 | 0 |  |  |  |  | # findings
| 1.j. | Level 3 findings in HFTD for patrol inspections - Distribution lines | NA | NA | 668 | 271 | 329 | 9 | 4 | 0 | 0 | 1 | 1 | 0 | 3 |  |  |  |  | # findings
| 1.k. | Level 3 findings in HFTD for detailed inspections - Distribution lines | NA | NA | 0 | 61 | 134 | 328 | 0 | 289 | 0 | 45 | 0 | 93 | 0 |  |  |  |  | # findings
| 1.l. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | NA | NA | 0 | 271 | 329 | 0 | 57 | 0 | 246 | 0 | 0 | 94 | 0 |  |  |  |  | # findings
1. Grid condition findings from inspection - Distribution lines total | 1.a.ii. | Number of total circuit miles inspected from patrol inspections - Distribution lines | NA | NA | 210.81 | 210.81 | 210.81 | 85.02 | 0.66 | 78.5 | 70.83 | 84.18 | 0.66 | 277.44 | 97.83 |  |  |  |  | # circuit miles
| 1.b.ii. | Number of total circuit miles inspected from detailed inspections - Distribution lines | NA | NA | NA | NA | 118.61 | 36.92 | 0 | 8.91 | 0 | 0 | 0 | 52.06 | 2.84 |  |  |  |  | # circuit miles
| 1.c.ii. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Distribution lines | NA | NA | NA | NA | 12 | 0 | 0 | 264.98 | 233.51 | 0 | 0 | 289.56 | 0 |  |  |  |  | # circuit miles
| 1.d.ii. | Level 1 findings for patrol inspections - Distribution lines | NA | NA | 0 | 2 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # findings
| 1.e.ii. | Level 1 findings for detailed inspections - Distribution lines | NA | NA | 0 | 4 | 3 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # findings
| 1.f.ii. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | NA | NA | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # findings
| 1.g.ii. | Level 2 findings for patrol inspections - Distribution lines | NA | NA | 0 | 127 | 14 | 40 | 5 | 0 | 0 | 0 | 0 | 2 | 1 |  |  |  |  | # findings
| 1.h.ii. | Level 2 findings for detailed inspections - Distribution lines | NA | NA | 0 | 307 | 248 | 14 | 1 | 38 | 0 | 1 | 0 | 3 | 0 |  |  |  |  | # findings
| 1.i.ii. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | NA | NA | 0 | 127 | 14 | 0 | 0 | 0 | 39 | 0 | 0 | 12 | 0 |  |  |  |  | # findings
| 1.j.ii. | Level 3 findings for patrol inspections - Distribution lines | NA | NA | 668 | 271 | 329 | 9 | 4 | 0 | 0 | 1 | 1 | 0 | 3 |  |  |  |  | # findings
| 1.k.ii. | Level 3 findings for detailed inspections - Distribution lines | NA | NA | 0 | 61 | 134 | 328 | 0 | 289 | 0 | 45 | 0 | 93 | 0 |  |  |  |  | # findings
| 1.l.ii. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | NA | NA | 0 | 271 | 329 | 0 | 57 | 0 | 246 | 0 | 0 | 94 | 0 |  |  |  |  | # findings
1. Grid condition findings from inspection - Transmission lines in HFTD | 1.a.iii. | Number of circuit miles inspected from patrol inspections in HFTD - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # circuit miles | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.b.iii. | Number of circuit miles inspected from detailed inspections in HFTD - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # circuit miles | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.c.iii. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # circuit miles | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.d.iii. | Level 1 findings in HFTD for patrol inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.e.iii. | Level 1 findings in HFTD for detailed inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.f.iii. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.g.iii. | Level 2 findings in HFTD for patrol inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.h.iii. | Level 2 findings in HFTD for detailed inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.i.iii. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.j.iii. | Level 3 findings in HFTD for patrol inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.k.iii. | Level 3 findings in HFTD for detailed inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.l.iii. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
1. Grid condition findings from inspection - Transmission lines total | 1.a.iv. | Number of total circuit miles inspected from patrol inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # circuit miles | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.b.iv. | Number of total circuit miles inspected from detailed inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # circuit miles | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.c.iv. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # circuit miles | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.d.iv. | Level 1 findings for patrol inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.e.iv. | Level 1 findings for detailed inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.f.iv. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.g.iv. | Level 2 findings for patrol inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.h.iv. | Level 2 findings for detailed inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.i.iv. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.j.iv. | Level 3 findings for patrol inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.k.iv. | Level 3 findings for detailed inspections - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.l.iv. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
2. Vegetation clearance findings from inspection - total | 2.a.i | Number of spans insepcted where at least some vegetation was found in non-compliant condition - total | NA | NA | NA | NA | NA | 486 | 157 | 395 | 285 | 239 | 133 | 107 | 41 |  |  |  |  | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | No data available prior to 2020
| 2.a.ii | Number of spans insepcted for vegetation compliance - total | NA | NA | NA | NA | NA | 863 | 328 | 659 | 648 | 675 | 567 | 5221 | 4029 |  |  |  |  | # of spans inspected for vegetation compliance | No data available prior to 2020
2. Vegetation clearance findings from inspection - in HFTD | 2.b.i | Number of spans insepcted where at least some vegetation was found in non-compliant condition in HFTD | NA | NA | NA | NA | NA | 486 | 157 | 395 | 285 | 239 | 133 | 107 | 41 |  |  |  |  | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | No data available prior to 2020
| 2.b.ii | Number of spans insepcted for vegetation compliance in HFTD | NA | NA | NA | NA | NA | 863 | 328 | 659 | 648 | 675 | 567 | 5221 | 4029 |  |  |  |  | # of spans inspected for vegetation compliance | No data available prior to 2020
3. Community outreach metrics | 3.a. | # Customers in an evacuation zone for utility-ignited wildfire | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # customers (if customer was in an evacuation zone for multiple wildfires, count the customer for each relevant wildfire)
| 3.b. | # Customers notified of evacuation orders | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # customers (count customer multiple times for each unique wildfire of which they were notified)
| 3.c. | % of customers notified of evacuation in evacuation zone of a utility-ignited wildfire | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Percentage of customers notified of evacuation

## Table 2
Utility | Bear Valley Electric Service, Inc. | Notes:
Table No. | 2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2022-01-17
Note: These columns are placeholders for future QR submissions.
Table 2: Recent performance on outcome metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Risk events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | 33 | 85 | 83 | 31 | 25 | 5 | 8 | 22 | 22 | 13 | 4 | 8 | 2 |  |  |  |  | Number per year
| 1.b. | Number of wires down (total) | 7 | 17 | 4 | 3 | 3 | 2 | 1 | 0 | 0 | 1 | 1 | 2 | 1 |  |  |  |  | Number of wires down per year
| 1.c. | Number of outage events not caused by contact with vegetation (total) | NA | 47 | 79 | 25 | 21 | 2 | 7 | 22 | 21 | 13 | 0 | 11 | 16 |  |  |  |  | Number of outage events per year
| 1.d. | Number of outage events caused by contact with vegetation (total) | NA | 28 | 16 | 9 | 5 | 3 | 1 | 0 | 1 | 0 | 0 | 1 | 5 |  |  |  |  | Number of outage events per year
2. Utility inspection findings - Distribution | 2.a. | Number of Level 1 findings (distribution - total) | NA | NA | 0 | 8 | 3 | 5 | 1 | 2 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # findings
| 2.b. | Number of Level 2 findings (distribution - total) | NA | NA | 0 | 561 | 276 | 54 | 6 | 38 | 39 | 1 | 4 | 17 | 1 |  |  |  |  | # findings
| 2.c. | Number of Level 3 findings (distribution - total) | NA | NA | 668 | 603 | 792 | 337 | 61 | 289 | 246 | 46 | 1 | 187 | 3 |  |  |  |  | # findings
| 2.d. | Number of distribution circuit miles inspected | NA | NA | 210.81 | 210.81 | 210.81 | 118.04 | 92.77 | 210.81 | 210.81 | 84.18 | 0.66 | 619.06 | 100.67 |  |  |  |  | # circuit miles
2. Utility inspection findings - Transmission | 2.a.ii | Number of Level 1 findings (transmission - total) | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 2.b.ii | Number of Level 2 findings (transmission - total) | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 2.c.ii | Number of Level 3 findings (transmission - total) | NA | NA | NA | NA | NA | [12 empty] | # findings | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 2.d.ii | Number of transmission circuit miles inspected | NA | NA | NA | NA | NA | [12 empty] | # circuit miles | BVES does not have any equipment 65kV or above | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
3. Utility ignited wildfire fatalities | 3.a. | Fatalities due to utility-ignited wildfire (total) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number of fatalities per year
| 3.b. | Injuries due to utility-ignited wildfire (total) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number of injuries per year
4. Value of assets destroyed by utility-ignited wildfire, listed by asset type | 4.a. | Value of assets destroyed by utility-ignited wildfire (total) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Dollars of damage or destruction per year
5. Structures damaged or destroyed by utility-ignited wildfire | 5.a. | Number of structures destroyed by utility-ignited wildfire (total) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number of structures destroyed per year
| 5.b. | Critical infrastructure damaged/destroyed by utility-ignited wildfire (total) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number of critical infrastructure damaged/destroyed per year
6. Acreage burned by utility-ignited wildfire | 6.a. | Acreage burned by utility-ignited wildfire (total) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Acres burned per year
7. Number of utility wildfire ignitons | 7.a. | Number of ignitions (total) according to existing ignition data reporting requirement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number per year
| 7.b. | Number of ignitions in HFTD (subtotal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number in HFTD per year
| 7.c. | Number of ignitions in HFTD Zone 1 | NA | NA | NA | NA | NA | [12 empty] | Number in HFTD Zone 1 per year | BVES does not have any part of its service area within Zone 1 HFTD | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 7.c.ii. | Number of ignitions in HFTD Tier 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number in HFTD Tier 2 per year
| 7.c.iii. | Number of ignitions in HFTD Tier 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number in HFTD Tier 3 per year
| 7.d. | Number of ignitions in non-HFTD (subtotal) | NA | NA | NA | NA | NA | [12 empty] | Number in non-HFTD per year | BVES does not have any part of its service area that's non-HFTD | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
8. Fatalities resulting from utility wildfire mitigation initiatives | 8.a. | Fatalities due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number of fatalities per year
9. OSHA-reportable injuries from utility wildfire mitigation initiatives | 9.a. | OSHA-reportable injuries due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number of OSHA-reportable injuries per year | On July 19, 2018, a line worker and the owner of Teele Tree Services made contact with a high voltage power line and sustained non-fatal injuries. The injury did not require reporting under CalOSHA guidelines but BVES chose to report the incident.

## Table 3
Utility | Bear Valley Electric Service, Inc.
Table No. | 3
Date Modified | 2022-01-24
Note: These columns are placeholders for future QR submissions.
Table 3: List and description of additional metrics | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
Number of reportable fire incidents (D14-02-015 Appendix C: Fire Incident Data Collection Plan) | Count of reportable fires (self-propagating, travel > 1m, & utility knowledge) | Identify # of fire starts in order to reduce the #s | Assess overall effectiveness of the plan | Prior to 2019, BVES was not required to record this data. 2015-2018 values based on review of utility records. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Count of reportable fires (self-propagating, travel > 1m, & utility knowledge)
Number of bare line contact with vegetation | Count of bare wire contacts | Identify # of contacts in order to reduce #s & possibility of fire | Assess if plan has reduced risk events | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | 6 | 39 | 17 | 9 | 5 | 3 | 1 | 0 | 1 | 0 | 0 | 1 | 5 |  |  |  |  | Count of bare wire contacts | No data recorded in May 2020
Number of live wire down events | Count of wire down events | Identify # of wire down events in order to reduce #s & possibility of fire | Assess if plan has reduced risk events | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | 7 | 17 | 4 | 3 | 1 | 2 | 1 | 0 | 0 | 2 | 1 | 2 | 1 |  |  |  |  | Count of wire down events | No data recorded in May 2020
Number of conventional blown fuse events | Count of conventional fuses blown | Identify # of conventional fuses blown events in order to reduce #s & possibility of fire | Assess if plan has reduced risk events | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | 22 | 18 | 29 | 11 | 4 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Count of conventional fuses blown | No data recorded in May 2020
Number of poles assessed | Count of poles assessed | Identify # of inspected poles to reduce the number of pole failures & possibility of fire | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 924 | 1588 | 10 | 12 | 51 | 118 | 279 | 73 | 48 | 157 |  |  |  |  | Count of poles assessed | Metric not recorded prior to 2018
Number of poles that failed assessment (wind loading, age, deterioraton, unfixable GO-95 violation) | Count of poles that fail assessment | Identify proper pole replacement periodicty, lifespan, etc. and reduce possibility of fire | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 655 | 393 | 9 | 11 | 37 | 50 | 98 | 41 | 11 | 129 |  |  |  |  | Count of poles that fail assessment | Metric not recorded prior to 2018
Number of poles replaced as a result of failed assessments | Count of poles replaced | Demonstrates progress of fire resilience efforts | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 210 | 305 | 44 | 87 | 60 | 45 | 48 | 62 | 48 | 58 |  |  |  |  | Count of poles replaced | Metric not recorded prior to 2018
Number of poles remediated as a result of failed assessments | Count of poles remediated as a result of failed assessment | Demonstrates progress of fire resilience efforts | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 40 | 66 | 0 | 7 | 0 | 0 | 1 | 3 | 2 | 1 |  |  |  |  | Count of poles remediated as a result of failed assessment | Metric not recorded prior to 2018
Number of Tree Attachments Removed | Count of tree attachments removed | Demonstrates progress toward goal of zero tree attachment and reduce possibility of fire | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 230 | 43 | 59 | 114 | 24 | 17 | 0 | 4 | 0 | 70 |  |  |  |  | Count of tree attachments removed | Metric not recorded prior to 2018
Number of new poles installed as a result of Tree Attachments Removed | Count of poles installed to replace wiring attachment from prior tree attachment | Demonstrates progress in reducing direct vegetation contact risk and installing more resilient poles in place of the prior attachment. | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | NA | 9 | 57 | 89 | 22 | 6 | 0 | 4 | 0 | 36 |  |  |  |  | Count of poles installed to replace wiring attachment from prior tree attachment | Metric not recorded prior to 2019. Year 2019 only includes pole number from June 2019 - December 2019 due to prior tracking cycle of June through May as opposed to calendar or fiscal year cycle.
Length of Covered Bare Wire (Circuit Miles) | Miles of covered bare wire | Demonstrates progress in covering bare wire | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | NA | 0.52 | 0 | 1.815 | 0.52 | 5.5 | 0 | 5.15 | 3.74 | 3.41 |  |  |  |  | Miles of covered bare wire | Metric not recorded prior to 2019 WMP No data for May 2020
Number of conventional fuses replaced by current limiting fuses | Count of conventional fuses replaced by current limiting fuses | Demonstrates efforts to replace conventional fuses with safer current limiting fuses | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | NA | 275 | 850 | 95 | 245 | 473 | 471 | 169 | 0 | 0 |  |  |  |  | Count of conventional fuses replaced by current limiting fuses | Metric not recorded prior to 2019 WMP
Number of conventional fuses replaced by fused trip savers (vacuum style) | Count of conventional fuses replaced by electronic fuses | Demonstrates efforts to replace conventional fuses with safer current limiting fuses | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 9 | 8 | 103 | 50 | 54 | 90 | 16 | 206 | 0 | 0 |  |  |  |  | Count of conventional fuses replaced by electronic fuses | Metric not recorded prior to 2018
Number of Conventional fuses in system | Count of conventional fuses | Demonstrates number of remaining conventional fuses which increases fire risk | Assess overall system hardening | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | 3114 | 3105 | 2822 | 1869 | 1724 | 1425 | 862 | 375 | 0 | 0 | 0 |  |  |  |  | Count of conventional fuses | Metric not recorded prior to 2018 Metric reported total number at the end of the quarter.
Percent of 34.5 kV System that is Overhead Bare Wire | Percent of 34.5 kV System that is Overhead Bare Wire | Inventory | Assess overall system hardening | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 0.97 | 0.97 | 0.96 | 0.929 | 0.929 | 0.83 | 0.83 | 0.722 | 0.71 | 0.669 |  |  |  |  | Percent of 34.5 kV System that is Overhead Bare Wire | Metric not recorded prior to 2018 Metric reported total percentage at the end of the quarter.
Percent of 34.5 kV System that is Underground | Percent of 34.5 kV System that is underground | Inventory | Assess overall system hardening | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 |  |  |  |  | Percent of 34.5 kV System that is underground | Metric not recorded prior to 2018 Metric reported total percentage at the end of the quarter.
Percent of 34.5 kV System that is Covered Wire | Percent of 34.5 kV System that is underground | Inventory | Assess overall system hardening | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 0 | 0 | 0.01 | 0.04 | 0.04 | 0.139 | 0.139 | 0.198 | 0.26 | 0.301 |  |  |  |  | Percent of 34.5 kV System that is underground | Metric not recorded prior to 2018 Metric reported total percentage at the end of the quarter.
Percent of 4 kV System that is Overhead Bare Wire | Percent of 34.5 kV System that is overhead | Inventory | Assess overall system hardening | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 0.773 | 0.773 | 0.773 | 0.772 | 0.772 | 0.759 | 0.759 | 0.744 | 0.736 | 0.722 |  |  |  |  | Percent of 34.5 kV System that is overhead | Metric not recorded prior to 2018 Metric reported total percentage at the end of the quarter.
Percent of 4 kV System that is Underground | Percent of 4 kV System that is underground | Inventory | Assess overall system hardening | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 0.227 | 0.227 | 0.226 | 0.226 | 0.226 | 0.226 | 0.226 | 0.226 | 0.226 | 0.226 |  |  |  |  | Percent of 4 kV System that is underground | Metric not recorded prior to 2018 Metric reported total percentage at the end of the quarter.
Percent of 4 kV System that is Covered Wire | Percent of 34.5 kV System that is underground | Inventory | Assess overall system hardening | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 0 | 0 | 0.001 | 0.002 | 0.002 | 0.015 | 0.015 | 0.029 | 0.038 | 0.052 |  |  |  |  | Percent of 34.5 kV System that is underground | Metric not recorded prior to 2018 Metric reported total percentage at the end of the quarter.
Number of Tree Attachments Remaining in System | Count of tree attachments | Demonstrates progress toward goal of zero tree attachment and reduce possibility of fire | Assess overall system hardening | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 977 | 934 | 875 | 761 | 737 | 720 | 720 | 716 | 716 | 646 |  |  |  |  | Count of tree attachments | Metric not recorded prior to 2018 Metric reported total number at the end of the quarter.
Number of Trees Trimmed | Count of trees trimmed as part of veg mgmt work | Inventory and identify trends | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 5526 | 6671 | 866 | 761 | 1201 | 1708 | 2330 | 1980 | 1688 | 1841 |  |  |  |  | Count of trees trimmed as part of veg mgmt work | Metric not recorded prior to 2019 WMP
Number of Trees Removed | Count of trees removed as part of veg mgmt work | Inventory and identify trends | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | 80 | 123 | 16 | 34 | 35 | 43 | 19 | 36 | 85 | 17 |  |  |  |  | Count of trees removed as part of veg mgmt work | Metric not recorded prior to 2019 WMP
Number of Poles Intrusively Inspected | Number of Poles Intrusively Inspected | Inventory and identify performance trends | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | 994 | 927 | 1013 | 155 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 876 | 0 |  |  |  |  | Number of Poles Intrusively Inspected
Number of Poles Failing Instrusive Inspection | Number of Poles Failing Intrusively Inspection | Inventory and identify trends | Determine if plan is on schedule | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | 8 | 7 | 4 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 |  |  |  |  | Number of Poles Failing Intrusively Inspection
Number of Customer Service Calls about Tree Trimming | Number of Customer Service Calls about Tree Trimming | Inventory and identify trends | Monitor changing climatic and weather patterns | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Number of Customer Service Calls about Tree Trimming | Metric not recorded prior to 2019 WMP
SAIDI due to PSPS | SAIDI Reliability Performance impacts due to PSPS | Identify impacts to SAIDI performance from PSPS events | Monitor the need for PSPS events over time as an indicator of changing climatic and weather patterns | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | SAIDI Reliability Performance impacts due to PSPS | BVES has not initiated any PSPS activation to date.
Number of NFDRS “Very Dry” and “Dry” Days | Count of NFDRS "very dry" and "dry" days | Inventory and identify trends | Monitor the need for PSPS events over time as an indicator of changing climatic and weather patterns | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | NA | 150 | 21 | 57 | 92 | 86 | 34 | 86 | 92 | 65 |  |  |  |  | Count of NFDRS "very dry" and "dry" days | Metric not recorded prior to 2019 WMP. BVES has missing monthly data for Feb. - June 2020
Number of PSPS Events | Count of PSPS events | Inventory and identify trends | Monitor the need for PSPS events over time as an indicator of changing climatic and weather patterns | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Count of PSPS events | Metric not recorded prior to 2019 WMP
Maximum recorded sustained winds Recorded | Highest recorded sutained wind speed recorded | Inventory and identify trends | Monitor the need for PSPS events over time as an indicator of changing climatic and weather patterns | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | NA | 41 | 25 | 22 | 22 | 30 | 37 | 22 | 30 | 33 |  |  |  |  | Highest recorded sutained wind speed recorded | Metric not recorded prior to 2019 WMP BVES does not readily have Q2 2020 data available for this filing.
Maximum recorded wind gusts Recorded | Highest recorded sutained wind gust recorded | Inventory and identify trends | Monitor the need for PSPS events over time as an indicator of changing climatic and weather patterns | Contracted 3rd party analysts or academic researchers could review open as well as closed work orders, BVES GIS databases, staff interviews, as well as spot-checking select items for confirmation of status. | NA | NA | NA | NA | 53 | 43 | 43 | 35 | 45 | 50 | 37 | 44 | 55 |  |  |  |  | Highest recorded sutained wind gust recorded | Metric not recorded prior to 2019 WMP BVES does not readily have Q2 2020 data available for this filing.
Frequency of sustained high winds (number of days sustained wind > 50 mph) | Count of sustained high wind days recorded | Inventory and identify trends | Monitor the need for PSPS events over time as an indicator of changing climatic and weather patterns | Data obtained from BVES owned weather stations | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Count of sustained high wind days recorded | Metric not recorded prior to 2019 WMP BVES does not readily have Q2 2020 data available for this filing.
Frequency of high wind gusts (number of days wind gusts > 50 mph) recorded | Count of days with high wind gusts recorded | Inventory and identify trends | Monitor the need for PSPS events over time as an indicator of changing climatic and weather patterns | Data obtained from BVES owned weather stations | NA | NA | NA | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | Count of days with high wind gusts recorded | Metric not recorded prior to 2019 WMP BVES does not readily have Q2 2020 data available for this filing.

## Table 4
Utility | Bear Valley Electric Service, Inc.
Table No. | 4
Date Modified | 2022-01-17
Note: These columns are placeholders for future QR submissions.
Table 4: Fatalities due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Fatalities - Full-time Employee | 1.a. | Fatalities due to utility inspection - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 1.b. | Fatalities due to vegetation management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 1.c. | Fatalities due to utility fuel management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 1.d. | Fatalities due to grid hardening - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 1.e. | Fatalities due to other - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
2. Fatalities - Contractor | 2.a. | Fatalities due to utility inspection - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 2.b. | Fatalities due to vegetation management - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 2.c. | Fatalities due to utility fuel management - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 2.d. | Fatalities due to grid hardening - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 2.e. | Fatalities due to other - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
3. Fatalities - Member of public | 3.a. | Fatalities due to utility inspection - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 3.b. | Fatalities due to vegetation management - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 3.c. | Fatalities due to utility fuel management - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 3.d. | Fatalities due to grid hardening - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities
| 3.e. | Fatalities due to other - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # fatalities

## Table 5
Utility | Bear Valley Electric Service, Inc.
Table No. | 5
Date Modified | 2022-01-17
Note: These columns are placeholders for future QR submissions.
Table 5: OSHA-reportable injuries due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. OSHA injuries - Full-time Employee | 1.a. | OSHA injuries due to utility inspection - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 1.b. | OSHA injuries due to vegetation management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 1.c. | OSHA injuries due to utility fuel management - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 1.d. | OSHA injuries due to grid hardening - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 1.e. | OSHA injuries due to other - Full-time employee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
2. OSHA injuries - Contractor | 2.a. | OSHA injuries due to utility inspection - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 2.b. | OSHA injuries due to vegetation management - Contractor | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries | On July 19, 2018, a line worker and the owner of Teele Tree Services made contact with a high voltage power line and sustained non-fatal injuries. The injury did not require reporting under CalOSHA guidelines but BVES chose to report the incident.
| 2.c. | OSHA injuries due to utility fuel management - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 2.d. | OSHA injuries due to grid hardening - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 2.e. | OSHA injuries due to other - Contractor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
3. OSHA injuries - Member of public | 3.a. | OSHA injuries due to utility inspection - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 3.b. | OSHA injuries due to vegetation management - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 3.c. | OSHA injuries due to utility fuel management - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 3.d. | OSHA injuries due to grid hardening - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries
| 3.e. | OSHA injuries due to other - Public | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | # OSHA-reportable injuries

## Table 6
Utility | Bear Valley Electric Service, Inc.
Table No. | 6
Date Modified | 2022-01-25
Note: These columns are placeholders for future QR submissions.
Table 6: Weather patterns | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Red Flag Warning Overhead circuit mile Days | 1.a. | Red Flag Warning Overhead circuit mile days - entire utility territory | 615.1953 | 2987.8203 | 3312.8172 | 2231.9547 | 1335.6297 | 0 | 0 | 386.5797 | 1704.7047 | 0 | 0 | 0 | 579.975 |  |  |  |  | Sum of overhead circuit miles of utility grid subject to Red Flag Warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW multiplied by the number of days those circuit miles were under said RFW. For example, if 100 overhead circuit miles were under an RFW for 1 day, and 10 of those miles were under RFW for an additional day, then the total RFW OH circuit mile days would be 110. | The utility's weather consultant collects and reports data using the NFDRS and RFW systems for the utility's entire service territory as opposed to on a circuit-by-circuit basis; when a Red Flag Warning is issued for the San Bernardino Mountains, - including Big Bear Valley, which encompasses the entirey of BVES' service territory - the Warning applies to 100% of BVES' service territory, which is just 32 square miles.
| 1.b. | Red Flag Warning Overhead circuit mile days - HFTD Zone 1 | NA | NA | NA | NA | NA | [12 empty] | Red Flag Warning Overhead circuit mile days, see above for definition | BVES does not have any Zone 1 HFTD designations | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
| 1.c. | Red Flag Warning Overhead circuit mile days - HFTD Tier 2 | 611.4907 | 2969.8282 | 3292.868 | 2218.5143 | 1327.5868 | 0 | 0 | 384.2518 | 1694.4393 | 0 | 0 | 0 | 576.4825 |  |  |  |  | Red Flag Warning Overhead circuit mile days, see above for definition | The entirety of the utility's service territory is in HFTD Tier 2 with the exception of 1.27 miles of the Radford 34.5 kV line which are HFTD Tier 3. The data above apply to all of the circuits within the utility's service territory.
| 1.d. | Red Flag Warning Overhead circuit mile days - HFTD Tier 3 | 3.7046 | 17.9921 | 19.9492 | 13.4404 | 8.0429 | 0 | 0 | 2.3279 | 10.2654 | 0 | 0 | 0 | 3.4925 |  |  |  |  | Red Flag Warning Overhead circuit mile days, see above for definition | The entirety of the utility's service territory is in HFTD Tier 2 with the exception of 1.27 miles of the Radford 34.5 kV line which are HFTD Tier 3. The data above apply to all of the circuits within the utility's service territory.
| 1.e. | Red Flag Warning Overhead circuit mile days - Non-HFTD | NA | NA | NA | NA | NA | [12 empty] | Red Flag Warning Overhead circuit mile days, see above for definition | BVES does not have any applicable non-HFTD designations | bar: 1 to Note: These columns are placeholders for future QR submissions. 4
2. Wind conditions | 2.a. | High wind warning overhead circuit mile days | NA | NA | NA | NA | NA | 1021.5996 | 0 | 0 | 832.6332 | 1116.0828 | 0 | 0 | 536.1078 |  |  |  |  | Sum of overhead circuit miles of utility grid subject to High Wind Warnings (HWW, as defined by the National Weather Service) each day within a given time period, calculated as the number of overhead circuit miles that were under an HWW multiplied by the number of days those miles were under said HWW. For example, if 100 overhead circuit miles were under an HWW for 1 day, and 10 of those miles were under HWW for an additional day, then the total HWW OH circuit mile days would be 110. | BVES has not historically tracked these types of hazard warnings prior to 2020. Going forward, BVES will include this metric with ongoing recordkeeping as confirmed with the utility's weather monitoring third-party. Q3 QDR Update: Additional data was made available for Q1 following Q3 filling and the entries were updated
3. Other | 3.a. | Other relevant weather pattern metrics tracked (add additional rows as needed) | NA | NA | NA | NA | NA | [13 empty] | Additional weather pattern metrics tracked located in Table 3 | bar: 1 to Note: These columns are placeholders for future QR submissions. 4

## Table 7.1
| Utility | Bear Valley Electric Service, Inc. | Notes:
| Table No. | 7.1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2022-01-18 | Data from 2015 - 2020 Q2 should be actual numbers. 2020 Q3 - 2023 should be projected. In future submissions update projected numbers with actuals
[6 empty] | Number of risk events | [12 empty] | Projected risk events
| Table 7.1: Key recent and projected drivers of risk events | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| Risk Event category | Cause category | # | Sub-cause category | Are risk events tracked for ignition driver? (yes / no) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
x | Wire down event - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | Yes | NA | 13 | 4 | 2 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.9375 | 0.9375 | 0.9375 | 0.9375 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 1.b. | Animal contact- Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 1.c. | Balloon contact- Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 1.d. | Vehicle contact- Distribution | Yes | NA | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0.1875 | 0.1875 | 0.1875 | 0.1875 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 1.e. | Other contact from object - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 2. Equipment / facility failure - Distribution | 2.a. | Connector damage or failure- Distribution | Yes | NA | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03125 | 0.03125 | 0.03125 | 0.03125 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 2.b. | Splice damage or failure — Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 2.c. | Crossarm damage or failure - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 2.d. | Insulator damage or failure- Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 2.e. | Lightning arrestor damage or failure- Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 2.f. | Tap damage or failure - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 2.g. | Tie wire damage or failure - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 2.h. | Other - Distribution | Yes | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03125 | 0.03125 | 0.03125 | 0.03125 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 4. Contamination - Distribution | 4.a. | Contamination - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 5. Utility work / Operation | 5.a. | Utility work / Operation | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 7. Other- Distribution | 7.a. | All Other- Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 8. Unknown- Distribution | 8.a. | Unknown - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
x | Wire down event - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 9.b. | Animal contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 9.c. | Balloon contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 9.d. | Vehicle contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 9.e. | Other contact from object - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 10. Equipment / facility failure - Transmission | 10.a. | Connector damage or failure- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 10.b. | Splice damage or failure — Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 10.c. | Crossarm damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 10.d. | Insulator damage or failure- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 10.e. | Lightning arrestor damage or failure- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 10.f. | Tap damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 10.g. | Tie wire damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 10.h. | Other - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 12. Contamination - Transmission | 12.a. | Contamination - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 13. Utility work / Operation | 13.a. | Utility work / Operation | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 15. Other- Transmission | 15.a. | All Other- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 16. Unknown- Transmission | 16.a. | Unknown - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
x | Outage - Distribution | 17. Contact from object - Distribution | 17.a. | Veg. contact- Distribution | Yes | NA | 15 | 12 | 7 | 2 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 5 | 1.5 | 1.5 | 1.5 | 1.5 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 17.b. | Animal contact- Distribution | Yes | NA | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0.1875 | 0.1875 | 0.1875 | 0.1875 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 17.c. | Balloon contact- Distribution | Yes | NA | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0.15625 | 0.15625 | 0.15625 | 0.15625 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 17.d. | Vehicle contact- Distribution | Yes | NA | 5 | 9 | 1 | 0 | 0 | 2 | 2 | 0 | 2 | 1 | 1 | 2 | 0.96875 | 0.96875 | 0.96875 | 0.96875 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 17.e. | Other contact from object - Distribution | Yes | NA | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 18. Equipment / facility failure - Distribution | 18.a. | Capacitor bank damage or failure- Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.b. | Conductor damage or failure — Distribution | Yes | NA | 0 | 5 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0.4375 | 0 | 1 | 0.3125 | 0.3125 | 0.3125 | 0.3125 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.c. | Fuse damage or failure - Distribution | Yes | NA | 15 | 27 | 13 | 2 | 0 | 2 | 4 | 9 | 6 | 0 | 0 | 6 | 3.6562 | 3.6562 | 3.6562 | 3.6562 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.d. | Lightning arrestor damage or failure- Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 1.125 | 1.125 | 1.125 | 1.125 | # risk events (excluding ignitions) | Overload-Lightening were counted here because BVES's categories don’t align 1 to 1 and a reference to a blown fuse or trasformer was not made in the comments Projected values based off quarterly average for 2016-2020
|  |  | 18.e. | Switch damage or failure- Distribution | Yes | NA | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.21875 | 0.21875 | 0.21875 | 0.21875 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.f. | Pole damage or failure - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.g. | Insulator and brushing damage or failure - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.h. | Crossarm damage or failure - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.i. | Voltage regulator / booster damage or failure - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.j. | Recloser damage or failure - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.375 | 0.375 | 0.375 | 0.375 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.k. | Anchor / guy damage or failure - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.l. | Sectionalizer damage or failure - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.m. | Connection device damage or failure - Distribution | Yes | NA | 11 | 25 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1.4375 | 1.4375 | 1.4375 | 1.4375 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.n. | Transformer damage or failure - Distribution | Yes | NA | 5 | 3 | 0 | 7 | 1 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  |  | 18.o. | Other - Distribution | Yes | NA | 0 | 0 | 4 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 19. Wire-to-wire contact - Distribution | 19.a. | Wire-to-wire contact / contamination- Distribution | Yes | NA | 0 | 5 | 4 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0.59375 | 0.59375 | 0.59375 | 0.59375 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 20. Contamination - Distribution | 20.a. | Contamination - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 21. Utility work / Operation | 21.a. | Utility work / Operation | Yes | NA | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.21875 | 0.21875 | 0.21875 | 0.21875 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 22. Vandalism / Theft - Distribution | 22.a. | Vandalism / Theft - Distribution | Yes | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 23. Other- Distribution | 23.a. | All Other- Distribution | Yes | NA | 4 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 5 | 1 | 0.40625 | 0.40625 | 0.40625 | 0.40625 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
|  | 24. Unknown- Distribution | 24.a. | Unknown - Distribution | Yes | NA | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 3 | 0.3125 | 0.3125 | 0.3125 | 0.3125 | # risk events (excluding ignitions) | Projected values based off quarterly average for 2016-2020
x | Outage - Transmission | 25. Contact from object - Transmission | 25.a. | Veg. contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 25.b. | Animal contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 25.c. | Balloon contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 25.d. | Vehicle contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 25.e. | Other contact from object - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 26. Equipment / facility failure - Transmission | 26.a. | Capacitor bank damage or failure- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.b. | Conductor damage or failure — Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.c. | Fuse damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.d. | Lightning arrestor damage or failure- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.e. | Switch damage or failure- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.f. | Pole damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.g. | Insulator and brushing damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.h. | Crossarm damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.i. | Voltage regulator / booster damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.j. | Recloser damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.k. | Anchor / guy damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.l. | Sectionalizer damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.m. | Connection device damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.n. | Transformer damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 26.o. | Other - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 27. Wire-to-wire contact - Transmission | 27.a. | Wire-to-wire contact / contamination- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 28. Contamination - Transmission | 28.a. | Contamination - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 29. Utility work / Operation | 29.a. | Utility work / Operation | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 30. Vandalism / Theft - Transmission | 30.a. | Vandalism / Theft - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 31. Other- Transmission | 31.a. | All Other- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 32. Unknown- Transmission | 32.a. | Unknown - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # risk events (excluding ignitions) | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
x | Ignition - Distribution | 33. Contact from object - Distribution | 33.a. | Veg. contact- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 33.b. | Animal contact- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 33.c. | Balloon contact- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 33.d. | Vehicle contact- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 33.e. | Other contact from object - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 34. Equipment / facility failure - Distribution | 34.a. | Capacitor bank damage or failure- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.b. | Conductor damage or failure — Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.c. | Fuse damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.d. | Lightning arrestor damage or failure- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.e. | Switch damage or failure- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.f. | Pole damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.g. | Insulator and brushing damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.h. | Crossarm damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.j. | Recloser damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.k. | Anchor / guy damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.l. | Sectionalizer damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.m. | Connection device damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.n. | Transformer damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.o. | Other - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 35. Wire-to-wire contact - Distribution | 35.a. | Wire-to-wire contact / contamination- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 36. Contamination - Distribution | 36.a. | Contamination - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 37. Utility work / Operation | 37.a. | Utility work / Operation | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 38. Vandalism / Theft - Distribution | 38.a. | Vandalism / Theft - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 39. Other- Distribution | 39.a. | All Other- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 40. Unknown- Distribution | 40.a. | Unknown - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
x | Ignition - Transmission | 41. Contact from object - Transmission | 41.a. | Veg. contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 41.b. | Animal contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 41.c. | Balloon contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 41.d. | Vehicle contact- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 41.e. | Other contact from object - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 42. Equipment / facility failure - Transmission | 42.a. | Capacitor bank damage or failure- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.b. | Conductor damage or failure — Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.c. | Fuse damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.d. | Lightning arrestor damage or failure- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.e. | Switch damage or failure- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.f. | Pole damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.g. | Insulator and brushing damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.h. | Crossarm damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.i. | Voltage regulator / booster damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.j. | Recloser damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.k. | Anchor / guy damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.l. | Sectionalizer damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.m. | Connection device damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.n. | Transformer damage or failure - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  |  | 42.o. | Other - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 43. Wire-to-wire contact - Transmission | 43.a. | Wire-to-wire contact / contamination- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 44. Contamination - Transmission | 44.a. | Contamination - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 45. Utility work / Operation | 45.a. | Utility work / Operation | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 46. Vandalism / Theft - Transmission | 46.a. | Vandalism / Theft - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 47. Other- Transmission | 47.a. | All Other- Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4
|  | 48. Unknown- Transmission | 48.a. | Unknown - Transmission | No | NA | NA | NA | NA | NA | [12 empty] | # ignitions | BVES does not own/operate any overhead transmission lines that are 65kV or greater. | bar: 1 to Projected risk events 4

## Table 7.2
| Utility | Bear Valley Electric Service, Inc. | Notes:
| Table No. | 7.2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2022-01-19 | Data from 2015 - 2019 should be actual numbers. 2020 - 2023 should be projected. In future submissions update projected numbers with actuals
[6 empty] | Number of ignitions by HFTD tier | [27 empty] | Projected ignitions by HFTD tier
| Table 7.2: Key recent and projected drivers of ignitions by HFTD region |  |  |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
|  | Metric type | # | Ignition driver | Are ignitions tracked for ignition driver? (yes / no) | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
x | Ignition - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 1.b. | Animal contact- Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 1.c. | Balloon contact- Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 1.d. | Vehicle contact- Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 1.e. | Other contact from object - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  | 2. Equipment / facility failure - Distribution | 2.a. | Capacitor bank damage or failure- Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.b. | Conductor damage or failure — Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.c. | Fuse damage or failure - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.d. | Lightning arrestor damage or failure- Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.e. | Switch damage or failure- Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.f. | Pole damage or failure - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.g. | Insulator and brushing damage or failure - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.h. | Crossarm damage or failure - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.i. | Voltage regulator / booster damage or failure - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.j. | Recloser damage or failure - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.k. | Anchor / guy damage or failure - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.l. | Sectionalizer damage or failure - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.m. | Connection device damage or failure - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.n. | Transformer damage or failure - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  |  | 2.o. | Other - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  | 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  | 4. Contamination - Distribution | 4.a. | Contamination - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  | 5. Utility work / Operation | 5.a. | Utility work / Operation | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  | 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  | 7. Other- Distribution | 7.a. | All Other- Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
|  | 8. Unknown- Distribution | 8.a. | Unknown - Distribution | Yes | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | # ignitions | No data available for 2015
x | Ignition - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 9.b. | Animal contact- Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 9.c. | Balloon contact- Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 9.d. | Vehicle contact- Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 9.e. | Other contact from object - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  | 10. Equipment / facility failure - Transmission | 10.a. | Capacitor bank damage or failure- Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.b. | Conductor damage or failure — Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.c. | Fuse damage or failure - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.d. | Lightning arrestor damage or failure- Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.e. | Switch damage or failure- Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.f. | Pole damage or failure - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.g. | Insulator and brushing damage or failure - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.h. | Crossarm damage or failure - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.i. | Voltage regulator / booster damage or failure - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.j. | Recloser damage or failure - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.k. | Anchor / guy damage or failure - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.l. | Sectionalizer damage or failure - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.m. | Connection device damage or failure - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.n. | Transformer damage or failure - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  |  | 10.o. | Other - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  | 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  | 12. Contamination - Transmission | 12.a. | Contamination - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  | 13. Utility work / Operation | 13.a. | Utility work / Operation | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  | 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  | 15. Other- Transmission | 15.a. | All Other- Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.
|  | 16. Unknown- Transmission | 16.a. | Unknown - Transmission | No | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | # ignitions | BVES does not own or manage transmission lines/equipment rated at or above 65 kV.

## Table 8
| Utility | Bear Valley Electric Service, Inc.
| Table No. | 8
| Date Modified | 2022-01-19
Note: These columns are placeholders for future QR submissions.
| Table 8: State of service territory and utility equipment |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
x | 1. State of service territory and equipment in urban areas | 1.a. | Circuit miles (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 262.2 | 2.8 | NA | NA | 184.74 | 0 |  |  |  |  | Circuit miles | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.b. | Circuit miles in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 262.2 | 2.8 | NA | NA | 184.74 | 0 |  |  |  |  | Circuit miles in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.c. | Number of critical facilities (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 14 | 0 | NA | NA | 12 | 0 |  |  |  |  | Number of critical facilities | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.d. | Number of critical facilities in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 14 | 0 | NA | NA | 12 | 0 |  |  |  |  | Number of critical facilities in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.e. | Number of customers (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 24500 | 0 | NA | NA | 21097 | 0 |  |  |  |  | Number of customers | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.f. | Number of customers in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 24500 | 0 | NA | NA | 21097 | 0 |  |  |  |  | Number of customers in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of customers belonging to access and functional needs populations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.h. | Number of customers belonging to access and functional needs populations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Circuit miles of overhead transmission lines | BVES does not have any transmission circuits.
|  | 1.j. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Circuit miles of overhead transmission lines in WUI | BVES does not have any transmission circuits.
|  | 1.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 208.1 | 2.8 | NA | NA | 146.82 | 0 |  |  |  |  | Circuit miles of overhead distribution lines | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.l. | Circuit miles of overhead distribution lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 208.1 | 2.8 | NA | NA | 146.82 | 0 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.m. | Number of substations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 13 | 0 | NA | NA | 8 | 0 |  |  |  |  | Number of substations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.n | Number of substations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 13 | 0 | NA | NA | 8 | 0 |  |  |  |  | Number of substations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.o. | Number of weather stations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 17 | 1 | NA | NA | 8 | 0 |  |  |  |  | Number of weather stations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.p. | Number of weather stations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 17 | 1 | NA | NA | 8 | 0 |  |  |  |  | Number of weather stations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
x | 2. State of service territory and equipment in rural areas | 2.a. | Circuit miles (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 262.2 | 2.8 | NA | NA | 78.45 | 1.64 |  |  |  |  | Circuit miles | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.b. | Circuit miles in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 262.2 | 2.8 | NA | NA | 78.45 | 1.64 |  |  |  |  | Circuit miles in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.c. | Number of critical facilities (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 14 | 0 | NA | NA | 2 | 0 |  |  |  |  | Number of critical facilities | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.d. | Number of critical facilities in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 14 | 0 | NA | NA | 2 | 0 |  |  |  |  | Number of critical facilities in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.e. | Number of customers (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 24500 | 0 | NA | NA | 3530 | 1 |  |  |  |  | Number of customers | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.f. | Number of customers in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 24500 | 0 | NA | NA | 3530 | 1 |  |  |  |  | Number of customers in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of customers belonging to access and functional needs populations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.h. | Number of customers belonging to access and functional needs populations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Circuit miles of overhead transmission lines | BVES does not have any transmission circuits.
|  | 2.j. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Circuit miles of overhead transmission lines in WUI | BVES does not have any transmission circuits.
|  | 2.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 208.1 | 2.8 | NA | NA | 61.63 | 1.64 |  |  |  |  | Circuit miles of overhead distribution lines | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.l. | Circuit miles of overhead distribution lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 208.1 | 2.8 | NA | NA | 61.63 | 1.64 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.m. | Number of substations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 13 | 0 | NA | NA | 5 | 0 |  |  |  |  | Number of substations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.n | Number of substations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 13 | 0 | NA | NA | 5 | 0 |  |  |  |  | Number of substations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.o. | Number of weather stations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 17 | 1 | NA | NA | 10 | 2 |  |  |  |  | Number of weather stations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.p. | Number of weather stations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 17 | 1 | NA | NA | 10 | 2 |  |  |  |  | Number of weather stations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
x | 3. State of service territory and equipment in highly rural areas | 3.a. | Circuit miles (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Circuit miles | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.b. | Circuit miles in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Circuit miles in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.c. | Number of critical facilities (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of critical facilities | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.d. | Number of critical facilities in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of critical facilities in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.e. | Number of customers (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of customers | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.f. | Number of customers in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of customers in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of customers belonging to access and functional needs populations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.h. | Number of customers belonging to access and functional needs populations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Circuit miles of overhead transmission lines | BVES does not have any transmission circuits.
|  | 3.j. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Circuit miles of overhead transmission lines in WUI | BVES does not have any transmission circuits.
|  | 3.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Circuit miles of overhead distribution lines | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.l. | Circuit miles of overhead distribution lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Circuit miles of overhead distribution lines in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.m. | Number of substations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of substations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.n | Number of substations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of substations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.o. | Number of weather stations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of weather stations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.p. | Number of weather stations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | Number of weather stations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
Note on AE12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5 customers added

## Table 9
| Utility | Bear Valley Electric Service, Inc. | Notes:
| Table No. | 9 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Report net additions using positive numbers and net removals and undergrounding using negative numbers for circuit miles and numbers of substations. Only report changes expected within the target year.
| Date Modified | 2022-01-20 | For example, if 20 net overhead circuit miles are planned for addition by 2023, with 15 being added by 2022 and 5 more added by 2023, then report “15” for 2022 and “5” for 2023. Do not report cumulative change across years. In this case, do not report “20” for 2023, but instead the number planned to be added for just that year, which is “5”.
|  |  |  | Actual | [7 empty] | Projected
| Table 9: Location of actual and planned utility equipment additions or removal year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
x | 1. Planned utility equipment net addition (or removal) year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Circuit miles | BVES does not have any transmission circuits.
|  | 1.b. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Circuit miles | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.c. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles in WUI | BVES does not have any transmission circuits.
|  | 1.d. | Circuit miles of overhead distribution lines in WUI | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Circuit miles in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.e. | Number of substations (including WUI and non-WUI) | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Number of substations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.f. | Number of substations in WUI | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Number of substations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.g. | Number of weather stations (including WUI and non-WUI) | NA | NA | 8 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Number of weather stations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.h. | Number of weather stations in WUI | NA | NA | 8 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Number of weather stations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
x | 2. Planned utility equipment net addition (or removal) year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | 0 | 0 | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | Circuit miles | BVES does not have any transmission circuits.
|  | 2.b. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Circuit miles | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.c. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles in WUI | BVES does not have any transmission circuits.
|  | 2.d. | Circuit miles of overhead distribution lines in WUI | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Circuit miles in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.e. | Number of substations (including WUI and non-WUI) | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Number of substations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.f. | Number of substations in WUI | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | Number of substations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.g. | Number of weather stations (including WUI and non-WUI) | NA | 8 | 0 | 0 | NA | NA | 1 | 1 | 1 | NA | 0 | 0 | Number of weather stations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.h. | Number of weather stations in WUI | NA | 8 | 0 | 0 | NA | NA | 1 | 1 | 1 | NA | 0 | 0 | Number of weather stations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
x | 3. Planned utility equipment net addition (or removal) year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles | BVES does not have any transmission circuits.
|  | 3.b. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.c. | Circuit miles of overhead transmission lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles in WUI | BVES does not have any transmission circuits.
|  | 3.d. | Circuit miles of overhead distribution lines in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.e. | Number of substations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Number of substations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.f. | Number of substations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Number of substations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.g. | Number of weather stations (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Number of weather stations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.h. | Number of weather stations in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Number of weather stations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.

## Table 10
| Utility | Bear Valley Electric Service, Inc. | Notes:
| Table No. | 10 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2022-01-21 | In future submissions update planned upgrade numbers with actuals
|  |  | In the comments column on the far-right, enter the relevant program target(s) associated | Actual | [7 empty] | Projected
| Table 10: Location of actual and planned utility infrastructure upgrades year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
x | 1. Planned utility infrastructure upgrades year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles | BVES does not have any transmission circuits.
|  | 1.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | NA | NA | 0 | 0 | NA | NA | 6.87 | 0 | 0 | 0 | 0 | 0 | Circuit miles | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles in WUI | BVES does not have any transmission circuits.
|  | 1.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | NA | NA | 0 | 0 | NA | NA | 6.87 | 0 | 0 | 0 | 0 | 0 | Circuit miles in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.e. | Number of substations planned for upgrades (including WUI and non-WUI) | NA | NA | 1 | 0 | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.f. | Number of substations planned for upgrades in WUI | NA | NA | 1 | 0 | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | NA | NA | 0 | 0 | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 1.h. | Number of weather stations planned for upgrades in WUI | NA | NA | 0 | 0 | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
x | 2. Planned utility infrastructure upgrades year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles | BVES does not have any transmission circuits.
|  | 2.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | NA | NA | 7.8 | 0 | NA | NA | 5.81 | 0 | NA | NA | 12.9 | 0 | Circuit miles | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles in WUI | BVES does not have any transmission circuits.
|  | 2.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | NA | NA | 7.8 | 0 | NA | NA | 5.81 | 0 | NA | NA | 12.9 | 0 | Circuit miles in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.e. | Number of substations planned for upgrades (including WUI and non-WUI) | NA | NA | 1 | 0 | NA | NA | 1 | 0 | NA | NA | 0 | 0 | Number of substations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.f. | Number of substations planned for upgrades in WUI | NA | NA | 1 | 0 | NA | NA | 1 | 0 | NA | NA | 0 | 0 | Number of substations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | 0 | 0 | Number of weather stations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 2.h. | Number of weather stations planned for upgrades in WUI | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | 0 | 0 | Number of weather stations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
x | 3. Planned utility infrastructure upgrades year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles | BVES does not have any transmission circuits.
|  | 3.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently determined as rural, but may be revised due to calibration of coordinates at a future date. BVES plans to harden bare wire on 34.5kV lines with 4.3 circuit miles of hardening per year. The planned projects are reported under "Rural" for the Q4 QDR submission.
|  | 3.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles in WUI | BVES does not have any transmission circuits.
|  | 3.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Circuit miles in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps. A small extension of the Radford line, serving no customers, is currently determined as rural, but may be revised due to calibration of coordinates at a future date. BVES plans to harden bare wire on 34.5kV lines with 4.3 circuit miles of hardening per year. The planned projects are reported under "Rural" for the Q4 QDR submission.
|  | 3.e. | Number of substations planned for upgrades (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Number of substations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.f. | Number of substations planned for upgrades in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Number of substations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Number of weather stations | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.
|  | 3.h. | Number of weather stations planned for upgrades in WUI | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Number of weather stations in WUI | BVES recently executed GIS mapping of its WUI locations and found that a majority of the service area and assets fall under rural, with a proportion of the area surrounding the lake considered an urban area by the U.S. Census Data. BVES is continuing to enhance it's risk and asset maps and will provide updates in the next EC WMP QDR. A small extension of the Radford line, serving no customers, is currently assumed as highly rural, but may be revised due to calibration of coordinates at a future date. No reporting in the "highly rural" categories is found in the Q4 2021 QDR as BVES is continuing to enhance its GIS capabilities to better quantify the overlapping territory.

## Table 11
Utility | Bear Valley Electric Service, Inc. | Notes:
Table No. | 11 | "PSPS" = Public Safety Power Shutoff
Date Modified | 2022-01-19 | In future submissions update planned upgrade numbers with actuals
|  |  | Actual | [12 empty] | Projected
Table 11: Recent use of PSPS and other PSPS metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Recent use of PSPS | 1.a. | Frequency of PSPS events (total) | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
| 1.b. | Scope of PSPS events (total) | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year
| 1.c. | Duration of PSPS events (total) | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Customer hours per year
2. Customer hours of PSPS and other outages | 2.a. | Customer hours of planned outages including PSPS (total) | NA | 87254 | 5090613 | 359243 | 31890 | 0.33333 | 2582.0833 | 0 | 183.75 | 0 | 5.3667 | 0 | 0 | 346.4417 | 346.4417 | 346.4417 | 346.4417 | Total customer hours of planned outages per year | Customer Count: 2016 - 23876 2017 - 23975 2018 - 24296 2019 - 24366 2020 - 24446 2021 - 21097 Quarterly average of years 2018 and 2019 for projected values.
| 2.b. | Customer hours of unplanned outages, not including PSPS (total) | NA | 7726110 | 8686856 | 4415849 | 6306302 | 1127.1667 | 2329.95 | 53123.6167 | 116978.4667 | 23160.6333 | 25100.1 | 33061.3333 | 82853.0667 | 42216.7917 | 42216.7917 | 42216.7917 | 42216.7917 | Total customer hours of unplanned outages per year | Quarterly average of years 2018 and 2019 for projected values.
| 2.c. | System Average Interruption Duration Index (SAIDI) (including PSPS) | NA | 327.2476 | 574.6598 | 196.5382 | 260.1244 | 2.7673 | 12.056 | 130.386 | 287.5617 | 56.5767 | 61.2353 | 80.5326 | 201.5726 | 104.0861 | 104.0861 | 104.0861 | 104.0861 | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | Quarterly average of years 2018 and 2019 for projected values.
| 2.d. | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | NA | 327.2476 | 574.6598 | 196.5382 | 260.1244 | 2.7673 | 12.056 | 130.386 | 287.5617 | 56.5767 | 61.2353 | 80.5326 | 201.5726 | 104.0861 | 104.0861 | 104.0861 | 104.0861 | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | Quarterly average of years 2018 and 2019 for projected values.
| 2.e. | System Average Interruption Frequency Index (SAIFI) (including PSPS) | NA | 2.6932 | 3.9423 | 2.9249 | 1.9265 | 0.055878 | 0.20241 | 1.5199 | 2.9394 | 0.50265 | 1.0008 | 1.6361 | 2.5461 | 1.3004 | 1.3004 | 1.3004 | 1.3004 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | Quarterly average of years 2018 and 2019 for projected values.
| 2.f. | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | NA | 2.6932 | 3.9423 | 2.9249 | 1.9265 | 0.055878 | 0.20241 | 1.5199 | 2.9394 | 0.50265 | 1.0008 | 1.6361 | 2.5461 | 1.3004 | 1.3004 | 1.3004 | 1.3004 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | Quarterly average of years 2018 and 2019 for projected values.
3. Critical infrastructure impacted by PSPS | 3.a. | Critical infrastructure impacted by PSPS | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per year | Quarterly average of years 2018 and 2019 for projected values.
4. Community outreach of PSPS metrics | 4.a. | # of customers impacted by PSPS | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | Quarterly average of years 2018 and 2019 for projected values.
| 4.b. | # of medical baseline customers impacted by PSPS | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | Quarterly average of years 2018 and 2019 for projected values.
| 4.c. | # of customers notified prior to initiation of PSPS event | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | Quarterly average of years 2018 and 2019 for projected values.
| 4.d. | # of medical baseline customers notified prior to initiation of PSPS event | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | Quarterly average of years 2018 and 2019 for projected values.
| 4.e. | % of customers notified prior to a PSPS event impacting them | NA | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | =4.a. / 4.c.
| 4.f. | % of medical baseline customers notified prior to a PSPS event impacting them | NA | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | =4.a. / 4.c.
5. Other PSPS metrics | 5.a. | Number of PSPS de-energizations | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of de-energizations | Quarterly average of years 2018 and 2019 for projected values.
| 5.b. | Number of customers located on de-energized circuit | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of customers | Quarterly average of years 2018 and 2019 for projected values.
| 5.c. | Customer hours of PSPS per RFW OH circuit mile day | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | =1.c. / RFW OH circuit mile days in time period | Quarterly average of years 2018 and 2019 for projected values.
| 5.d. | Frequency of PSPS events (total) - High Wind Warning wind conditions | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Events over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Quarterly average of years 2018 and 2019 for projected values.
| 5.e. | Scope of PSPS events (total) - High Wind Warning wind conditions | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Estimated customers impacted over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Quarterly average of years 2018 and 2019 for projected values.
| 5.f. | Duration of PSPS events (total) - High Wind Warning wind conditions | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Customer hours over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Quarterly average of years 2018 and 2019 for projected values.

## Table 12
Utility | Bear Valley Electric Service, Inc. | Notes:
Table No. | 12 | Risk-Spend-Efficiency (RSE) is defined as "An estimate of the cost-effectiveness of initiative, calculated by dividing the mitigation risk reduction benefit by the mitigation cost estimate based on the full set of risk reduction benefits estimated from the incurred costs."
Date Modified | 2021-01-24 | CAPEX = Capital expenditure; OPEX = Operating expenditure. In future submissions update planned spend, line miles treated, RSE, etc. with updated projections and actuals. Additional instructions can be found in QR information.
[18 empty] | Actual | Actual | Actual | Actual | Projected | Projected | Projected | Projected | Projected | Projected | Projected | Projected
Table 12: Mitigation initiative financials | [17 empty] | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | Alternative units (if used) | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | Alternative units (if used) | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | Alternative units (if used)
Metric type | WMP Table # / Category | WMP Initiative # | Initative activity | Primary driver targeted | Secondary driver targeted | Year initiated | Estimated RSE in non-HFTD region | Estimated RSE in HFTD Zone 1 | Estimated RSE in HFTD Tier 2 | Estimated RSE in HFTD Tier 3 | If existing: most recent proceeding that has reviewed program | If new: memorandum account | Current compiance status - In / exceeding compliance with regulations | Associated rule(s) - if multiple, separate by semi-colon - ";" | If spend not disaggregated by category, note spend category or mark general operations | Alternative units in which initiative is reported (if not line miles); still required to report line miles | Comments | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023
Other | Risk Assessment & Mapping | 7.3.1.1. | A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment | Contact with vegetation | Other contact with object | 2021 | NA | NA | 3.28 | 3.28 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 |  | Percent of Progress on Risk Mapping Product Development | Bear Valley Electric Service has implemented the CPUC Fire Threat Map Adopted in D.17-12-024 December 14, 2017 throughout its service territory. This map shows the CPUC-designated fire hazard zone tiers within BVES's service territory, which quantify specific geography that could be subject to elevated fire risk under historically viable fire weather conditions. BVES has also identified seven sections of "at-risk" areas within its service territory based on the type of distribution facilities (overhead bare conductors, high voltage, etc.), tree and vegetation density, available dry fuel, and other factors that make certain locations more vulnerable to wildfire risk. The “at-risk” line sections are shown and further outlined in BVES's WMP submission. BVES's wildfire mapping efforts are foundational to determing and executing on priorities amongst BVES's risk mitigation efforts as well as its day-to-day operations. BVES employs tier designations to inform inspection, vegetation management, correction timeframes, and prioritized hardening efforts. Wildfire risk mapping is foundational to prioritizing efforts for a variety of activities undertaken throughout the business. Bear Valley Electric Service does not have a summarized risk map showing the overall ignition probability and estimated wildfire consequence, or match drop simulations, along electric lines and equipment. Within a future filing, BVES will develop a summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment. This has been completed as of Q4 2021. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 14799.77 | NA | NA | 0 | 7137 | NA | NA | 0 | 7315 | NA | NA
Other | Risk Assessment & Mapping | 7.3.1.2. | Climate-driven risk map and modelling based on various relevant weather scenarios | Contact with vegetation | Other contact with object | 2021 | NA | NA | 3.28 | 3.28 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 |  | Percent of Progress on Risk Mapping Product Development | Bear Valley Electric Service has implemented the CPUC Fire Threat Map Adopted in D.17-12-024 December 14, 2017 throughout its service territory. This map shows the CPUC-designated fire hazard zone tiers within BVES's service territory, which quantify specific geography that could be subject to elevated fire risk under historically viable fire weather conditions. BVES has also identified seven sections of "at-risk" areas within its service territory based on the type of distribution facilities (overhead bare conductors, high voltage, etc.), tree and vegetation density, available dry fuel, and other factors that make certain locations more vulnerable to wildfire risk. The “at-risk” line sections are shown and further outlined in BVES's WMP submission. BVES's wildfire mapping efforts are foundational to determing and executing on priorities amongst BVES's risk mitigation efforts as well as its day-to-day operations. BVES employs tier designations to inform inspection, vegetation management, correction timeframes, and prioritized hardening efforts. Wildfire risk mapping is foundational to prioritizing efforts for a variety of activities undertaken throughout the business. Bear Valley Electric Service does not have a summarized risk map showing the overall ignition probability and estimated wildfire consequence, or match drop simulations, along electric lines and equipment. Within a future filing, BVES will develop a summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment. This has been completed as of Q4 2021. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 14799.77 | NA | NA | 0 | 7137 | NA | NA | 0 | 7315 | NA | NA
Other | Risk Assessment & Mapping | 7.3.1.3. | Ignition probability mapping showing the probability of ignition along the electric lines and equipment | Contact with vegetation | Other contact with object | 2021 | NA | NA | 3.28 | 3.28 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 |  | Percent of Progress on Risk Mapping Product Development | Bear Valley Electric Service has implemented the CPUC Fire Threat Map Adopted in D.17-12-024 December 14, 2017 throughout its service territory. This map shows the CPUC-designated fire hazard zone tiers within BVES's service territory, which quantify specific geography that could be subject to elevated fire risk under historically viable fire weather conditions. BVES has also identified seven sections of "at-risk" areas within its service territory based on the type of distribution facilities (overhead bare conductors, high voltage, etc.), tree and vegetation density, available dry fuel, and other factors that make certain locations more vulnerable to wildfire risk. The “at-risk” line sections are shown and further outlined in BVES's WMP submission. BVES's wildfire mapping efforts are foundational to determing and executing on priorities amongst BVES's risk mitigation efforts as well as its day-to-day operations. BVES employs tier designations to inform inspection, vegetation management, correction timeframes, and prioritized hardening efforts. Wildfire risk mapping is foundational to prioritizing efforts for a variety of activities undertaken throughout the business. Bear Valley Electric Service does not have a summarized risk map showing the overall ignition probability and estimated wildfire consequence, or match drop simulations, along electric lines and equipment. Within a future filing, BVES will develop a summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment. This has been completed as of Q4 2021. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 14799.77 | NA | NA | 0 | 7137 | NA | NA | 0 | 7315 | NA | NA
Other | Risk Assessment & Mapping | 7.3.1.4. | Initiative mapping and estimation of wildfire and PSPS risk-reduction impact | Contact with vegetation | Other contact with object | 2020 | NA | NA | 3.28 | 3.28 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 |  | Percent of Progress on Risk Mapping Product Development | Bear Valley Electric Service has implemented the CPUC Fire Threat Map Adopted in D.17-12-024 December 14, 2017 throughout its service territory. This map shows the CPUC-designated fire hazard zone tiers within BVES's service territory, which quantify specific geography that could be subject to elevated fire risk under historically viable fire weather conditions. BVES has also identified seven sections of "at-risk" areas within its service territory based on the type of distribution facilities (overhead bare conductors, high voltage, etc.), tree and vegetation density, available dry fuel, and other factors that make certain locations more vulnerable to wildfire risk. The “at-risk” line sections are shown and further outlined in BVES's WMP submission. BVES's wildfire mapping efforts are foundational to determing and executing on priorities amongst BVES's risk mitigation efforts as well as its day-to-day operations. BVES employs tier designations to inform inspection, vegetation management, correction timeframes, and prioritized hardening efforts. Wildfire risk mapping is foundational to prioritizing efforts for a variety of activities undertaken throughout the business. Bear Valley Electric Service does not have a summarized risk map showing the overall ignition probability and estimated wildfire consequence, or match drop simulations, along electric lines and equipment. Within a future filing, BVES will develop a summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment. This has been completed as of Q4 2021. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 14799.77 | NA | NA | 0 | 7137 | NA | NA | 0 | 7315 | NA | NA
Other | Risk Assessment & Mapping | 7.3.1.5. | Match drop simulations showing the potential wildfire consequence of ignitions that occur along the electric lines and equipment | Contact with vegetation | Other contact with object | 2021 | NA | NA | 3.28 | 3.28 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 |  | Percent of Progress on Risk Mapping Product Development | Bear Valley Electric Service has implemented the CPUC Fire Threat Map Adopted in D.17-12-024 December 14, 2017 throughout its service territory. This map shows the CPUC-designated fire hazard zone tiers within BVES's service territory, which quantify specific geography that could be subject to elevated fire risk under historically viable fire weather conditions. BVES has also identified seven sections of "at-risk" areas within its service territory based on the type of distribution facilities (overhead bare conductors, high voltage, etc.), tree and vegetation density, available dry fuel, and other factors that make certain locations more vulnerable to wildfire risk. The “at-risk” line sections are shown and further outlined in BVES's WMP submission. BVES's wildfire mapping efforts are foundational to determing and executing on priorities amongst BVES's risk mitigation efforts as well as its day-to-day operations. BVES employs tier designations to inform inspection, vegetation management, correction timeframes, and prioritized hardening efforts. Wildfire risk mapping is foundational to prioritizing efforts for a variety of activities undertaken throughout the business. Bear Valley Electric Service does not have a summarized risk map showing the overall ignition probability and estimated wildfire consequence, or match drop simulations, along electric lines and equipment. Within a future filing, BVES will develop a summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment. This has been completed as of Q4 2021. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 14799.77 | NA | NA | 0 | 7137 | NA | NA | 0 | 7315 | NA | NA
Other | Situational Awareness & Forecasting | 7.3.2.1. | Advanced weather monitoring and weather stations | Contact with vegetation | Wire-to-wire contact | 2018 | NA | NA | 8.4 | 8.4 | GRC | WMP Memorandum Account and GRC | In Compliance | GO 95 |  | # of Weather Stations Installed | Project Overview: Install 2 weather stations in 2021. Allows BVES to prepare response ahead of time and take precautionary and/or advanced action. Also, allows BVES to validate actual conditions in the field such as before and after PSPS events. N/As: Bear Valley Electric Service has not calculated RSE values that differentiate between HFTD Tier 2 and Tier 3. Over the next period covering the WMP comprehensive update, BVES will make adjustments to its risk models to produce precise values. BVES' service territory is mostly HFTD Tier 2 with some HFTD Tier 3. For this filing, BVES has duplicated the RSE value for each cell. "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. | 24780 | 0 | NA | 2 | 0 | 0 | NA | 0 | 0 | 0 | NA | 0
Other | Situational Awareness & Forecasting | 7.3.2.2. | Continuous monitoring sensors | Contact with vegetation | Other contact with object | 2020 | NA | NA | 3.98 | 3.98 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 |  | # of HD cameras installed | Project Overview: Install ALERT Wildfire HD Cameras throughout the service area allowing rapid detection and direction of first responders to any fires. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 111099.57 | 0 | NA | 2 | 0 | 0 | NA | 0 | 0 | 0 | NA | 0
Other | Situational Awareness & Forecasting | 7.3.2.2. | Continuous monitoring sensors | Contact with vegetation | Other contact with object | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Situational Awareness Hardware Program / / Remote Sensor Technology This is a prgram that is still under evaluation by BVES | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Other | Situational Awareness & Forecasting | 7.3.2.3. | Fault indicators for detecting faults on electric lines and equipment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Determine Plan for Fault Indicators | BVES is monitoring Down wire Detection Technology and once the technology is ready for field use, BVES will develop a Down Wire Detection Installment Program in future WMPs. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 0 | NA | NA | 149563 | 0 | NA | 117 | 0 | 0 | NA | 0
Other | Situational Awareness & Forecasting | 7.3.2.4. | Forecast of a fire risk index, fire potential index, or similar | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service has not established a plan to develop a forecast of a fire risk index, fire potential index, or similar beyond that which it has communicated in its 2019 and 2020 WMPs at this time. This will be considered for the scope of work addressing risk modeling tools starting mid-2021 to 2022. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. BVES's Subject Matter Expert evaluates the frequency of potential ignition events versus a set of impact categories (reliability, compliance, quality of service, safety and environmental) to develop total risk impact and scores. In addition, no specific incremental spend has been identified for this initiative. Bear Valley Electric Service does not have a proprietary model or methodology for evaluating the potential impact of ignitions. | 0 | 12700 | NA | NA | 0 | 22500 | NA | NA | 0 | 25000 | NA | NA
Other | Situational Awareness & Forecasting | 7.3.2.5. | Personnel monitoring areas of electric lines and equipment in elevated fire risk conditions | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | During high fire threat weather that could lead to PSPS events, BVES does deploy crews to monitor conditions in the field, in the high threat areas. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 0 | NA | NA | 0 | 43697 | NA | NA | 0 | 44789 | NA | NA
Other | Situational Awareness & Forecasting | 7.3.2.6. | Weather forecasting and estimating impacts on electric lines and equipment | Contact with vegetation | Wire-to-wire contact | 2018 | NA | NA | 0.26 | 0.26 | NA | WMP Memorandum Account | Exceeding Compliance | ESRB-8 |  | NA | Project. Installs complete Distribution Management Control Center with the following equipment and applications that provide full information capabilities available to Distribution decision makers relevant to the following functional areas: (1) Energy Resources (2) T&D Assets (3) SCADA, Outage Management System & GIS Other Applications (4) Weather Information (5) HD Cameras (6) Media access (Internet, BVES Website & Social Media, Local Radio, TV, etc. (7) Communications Equipment and (8) Dispatch services. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 12700 | NA | NA | 0 | 22500 | NA | NA | 0 | 25000 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.1. | Capacitor maintenance and replacement program | Equipment failure | Contamination | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service has 25 capacitor locations and maintenance and replacement is included in the company's standard inspection, maintenance, and replacement protocols. The capacitors are fixed (either on service or off service) and part of our Overhead Facility Patrol and Inspection program objectives is to ensure they are not leaking or visually damaged. N/As: Col Q: "General Operations" "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 7276 | NA | NA | 0 | 8110 | NA | NA | 0 | 8313 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.2. | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault | Equipment failure | PSPS - for sectionalization, etc. | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Circuit breakers are generally installed for all distribution circuits to detect fault current and protect equipment in the event that a fault is detected. Circuit breaker replacement and maintenance is included in the company’s standard inspection, maintenance, and replacement protocols. Any enhanced inspections or accelerated correction timeframe/replacements are captured in Asset management and inspections under Section 7.3 of the WMP. Installation of system automation equipment. N/As: Col Q: "General Operations" "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 37240 | NA | NA | 0 | 42743 | NA | NA | 0 | 43812 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.3.1 | Covered conductor installation | Contact with vegetation | Wire-to-wire contact | 2019 | NA | NA | 0.4 | 0.4 | NA | WMP Memorandum Account | NA | NA |  | NA | Covered Conductor Project - (4kV & 34 kV Systems) 2019 and 2020 costs include the Covered Conductor Replacement Pilot Program and the Covered Conductor Wrap Pilot Program. Program replaces all 205.2 line miles of 34.5 kV overhead sub-transmission lines (beginning in 2020) and 4 kV distribution lines (beginning in 2021) with covered wire over a 6-year period, 2020-2026. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 6374192 | 0 | NA | 12.3 | 5438095 | 0 | NA | 12.9 | 5438095 | 0 | NA | 12.9
Grid hardening | Grid Design & System Hardening | 7.3.3.3.2 | Covered conductor installation | Contact with vegetation | Wire-to-wire contact | 2019 | NA | NA | 0.4 | 0.4 | NA | WMP Memorandum Account | NA | NA |  | NA | Covered Conductor Pilot Program 2020 and 2021 costs include the Covered Conductor Replacement Pilot Program and the Covered Conductor Wrap Pilot Program. Program replaces all 205.2 line miles of 34.5 kV overhead sub-transmission lines (beginning in 2020) and 4 kV distribution lines (beginning in 2021) with covered wire over a 6-year period, 2020-2026. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.3.3 | Covered conductor installation | Contact with vegetation | Wire-to-wire contact | 2019 | NA | NA | 0.21 | 0.21 | NA | WMP Memorandum Account | NA | NA |  | NA | Covered Conductor Project - Radford Line 2021 and 2020 costs include the Covered Conductor Replacement Pilot Program and the Covered Conductor Wrap Pilot Program. Program replaces all 205.2 line miles of 34.5 kV overhead sub-transmission lines (beginning in 2020) and 4 kV distribution lines (beginning in 2021) with covered wire over a 6-year period, 2020-2026. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 39808 | 0 | NA | NA | 1188047 | 0 | 8.46 | NA | 0 | 0 | 0 | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.4. | Covered conductor maintenance | Contact with vegetation | Wire-to-wire contact | 2019 | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | BVES will continue to evaluate covered conductor maintenance initiatives specific to wildfire mitigation. N/As: Col Q: "General Operations" "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 22047 | NA | NA | 0 | 36074 | NA | NA | 0 | 36976 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.5. | Crossarm maintenance, repair, and replacement | Equipment failure | Other contact with object | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Routine crossarm maintenance, repair, and replacement are included in the company’s standard inspection and correction programs, with an accelerated timeline for correction under the company’s Inspection program improvement N/As: Col Q: "General Operations" "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 36745 | NA | NA | 0 | 60124 | NA | NA | 0 | 61627 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.6.1 | Distribution pole replacement and reinforcement, including with composite poles | Equipment failure | Wire-to-wire contact | 2018 | NA | NA | 0.09 | 0.09 | D. 19-08-027 | NA | In Compliance | GO 95 |  | Number of Poles Replaced or Remidiated as a result of Failed Assessment | Test all poles to loading standards, GO95 requirements, intrusive inspection criteria and age and then, replaces or remediates non-compliant poles. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 536817 | 0 | NA | 216 | 925000 | 0 | NA | 200 | 925000 | 0 | NA | 200
Grid hardening | Grid Design & System Hardening | 7.3.3.6.2 | Distribution pole replacement and reinforcement, including with composite poles | Equipment failure | Wire-to-wire contact | 2019 | NA | NA | 0.21 | 0.021 | NA | WMP Memorandum Account | NA | GO 95 |  | Number of Poles Replaced or Remidiated as a result of Failed Assessment | Covered Conductor Project - Radford Line | 141137 | 0 | NA | NA | 4212167 | 0 | NA | 67 | 0 | 0 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.6.3 | Distribution pole replacement and reinforcement, including with composite poles | Equipment failure | Wire-to-wire contact | 2020 | NA | NA | 0.15 | 0.15 | NA | WMP Memorandum Account | NA | NA |  | Number of Poles Hardened | Evacuation Route Hardening Program - Pilot | 16081 | 0 | NA | 5 | 0 | 0 | NA | NA | 0 | 0 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.6.4 | Distribution pole replacement and reinforcement, including with composite poles | Equipment failure | NA | 2021 | NA | NA | 0.15 | 0.15 | NA | WMP Memorandum Account | NA | NA |  | Number of Poles Hardened | Evacuation Route Hardening Program | 560072 | 0 | NA | 400 | 390000 | 0 | NA | 400 | 0 | 0 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.7. | Expulsion fuse replacement | Equipment failure | Other contact with object | 2018 | NA | NA | 0.09 | 0.09 | R. 18-10-007 | NA | Exceeding Compliance | GO 95 |  | Number of Fuses Replaced | Replaces all conventional (expulsion) fuses with current limiting (ELF) and electronic fuses (Fuse TripSavers). N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 1486593 | 0 | NA | 862 | 0 | 0 | NA | NA | 0 | 0 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.8. | Grid topology improvements to mitigate or reduce PSPS events | Other contact with object | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have a specific wildfire mitigation grid design and system hardening initiative focused on grid topology improvements to mitigate or reduce PSPS events in addition to those described elsewhere in Table 12 N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.9.1 | Installation of system automation equipment | Equipment failure | Wire-to-wire contact | 2019 | NA | NA | 0.26 | 0.26 | D. 19-08-027 | NA | In Compliance | NA |  | Yearly Percent of Overall Program Target | Install grid automation. Fully instruments and automates BVES grid. Consists of installing a service area wide network operating on a SCADA system, substation automation, remote fault indicators, remote metering and power sensors and remote switching equipment to enable BVES to significantly improve its capability to detect and isolate faults rapidly before ever rolling out a crew. N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. Units - Yearly Percent of Overall Program Target | 3155054 | 0 | NA | 10 | 915833 | 0 | NA | NA | 0 | 0 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.9.2 | Installation of system automation equipment | Equipment failure | Wire-to-wire contact | 2019 | NA | NA | 1.18 | 1.18 | GRC | NA | In Compliance | NA |  | NA | Fault Isolation Localization and Service Restoration (FLISR) | 189512 | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.10. | Maintenance, repair, and replacement of connectors, including hotline clamps | Equipment failure | Wire-to-wire contact | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | N/As: Col Q: "General Operations" "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 10914 | NA | NA | 0 | 12164 | NA | NA | 0 | 12468 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.11. | Mitigation of impact on customers and other residents affected during PSPS event | PSPS - for sectionalization, etc. | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have specific wildfire mitigation grid design and system hardening initiatives focused on mitigation of impact on customers and other residents affected during PSPS events Both of these programs are combined as relevant grid topology improvements pertaining to grid design and system hardening that reduce PSPS events inherently also mitigate the impact on customers. Furthermore, BVES’s additional programs or efforts to mitigate the impact on customers and other residents affected during a PSPS event are captured later in this Table (12) N/As: "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.12. | Other corrective action | Other contact with object | Equipment failure | 2019 | NA | NA | 0.01 | 0.01 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 |  | NA | Safety & Technical Upgrades of Substations | 1674576 | 7276 | NA | NA | 410000 | 81096 | 0 | NA | 410000 | 83123 | 0 | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.12. | Other corrective action | Other contact with object | Equipment failure | 2018 | NA | NA | 1.57 | 1.57 | GRC | NA | NA | GO 95 |  | Number of Tree Attachments Removed | Tree Attachment Removal Program (TARP) | 276378 | 0 | NA | 400 | 500000 | 0 | NA | 70 | 500000 | 0 | NA | 70
Grid hardening | Grid Design & System Hardening | 7.3.3.12. | Other corrective action | Equipment failure | Wire-to-wire contact | 2020 | NA | NA | 0.15 | 0.15 | NA | WMP Memorandum Account | NA | NA |  | Number of Poles Hardened | Evacuation Route Hardening - cost accounting under 7.3.3.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.13. | Pole loading infrastructure hardening and replacement program based on pole loading assessment program | Equipment failure | Contamination | 2018 | NA | NA | 0.36 | 0.36 | GRC | NA | In Compliance | GO 95 |  | Number of Poles Replaced or Remidiated as a result of Failed Assessment | "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 1746224 | 0 | NA | 557 | 1475442 | 0 | NA | 450 | 1475442 | 0 | NA | 450
Grid hardening | Grid Design & System Hardening | 7.3.3.14. | Transformers maintenance and replacement | Equipment failure | Contamination | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Col Q: "General Operations" "Line miles treated" will not apply to this entry as this is a system-wide initaitive for BVES. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | 0 | 7944 | NA | NA | 310000 | 20215 | NA | NA | 310000 | 20720 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.15. | Transmission tower maintenance and replacement | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have a specific wildfire mitigation grid design and system hardening initiative focused on transmission tower maintenance and replacement because BVES does not own any transmission. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.16. | Undergrounding of electric lines and/or equipment | NA | NA | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA |  | 508649 | 0 | NA | NA | 105000 | 0 | NA | NA | 105000 | 0 | NA | NA
Grid hardening | Grid Design & System Hardening | 7.3.3.17. | Updates to grid topology to minimize risk of ignition in HFTDs | NA | NA | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Other grid design and system hardening programs include, as a component, grid topology improvements to minimize the risk of ignition in the HFTD. BVES recognizes that it is challenging to mitigate wildfire risk through grid topology changes alone and therefore focuses more on augmentation of existing circuitry through system hardening efforts . | NA | 0 | NA | NA | 0 | 0 | NA | NA | 0 | 0 | NA | NA
Asset inspection | Asset Management & Inspections | 7.3.4.1. | Detailed inspections of distribution electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA |  | NA | 8178 | 54.9 | NA | NA | 16176 | 50 | NA | NA | 16580 | 50 | NA
Asset inspection | Asset Management & Inspections | 7.3.4.2. | Detailed inspections of transmission electric lines and equipment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Asset inspection | Asset Management & Inspections | 7.3.4.3. | Improvement of inspections | Equipment failure | Wire-to-wire contact | 2019 | NA | NA | NA | NA | R. 18-10-007 | NA | In Compliance | GO 95; GO 165 |  | NA | Improvements of Bear Valley Electric Service's inspections have already been captured in other initiatives | NA | 22080 | NA | NA | NA | 17842 | NA | NA | NA | 18288 | NA | NA
Asset inspection | Asset Management & Inspections | 7.3.4.4. | Infrared inspections of distribution electric lines and equipment | Other contact with object | Equipment failure | 2018 | NA | NA | 0.8 | 0.8 | GRC | NA | Exceeding Compliance | Go 95 |  | NA | Contract Exacter Services. Conduct survey of BVES overhead system on 3-year cycle using infrared, ultrasonic and EMI sensors. Approximately 1/3 of OH system surveyed each year.” to read: “Contract Exacter Services. Conducted survey of BVES overhead system using infrared, ultrasonic and EMI sensors. BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | 53378 | 211 | NA | NA | 60000 | 211 | NA | NA | 60000 | 211 | NA
Asset inspection | Asset Management & Inspections | 7.3.4.5. | Infrared inspections of transmission electric lines and equipment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Asset inspection | Asset Management & Inspections | 7.3.4.6. | Intrusive pole inspections | Equipment failure | Contamination | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Test all poles to loading standards, GO95 requirements, intrusive inspection criteria and age and then, replaces or remediates non-compliant poles. Covered under 7.3.3.6. and 7.3.3.13 as the primary. | NA | 30512 | 876 | NA | NA | 150000 | NA | 850 | NA | 150000 | NA | 850
Asset inspection | Asset Management & Inspections | 7.3.4.7. | LiDAR inspections of distribution electric lines and equipment | Other contact with object | Equipment failure | 2018 | NA | NA | 0.7 | 0.7 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 |  | NA | Conduct LiDAR surveys of BVES overhead system on a semi-annual basis. N/As: BVES has RSE calculations for its entire service territory, which is primarily Tier 2, some Tier 3 and no nonHFTD or Zone 1 areas. BVES will enhance its methodology to account for distinct RSE values for Tier 2 and Tier 3 in the future. For this filing, BVES has duplicated the RSE value for each cell. | NA | 59560 | 289.56 | NA | NA | 120000 | 211 | NA | NA | 120000 | 211 | NA
Asset inspection | Asset Management & Inspections | 7.3.4.8. | LiDAR inspections of transmission electric lines and equipment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Asset inspection | Asset Management & Inspections | 7.3.4.9.1 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations | NA | NA | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | BVES has a contract with a supplier t conduct annual 3rd Part Ground Patrols. | NA | 7965 | 0 | NA | NA | 45000 | 211 | NA | NA | 45000 | 211 | NA
Asset inspection | Asset Management & Inspections | 7.3.4.9.2 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations | NA | NA | 2021 | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | BVES will be contracting for UAV HD Imagery in 2021 | NA | 53378 | 211 | NA | NA | 60000 | 211 | NA | NA | 60000 | 211 | NA
Asset inspection | Asset Management & Inspections | 7.3.4.10. | Other discretionary inspection of transmission electric lines and | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Asset inspection | Asset Management & Inspections | 7.3.4.11. | Patrol inspections of distribution electric lines and equipment (combined with Detailed Inspection Costs) | Other contact with object | Equipment failure | 2018 | NA | NA | 0.09 | 0.09 | NA | WMP Memorandum Account | Exceeding Compliance | GO 95 |  | NA |  | NA | 19082 | 460.11 | NA | 0 | 37745 | 211 | NA | 0 | 38689 | 211 | NA
Asset inspection | Asset Management & Inspections | 7.3.4.12. | Patrol inspections of transmission electric lines and equipment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Asset inspection | Asset Management & Inspections | 7.3.4.13. | Pole loading assessment program to determine safety factor | Equipment failure | Contamination | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Bear Valley Electric Service's wildfire mitigation asset management and inspections pole loading assessment program to determine safety factor is fully captured in 7.3.4.6. Intrusive pole inspections and 7.3.3.13 as the primary | 91907 | 0 | NA | 557 | 77655 | 0 | NA | 400 | 77655 | 0 | NA | 400
Asset inspection | Asset Management & Inspections | 7.3.4.14. | Quality assurance / quality control of inspections | Equipment failure | Other contact with object | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | General initiative and best practices applied to and accounted for in other relevant initiatives | NA | 22080 | NA | NA | NA | 17842 | NA | NA | NA | 18288 | NA | NA
Asset inspection | Asset Management & Inspections | 7.3.4.15. | Substation inspections | Equipment failure | Vandalism / Theft | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | Number of Monthly Sustations Inspected | Bear Valley Electric Service's substation inspections are fully captured in 7.3.4.11. Patrol inspections of distribution electric lines and equipment | NA | 99460 | NA | 144 | 0 | 176384 | NA | 144 | NA | 180794 | NA | 144
Vegetation management project | Vegetation Management & Inspections | 7.3.5.1. | Additional efforts to manage community and environmental impacts | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA |  | NA | 35824 | NA | NA | 0 | 40027 | NA | NA | NA | 41028 | NA | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.2. | Detailed inspections of vegetation around distribution electric lines and equipment | Contact with vegetation | Equipment failure | 2019 | NA | NA | 0.35 | 0.35 | D.19-08-027 | NA | Exceeding Compliance | GO-95 |  | NA | Increases vegetation clearances, criterial for tree removals, and eliminates overhang on sub-transmission. These are above the 2017 baseline vegetation clearances that were in effect before CPUC Decision 17-12-024 was adopted. | NA | 8178 | 54.9 | NA | 0 | 16176 | NA | NA | NA | 16580 | NA | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.3. | Detailed inspections of vegetation around transmission electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Vegetation management project | Vegetation Management & Inspections | 7.3.5.4. | Emergency response vegetation management due to red flag warning or other urgent conditions | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA |  | NA | 117630 | NA | NA | NA | 111395 | NA | NA | NA | 111395 | NA | NA
Vegetation management project | Vegetation Management & Inspections | 7.3.5.5. | Fuel management and reduction of “slash” from vegetation management activities | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA |  | NA | 141311 | NA | NA | NA | 130000 | NA | NA | NA | 130000 | NA | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.6. | Improvement of inspections | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA |  | NA | 35824 | NA | NA | NA | 40027 | NA | NA | NA | 41028 | NA | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.7. | LiDAR inspections of vegetation around distribution electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Bear Valley Electric Service's LiDAR inspections of vegetation around distribution electric lines and equipment are captured in LiDAR inspections of distribution electric lines and equipment. | NA | 59560 | 289.56 | NA | NA | 120000 | 211 | NA | NA | 120000 | 211 | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.8. | LiDAR inspections of vegetation around transmission electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.9.1 | Other discretionary inspections of vegetation around distribution electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | BVES has a contract with a supplier t conduct annual 3rd Part Ground Patrols. | NA | 7965 | 0 | NA | 0 | 45000 | 211 | NA | NA | 45000 | 211 | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.9.2 | Other discretionary inspections of vegetation around distribution electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | BVES will be contracting for UAV HD Imagery in 2021 | NA | 53378 | 211 | NA | 0 | 60000 | 211 | NA | 0 | 60000 | 211 | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.10. | Other discretionary inspections of vegetation around transmission electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.11. | Patrol inspections of vegetation around distribution electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Bear Valley Electric Service's patrol inspections of vegetation around distribution electric lines and equipment are fully captured in Detailed inspection of vegetation around distribution electric lines and equipment and Patrol inspections of distribution electric lines and equipment. | NA | 19082 | 460.11 | NA | NA | 37745 | 211 | NA | NA | 38688 | 211 | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.12. | Patrol inspections of vegetation around transmission electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have any transmission lines or equipment as all of BVES's lines are below 65 kV. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.13. | Quality assurance / quality control of vegetation inspections | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA |  | NA | 44987 | NA | 112 | NA | 54817 | NA | NA | NA | 56187 | NA | NA
Vegetation management project | Vegetation Management & Inspections | 7.3.5.14. | Recruiting and training of vegetation management personnel | Contact with vegetation | Equipment failure | 2020 | NA | NA | 0.58 | 0.58 | GRC | WMP Memorandum Account | Exceeding Compliance | GO-95 |  | NA | Places a full-time contract utility forester as part of the BVES team. The job duties of the contract forester would include: Inspections: Inspect and evaluate circuits for hot spot locations, hazard tree identification and outage investigations. Auditing: Perform site-specific work audits to ensure contractors are performing within the specifications set forth by BVES. Customer Contacts/Issue Resolution: initiate or follow up in a timely and professional manner on all customer issues that may arise in a manner that will support the policies and procedures of BVES. This includes customer notifications, permit negotiations, conflict resolution, outage support/investigations and providing shared resources to construction, substation, lines and/or various work groups related to BVES’s Vegetation Management group. Administrative: Perform data entry, spreadsheet work, monitor crew activity sheets, track completed work, capture photo documentation of specific conditions and other administrative tasks as needed. Developing Work Plans: Develop work plans that specify the pruning and removal requirements to maintain BVES ROWs. These plans will be developed in an efficient and straightforward manner for a seamless transition to the tree contractors. Specialized Projects: Develop and manage specialized projects with an emphasis on reliability and risk management. Perform enhanced outage investigations, integrated storm hardening projects, performed risk assessment and prioritization studies, developed storm response protocols and implemented hazard tree programs that are focused on improving system safety. Contractor Safety Observations: Observe contractors as they work and provide safety behavior modification to help ensure a program that is best in class not only in vegetation management, but safety as well. RSE is an estimate based on latest available risk assessment. | NA | 22576 | NA | NA | NA | 29322 | NA | NA | NA | 30055 | NA | NA
Vegetation management project | Vegetation Management & Inspections | 7.3.5.15. | Remediation of at-risk species | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Remediation of at-risk species is a subset to the company’s vegetation management practices to achieve clearances around electric lines and equipment as well as being outlined in the reoccuring training of vegetation managment personnel. As such, Bear Valley Electric Service does not have a specific wildfire mitigation initiative for remediation of at-risk species at this time. Col Q: "General Operations" | NA | 150474 | NA | NA | NA | 144790 | NA | NA | NA | 144790 | NA | NA
Vegetation management project | Vegetation Management & Inspections | 7.3.5.16. | Removal and remediation of trees with strike potential to electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Removal and remediation of trees with strike potential to electric lines and equipment is a subset to the company’s vegetation management practices to achieve clearances around electric lines and equipment as described in reoccuring training of vegetation management personnel. As such, Bear Valley Electric Service does not have a specific wildfire mitigation initiative for removal and remediation of trees with strike potential at this time. | NA | 150474 | NA | NA | NA | 144790 | NA | NA | NA | 144790 | NA | NA
Vegetation inspection | Vegetation Management & Inspections | 7.3.5.17. | Substation inspection | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Substation vegetation management is a subset to the company’s overall vegetation management initiatives as described in Vegetation Management | NA | 5051 | NA | 144 | NA | 7088 | NA | NA | NA | 7265 | NA | NA
Vegetation management project | Vegetation Management & Inspections | 7.3.5.18. | Substation vegetation management | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Substation inspections are a subset to the company’s overall vegetation management inspections as described in Detailed Inspection of vegetation around distribution e;ectric lines and equipemnt, and Recruitting and training of vegetation management personnel | NA | 17341 | NA | NA | NA | 12000 | NA | NA | NA | 12300 | NA | NA
Vegetation management project | Vegetation Management & Inspections | 7.3.5.19. | Vegetation inventory system | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA |  | NA | 150474 | NA | NA | NA | 144790 | NA | NA | NA | 144790 | NA | NA
Vegetation management project | Vegetation Management & Inspections | 7.3.5.20 | Vegetation management to achieve clearances around electric lines and equipment | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Vegetation management to achieve clearances around electric lines and equipment is captured in Detailed Inspection of vegetation around distribution electric lines and equipemnt, and Recruitting and training of vegetation management personnel | NA | 2232712 | NA | NA | NA | 2054000 | NA | NA | NA | 2054000 | NA | NA
Other | Grid Operations & Operating Protocols | 7.3.6.1. | Automatic recloser operations | Other contact with object | Equipment failure | 2019 | NA | NA | 0.41 | 0.41 | D.19-08-027 | GRC | In Compliance | NA |  | NA | Automatic Recloser Upgrades. Recloser replacement to reduce electrical sparking, while also helping mitigate power outages and equipment damage. | NA | 22080 | NA | NA | NA | 17842 | NA | NA | NA | 18288 | NA | NA
Other | Grid Operations & Operating Protocols | 7.3.6.2. | Crew-accompanying ignition prevention and suppression resources and services | Other contact with object | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not currently deploy crew-accompanying ignition prevention and suppression resources and services as part of its routine operational practices. When an emergency occurs, BVES communicates and collaborates with local emergency response teams, which can include crew-accompanying ignition prevention and suppression resources and services. Additionally, during elevated risk conditions or during fire season, BVES leverages specific work practices and protocols and makes available specific resources and tools for use by operations personnel as included in Grid Operation and Protocols. However, BVES does not currently have a specific grid operations and protocols wildfire mitigation initiative focused on crew-accompanying ignition prevention and suppression resources and services. The use of these services will be re-evaluated and considered for future incorporation as part of the annual WMP review process. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Other | Grid Operations & Operating Protocols | 7.3.6.3. | Personnel work procedures and training in conditions of elevated fire risk | Other contact with object | Equipment failure | 2019 | NA | NA | 2.23 | 2.23 | D.19-08-027 | GRC | In Compliance | NA |  | NA | Wildfire Infrastructure Protection Teams. Roles and responsibilities for staff to respond to protect system infrastructure in case of emergencies. | NA | 8832 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Grid Operations & Operating Protocols | 7.3.6.4. | Protocols for PSPS re-energization | Other contact with object | Equipment failure | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Bear Valley Electric Service considers re-energization after a PSPS event to be a subset of outage restoration and re-energization protocols generally included in Grid Operations and Protocol Therefore, the BVES does not have a separate protocol for PSPS. | NA | 8832 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Grid Operations & Operating Protocols | 7.3.6.5. | PSPS events and mitigation of PSPS impacts | Other contact with object | Other contact with object | 2019 | NA | NA | 5.26 | 5.26 | D.19-08-027 | GRC and Fire Hazard Prevt. Memorandum Account | In Compliance | R.18-12-005 |  | NA | PSPS Protocols. Protocols and procedures to respond to and recover from de-energization events, which proactively prevent wildfires. Costs partially recovered. RSE is an estimate based on latest risk assessment. | NA | 8832 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Grid Operations & Operating Protocols | 7.3.6.6. | Stationed and on-call ignition prevention and suppression resources and services | Other contact with object | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not currently have stationed and on-call ignition prevention and suppression resources and services not captured in existing initiatives. | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Other | Data Governance | 7.3.7.1. | Centralized repository for data | Contact with vegetation | Equipment failure | NA | NA | NA | NA | NA | D. 19-08-027 | GRC | In Compliance | NA |  | NA | GIS Data Collection & Sharing. Maintain and share Geographic Information System (GIS) database on system infrastructure for asset management and planning with key stakeholders. | NA | 209746 | NA | NA | NA | 106165 | NA | NA | NA | 106165 | NA | NA
Other | Data Governance | 7.3.7.2. | Collaborative research on utility ignition and/or wildfire | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA | Bear Valley Electric Service does not have a specific wildfire mitigation data governance plan focused on collaborative research on utility ignition or wildfire at this time. The company generally collaborates with Mutual Aid Partners and first responders to develop protocols, procedures, and communication plans to prevent, manage, and respond to utility ignition or wildfire. Col Q: "General Operations" | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Other | Data Governance | 7.3.7.3. | Documentation and disclosure of wildfire-related data and algorithms | NA | NA | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Col Q: "General Operations" | NA | 8832 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Data Governance | 7.3.7.4. | Tracking and analysis of near miss data | NA | NA | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA |  | NA | 8832 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Resource Allocation Methodology | 7.3.8.1. | Allocation methodology development and application | NA | NA | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA |  | NA | 8832 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Resource Allocation Methodology | 7.3.8.2. | Risk reduction scenario development and analysis | NA | NA | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | BVES is committed to the continued development and improvement of the company’s risk-based decision making framework. | NA | 14799.77 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Resource Allocation Methodology | 7.3.8.3. | Risk spend efficiency analysis | NA | NA | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | BVES is committed to the continued development and improvement of the company’s risk-based decision making framework The risk modeling process will enhance predictive tools to influence the 2022 and 2023 WMP | NA | 14799.77 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Emergency Planning & Preparedness | 7.3.9.1. | Adequate and trained workforce for service restoration | NA | NA | NA | NA | NA | NA | NA | GRC | NA | In Compliance | GO 166 |  | NA |  | NA | 8832 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Emergency Planning & Preparedness | 7.3.9.2. | Community outreach, public awareness, and communications efforts | Other contact with object | NA | NA | NA | NA | NA | NA | GRC | NA | In Compliance | GO 167 |  | Number of Engagements (Radio, Newspaper, Online, Mail) | BVES will be enhancing its communications and notification plans across multiple customer groups and stakeholder continuing in 2022 | NA | 81780 | NA | 602 | NA | 15750 | NA | 360 | NA | 16144 | NA | 360
Other | Emergency Planning & Preparedness | 7.3.9.3 | Customer support in emergencies | NA | NA | NA | NA | NA | NA | NA | GRC | NA | In Compliance | R. 18-12-005 |  | Number of Emergencies |  | NA | 57603 | NA | NA | NA | 62475 | NA | NA | NA | 64037 | NA | NA
Other | Emergency Planning & Preparedness | 7.3.9.4. | Disaster and emergency preparedness plan | Other contact with object | Wire-to-wire contact | NA | NA | NA | NA | NA | D. 19-08-027 | NA | In Compliance | GO 166 |  | NA | Emergency Reporting & Procedures. Protocols and procedures for staff to respond to faults, emergencies, outages, dissaster events (such as earthquake, wildfire, etc.), etc. | NA | 8832 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Emergency Planning & Preparedness | 7.3.9.5. | Preparedness and planning for service restoration | NA | NA | NA | NA | NA | NA | NA | D. 19-08-027 | CEMA, if applicable | In Compliance | GO 166 |  | Number of Emergencies | Post-Incident Recovery, Restoration & Remediation. Protocols and procedures to respond to and recover from any wildfire or related emergency events. | NA | 6259 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Emergency Planning & Preparedness | 7.3.9.6. | Protocols in place to learn from wildfire events | NA | NA | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | Bear Valley Electric Service leverages the protocols included in the company’s Emergency Preparedness and Response Plan to learn from wildfire events in the same manner BVES learns from any emergency event. Therefore, Bear Valley Electric Service does not have specific protocols in place to learn from wildfire events that are not already covered in a previous program. | NA | 8832 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.1 | Community engagement | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | In Compliance | NA |  | NA | BVES values community engagement as a wildfire risk mitigation strategy and has incorporated community engagement as a component of its overall Emergency Preparedness and Response Programs. BVES will be enhancing its communications and notification plans across multiple customer groups and stakeholder continuing in 2022 | NA | 67080 | NA | 602 | NA | 28111 | NA | NA | NA | 28814 | NA | NA
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.2 | Cooperation and best practice sharing with agencies outside CA | NA | NA | NA | NA | NA | NA | NA | NA | NA | In Compliance | NA |  | NA | This is a System Wide Initiative that targets all ignition probabilty drivers. As a System Wide Initiative, this initiative does not have a specified risk reduction or a risk spend efficiency. BVES' effort reduces the risk of escalation through support of accelerated restoration. | NA | 8832 | NA | NA | NA | 15000 | NA | NA | NA | 15000 | NA | NA
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.3 | Cooperation with suppression agencies | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | In Compliance | NA |  | NA | During emergency situations, Bear Valley Electric Service's [emergency management group] communicates and collaborates with federal and state emergency responders and mutual assistance groups, including fire suppression agencies. The emergency manager has contact information for [state, county and tribal emergency managers, the state’s Emergency Operations Center Emergency Support Functions (ESF) personnel, and the Geographic Area Coordination Centers dispatch centers for fire-related emergency response. Col Q: "General Operations" | NA | 8832 | NA | NA | NA | 7137 | NA | NA | NA | 7315 | NA | NA
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.4 | Forest service and fuel reduction cooperation and joint roadmap | NA | NA | 2021 | NA | NA | 0 | 0 | NA | NA | In Compliance | NA |  | NA | While collaboration such as this is critical to the overall reduction of wildfire risk in the state of CA, Bear Valley Electric Service does not have program dedicated to cooperation with the forest service and fuel reduction and the development of a joint roadmap specific to this Wildfire Mitigation Plan. BVES views these efforts on an as-needed basis and incorporates additional efforts to manage community environments within other programs, such as those included in the company’s overall vegetation management and inspections programs. | NA | 9162.736 | NA | NA | NA | 14790 | NA | NA | NA | 14790 | NA | NA

## Sheet1 (hidden)
Contact with vegetation
Other contact with object
Equipment failure
Wire-to-wire contact
Contamination
Vandalism / Theft
PSPS - for sectionalization, etc.