## Quarterly Submission Guide (hidden)
| Yes | No | <-- for dropdowns
Wildfire Safety Division Attachment 2.3
Wildfire Mitigation Plan Quarterly report - non-spatial data template
Resolution WSD-011 Attachment 2.3
Instructions for use |  |  |  | Relevant options for mitigations table: Table 12
1 | Fill out the tan cells (color represented here) starting with the cell below (D17: Utility). The Utility name will populate the Table tabs to follow. Date modified will vary by table
2 | For each Table tab, after a modification is made, denote the date of the change in cell C4 for each Table tab. |  |  |  | Initiative categories | WMP Maturity model Categories | Driver options
3 | Some columns have an additional header in row 5 to serve as clarification for several columns. With the exception of projected data, row 5 will be highlighted in blue (color represented here)
4 | Some required metrics are future projections. For these, row 5, above the projections will be highlighted light green (color represented here) |  |  |  | Vegetation inspection | Risk Assessment & Mapping | 1. Ignitions | Contact with vegetation
| In future submissions, report updated projected numbers if / when projections have changed, and report actuals once the quarter / year has passed. |  |  |  | Vegetation management project | Situational Awareness & Forecasting |  | Other contact with object
5 | For data required annually rather than quarterly (see Tables 7.3 - 10), report for entire year even if part of the year is projected. Once year has passed, update cell with actuals |  |  |  | Asset inspection | Grid Design & System Hardening |  | Equipment failure
6 | Some tables will have additional instructions provided in a Notes box located in cells D2 - D4 |  |  |  | Grid hardening | Asset Management & Inspections |  | Wire-to-wire contact
Notes will explain terms, signal where projections are required, and provide other useful information.
7 | For the initial quarterly submission, utilities are required to submit data on annual metrics for 2015 - 2020, which should represent the most updated data from the 2020 WMP for years 2015-2019 |  |  |  | Other | Vegetation Management & Inspections |  | Contamination
* | Do not add or manipulate the template for any of the tabs |  |  |  |  | Data Governance |  | Vandalism / Theft
[6 empty] | Emergency Planning & Preparedness | 2. PSPS | PSPS - for sectionalization, etc.
Update the below table to establish which year, quarter of the WMP cycle this submission this represents.
Utility |  | Pacific Gas & Electric Company |  |  |  | Stakeholder Cooperation & Community Engagement
First year of 3-year WMP cycle |  | 2020
Submission year |  | 2021
Submission quarter |  | Q1 of 2021
Date Modified |  | 2020-05-03

## SME-RD Leads AND INSTRUCTIONS (hidden)
Timeline: SME to submit final data by April 16, 2021. Responsible Director review is due on April 21, 2021.
Tracker
Table Number | SME Lead | Responsible Director | Scope of the quarterly update | CWSP PMO Lead | PMO Outreach to SMEs (Yes/No) | SME Lead updated data (Yes/No) | Responsible Director Approval (Yes/No)
Table 1 | Marc Zimmerman, Heather Duncan, Stacie Doyle, John Birch, Damon Thayer, Michelle Sakamoto, April Schneider | Anne Beech, Heather Duncan | Update the Q1 2021 Column | Nelson Lau | Yes | 100% | Anne Beech - Approved
Table 2 | Marc Zimmerman, Jeremy Crowe, Manuel Camara, Shaun Hoppes, Kevin Skaggs | Anne Beech | Update the Q1 2021 Column | Nelson Lau | Yes | 100% | Anne Beech - Approved
Table 3 | N/A | N/A | N/A | Nelson Lau |  | 100%
Table 4 | Marc Zimmerman, James Fontes, Renee Records | Anne Beech | Update the Q1 2021 Column | Nelson Lau | Yes | 100% | Anne Beech - Approved
Table 5 | Marc Zimmerman, Ryan Blake | Anne Beech | Update the Q1 2021 Column | Nelson Lau | Yes | 100% | Anne Beech - Approved
Table 6 | Scott Strenfel, Kevin Oram | Scott Strenfel | Update the Q1 2021 Column | Nelson Lau, Alex Castillo | Yes | 100% | Scott Strenfel - Approved
Table 7.1 | Actuals: Nick Babb and Jeremy Crowe Projected: Devika Pant | Anne Beech | 1) Confirm if we have any updated numbers for 2020 ACTUALS. If so, please make changes in PURPLE. Provide explanation for the change in the "Notes on any changes made" column. Update 2021 PROJECTED numbers based on any changes to the ACTUALS. 2) Confirm if we have any NEW information that would change the PROJECTED numbers. If so, please make changes in PURPLE. Provide explanation for the change in the "Notes on any changes made" column. | Nelson Lau | Yes | 100% | Anne Beech - Pending
Table 7.2 | Actuals: Nick Babb and Jeremy Crowe Projected: Devika Pant | Anne Beech | 1) Confirm if we have any updated numbers for 2020 ACTUALS. If so, please make changes in PURPLE. Provide explanation for the change in the "Notes on any changes made" column. Update 2021 PROJECTED numbers based on any changes to the ACTUALS. 2) Confirm if we have any NEW information that would change the PROJECTED numbers. If so, please make changes in PURPLE. Provide explanation for the change in the "Notes on any changes made" column. | Nelson Lau | Yes | 100% | Anne Beech - Approved
Table 8 | Jason Bright, Kassim Visram | Maria Ly, Brad Koelling, Ben Almario | 1) Update the Non-HFTD, HFTD-Zone 1, HFTD-Tier 2, and HFTD-Tier 3 columns as of Q1 of 2021. 2) Update substation asset numbers in PURPLE. Provide justification for the change in the "Notes on any changes made" column. | Nelson Lau | Yes | 100% | Maria Ly - Approved Brad Koelling - Pending Ben Almario - Pending
Table 9 | Jason Bright, Kassim Visram, Michelle Sakamoto, Kathleen Gonos, Amanda Miller, Trish Fabris, Aster Mehari, Buba Jallow | Ali Moazed, Maria Ly, Jeff Borders, Sandra Cullings, Ben Almario | Confirm if we have any NEW information that would change the PROJECTED numbers. If so, please make changes in PURPLE. Provide explanation for the change in the "Notes on any changes made" column. | Nelson Lau | Yes | WIP
Table 10 | Jason Bright, Michelle Sakamoto, Buba Jallow, Aster Mehari, Gary Long, Jean-Pierre Jodoin, Patsy Baynard | Ali Moazed, Maria Ly, Jeff Borders, Sandra Cullings, Ben Almario | Confirm if we have any NEW information that would change the PROJECTED numbers. If so, please make changes in PURPLE. Provide explanation for the change in the "Notes on any changes made" column. | Nelson Lau | Yes | WIP
Table 11 | Gareth Stamp and Kevin Oram | Gareth Stamp | Replace Q1 projected with Q1 actuals data | Nelson Lau, Lenine Umali | Yes | 100% | Gareth Stamp - Approved
Table 12 | Risk data: Benson Wong, Devika Pant, Dylan Shariatpanahy Finance data: Chris Wong, Kamran Bhatti | Matt Pender, Paul McGregor | 1) If there are material changes to the budget for each initiative, we need to update the financials. 2) Update RSE calculations (as needed) based on any new information. | Justina Louie | Yes | WIP
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: EE fatality/injury data = Ryan Blake EO Contractor fatality/injury data = James Fontes Veg Mgt fatality/injury data = Joe Echols JxEv/Renee Baur RCNe

## Table 1 (hidden)
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. | [9 empty] | UPDATE WITH Q1 DATA HERE - please make all changes in PURPLE
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 1: Recent performance on progress metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Progress metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments | SME / POC | Internal Comments
1. Grid condition findings from inspection - Distribution lines in HFTD | 1.a. | Number of circuit miles inspected from patrol inspections in HFTD - Distribution lines | 14387.9332 | 14356.0438 | 13003.3088 | 26291.4698 | 12705.0356 | 1: 4956.6152; 2: 6521.2204; 3: 6623.6717; 4: 1273.9693; Note: These columns are placeholders for future QR submissions. 1: 9676 | # circuit miles | Totals represent the number of poles patrolled in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the patrol program is measured by pole count only. | Stacie Doyle or Heather Duncan | Totals represent the number of poles patrolled in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the patrol program is measured by pole count only.
| 1.b. | Number of circuit miles inspected from detailed inspections in HFTD - Distribution lines | 5350.1353 | 5899.5323 | 6570.7741 | 6782.3004 | 25223 | 1: 165.5898; 2: 6937.3393; 3: 5953.6485; 4: 61.3913; Note: These columns are placeholders for future QR submissions. 1: 863 | # circuit miles | Totals represent the number of poles inspected in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the inspection program is measured by pole count only. | Stacie Doyle or Heather Duncan | Totals represent the number of poles inspected in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the inspection program is measured by pole count only.
| 1.c. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Distribution lines | 1415.4965 | 3485.7618 | 3804.6946 | 1294.9429 | 1652.0647 | 1: 259.5034; 2: 960.0238; 3: 180.1236; 4: 509.0795; Note: These columns are placeholders for future QR submissions. 1: 122 | # circuit miles | Totals represent the number of inspections from Pole Test and Treat program in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the program is measured by pole count only. | Stacie Doyle or Heather Duncan | Totals represent the number of inspections from Pole Test and Treat program in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the program is measured by pole count only.
| 1.d. | Level 1 findings in HFTD for patrol inspections - Distribution lines | 9 | 9 | 77 | 229 | 0 | 1: 4; 2: 16; 3: 431; 4: 4; Note: These columns are placeholders for future QR submissions. 1: 68 | # findings |  | Stacie Doyle or Heather Duncan | Totals represent priority A findings which is equivalent to level 1.
| 1.e. | Level 1 findings in HFTD for detailed inspections - Distribution lines | 3 | 6 | 1067 | 239 | 352 | 1: 135; 2: 208; 3: 1497; 4: 28; Note: These columns are placeholders for future QR submissions. 1: 51 | # findings |  | Stacie Doyle or Heather Duncan | Totals represent priority A findings which is equivalent to level 1.
| 1.f. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 2; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 0 | # findings |  | Stacie Doyle or Heather Duncan
| 1.g. | Level 2 findings in HFTD for patrol inspections - Distribution lines | 25 | 23 | 34 | 94 | 131 | 1: 16; 2: 14; 3: 30; 4: 3; Note: These columns are placeholders for future QR submissions. 1: 64 | # findings |  | Stacie Doyle or Heather Duncan | Total represents a combination of priority B and E which is equivalent to Level 2
| 1.h. | Level 2 findings in HFTD for detailed inspections - Distribution lines | 487 | 576 | 651 | 648 | 10349 | 1: 74; 2: 1405; 3: 1538; 4: 18; Note: These columns are placeholders for future QR submissions. 1: 2982 | # findings |  | Stacie Doyle or Heather Duncan | Total represents a combination of priority B and E which is equivalent to Level 2
| 1.i. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 4 | 1 | 4 | 28 | 2 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 10 | # findings | Pole Test and Treat | Stacie Doyle or Heather Duncan | Total represents a combination of priority B and E which is equivalent to Level 2
| 1.j. | Level 3 findings in HFTD for patrol inspections - Distribution lines | 92 | 83 | 55 | 316 | 462 | 1: 33; 2: 101; 3: 42; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 3 | # findings |  | Stacie Doyle or Heather Duncan | Total represents a combination of priority F and H which is equivalent to Level 3
| 1.k. | Level 3 findings in HFTD for detailed inspections - Distribution lines | 16735 | 19911 | 19667 | 16216 | 219664 | 1: 1267; 2: 39221; 3: 29915; 4: 197; Note: These columns are placeholders for future QR submissions. 1: 599 | # findings |  | Stacie Doyle or Heather Duncan | Total represents a combination of priority F and H which is equivalent to Level 3
| 1.l. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 622 | 1775 | 1208 | 255 | 444 | 1: 37; 2: 113; 3: 82; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # findings |  | Stacie Doyle or Heather Duncan
1. Grid condition findings from inspection - Distribution lines total | 1.a.ii. | Number of total circuit miles inspected from patrol inspections - Distribution lines | 41094.9594 | 39822.6237 | 39966.6637 | 55931.77 | 55583.0052 | 1: 12536.2868; 2: 11649.4964; 3: 13067.4628; 4: 19631.0591; Note: These columns are placeholders for future QR submissions. 1: 13022 | # circuit miles |  | Stacie Doyle or Heather Duncan | Totals represent the number of poles patrolled in relationship to total poles in the system and converted to circuit miles. Note the circuit miles is an approximation since the patrol program is measured by pole count only.
| 1.b.ii. | Number of total circuit miles inspected from detailed inspections - Distribution lines | 14885.9002 | 15602.6283 | 15882.3415 | 16002.1839 | 35989.2651 | 1: 162.5379; 2: 7700.9472; 3: 11401.9412; 4: 4203.1861; Note: These columns are placeholders for future QR submissions. 1: 947 | # circuit miles |  | Stacie Doyle or Heather Duncan | Totals represent the number of poles inspected in relationship to total poles in the system and converted to circuit miles. Note the circuit miles is an approximation since the inspection program is measured by pole count only.
| 1.c.ii. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Distribution lines | 9772.36 | 9098.1252 | 7982.0498 | 4986.4074 | 6733.7729 | 1: 1928.6223; 2: 1853.2088; 3: 1960.3699; 4: 2218.7724; Note: These columns are placeholders for future QR submissions. 1: 1429 | # circuit miles |  | Stacie Doyle or Heather Duncan | Totals represent the number of inspections from Pole Test and Treat program in relationship to total poles in system and converted to circuit miles. Note the circuit miles is an approximation since the program is measured by pole count only.
| 1.d.ii. | Level 1 findings for patrol inspections - Distribution lines | 33 | 22 | 50 | 86 | 269 | 1: 50; 2: 38; 3: 94; 4: 68; Note: These columns are placeholders for future QR submissions. 1: 62 | # findings | Non HFTD areas only | Stacie Doyle or Heather Duncan
| 1.e.ii. | Level 1 findings for detailed inspections - Distribution lines | 22 | 33 | 414 | 5708 | 517 | 1: 59; 2: 91; 3: 445; 4: 148; Note: These columns are placeholders for future QR submissions. 1: 149 | # findings | Non HFTD areas only | Stacie Doyle or Heather Duncan
| 1.f.ii. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 1 | 0 | 0 | 1 | 14 | 1: 3; 2: 3; 3: 5; 4: 4; Note: These columns are placeholders for future QR submissions. 1: 1 | # findings | Pole Test and Treat | Stacie Doyle or Heather Duncan
| 1.g.ii. | Level 2 findings for patrol inspections - Distribution lines | 156 | 90 | 96 | 132 | 310 | 1: 132; 2: 98; 3: 113; 4: 100; Note: These columns are placeholders for future QR submissions. 1: 163 | # findings | Non HFTD areas only | Stacie Doyle or Heather Duncan
| 1.h.ii. | Level 2 findings for detailed inspections - Distribution lines | 1153 | 1302 | 1077 | 1107 | 1894 | 1: 490; 2: 972; 3: 2380; 4: 1167; Note: These columns are placeholders for future QR submissions. 1: 3942 | # findings | Non HFTD areas only | Stacie Doyle or Heather Duncan
| 1.i.ii. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 65 | 117 | 68 | 104 | 1 | 1: 5; 2: 1; 3: 11; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 939 | # findings | Pole Test and Treat | Stacie Doyle or Heather Duncan
| 1.j.ii. | Level 3 findings for patrol inspections - Distribution lines | 317 | 239 | 195 | 405 | 1018 | 1: 228; 2: 149; 3: 195; 4: 54; Note: These columns are placeholders for future QR submissions. 1: 6 | # findings | Non HFTD areas only | Stacie Doyle or Heather Duncan
| 1.k.ii. | Level 3 findings for detailed inspections - Distribution lines | 35673 | 38733 | 31487 | 19278 | 39564 | 1: 1438; 2: 13837; 3: 49162; 4: 19010; Note: These columns are placeholders for future QR submissions. 1: 1051 | # findings | Non HFTD areas only | Stacie Doyle or Heather Duncan
| 1.l.ii. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 3527 | 5948 | 3554 | 3763 | 1179 | 1: 950; 2: 2; 3: 1468; 4: 811; Note: These columns are placeholders for future QR submissions. 1: 0 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR. | Stacie Doyle or Heather Duncan
1. Grid condition findings from inspection - Transmission lines in HFTD | 1.a.iii. | Number of circuit miles inspected from patrol inspections in HFTD - Transmission lines | 2585 | 3696 | 3048 | 3251 | 0 | 1: 663; 2: 1572; 3: 1259; 4: 1239; Note: These columns are placeholders for future QR submissions. 1: 56 | # circuit miles |  | Stacie Doyle or Heather Duncan | Pre-2020: Assume mileage not inspected was patrolled. 2020: Estimate from BFX orders with "PATR" (or similar) in description, using actual finish date (if available) otherwise basic finish date. If a structure/circuit was patrolled multiple times in a year, mileage is only counted once for that year.
| 1.b.iii. | Number of circuit miles inspected from detailed inspections in HFTD - Transmission lines | 2978 | 1867 | 2515 | 2312 | 5563 | 1: 22; 2: 1048; 3: 1624; 4: 229; Note: These columns are placeholders for future QR submissions. 1: 685 | # circuit miles |  | Stacie Doyle or Heather Duncan | Fraction of total HFTD mileage assumed proportional to percentage of structures inspected. HFTD mileage from WSIP scope "190502 Tx Update v10.xlsx". If a structure/circuit was inspected multiple times in a year, mileage is only counted once for that year.
| 1.c.iii. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Transmission lines | 1323 | 1323 | 1323 | 1323 | 1323 | 1: 331; 2: 331; 3: 331; 4: 331; Note: These columns are placeholders for future QR submissions. 1: 331 | # circuit miles | "Other" inspection methods include Pole Test and Treat and overhead IR. | Stacie Doyle or Heather Duncan | Assume mileage is primarily pole test and treat and IR. Assume evenly split by quarter. Pole test and treat: assume 1/10th of mileage annually for majority-wood circuits (circuits with 2-year pre-WSIP detailed inspection cycles). Pre-WSIP IR scope: assume 1/5 of total mileage, per 2018 ETPM cycles.
| 1.d.iii. | Level 1 findings in HFTD for patrol inspections - Transmission lines | - | - | - | - | 25 | 1: 0; 2: 1; 3: 133; 4: 10; Note: These columns are placeholders for future QR submissions. 1: 18 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.e.iii. | Level 1 findings in HFTD for detailed inspections - Transmission lines | 252 | 53 | 173 | 107 | 65 | 1: 0; 2: 10; 3: 11; 4: 5; Note: These columns are placeholders for future QR submissions. 1: 3 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.f.iii. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 123 | 1: 38; 2: 21; 3: 108; 4: 37; Note: These columns are placeholders for future QR submissions. 1: 52 | # findings | Includes any notification not found by patrol or detailed inspection. | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.g.iii. | Level 2 findings in HFTD for patrol inspections - Transmission lines | - | - | - | - | 549 | 1: 18; 2: 39; 3: 18; 4: 12; Note: These columns are placeholders for future QR submissions. 1: 37 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.h.iii. | Level 2 findings in HFTD for detailed inspections - Transmission lines | 3292 | 2346 | 2683 | 7664 | 48251 | 1: 116; 2: 3170; 3: 3872; 4: 631; Note: These columns are placeholders for future QR submissions. 1: 728 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.i.iii. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 2981 | 1: 359; 2: 735; 3: 743; 4: 204; Note: These columns are placeholders for future QR submissions. 1: 289 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR. | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.j.iii. | Level 3 findings in HFTD for patrol inspections - Transmission lines | - | - | - | - | 56 | 1: 1; 2: 0; 3: 0; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 1 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.k.iii. | Level 3 findings in HFTD for detailed inspections - Transmission lines | 662 | 554 | 999 | 710 | 4835 | 1: 25; 2: 2615; 3: 3476; 4: 465; Note: These columns are placeholders for future QR submissions. 1: 385 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.l.iii. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 539 | 1: 37; 2: 142; 3: 246; 4: 40; Note: These columns are placeholders for future QR submissions. 1: 73 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR. | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
1. Grid condition findings from inspection - Transmission lines total | 1.a.iv. | Number of total circuit miles inspected from patrol inspections - Transmission lines | 8385 | 11523 | 10015 | 11198 | 7671 | 1: 2594; 2: 5742; 3: 4122; 4: 4208; Note: These columns are placeholders for future QR submissions. 1: 133 | # circuit miles |  | Stacie Doyle or Heather Duncan | Pre-2020: Assume mileage not inspected was patrolled. 2020: Estimate from BFX orders with "PATR" or similar in description, using actual finish date (if available) otherwise basic finish date. If a structure/circuit was patrolled multiple times in a year, mileage is only counted once for that year.
| 1.b.iv. | Number of total circuit miles inspected from detailed inspections - Transmission lines | 9944 | 6807 | 8315 | 7131 | 10658 | 1: 36; 2: 1548; 3: 3847; 4: 1094; Note: These columns are placeholders for future QR submissions. 1: 1063 | # circuit miles |  | Stacie Doyle or Heather Duncan | Fraction of total HFTD mileage assumed proportional to percentage of structures inspected. If a structure/circuit was inspected multiple times in a year, mileage is only counted once for that year.
| 1.c.iv. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Transmission lines | 4393 | 4393 | 4393 | 4393 | 4393 | 1: 1098; 2: 1098; 3: 1098; 4: 1098; Note: These columns are placeholders for future QR submissions. 1: 1098 | # circuit miles | "Other" inspection methods include Pole Test and Treat and overhead IR. | Stacie Doyle or Heather Duncan | Assume this is primarily pole test and treat and IR. Assume evenly split by quarter.
| 1.d.iv. | Level 1 findings for patrol inspections - Transmission lines | - | - | - | - | 63 | 1: 1; 2: 4; 3: 160; 4: 14; Note: These columns are placeholders for future QR submissions. 1: 62 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.e.iv. | Level 1 findings for detailed inspections - Transmission lines | 985 | 317 | 623 | 351 | 72 | 1: 0; 2: 59; 3: 45; 4: 94; Note: These columns are placeholders for future QR submissions. 1: 16 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.f.iv. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 355 | 1: 106; 2: 89; 3: 228; 4: 105; Note: These columns are placeholders for future QR submissions. 1: 156 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR. | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.g.iv. | Level 2 findings for patrol inspections - Transmission lines | - | - | - | - | 1503 | 1: 79; 2: 218; 3: 131; 4: 114; Note: These columns are placeholders for future QR submissions. 1: 97 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.h.iv. | Level 2 findings for detailed inspections - Transmission lines | 9569 | 8779 | 10613 | 15588 | 54638 | 1: 249; 2: 6846; 3: 12375; 4: 7029; Note: These columns are placeholders for future QR submissions. 1: 1546 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.i.iv. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 10621 | 1: 704; 2: 1336; 3: 1762; 4: 465; Note: These columns are placeholders for future QR submissions. 1: 958 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR. | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.j.iv. | Level 3 findings for patrol inspections - Transmission lines | - | - | - | - | 158 | 1: 5; 2: 5; 3: 7; 4: 18; Note: These columns are placeholders for future QR submissions. 1: 1 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.k.iv. | Level 3 findings for detailed inspections - Transmission lines | 951 | 1065 | 2223 | 1614 | 5925 | 1: 117; 2: 4878; 3: 9034; 4: 3690; Note: These columns are placeholders for future QR submissions. 1: 780 | # findings |  | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
| 1.l.iv. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 2740 | 1: 112; 2: 189; 3: 506; 4: 107; Note: These columns are placeholders for future QR submissions. 1: 118 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR. | Stacie Doyle or Heather Duncan | Findings by inspection/patrol type not available before 2019; all findings assigned to detailed inspections. 2019-2020: see separate data notes below.
2. Vegetation clearance findings from inspection - total | 2.a.i | Number of spans inspected where at least some vegetation was found in non-compliant condition - total | 2402 | 3010 | 3372 | 5072 | 37914 | 1: 9637; 2: 11055; 3: 15783; 4: 15773; Note: These columns are placeholders for future QR submissions. 1: 8543 | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | See comments for this section. | April Schneider
| 2.a.ii | Number of spans inspected for vegetation compliance - total | 1443176 | 1562166 | 1458738 | 1496906 | 1525349 | 1: 428110; 2: 417774; 3: 335799; 4: 468295; Note: These columns are placeholders for future QR submissions. 1: 445641 | # of spans inspected for vegetation compliance | See comments for this section. | April Schneider
2. Vegetation clearance findings from inspection - in HFTD | 2.b.i | Number of spans inspected where at least some vegetation was found in non-compliant condition in HFTD | 204 | 442 | 912 | 1919 | 14469 | 1: 4385; 2: 6844; 3: 8078; 4: 5691; Note: These columns are placeholders for future QR submissions. 1: 4307 | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | See comments for this section. | April Schneider
| 2.b.ii | Number of spans inspected for vegetation compliance in HFTD | 170577 | 337899 | 323228 | 428070 | 457740 | 1: 137694; 2: 165572; 3: 122804; 4: 120114; Note: These columns are placeholders for future QR submissions. 1: 152931 | # of spans inspected for vegetation compliance | See comments for this section. | April Schneider
3. Community outreach metrics | 3.a. | # Customers in an evacuation zone for utility-ignited wildfire | - | - | - | - | - | [12 empty] | # customers (if customer was in an evacuation zone for multiple wildfires, count the customer for each relevant wildfire) | See comments for this section. |  | MZ: Q1 2021 update: SCE and SDG&E did not provide this data and indicated "N/A". To be consistent with the other IOU's we will do the same. From SCE: "SCE has no jurisdiction over evacuation orders. SCE diligently requested and followed up with local governments and law enforcement, and was only able to obtain information from one county. Even then, the information provided included high-level estimations of evacuation counts estimated by the local government and law enforcement entity for a limited amount of fires. Because of this, SCE is unable to obtain the requested data, analyze it, and report on evacuation related requirements in this table. SCE anticipates this to be a recurring challenge going forward. " | bar: 1 to Note: These columns are placeholders for future QR submissions. 1
| 3.b. | # Customers notified of evacuation orders | - | - | - | - | - | [12 empty] | # customers (count customer multiple times for each unique wildfire of which they were notified) | See comments for this section. |  | MZ: We don't track this data and are not responsible for providing wildfire evacuation notices. | bar: 1 to Note: These columns are placeholders for future QR submissions. 1
| 3.c. | % of customers notified of evacuation in evacuation zone of a utility-ignited wildfire | - | - | - | - | - | [12 empty] | Percentage of customers notified of evacuation | See comments for this section. |  | MZ: We don't track this data and are not responsible for providing wildfire evacuation notices. | bar: 1 to Note: These columns are placeholders for future QR submissions. 1
Comments for Table 1: Item 1. Description – Grid Condition Findings From Inspection – Distribution: · Level 1 findings are defined as Priority A tags. Level 2 findings are defined as Priority B and E tags. Level 3 findings are defined as priority F and H tags. · PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. Item 1. Description – Grid Condition Findings From Inspection – Transmission: · Findings by inspection/patrol type are not available before 2019; all findings were assigned to Detailed Inspections. · Level 1 findings are defined as Priority A tags. Level 2 findings are defined as Priority B and E tags. Level 3 findings are defined as priority F tags. · PG&E does not track inspection data by circuit mile. If a structure/circuit was patrolled multiple times in a year, mileage is only counted once for that year. Fraction of total mileage was assumed proportional to the percentage of structures inspected. Item 2. Description – Vegetation Clearance Findings From Inspection: · The number of spans inspected with noncompliant clearance is based on applicable rules and regulations at the time of inspection. · PG&E does not track the precise data requested as PG&E’s vegetation management data is generally tracked by tree. Therefore, the closest available data has been provided with an estimated translation to the “Percentage of right-of-way with noncompliant clearance” data that was requested. PG&E vegetation management pre-inspectors identify a tree that is currently violating minimum clearance distances, or may violate minimum clearance in the near future, with a special designation of being a Hazard Notification (HN). Not all HNs represent actively non-compliant trees, as in many cases the tree is currently compliant but may be at risk of violating minimum clearances before the normal tree work cycle can be completed. Nonetheless, HNs are the best estimate PG&E has for the number of trees that were identified as being inside or near the minimum clearance requirements and have been provided above as the “Trees identified as being currently, or at risk in the near future, of being out of compliance” data. · This estimate for the number of electric overhead spans has been determined by assuming an average span length (distance between poles) of 275 feet. Item 3. Description – Community Outreach Metrics: # Customers in an Evacuation Zone for Utility-Ignited Wildfire; # Customers Notified of Evacuation Orders: · PG&E does not issue wildfire evacuation notices to customers and does not maintain metrics on the number of customers in an evacuation zone or the number of customers notified of evacuation orders. In an effort to gather this data, PG&E’s Public Safety Specialists reached out to safety personnel from 38 counties to determine if any evacuation data was available for the utility-ignited wildfires as defined in Table 2. Most replies from county personnel provided limited or incomplete data or indicated that the requested data was not available. Because of this, PG&E is unable to report on evacuation related requirements in this table. PG&E anticipates this to be a recurring challenge going forward. Item 4. Assumptions for Inspection Data in 1.a,1.b,1.c · See note below regarding Table 8 (historical grid data unavailable for 2014-2018); circuit mileage is assumed to be the same as our 2019 data for 2015-2018 for the purposes of Table 1 · Mileage was extrapolated using approximate unit counts of historical detailed inspection & Pole Test & Treat data & relative circuit mileage in High Fire Threat District (HFTD) and Non HFTD

## Table 2 (hidden)
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. | [9 empty] | UPDATE WITH Q1 DATA HERE - please make all changes in PURPLE
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 2: Recent performance on outcome metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments | SME / POC | Internal Comments
1. Risk events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | 36643 | 37078 | 50711 | 34129 | 45989 | 1: 9455; 2: 9060; 3: 11358; 4: 9465; Note: These columns are placeholders for future QR submissions. 1: 15154 | Number per year |  | Manuel Camara | Metric Type: Near Misses not Risk Events
| 1.b. | Number of wires down (total) | 3280 | 3646 | 6475 | 2994 | 5577 | 1: 1174; 2: 677; 3: 804; 4: 639; Note: These columns are placeholders for future QR submissions. 1: 1968 | Number of wires down per year |  | Manuel Camara | Metric Type: Near Misses not Risk Events; Table 2, row 1.c.
| 1.c. | Number of outage events not caused by contact with vegetation (total) | 32826 | 32596 | 42293 | 30741 | 37715 | 1: 7769; 2: 8236; 3: 10495; 4: 8788; Note: These columns are placeholders for future QR submissions. 1: 12491 | Number of outage events per year |  | Manuel Camara | Not mentioned in 2020 WMP
| 1.d. | Number of outage events caused by contact with vegetation (total) | 3817 | 4482 | 8418 | 3388 | 8274 | 1: 1686; 2: 824; 3: 863; 4: 677; Note: These columns are placeholders for future QR submissions. 1: 2663 | Number of outage events per year |  | Manuel Camara | Not mentioned in 2020 WMP
2. Utility inspection findings - Distribution | 2.a. | Number of Level 1 findings (distribution - total) | 68 | 70 | 1608 | 6263 | 1152 | 1: 251; 2: 356; 3: 2474; 4: 253; Note: These columns are placeholders for future QR submissions. 1: 331 | # findings |  |  | metric Type: Utility Inspection Findings,broke down be EC-Distribution and LC-Transmission (Same as 2020 WMP). MZ: confirm if this is a summary of the same data in Table 1.
| 2.b. | Number of Level 2 findings (distribution - total) | 1890 | 2109 | 1930 | 2113 | 12687 | 1: 717; 2: 2490; 3: 4072; 4: 1288; Note: These columns are placeholders for future QR submissions. 1: 8100 | # findings |  |  | Same as 2020 WMP
| 2.c. | Number of Level 3 findings (distribution - total) | 56966 | 66689 | 56166 | 40233 | 262331 | 1: 3953; 2: 53423; 3: 80864; 4: 20073; Note: These columns are placeholders for future QR submissions. 1: 1659 | # findings |  |  | Same as 2020 WMP
| 2.d. | Number of distribution circuit miles inspected | 86040 | 87873 | 87590 | 111591 | 139400 | 1: 20367; 2: 36074; 3: 39402; 4: 25675; Note: These columns are placeholders for future QR submissions. 1: 15398 | # circuit miles |  |  | Not mentioned in 2020 WMP
2. Utility inspection findings - Transmission | 2.a.ii | Number of Level 1 findings (transmission - total) | 1237 | 370 | 796 | 458 | 703 | 1: 145; 2: 184; 3: 685; 4: 265; Note: These columns are placeholders for future QR submissions. 1: 234 | # findings |  |  | metric Type: Utility Inspection Findings,broke down be EC-Distribution and LC-Transmission (Same as 2020 WMP)
| 2.b.ii | Number of Level 2 findings (transmission - total) | 12861 | 11125 | 13296 | 23252 | 118543 | 1: 1525; 2: 12344; 3: 18901; 4: 8455; Note: These columns are placeholders for future QR submissions. 1: 2601 | # findings |  |  | Same as 2020 WMP
| 2.c.ii | Number of Level 3 findings (transmission - total) | 1613 | 1619 | 3222 | 2324 | 14253 | 1: 297; 2: 7829; 3: 13269; 4: 4321; Note: These columns are placeholders for future QR submissions. 1: 899 | # findings |  |  | Same as 2020 WMP
| 2.d.ii | Number of transmission circuit miles inspected | 22722 | 22723 | 22723 | 22722 | 22722 | 1: 3728; 2: 8388; 3: 9067; 4: 6400; Note: These columns are placeholders for future QR submissions. 1: 2294 | # circuit miles |  |  | Not mentioned in 2020 WMP; data was double counted and will need to be revised to extract the HFTD data out
3. Utility ignited wildfire fatalities | 3.a. | Fatalities due to utility-ignited wildfire (total) | 2 | 0 | 22 | 85 | 0 | 1: 0; 2: 0; 3: 4; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | Number of fatalities per year |  | Jeremy Crowe | Same as 2020 WMP
| 3.b. | Injuries due to utility-ignited wildfire (total) | - | - | - | - | - | 1: 0; 2: 0; 3: 1; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | Number of injuries per year |  | Jeremy Crowe | Not mentioned in 2020 WMP
4. Value of assets destroyed by utility-ignited wildfire, listed by asset type | 4.a. | Value of assets destroyed by utility-ignited wildfire (total) | $895.5M | $880k | $25.5B | $36k | $39k | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | Dollars of damage or destruction per year |  | Jeremy Crowe | Same as 2020 WMP; Table 2, row 7a
5. Structures damaged or destroyed by utility-ignited wildfire | 5.a. | Number of structures destroyed by utility-ignited wildfire (total) | 965 | 0 | 2299 | 18805 | 377 | 1: 0; 2: 0; 3: 209; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | Number of structures destroyed per year | Three structures have been added to the 2020 total since the last submittal | Jeremy Crowe | Same as 2020 WMP; Table 2, row 8a
| 5.b. | Critical infrastructure damaged/destroyed by utility-ignited wildfire (total) | 2 | 0 | 20 | 33 | 3 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | Number of critical infrastructure damaged/destroyed per year |  | Shaun Hoppes/Kevin Skaggs | Not mentioned in 2020 WMP; Not able to provide since this information is not available; Shaun Hoppes is looking at Red Tagged customer info
6. Acreage burned by utility-ignited wildfire | 6.a. | Acreage burned by utility-ignited wildfire (total) | 73328 | 2042 | 172205 | 167602 | 83643 | 1: 70; 2: 2209; 3: 58548; 4: 290; Note: These columns are placeholders for future QR submissions. 1: 745 | Acres burned per year |  | Jeremy Crowe | Same as 2020 WMP; Table 2, row 9.a.
7. Number of utility wildfire ignitions | 7.a. | Number of ignitions (total) according to existing ignition data reporting requirement | 20 | 15 | 52 | 25 | 25 | 1: 0; 2: 15; 3: 13; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 3 | Number per year | The total number of historical ignitions has risen since the initial submission due to ongoing audits of systems of records including FAS, the EIR database, and CAP. It is likely the number of historical ignitions will continue to increase as other systems of record are audited for potential missed ignitions. | Jeremy Crowe | Same as 2020 WMP; Table 2, row 10.a.; Fix typo "ignitions" in cell B26
| 7.b. | Number of ignitions in HFTD (subtotal) | 9 | 8 | 21 | 10 | 5 | 1: 0; 2: 4; 3: 6; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 2 | Number in HFTD per year |  | Jeremy Crowe | Same as 2020 WMP; Table 2, row 10.c.
| 7.c. | Number of ignitions in HFTD Zone 1 | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | Number in HFTD Zone 1 per year |  | Jeremy Crowe | Same as 2020 WMP; Table 2, row 10.c.i.
| 7.c.ii. | Number of ignitions in HFTD Tier 2 | 7 | 6 | 15 | 8 | 4 | 1: 0; 2: 4; 3: 6; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 1 | Number in HFTD Tier 2 per year |  | Jeremy Crowe | Same as 2020 WMP;Table 2, row 10.c.ii.
| 7.c.iii. | Number of ignitions in HFTD Tier 3 | 2 | 2 | 6 | 2 | 1 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 1 | Number in HFTD Tier 3 per year |  | Jeremy Crowe | Same as 2020 WMP; Table 2, row 10.c.iii.
| 7.d. | Number of ignitions in non-HFTD (subtotal) | 11 | 7 | 31 | 15 | 20 | 1: 0; 2: 11; 3: 7; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 1 | Number in non-HFTD per year |  | Jeremy Crowe | Same as 2020 WMP; Table 2, row 10.e.
8. Fatalities resulting from utility wildfire mitigation initiatives | 8.a. | Fatalities due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | - | - | - | 0 | 1 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 1 | Number of fatalities per year |  |  | Same as 2020 WMP; Table 2 row 5a; should these numbers equal the totals from Table 4?
9. OSHA-reportable injuries from utility wildfire mitigation initiatives | 9.a. | OSHA-reportable injuries due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | - | - | - | 0 | 53 | 1: 14; 2: 12; 3: 25; 4: 19; Note: These columns are placeholders for future QR submissions. 1: 1 | Number of OSHA-reportable injuries per year |  |  | Same as 2020 WMP; Table 2 row 6.a. Should these numbers equal the totals from Table 5?
Updated comments for Table 2: 5/3/2021 1) PG&E’s Electric Incident Investigation (EII) team is conducting a system of record audit for ignition events. The updated counts in Table 7.1 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. Changes are reflected in Purple font. 2) 2020 includes data related to the Zogg Fire, which is reported in compliance with D.19-05-037. PG&E's investigation into the cause of the Zogg Fire is ongoing. PG&E has included information related to the Zogg Fire in this table because CAL FIRE has announced its determination that PG&E's facilities caused the fire. Comments for Table 2: The data in Table 2 is derived from ignitions that are linked to a wildfire, which is defined as a fire greater than 10 acres in size. · Items 3.a (Fatalities due to utility-ignited wildfire [total]) and 3.b (Injuries due to utility-ignited wildfire (total)): PG&E provides in the attached data table 2015 through 2019 for wildfires that the California Department of Forestry and Fire protection (CAL FIRE) concluded were caused by PG&E equipment. · Item 4a (Value of assets destroyed by utility-ignited wildfire [total]): PG&E provides in the attached data table all 2015-2020 wildfires that involve disputes regarding destroyed assets that have settled. These settlements are lump sum settlements that do not break out the settlement dollars by damage category. In addition, the settlements reached related to the 2017 North Bay Fires and the 2018 Camp Fire (other than the settlement with the cities and counties) do not break out the settlement dollars by fire. Any attempt to break out the dollars by fire and/or damage category would be speculative. The settlements are totaled based on the year of the fire. The one exception is the 2018 Camp Fire which is reported with the 2017 North Bay Fires for the reasons described above. The chart does not include 2015-2020 wildfires that have not settled, which remain under investigation and/or civil discovery on causation issues, damages issues, or both. · Item 5b (Critical infrastructure damaged/destroyed by utility-ignited wildfire [total]): ‘Critical infrastructure’ is defined in accordance with the definition adopted in Decision (D.) 19-05-042 and modified in D.20-05-051. The number of critical infrastructure damaged/destroyed reflects the count of unique Service Point ID’s (meters) for red-tagged structures defined as critical infrastructure at the time of the wildfire. · Item 7a-d (Number of utility wildfire ignitions): The 2015 through 2018 ignition data is primarily based on fire incident reports filed with the California Public Utilities Commission (CPUC or Commission) annually in accordance with D.14-02-015. These reports include fire incidents that may be associated with PG&E facilities and meet the following conditions: (1) a self-propagating fire of material other than electrical and/or communication facilities (2) the resulting fire traveled greater than one linear meter from the ignition point, and (3) PG&E has knowledge that the fire occurred. Where not already included as part of the CPUC fire incidents report data, PG&E also included data for 2015 through 2018 wildfires that CAL FIRE concluded were caused by PG&E equipment. As of the time of the 2021 WMP submission, 2020 ignition data is being reviewed by PG&E in preparation for our 2020 fire incident that will be submitted by April 1, 2021 pursuant to D.14-02-015. The 2020 data in this table is preliminary and may be revised by the time that report is submitted.

## Table 3 (hidden)
Utility | Pacific Gas & Electric Company
Table No. | 3
Date Modified | 2021-02-05
Note: These columns are placeholders for future QR submissions.
Table 3: List and description of additional metrics | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
PG&E provided several metrics in the 2020 WMP for this section. With the update of the WMP template, all of these metrics were incorporated and included in other parts of the 2021 WMP. PG&E has no new or additional metrics to include to evaluate wildfire mitigation that are not already captured in other sections of the 2021 WMP. However, PG&E may analyze and look to reuse these metrics in ways not documented in the WMP as we continue to mature our data sets and modeling.

## Table 4 (hidden)
Utility | Pacific Gas & Electric Company
Table No. | 4 | [10 empty] | UPDATE WITH Q1 DATA HERE - please make all changes in PURPLE
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 4: Fatalities due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments | SME / POC | Internal Comments(CSWP)
1. Fatalities - Full-time Employee | 1.a. | Fatalities due to utility inspection - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | James Fontes | Used to be table 5, same data
| 1.b. | Fatalities due to vegetation management - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | James Fontes | Same
| 1.c. | Fatalities due to utility fuel management - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | James Fontes | Same
| 1.d. | Fatalities due to grid hardening - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | James Fontes | Confirmed that Grid Hardening = system Hardening
| 1.e. | Fatalities due to other - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | James Fontes | New
2. Fatalities - Contractor | 2.a. | Fatalities due to utility inspection - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | James Fontes | Used to be table 5, same data
| 2.b. | Fatalities due to vegetation management - Contractor | - | - | - | 0 | 0 | 1: 1; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 1 | # fatalities |  | James Fontes | Same
| 2.c. | Fatalities due to utility fuel management - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | James Fontes | Same
| 2.d. | Fatalities due to grid hardening - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | James Fontes | Confirmed that Grid Hardening = system Hardening
| 2.e. | Fatalities due to other - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | James Fontes | New
3. Fatalities - Member of public | 3.a. | Fatalities due to utility inspection - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | Renee Records, Claims | Used to be table 5, same data
| 3.b. | Fatalities due to vegetation management - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | Renee Records, Claims | Same
| 3.c. | Fatalities due to utility fuel management - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | Renee Records, Claims | Same
| 3.d. | Fatalities due to grid hardening - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | Renee Records, Claims | Confirmed that Grid Hardening = system Hardening
| 3.e. | Fatalities due to other - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # fatalities |  | Renee Records, Claims | New
Comments for Table 4: 1. Data for “Member of public” was derived from review of PG&E’s “Riskmaster” database, which tracks third party claims. 2. PG&E’s Community Wildfire Safety Program (CWSP), under which PG&E tracks our wildfire mitigation activities, was developed in 2018, with the above activities implemented in late 2018. Therefore, the “Year 2018” data above represents data from late 2018.
Note on N14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Date: 3/9/2021 CAP: 120618048 At approximately 1400-1500 hours near Watsonville, a Davey Resource Group inspector performing work for Vegetation Management suffered fatal injuries after being struck by a third-party vehicle. Reply: This is only counted in Table 4, not counted in Table 5 so that we don't double count. 4/30/2021 J4LQ

## Table 5 (hidden)
Utility | Pacific Gas & Electric Company
Table No. | 5 | [10 empty] | UPDATE WITH Q1 DATA HERE - please make all changes in PURPLE
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 5: OSHA-reportable injuries due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments | SME / POC | Internal Comments (CWSP)
1. OSHA injuries - Full-time Employee | 1.a. | OSHA injuries due to utility inspection - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Used to be table 6, same data
| 1.b. | OSHA injuries due to vegetation management - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Same
| 1.c. | OSHA injuries due to utility fuel management - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Same
| 1.d. | OSHA injuries due to grid hardening - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Confirmed that Grid Hardening = system Hardening
| 1.e. | OSHA injuries due to other - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | New
2. OSHA injuries - Contractor | 2.a. | OSHA injuries due to utility inspection - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Used to be table 6, same data
| 2.b. | OSHA injuries due to vegetation management - Contractor | - | - | - | 1 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Same
| 2.c. | OSHA injuries due to utility fuel management - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Same
| 2.d. | OSHA injuries due to grid hardening - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Confirmed that Grid Hardening = system Hardening
| 2.e. | OSHA injuries due to other - Contractor | - | - | - | 0 | 1 | 1: 0; 2: 0; 3: 1; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | New
3. OSHA injuries - Member of public | 3.a. | OSHA injuries due to utility inspection - Public | - | - | - | 0 | 0 | 1: 0; 2: 1; 3: 0; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Used to be table 6, same data
| 3.b. | OSHA injuries due to vegetation management - Public | - | - | - | 1 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Same
| 3.c. | OSHA injuries due to utility fuel management - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Same
| 3.d. | OSHA injuries due to grid hardening - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | Confirmed that Grid Hardening = system Hardening
| 3.e. | OSHA injuries due to other - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0 | # OSHA-reportable injuries |  | Ryan Blake | New
Comments for Table 5: 1. PG&E has limited information regarding injuries to contractors and members of the public, and any related medical treatment, during wildfire mitigation initiatives because PG&E is not responsible for reporting those injuries to OSHA. Thus, the figures in Table 5 relating to OSHA-reportable injuries to contractors and members of the public due to wildfire mitigation initiatives are based on PG&E's best available data for injuries that, given their severity, would have likely been reported to OSHA by PG&E had the injuries occurred to a PG&E employee. 2. PG&E’s CWSP, under which PG&E tracks our wildfire mitigation activities, was developed in 2018, with the above activities implemented in late 2018. Therefore, the “Year 2018” data above represents data from late 2018. 3. PG&E previously submitted data for OSHA-recordable injuries to employees, contractors, and members of the public due to wildfire mitigation initiatives as part of Table 6 of our 2020 Wildfire Mitigation Plan (WMP) and Table 5 of our 2021 WMP. In order to align with the WSD and the other utilities, we re-reviewed our records regarding injuries to employees, contractors, and members of the public to determine which injuries may be more specifically classified as OSHA-reportable injuries due to wildfire mitigation initiatives from 2018-2020 and amended Table 5 accordingly. The amendment was made on April 12, 2021 in response to California Public Advocates WMP Data Request 41. This Quarterly update to Table 5 is based on the amended version of Table 5 served on April 12, 2021. 4. OSHA-reportable injuries resulting in fatalities due to wildfire mitigation activities are captured in Table 4 rather than Table 5 to avoid double-counting.
Note on N14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Date: 3/9/2021 CAP: 120618048 At approximately 1400-1500 hours near Watsonville, a Davey Resource Group inspector performing work for Vegetation Management suffered fatal injuries after being struck by a third-party vehicle. Reply: This should be marked as 0. Already captured in Table 4 (Fatality), so that we do not double count. 4/30/2021 J4LQ
Note on B25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Table 6? Should this comment refer to table 5?

## Table 6 (hidden)
Utility | Pacific Gas & Electric Company
Table No. | 6 | [10 empty] | UPDATE WITH Q1 ACTUALS HERE - please make all changes in PURPLE
Date Modified | 2021-05-03
Note: These columns are placeholders for future QR submissions.
Table 6: Weather patterns | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Red Flag Warning Circuit Mile Days | 1.a. | Red Flag Warning overhead Circuit Mile days - entire utility territory | 148629.78 | 171642.81 | 594877.94 | 632033.39 | 577409.39 | 1: 0; 2: 104375.13; 3: 285515.17; 4: 365180.7; Note: These columns are placeholders for future QR submissions. 1: 6403.91 | Sum of circuit miles of utility grid subject to Red Flag Warning each day within a given time period, calculated as the number of circuit miles that were under an RFW multiplied by the number of days those miles were under said RFW. For example, if 100 circuit miles were under an RFW for 1 day, and 10 of those miles were under RFW for an additional day, then the total RFW circuit mile days would be 110.
| 1.b. | Red Flag Warning overhead Circuit Mile days - HFTD Zone 1 | 87.81 | 8.42 | 65.48 | 347.77 | 164.27 | 1: 0; 2: 0; 3: 154.46; 4: 163.51; Note: These columns are placeholders for future QR submissions. 1: - | Red Flag Warning OH Circuit Mile days, see above for definition
| 1.c. | Red Flag Warning overhead Circuit Mile days - HFTD Tier 2 | 30101.21 | 48603.57 | 169935.61 | 166968.54 | 132579.98 | 1: 0; 2: 14708.29; 3: 85128.14; 4: 105136.89; Note: These columns are placeholders for future QR submissions. 1: 2673.32 | Red Flag Warning OH Circuit Mile days, see above for definition
| 1.d. | Red Flag Warning overhead Circuit Mile days - HFTD Tier 3 | 12210.71 | 21835.32 | 89698.22 | 70654.04 | 56819.47 | 1: 0; 2: 3346.08; 3: 29214.41; 4: 56324.3; Note: These columns are placeholders for future QR submissions. 1: 516.29 | Red Flag Warning OH Circuit Mile days, see above for definition
| 1.e. | Red Flag Warning overhead Circuit Mile days - Non-HFTD | 106230.05 | 101195.51 | 335178.62 | 394063.04 | 387845.67 | 1: 0; 2: 86320.76; 3: 171018.16; 4: 203556; Note: These columns are placeholders for future QR submissions. 1: 3214.31 | Red Flag Warning OH Circuit Mile days, see above for definition
2. Wind conditions | 2.a. | High wind warnings | 2393.63 | 28023 | 140758.36 | 3996.58 | 83181.8 | 1: 3142.43; 2: 581.79; 3: 0; 4: 1137.73; Note: These columns are placeholders for future QR submissions. 1: 8415.73 | Sum of circuit miles of utility grid subject to High Wind Warnings (HWW, as defined by the National Weather Service) each day within a given time period, calculated as the number of circuit miles that were under an HWW multiplied by the number of days those miles were under said HWW. For example, if 100 circuit miles were under an HWW for 1 day, and 10 of those miles were under HWW for an additional day, then the total HWW circuit mile days would be 110.
3. Other | 3.a. | Other relevant weather pattern metrics tracked (add additional rows as needed)
Comments for Table 6: Table 6 shows the trends of National Weather Service (NWS) issued Red Flag Warnings (RFWs) and High Wind Warnings (HWWs) over the last 5 years impacting PG&E circuits across the territory through the metrics RFW Circuit Mile Days and HWW Circuit Mile Days. NWS RFWs are a proxy for high fire danger conditions, while HWWs are issued for solely high wind threats, regardless of humidity values and fire danger. These values have changed from previous reports, which calculated RFW Day Circuit miles based on Fire Index Areas. For these metrics, circuit miles are now calculated by the NWS RFW and HWW polygons to give a more accurate and precise values for RFW Circuit Mile Days and HWW Circuit Mile Days.

## Table 7.1 (hidden)
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 7.1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. | [11 empty] | REPLACE WITH Q1 ACTUALS HERE - please make all changes in PURPLE
| Date Modified | 2021-05-03 | Data from 2015 - 2020 Q2 should be actual numbers. 2020 Q3 - 2023 should be projected. In future submissions update projected numbers with actuals
[6 empty] | Number of risk events | [8 empty] | Projected risk events
| Table 7.1: Key recent and projected drivers of risk events | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| Risk Event category | Cause category | # | Sub-cause category | Are risk events tracked for ignition driver? (yes / no) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Notes on any changes made | Comments | Internal SME Contact
x | Wire down event - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | Yes | 1387 | 1618 | 3566 | 1052 | 3267 | 665 | 238 | 270 | 176 | 1103 | 236.2659 | 268.0328 | 174.7176 | 654.9114 | 234.3893 | 265.9039 | 173.3299 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. | Manuel C
|  |  | 1.b. | Animal contact- Distribution | Yes | 99 | 96 | 93 | 107 | 100 | 35 | 28 | 24 | 31 | 22 | 27.8941 | 23.9092 | 30.8827 | 34.7124 | 27.7699 | 23.8028 | 30.7453 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 1.c. | Balloon contact- Distribution | Yes | 38 | 36 | 32 | 53 | 35 | 6 | 20 | 14 | 7 | 6 | 20 | 14 | 7 | 6 | 20 | 14 | 7 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 1.d. | Vehicle contact- Distribution | Yes | 551 | 629 | 600 | 602 | 561 | 126 | 153 | 187 | 157 | 135 | 153 | 187 | 157 | 126 | 153 | 187 | 157 | # risk events (excluding ignitions) | Q4 2020 includes minor updates based on post outage reviews. | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 1.e. | Other contact from object - Distribution | Yes | 104 | 123 | 108 | 102 | 106 | 26 | 17 | 20 | 18 | 31 | 17 | 20 | 18 | 26 | 17 | 20 | 18 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 2. Equipment / facility failure - Distribution | 2.a. | Connector damage or failure- Distribution | Yes | 518 | 518 | 943 | 500 | 767 | 144 | 109 | 113 | 116 | 367 | 108.3967 | 112.3745 | 115.3579 | 142.2412 | 107.6687 | 111.6198 | 114.5832 | # risk events (excluding ignitions) |  | Assumed this was meant to indicate conductor damage and not connector damage since these would be covered as splices. This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.b. | Splice damage or failure — Distribution | Yes | 231 | 262 | 320 | 225 | 245 | 64 | 47 | 48 | 54 | 85 | 46.7398 | 47.7343 | 53.7011 | 63.2183 | 46.426 | 47.4137 | 53.3405 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.c. | Crossarm damage or failure - Distribution | Yes | 36 | 50 | 86 | 46 | 69 | 13 | 10 | 6 | 19 | 32 | 9.9446 | 5.9668 | 18.8948 | 12.8412 | 9.8779 | 5.9267 | 18.7679 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.d. | Insulator damage or failure- Distribution | Yes | 20 | 20 | 37 | 34 | 26 | 11 | 7 | 4 | 6 | 5 | 6.9613 | 3.9779 | 5.9668 | 10.8656 | 6.9145 | 3.9511 | 5.9267 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.e. | Lightning arrestor damage or failure- Distribution | Yes | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.f. | Tap damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | Unclear what is requested and assumed this data detail is not readily available.
|  |  | 2.g. | Tie wire damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data detail is not readily available and jumper wire failures are included with the splice failure data.
|  |  | 2.h. | Other - Distribution | Yes | 118 | 151 | 319 | 141 | 208 | 38 | 16 | 23 | 35 | 99 | 15.9114 | 22.8727 | 34.8063 | 37.5359 | 15.8046 | 22.7191 | 34.5725 | # risk events (excluding ignitions) |  | Includes ignition events since this detail is not readily available to be excluded.
|  | 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | Generally not applicable to wire down events.
|  | 4. Contamination - Distribution | 4.a. | Contamination - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | Not applicable. PG&E uses contamination more as a condition of the equipment and not normally as a basic cause.
|  | 5. Utility work / Operation | 5.a. | Utility work / Operation | No | 8 | 22 | 9 | 12 | 15 | 3 | 2 | 6 | 3 | 5 | 1.9558 | 5.8675 | 2.9337 | 2.9329 | 1.9553 | 5.8658 | 2.9329 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | Yes | 4 | 2 | 2 | 6 | 4 | 0 | 0 | 1 | 2 | 0 | 0 | 0.992 | 1.984 | 0 | 0 | 0.98433 | 1.9687 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 7. Other- Distribution | 7.a. | All Other- Distribution | Yes | 100 | 72 | 264 | 69 | 97 | 22 | 23 | 78 | 8 | 35 | 22.8979 | 77.6538 | 7.9645 | 21.788 | 22.7783 | 77.2482 | 7.9229 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 8. Unknown- Distribution | 8.a. | Unknown - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | Generally not applicable to wire down events.
x | Wire down event - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | Yes | 20 | 10 | 35 | 5 | 18 | 5 | 0 | 0 | 1 | 11 | 0 | 0 | 1 | 5 | 0 | 0 | 1 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. | David Greggory
|  |  | 9.b. | Animal contact- Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.c. | Balloon contact- Transmission | Yes | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.d. | Vehicle contact- Transmission | Yes | 8 | 5 | 8 | 10 | 9 | 4 | 1 | 0 | 2 | 3 | 1 | 0 | 2 | 4 | 1 | 0 | 2 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.e. | Other contact from object - Transmission | Yes | 5 | 4 | 4 | 4 | 1 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 10. Equipment / facility failure - Transmission | 10.a. | Connector damage or failure- Transmission | Yes | 7 | 14 | 8 | 7 | 28 | 6 | 1 | 1 | 3 | 23 | 1 | 1 | 3 | 6 | 1 | 1 | 3 | # risk events (excluding ignitions) |  | Assume CPUC meant "Conductor"; does not exclude events that led to CPUC reportable ignition
|  |  | 10.b. | Splice damage or failure — Transmission | Yes | 5 | 3 | 7 | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 2 | 0 | # risk events (excluding ignitions) |  | Includes "Connector" failures; does not exclude events that led to CPUC reportable ignition
|  |  | 10.c. | Crossarm damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.d. | Insulator damage or failure- Transmission | Yes | 3 | 0 | 2 | 2 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 2 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.e. | Lightning arrestor damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.f. | Tap damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.g. | Tie wire damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.h. | Other - Transmission | Yes | 5 | 2 | 15 | 2 | 3 | 2 | 0 | 1 | 0 | 4 | 0 | 1 | 0 | 2 | 0 | 1 | 0 | # risk events (excluding ignitions) |  | Pole & Line Switch failures; does not exclude events that led to CPUC reportable ignition
|  | 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 12. Contamination - Transmission | 12.a. | Contamination - Transmission | Yes | 2 | 0 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 13. Utility work / Operation | 13.a. | Utility work / Operation | No | 1 | 0 | 1 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | Yes | 1 | 3 | 4 | 2 | 4 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 15. Other- Transmission | 15.a. | All Other- Transmission | Yes | 7 | 4 | 11 | 7 | 6 | 1 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 3 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 16. Unknown- Transmission | 16.a. | Unknown - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
x | Outage - Distribution | 17. Contact from object - Distribution | 17.a. | Veg. contact- Distribution | Yes | 3760 | 4432 | 8277 | 3361 | 8198 | 1665 | 823 | 863 | 674 | 2627 | 817.0035 | 856.7121 | 669.0892 | 1639.7405 | 810.5144 | 849.9075 | 663.7748 | # risk events (excluding ignitions) | Q4 2020 includes minor updates based on post outage reviews. | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. | Manuel C
|  |  | 17.b. | Animal contact- Distribution | Yes | 2354 | 2242 | 2197 | 2448 | 2071 | 402 | 648 | 632 | 757 | 496 | 645.5481 | 629.6087 | 754.1357 | 398.6968 | 642.6754 | 626.8069 | 750.7797 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 17.c. | Balloon contact- Distribution | Yes | 476 | 526 | 526 | 647 | 465 | 105 | 214 | 158 | 129 | 153 | 214 | 158 | 129 | 105 | 214 | 158 | 129 | # risk events (excluding ignitions) | Q4 2020 includes minor updates based on post outage reviews. | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 17.d. | Vehicle contact- Distribution | Yes | 1819 | 2041 | 1917 | 1917 | 1837 | 418 | 592 | 567 | 544 | 466 | 592 | 567 | 544 | 418 | 592 | 567 | 544 | # risk events (excluding ignitions) | Q4 2020 includes minor updates based on post outage reviews. | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 17.e. | Other contact from object - Distribution | Yes | 729 | 645 | 629 | 693 | 735 | 158 | 184 | 181 | 185 | 186 | 184 | 181 | 185 | 158 | 184 | 181 | 185 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 18. Equipment / facility failure - Distribution | 18.a. | Capacitor bank damage or failure- Distribution | Yes | 57 | 65 | 83 | 55 | 70 | 7 | 22 | 17 | 21 | 20 | 21.8782 | 16.9059 | 20.8838 | 6.9145 | 21.7313 | 16.7924 | 20.7435 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.b. | Conductor damage or failure — Distribution | Yes | 1281 | 1359 | 2063 | 1238 | 1926 | 384 | 281 | 297 | 322 | 808 | 279.4446 | 295.356 | 320.2177 | 379.3099 | 277.5679 | 293.3725 | 318.0672 | # risk events (excluding ignitions) | Q4 2020 includes minor updates based on post outage reviews. | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.c. | Fuse damage or failure - Distribution | Yes | 373 | 352 | 479 | 305 | 341 | 48 | 84 | 190 | 125 | 171 | 83.535 | 188.9483 | 124.3081 | 47.4137 | 82.974 | 187.6794 | 123.4733 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.d. | Lightning arrestor damage or failure- Distribution | Yes | 144 | 145 | 139 | 135 | 131 | 26 | 42 | 31 | 46 | 36 | 41.7675 | 30.8284 | 45.7454 | 25.6824 | 41.487 | 30.6214 | 45.4382 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.e. | Switch damage or failure- Distribution | Yes | 141 | 156 | 178 | 188 | 188 | 30 | 50 | 44 | 35 | 52 | 49.7232 | 43.7565 | 34.8063 | 29.6336 | 49.3893 | 43.4626 | 34.5725 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.f. | Pole damage or failure - Distribution | Yes | 502 | 628 | 1111 | 665 | 1149 | 193 | 210 | 173 | 247 | 403 | 208.8376 | 172.0424 | 245.6328 | 190.6427 | 207.4351 | 170.887 | 243.9832 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.g. | Insulator and brushing damage or failure - Distribution | Yes | 253 | 295 | 384 | 272 | 375 | 74 | 86 | 66 | 84 | 130 | 85.524 | 65.6347 | 83.535 | 73.0962 | 84.9496 | 65.1939 | 82.974 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.h. | Crossarm damage or failure - Distribution | Yes | 573 | 717 | 777 | 771 | 995 | 207 | 190 | 179 | 253 | 297 | 188.9483 | 178.0092 | 251.5996 | 204.4717 | 187.6794 | 176.8137 | 249.9099 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 59 | 62 | 59 | 52 | 59 | 13 | 22 | 17 | 16 | 12 | 21.8782 | 16.9059 | 15.9114 | 12.8412 | 21.7313 | 16.7924 | 15.8046 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.j. | Recloser damage or failure - Distribution | Yes | 61 | 60 | 102 | 90 | 112 | 12 | 10 | 19 | 15 | 37 | 9.9446 | 18.8948 | 14.917 | 11.8534 | 9.8779 | 18.7679 | 14.8168 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.k. | Anchor / guy damage or failure - Distribution | Yes | 36 | 41 | 47 | 47 | 57 | 14 | 9 | 19 | 14 | 23 | 8.9502 | 18.8948 | 13.9225 | 13.829 | 8.8901 | 18.7679 | 13.829 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.l. | Sectionalizer damage or failure - Distribution | Yes | 4 | 3 | 2 | 4 | 3 | 0 | 0 | 2 | 0 | 3 | 0 | 1.9889 | 0 | 0 | 0 | 1.9756 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.m. | Connection device damage or failure - Distribution | Yes | 1210 | 1250 | 1687 | 1095 | 1386 | 322 | 264 | 264 | 325 | 558 | 262.5387 | 262.5387 | 323.2011 | 318.0672 | 260.7756 | 260.7756 | 321.0305 | # risk events (excluding ignitions) | Q4 2020 includes minor updates based on post outage reviews. | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.n. | Transformer damage or failure - Distribution | Yes | 4224 | 3947 | 4977 | 3136 | 3969 | 728 | 1104 | 1856 | 1088 | 1199 | 1097.8891 | 1845.7266 | 1081.9777 | 719.1084 | 1090.516 | 1833.3312 | 1074.7114 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.o. | Other - Distribution | Yes | 2241 | 2426 | 2612 | 2094 | 2242 | 376 | 529 | 640 | 448 | 664 | 526.0719 | 636.4575 | 445.5202 | 371.4076 | 522.5389 | 632.1832 | 442.5282 | # risk events (excluding ignitions) | Q4 2020 includes minor updates based on post outage reviews. | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 19. Wire-to-wire contact - Distribution | 19.a. | Wire-to-wire contact / contamination- Distribution | Yes | 4900 | 5239 | 6731 | 5276 | 6732 | 1700 | 1178 | 1087 | 1383 | 2416 | 1178 | 1087 | 1383 | 1700 | 1178 | 1087 | 1383 | # risk events (excluding ignitions) | Q4 2020 includes minor updates based on post outage reviews. | PG&E uses contamination more as a condition of the equipment and not normally as a basic cause. Assumed this cause refers to a Basic Cause of "Unknown" and a Fault Type of "Line to Line". This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 20. Contamination - Distribution | 20.a. | Contamination - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | PG&E typically uses contamination as a condition of the equipment and not normally as a basic cause.
|  | 21. Utility work / Operation | 21.a. | Utility work / Operation | No | 431 | 650 | 793 | 680 | 886 | 185 | 240 | 240 | 204 | 292 | 234.6987 | 234.6987 | 199.4939 | 180.8624 | 234.6323 | 234.6323 | 199.4375 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 22. Vandalism / Theft - Distribution | 22.a. | Vandalism / Theft - Distribution | Yes | 45 | 26 | 26 | 58 | 44 | 10 | 13 | 17 | 16 | 14 | 12.896 | 16.8639 | 15.872 | 9.8433 | 12.7963 | 16.7337 | 15.7493 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 23. Other- Distribution | 23.a. | All Other- Distribution | Yes | 1818 | 752 | 1488 | 1232 | 978 | 111 | 255 | 1402 | 95 | 181 | 253.8683 | 1395.7777 | 94.5784 | 109.9302 | 252.5423 | 1388.4873 | 94.0844 | # risk events (excluding ignitions) | Q4 2020 includes minor updates based on post outage reviews. | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 24. Unknown- Distribution | 24.a. | Unknown - Distribution | Yes | 7974 | 8185 | 12158 | 6726 | 9503 | 1978 | 1715 | 1971 | 2137 | 3515 | 1707.3885 | 1962.2524 | 2127.5156 | 1958.9357 | 1698.4705 | 1952.0032 | 2116.4032 | # risk events (excluding ignitions) | Q4 2020 includes minor updates based on post outage reviews. | Omits the outages reported with an unknown cause that are shown in the row above for wire-to-wire contacts. This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
x | Outage - Transmission | 25. Contact from object - Transmission | 25.a. | Veg. contact- Transmission | Yes | 57 | 50 | 141 | 27 | 76 | 21 | 1 | 0 | 3 | 36 | 1 | 0 | 3 | 21 | 1 | 0 | 3 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. | David Greggory
|  |  | 25.b. | Animal contact- Transmission | Yes | 56 | 58 | 65 | 58 | 44 | 15 | 8 | 11 | 13 | 0 | 8 | 11 | 13 | 15 | 8 | 11 | 13 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.c. | Balloon contact- Transmission | Yes | 13 | 8 | 14 | 20 | 12 | 4 | 5 | 6 | 1 | 2 | 5 | 6 | 1 | 4 | 5 | 6 | 1 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.d. | Vehicle contact- Transmission | Yes | 61 | 66 | 69 | 79 | 49 | 18 | 14 | 17 | 24 | 23 | 14 | 17 | 24 | 18 | 14 | 17 | 24 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.e. | Other contact from object - Transmission | Yes | 34 | 22 | 20 | 14 | 26 | 2 | 5 | 19 | 2 | 9 | 5 | 19 | 2 | 2 | 5 | 19 | 2 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 26. Equipment / facility failure - Transmission | 26.a. | Capacitor bank damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.b. | Conductor damage or failure — Transmission | Yes | 14 | 29 | 23 | 24 | 53 | 16 | 3 | 5 | 15 | 26 | 3 | 5 | 15 | 16 | 3 | 5 | 15 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.d. | Lightning arrestor damage or failure- Transmission | Yes | 0 | 2 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 2 | 1 | 0 | 0 | 2 | 1 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.e. | Switch damage or failure- Transmission | Yes | 67 | 24 | 25 | 17 | 34 | 8 | 6 | 5 | 3 | 4 | 6 | 5 | 3 | 8 | 6 | 5 | 3 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.f. | Pole damage or failure - Transmission | Yes | 27 | 15 | 53 | 42 | 68 | 7 | 7 | 8 | 5 | 19 | 7 | 8 | 5 | 7 | 7 | 8 | 5 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.g. | Insulator and brushing damage or failure - Transmission | Yes | 51 | 75 | 78 | 86 | 65 | 19 | 40 | 26 | 33 | 11 | 40 | 26 | 33 | 19 | 40 | 26 | 33 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.h. | Crossarm damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 5 | 7 | 8 | 1 | 6 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.j. | Recloser damage or failure - Transmission | Yes | 36 | 30 | 44 | 29 | 29 | 10 | 4 | 12 | 9 | 5 | 4 | 12 | 9 | 10 | 4 | 12 | 9 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.k. | Anchor / guy damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 0 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.l. | Sectionalizer damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.m. | Connection device damage or failure - Transmission | Yes | 19 | 37 | 32 | 18 | 51 | 3 | 16 | 24 | 8 | 3 | 16 | 24 | 8 | 3 | 16 | 24 | 8 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.n. | Transformer damage or failure - Transmission | Yes | 1 | 6 | 0 | 2 | 9 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.o. | Other - Transmission | Yes | 63 | 45 | 56 | 40 | 49 | 12 | 19 | 7 | 9 | 13 | 19 | 7 | 9 | 12 | 19 | 7 | 9 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 27. Wire-to-wire contact - Transmission | 27.a. | Wire-to-wire contact / contamination- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 28. Contamination - Transmission | 28.a. | Contamination - Transmission | Yes | 22 | 18 | 25 | 51 | 17 | 6 | 13 | 9 | 6 | 4 | 13 | 9 | 6 | 6 | 13 | 9 | 6 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 29. Utility work / Operation | 29.a. | Utility work / Operation | No | 51 | 36 | 50 | 76 | 451 | 25 | 56 | 70 | 109 | 77 | 56 | 70 | 109 | 25 | 56 | 70 | 109 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 30. Vandalism / Theft - Transmission | 30.a. | Vandalism / Theft - Transmission | Yes | 7 | 10 | 9 | 5 | 21 | 2 | 2 | 4 | 1 | 1 | 2 | 4 | 1 | 2 | 2 | 4 | 1 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 31. Other- Transmission | 31.a. | All Other- Transmission | Yes | 436 | 138 | 388 | 168 | 314 | 93 | 57 | 163 | 25 | 115 | 57 | 163 | 25 | 93 | 57 | 163 | 25 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 32. Unknown- Transmission | 32.a. | Unknown - Transmission | Yes | 158 | 158 | 168 | 187 | 162 | 26 | 34 | 36 | 34 | 45 | 34 | 36 | 34 | 26 | 34 | 36 | 34 | # risk events (excluding ignitions) |  | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
x | Ignition - Distribution | 33. Contact from object - Distribution | 33.a. | Veg. contact- Distribution | Yes | 108 | 108 | 171 | 126 | 138 | 10 | 38 | 55 | 25 | 32 | 37.5971 | 54.4168 | 24.7349 | 9.7789 | 37.1598 | 53.784 | 24.4473 | # ignitions | The total number of historical ignitions has risen since the initial submission due to ongoing audits of systems of records including FAS, the EIR database, and CAP. It is likely the number of historical ignitions will continue to increase as other systems of record are audited for potential missed ignitions. |  | Nick Babb, Jeremy Crowe
|  |  | 33.b. | Animal contact- Distribution | Yes | 45 | 37 | 56 | 56 | 67 | 3 | 15 | 21 | 6 | 5 | 14.9379 | 20.9131 | 5.9752 | 2.9731 | 14.8655 | 20.8117 | 5.9462 | # ignitions
|  |  | 33.c. | Balloon contact- Distribution | Yes | 23 | 13 | 11 | 13 | 15 | 0 | 5 | 5 | 4 | 1 | 4.9854 | 4.9854 | 3.9884 | 0 | 4.9685 | 4.9685 | 3.9748 | # ignitions
|  |  | 33.d. | Vehicle contact- Distribution | Yes | 47 | 36 | 55 | 28 | 36 | 4 | 18 | 24 | 9 | 3 | 17.9282 | 23.9043 | 8.9641 | 3.9654 | 17.8445 | 23.7927 | 8.9223 | # ignitions
|  |  | 33.e. | Other contact from object - Distribution | Yes | 13 | 5 | 9 | 53 | 23 | 2 | 16 | 6 | 1 | 2 | 15.9258 | 5.9722 | 0.99536 | 1.9799 | 15.8392 | 5.9397 | 0.98995 | # ignitions
|  | 34. Equipment / facility failure - Distribution | 34.a. | Capacitor bank damage or failure- Distribution | Yes | 13 | 11 | 13 | 7 | 7 | 0 | 5 | 2 | 0 | 0 | 4.9977 | 1.9991 | 0 | 0 | 4.995 | 1.998 | 0 | # ignitions
|  |  | 34.b. | Conductor damage or failure — Distribution | Yes | 49 | 58 | 70 | 40 | 81 | 4 | 28 | 20 | 19 | 10 | 27.9018 | 19.9298 | 18.9333 | 3.9696 | 27.7872 | 19.848 | 18.8556 | # ignitions
|  |  | 34.c. | Fuse damage or failure - Distribution | Yes | 8 | 6 | 9 | 2 | 5 | 1 | 2 | 7 | 1 | 0 | 1.9878 | 6.9571 | 0.99388 | 0.98702 | 1.974 | 6.9091 | 0.98702 | # ignitions
|  |  | 34.d. | Lightning arrestor damage or failure- Distribution | Yes | 7 | 2 | 6 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0.92863 | 0 | 0 | 0 | 0.60821 | 0 | 0 | # ignitions
|  |  | 34.e. | Switch damage or failure- Distribution | Yes | 3 | 2 | 4 | 0 | 2 | 0 | 1 | 2 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 2 | 0 | # ignitions
|  |  | 34.f. | Pole damage or failure - Distribution | Yes | 6 | 6 | 12 | 11 | 6 | 0 | 5 | 3 | 4 | 2 | 4.9889 | 2.9934 | 3.9911 | 0 | 4.976 | 2.9856 | 3.9808 | # ignitions
|  |  | 34.g. | Insulator and brushing damage or failure - Distribution | Yes | 6 | 4 | 8 | 5 | 4 | 0 | 1 | 2 | 3 | 1 | 0.9978 | 1.9956 | 2.9934 | 0 | 0.99523 | 1.9905 | 2.9857 | # ignitions
|  |  | 34.h. | Crossarm damage or failure - Distribution | Yes | 3 | 4 | 12 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0.99494 | 0.99494 | 0 | 0 | 0.98904 | 0.98904 | 0 | # ignitions
|  |  | 34.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 1 | 1 | 4 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 1.9944 | 1.9944 | 0 | 0 | 1.9878 | 1.9878 | 0 | # ignitions
|  |  | 34.j. | Recloser damage or failure - Distribution | Yes | 0 | 3 | 3 | 0 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  |  | 34.k. | Anchor / guy damage or failure - Distribution | Yes | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98574 | 0 | 0 | 0 | # ignitions
|  |  | 34.l. | Sectionalizer damage or failure - Distribution | Yes | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.m. | Connection device damage or failure - Distribution | Yes | 44 | 21 | 39 | 3 | 1 | 0 | 13 | 15 | 9 | 2 | 12.9551 | 14.9482 | 8.9689 | 0 | 12.9029 | 14.8879 | 8.9327 | # ignitions
|  |  | 34.n. | Transformer damage or failure - Distribution | Yes | 18 | 11 | 23 | 17 | 20 | 1 | 6 | 14 | 0 | 2 | 5.9795 | 13.9522 | 0 | 0.99261 | 5.9556 | 13.8965 | 0 | # ignitions
|  |  | 34.o. | Other - Distribution | Yes | 21 | 25 | 25 | 44 | 25 | 1 | 8 | 7 | 8 | 3 | 7.9783 | 6.981 | 7.9783 | 0.99412 | 7.953 | 6.9589 | 7.953 | # ignitions
|  | 35. Wire-to-wire contact - Distribution | 35.a. | Wire-to-wire contact / contamination- Distribution | Yes | 6 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 36. Contamination - Distribution | 36.a. | Contamination - Distribution | Yes | 1 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 4 | 0 | 1 | 0 | 4 | 0 | 1 | 0 | 4 | # ignitions
|  | 37. Utility work / Operation | 37.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 38. Vandalism / Theft - Distribution | 38.a. | Vandalism / Theft - Distribution | Yes | 6 | 2 | 4 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 2 | 1 | # ignitions
|  | 39. Other- Distribution | 39.a. | All Other- Distribution | Yes | 0 | 5 | 7 | 7 | 5 | 0 | 1 | 2 | 4 | 1 | 0.99642 | 1.9928 | 3.9857 | 0 | 0.99225 | 1.9845 | 3.969 | # ignitions
|  | 40. Unknown- Distribution | 40.a. | Unknown - Distribution | Yes | 27 | 10 | 4 | 25 | 14 | 0 | 1 | 0 | 0 | 0 | 0.99537 | 0 | 0 | 0 | 0.98997 | 0 | 0 | # ignitions
x | Ignition - Transmission | 41. Contact from object - Transmission | 41.a. | Veg. contact- Transmission | Yes | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | # ignitions |  |  | Nick Babb, Jeremy Crowe
|  |  | 41.b. | Animal contact- Transmission | Yes | 6 | 9 | 5 | 11 | 8 | 0 | 0 | 7 | 1 | 0 | 0 | 7 | 1 | 0 | 0 | 7 | 1 | # ignitions
|  |  | 41.c. | Balloon contact- Transmission | Yes | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | # ignitions
|  |  | 41.d. | Vehicle contact- Transmission | Yes | 0 | 1 | 1 | 3 | 4 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | # ignitions
|  |  | 41.e. | Other contact from object - Transmission | Yes | 1 | 0 | 6 | 3 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 1 | 0 | 0 | 2 | 1 | 0 | # ignitions
|  | 42. Equipment / facility failure - Transmission | 42.a. | Capacitor bank damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.b. | Conductor damage or failure — Transmission | Yes | 1 | 3 | 3 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | # ignitions
|  |  | 42.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.d. | Lightning arrestor damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.e. | Switch damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.f. | Pole damage or failure - Transmission | Yes | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.g. | Insulator and brushing damage or failure - Transmission | Yes | 1 | 0 | 2 | 1 | 2 | 0 | 0 | 2 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | # ignitions
|  |  | 42.h. | Crossarm damage or failure - Transmission | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | # ignitions
|  |  | 42.j. | Recloser damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.k. | Anchor / guy damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.l. | Sectionalizer damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.m. | Connection device damage or failure - Transmission | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.n. | Transformer damage or failure - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.o. | Other - Transmission | Yes | 0 | 1 | 1 | 1 | 3 | 0 | 0 | 1 | 3 | 1 | 0 | 1 | 3 | 0 | 0 | 1 | 3 | # ignitions
|  | 43. Wire-to-wire contact - Transmission | 43.a. | Wire-to-wire contact / contamination- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 44. Contamination - Transmission | 44.a. | Contamination - Transmission | Yes | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  | 45. Utility work / Operation | 45.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 46. Vandalism / Theft - Transmission | 46.a. | Vandalism / Theft - Transmission | Yes | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 47. Other- Transmission | 47.a. | All Other- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  | 48. Unknown- Transmission | 48.a. | Unknown - Transmission | Yes | 2 | 0 | 1 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
Updated comments for Table 7.1 (5/3/2021): 1) PG&E’s Electric Incident Investigation (EII) team is conducting a system of record audit for ignition events. The updated counts in Table 7.1 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. Changes are reflected in Purple font. 2) 7.1 Q1 2021 values are based on actuals. Projections from Q2 2021 - Q4 2022 are based on the respective 2020 values Updated comments for Table 7.1 (3/17/2021): PG&E’s Electric Incident Investigation (EII) team is conducting a system of record audit for ignition events. The updated counts in Table 7.1 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. Changes are reflected in Red font. Original Comments for Table 7.1: The fire ignition data provided in this table is based on fire incident reports filed with the CPUC annually in accordance with D.14-02-015. The ignition data provided in these tables was pulled from PG&E’s systems in mid-January 2021 and reflects preliminary data for two reasons: first, PG&E’s final 2020 fire ignition report is due on April 1, 2021 and 2020 data will be further reviewed in advance of that filing. Second, in late 2020 PG&E self-identified a data omission regarding prior year’s fire ignition data in the annual reports submitted and notified the CPUC of this issue on December 23, 2020. We anticipate completing an investigation into this issue to determine any fire ignition data that were omitted from our 2014-2019 reports by the end of the first quarter of 2021. Based on the results of our investigation, we plan to submit amendments to our annual reports and provide a supplemental filing updating the ignition data in Tables 7.1 and 7.2. More detail is provided in WMP Section 6.7 discussion.
Comments for Table 7.1: Key Recent and Projected Drivers of Ignition Probability, Last 5 Years (Distribution System): To the extent available, PG&E’s Integrated Logging Information System – Operations Data Base (ILIS-ODB) was used to provide the level of detail contained in Table 7.1 (Distribution) that includes both sustained and momentary outages experienced on our distribution system. When reviewing this data, the following should be noted: · Based on PG&E’s standard definition, a distribution wire down event results in a reportable outage event and occurs when a normally energized electric primary distribution conductor is broken, or stays intact, and falls from its intended position to rest on the ground or a foreign object. PG&E used this standard definition in this year’s report and thus it does not include any secondary related wire down events. However, it should also be noted that any primary or secondary wire down condition that resulted in an outage event is also reported in the distribution outage results. · In our 2020 WMP, PG&E utilized a different data extraction method attempting to identify a larger number of distribution wire down event conditions. However, it was subsequently determined this method resulted in an erroneously higher number of distribution wire down events due to various data issues such as momentary outages resulting from the same wire down event/condition that was also reported as a sustained outage. · For sub-cause category 2.a.”Connector damage or failure – Distribution,” it was assumed that the word “Connector” was meant to indicate “Conductor” since connector damage would typically be reported as splice damage. · For sub-cause category 8.a. “Unknown – Distribution,” this generally does not apply to distribution wire down events. · PG&E was unsure what was intended by the use of the term “Fuse damage or failure” because when a fuse isolates a fault condition, it will become permanently damaged and by design will no longer conduct electricity. For this subcategory, PG&E has interpreted it as only those outage events when a fuse was reported as the actual failed equipment. · PG&E does not have an outage cause classification that specifically matches the terms, “Tap damage or failure – Distribution” and “Tie wire damage or failure – Distribution” and thus did not use these categories in this report. · For “Wire-to-wire contact/Contamination,” PG&E typically does not use this term for distribution wire down events. In addition, PG&E typically uses contamination more as a condition of the equipment and not normally as a basic cause. For this category under the Distribution outages, PG&E assumed this cause refers to a Basic Cause of “Unknown” and a Fault Type of “Line to Line.” · For “Contamination – Distribution,” PG&E uses contamination more as a condition of the equipment and not as a basic cause. As such, PG&E does not have an outage classification that matches this term. · For “Unknown – Distribution” outages, this category omits outages reported with a Basic Cause of “Unknown” and a Fault Type of “Line to Line” covered as “Wire-to-wire contact/Contamination” outages noted in the above bullet item. · Due to their relatively small contribution, the Commission does not require transformer-only outages be reported in the annual electric system reliability metrics. However, transformer-only outages are reported within PG&E’s Field Automation System (FAS) and most were also reported in PG&E’s ILIS-ODB outage data base. PG&E is including these transformer-only outages in the WMP reporting to reflect the full picture of outage incidents which could have represented ignition potential. PG&E also further enhanced our reporting process/controls in September 2020 to ensure future transformer-only outages are fully reported in our ILIS-ODB outage data base and is working to improve outage cause reporting. · In Table 7.1 (Distribution), columns under the category ‘Projected risk events’ depict the projections in the respective years. Projections are based on forecasts submitted in the 2020 RAMP Report.
Comments for Table 7.1: Key Recent and Projected Drivers of Ignition Probability, Last 5 Years (Transmission System): PG&E’s Transmission Operations Tracking & Logging (TOTL) application was used as the primary data source for Table 7.1 (Transmission) which includes unplanned outages experienced on the transmission (i.e., >50 kV) system. Unplanned outages include those due to an “automatic” operation (i.e., the transmission line relayed automatically by a protective device (typically a circuit breaker) and either automatically tested OK, tested no good, or was set up not to test (e.g., automatics disabled or cut out for wildfire risk mitigation)). Unplanned outages also include those where the line was manually removed from service by Operations on an “emergency” basis, usually to repair or replace an imminent failure of an asset. Such emergency forced outages (EFOs) are taken without securing approval from the California Independent System Operator (CAISO). Planned or “scheduled” outages are not included. Scheduled outages differ from EFOs in that PG&E garnered CAISO approval prior to the line being removed from service. Based on PG&E’s standard definition, a transmission wire down event (similar to distribution) results in a reportable outage event (note: customers may or may not have been de-energized) and occurs when a normally energized electric transmission conductor fails in service and falls from its intended position to rest on the ground or a foreign object. • Sub-cause category 10.a. “Connector damage or failure – Transmission,” PG&E assumed that the word “Connector” was meant to indicate “Conductor” since connector damage would be reported separately in 10.b. • Sub-cause category 10.f. “Tap damage or failure – Transmission,” PG&E does not have an outage cause classification that specifically matches such. • Sub-cause category 10.g. “Tie wire damage or failure – Transmission” does not exist in PG&E outage reporting. • Sub-cause category 11.a. and 27.a. “Wire-to-wire contact/Contamination-Transmission” does not exist in PG&E transmission outage reporting and therefore has no data entries. • Unlike distribution outage reporting, cause category “Contamination – Transmission” is tracked and reported accordingly. • Every effort is made to minimize the number of outages assigned a cause category “Unknown – Transmission” for automatic type outages. At least one and sometimes more patrols are conducted after the outage to determine cause and certainly to find and correct any damaged equipment, usually with the help of fault location data provided by System Protection to help focus on the failure point. It’s also important to note that any outage due to animal contact is one where the patrol found a carcass to support the cause of animal, otherwise the choice “Unknown” is used. • Sub-cause category 26.c. “Fuse damage or failure” has no meaning for unplanned transmission outages. • Sub-cause category 26.h. “Crossarm damage or failure – Transmission” is not separately reported but included as part of reporting in the Sub-cause category “Pole damage or failure – Transmission,” if applicable. • Sub-cause category 26.j. “Recloser damage or failure – Transmission” represents outages where a circuit breaker failed in service and led to an outage. • Sub-cause category 26.l. “Sectionalizer damage or failure – Transmission” has no entries; rather, transmission lines are sectionalized using line switches, hence such failures are captured in cause Category 26.e. “Switch damage or failure- Transmission.” • In Table 7.1 (Transmission), columns under the category ‘Projected risk events’ depict the projections in the respective years. Projections are based on forecasts submitted in the 2020 RAMP Report.

## Table 7.2 (hidden)
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 7.2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. |  | l | [24 empty] | Please make all changes in PURPLE
| Date Modified | 2021-05-03 | Data from 2015 - 2019 should be actual numbers. 2020 - 2023 should be projected. In future submissions update projected numbers with actuals
[6 empty] | Number of ignitions by HFTD tier | [23 empty] | Projected ignitions by HFTD tier
| Table 7.2: Key recent and projected drivers of ignitions by HFTD region |  |  |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
|  | Metric type | # | Ignition driver | Are ignitions tracked for ignition driver? (yes / no) | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Notes on any changes made | Comments
x | Ignition - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | Yes | 45 | 1 | 38 | 24 | 45 | 0 | 40 | 23 | 76 | 0 | 59 | 36 | 58 | 0 | 32 | 36 | 76 | 0 | 46 | 16 | 61 | 0 | 34 | 26 | 13 | 0 | 7 | 12 | 61 | 0 | 32.5715 | 24.9076 | # ignitions
|  |  | 1.b. | Animal contact- Distribution | Yes | 37 | 0 | 6 | 2 | 29 | 0 | 6 | 2 | 47 | 0 | 8 | 1 | 37 | 0 | 14 | 5 | 57 | 0 | 10 | 1 | 36 | 0 | 9 | 0 | 4 | 0 | 1 | 0 | 36 | 0 | 8.6152 | 0 | # ignitions
|  |  | 1.c. | Balloon contact- Distribution | Yes | 19 | 0 | 4 | 0 | 11 | 0 | 2 | 0 | 11 | 0 | 0 | 0 | 10 | 0 | 3 | 0 | 15 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | # ignitions
|  |  | 1.d. | Vehicle contact- Distribution | Yes | 37 | 0 | 9 | 1 | 23 | 0 | 13 | 0 | 40 | 0 | 11 | 4 | 18 | 0 | 8 | 2 | 31 | 0 | 5 | 0 | 42 | 0 | 10 | 3 | 3 | 0 | 0 | 0 | 42 | 0 | 9.6982 | 2.9095 | # ignitions
|  |  | 1.e. | Other contact from object - Distribution | Yes | 11 | 0 | 2 | 0 | 5 | 0 | 0 | 0 | 7 | 0 | 2 | 0 | 36 | 0 | 10 | 7 | 18 | 0 | 5 | 0 | 21 | 0 | 9 | 1 | 1 | 0 | 1 | 0 | 21 | 0 | 8.766 | 0.974 | # ignitions
|  | 2. Equipment / facility failure - Distribution | 2.a. | Capacitor bank damage or failure- Distribution | Yes | 11 | 0 | 2 | 0 | 9 | 0 | 1 | 1 | 11 | 0 | 1 | 1 | 4 | 0 | 1 | 2 | 7 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | # ignitions
|  |  | 2.b. | Conductor damage or failure — Distribution | Yes | 37 | 0 | 10 | 2 | 46 | 0 | 7 | 5 | 53 | 0 | 14 | 3 | 27 | 0 | 11 | 2 | 67 | 0 | 11 | 3 | 63 | 0 | 8 | 0 | 7 | 0 | 3 | 1 | 63 | 0 | 7.7444 | 0 | # ignitions
|  |  | 2.c. | Fuse damage or failure - Distribution | Yes | 5 | 0 | 2 | 1 | 6 | 0 | 0 | 0 | 7 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 7 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 6.9775 | 0 | 1.9085 | 1.9085 | # ignitions
|  |  | 2.d. | Lightning arrestor damage or failure- Distribution | Yes | 6 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61462 | 0 | 0 | 0 | # ignitions
|  |  | 2.e. | Switch damage or failure- Distribution | Yes | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | # ignitions
|  |  | 2.f. | Pole damage or failure - Distribution | Yes | 4 | 0 | 1 | 1 | 4 | 0 | 2 | 0 | 11 | 0 | 1 | 0 | 7 | 0 | 4 | 0 | 6 | 0 | 0 | 0 | 8 | 0 | 4 | 0 | 2 | 0 | 0 | 0 | 8 | 0 | 3.8604 | 0 | # ignitions
|  |  | 2.g. | Insulator and brushing damage or failure - Distribution | Yes | 5 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 4 | 0 | 0 | 1 | 3 | 0 | 0 | 1 | 4 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 1.9151 | 0 | # ignitions
|  |  | 2.h. | Crossarm damage or failure - Distribution | Yes | 3 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 5 | 0 | 4 | 3 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | # ignitions
|  |  | 2.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0.97756 | 0 | # ignitions
|  |  | 2.j. | Recloser damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  |  | 2.k. | Anchor / guy damage or failure - Distribution | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  |  | 2.l. | Sectionalizer damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 2.m. | Connection device damage or failure - Distribution | Yes | 39 | 1 | 2 | 2 | 17 | 0 | 3 | 1 | 29 | 0 | 8 | 2 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 29 | 0 | 8 | 0 | 1 | 0 | 0 | 0 | 29 | 0 | 7.6548 | 0 | # ignitions
|  |  | 2.n. | Transformer damage or failure - Distribution | Yes | 14 | 0 | 4 | 0 | 9 | 0 | 2 | 0 | 18 | 1 | 3 | 1 | 10 | 0 | 2 | 5 | 19 | 0 | 1 | 0 | 15 | 0 | 6 | 0 | 2 | 0 | 0 | 0 | 15 | 0 | 5.7271 | 0 | # ignitions
|  |  | 2.o. | Other - Distribution | Yes | 16 | 0 | 3 | 2 | 22 | 0 | 3 | 0 | 18 | 0 | 5 | 2 | 29 | 0 | 8 | 7 | 21 | 0 | 3 | 1 | 21 | 0 | 3 | 0 | 2 | 0 | 0 | 0 | 21 | 0 | 2.9168 | 0 | # ignitions
|  | 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | Yes | 3 | 0 | 2 | 1 | 1 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 4. Contamination - Distribution | 4.a. | Contamination - Distribution | Yes | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | # ignitions
|  | 5. Utility work / Operation | 5.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | Yes | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | # ignitions
|  | 7. Other- Distribution | 7.a. | All Other- Distribution | Yes | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 5 | 0 | 0 | 2 | 6 | 0 | 5 | 0 | 4 | 0 | 1 | 0 | 4 | 0 | 2 | 2 | 0 | 0 | 1 | 0 | 4 | 0 | 1.9262 | 1.9262 | # ignitions
|  | 8. Unknown- Distribution | 8.a. | Unknown - Distribution | Yes | 20 | 0 | 3 | 4 | 8 | 0 | 1 | 1 | 2 | 0 | 2 | 0 | 18 | 0 | 6 | 1 | 12 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
x | Ignition - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 9.b. | Animal contact- Transmission | Yes | 2 | 0 | 4 | 0 | 5 | 0 | 4 | 0 | 0 | 0 | 3 | 2 | 5 | 0 | 4 | 3 | 7 | 0 | 1 | 0 | 3 | 0 | 3 | 2 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 2 | # ignitions
|  |  | 9.c. | Balloon contact- Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | # ignitions
|  |  | 9.d. | Vehicle contact- Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | # ignitions
|  |  | 9.e. | Other contact from object - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | # ignitions
|  | 10. Equipment / facility failure - Transmission | 10.a. | Capacitor bank damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.b. | Conductor damage or failure — Transmission | Yes | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | # ignitions
|  |  | 10.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.d. | Lightning arrestor damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.e. | Switch damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.f. | Pole damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.g. | Insulator and brushing damage or failure - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | # ignitions
|  |  | 10.h. | Crossarm damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  |  | 10.j. | Recloser damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.k. | Anchor / guy damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.l. | Sectionalizer damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.m. | Connection device damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.n. | Transformer damage or failure - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.o. | Other - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 2 | 0 | 1 | 0 | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | # ignitions
|  | 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 12. Contamination - Transmission | 12.a. | Contamination - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  | 13. Utility work / Operation | 13.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 15. Other- Transmission | 15.a. | All Other- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  | 16. Unknown- Transmission | 16.a. | Unknown - Transmission | Yes | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
Updated comments for Table 7.2 (5/3/2021): 1) PG&E’s Electric Incident Investigation (EII) team is conducting a system of record audit for ignition events. The updated counts in Table 7.2 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. Changes are reflected in Purple font. 2021 values are based on actuals for Q1. 2022 values are projections for the entire year based on 2020 as baseline. 2) Changes are reflected in Purple font. 2021 values are based on actuals for Q1. 2022 values are projections for the entire year based on 2020 as baseline. Updated comments for Table 7.2 (3/17/2021): PG&E’s Electric Incident Investigation (EII) team is conducting a system of record audit for ignition events. The updated counts in Table 7.2 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. Changes are reflected in Red font. Original Comments for Table 7.2: The fire ignition data provided in this table is based on fire incident reports filed with the CPUC annually in accordance with D.14-02-015. The ignition data provided in these tables was pulled from PG&E’s systems in mid-January 2021 and reflects preliminary data for two reasons: first, PG&E’s final 2020 fire ignition report is due on April 1, 2021 and 2020 data will be further reviewed in advance of that filing. Second, in late 2020 PG&E self-identified a data omission regarding prior year’s fire ignition data in the annual reports submitted and notified the CPUC of this issue on December 23, 2020. We anticipate completing an investigation into this issue to determine any fire ignition data that were omitted from our 2014-2019 reports by the end of the first quarter of 2021. Based on the results of our investigation, we plan to submit amendments to our annual reports and provide a supplemental filing updating the ignition data in Tables 7.1 and 7.2. More detail is provided in WMP Section 6.7 discussion.

## Table 8 (hidden)
| Utility | Pacific Gas & Electric Company
| Table No. | 8 | [25 empty] | UPDATE THESE NUMBERS AS OF Q1 - please make all changes in PURPLE
| Date Modified | 2021-05-03 | [17 empty] | 2018 plus 2019 |  |  |  | 2018-2020 |  |  |  | 2018-2021
Note: These columns are placeholders for future QR submissions.
| Table 8: State of service territory and utility equipment |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Notes on changes made | Comments
x | 1. State of service territory and equipment in urban areas | 1.a. | Circuit miles (including WUI and non-WUI) | [16 empty] | 15604 | 9 | 996 | 395 | 16296 | 1 | 1064 | 383 | 16274.1315 | 0.51861 | 1062.6752 | 379.7936 |  |  |  |  | Circuit miles |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.b. | Circuit miles in WUI | [16 empty] | 4195 | 8 | 721 | 340 | 4791 | 0 | 754 | 319 | 4783.7525 | 0.34496 | 753.7782 | 316.7063 |  |  |  |  | Circuit miles in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.c. | Number of critical facilities (including WUI and non-WUI) | [16 empty] | 17009 | 7 | 442 | 204 | 51008 |  | 1356 | 477 | 50957 |  | 1349 | 483 |  |  |  |  | Number of critical facilities |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.d. | Number of critical facilities in WUI | [16 empty] | 4213 | 5 | 402 | 172 | 13782 |  | 1051 | 421 | 13763 |  | 1047 | 426 |  |  |  |  | Number of critical facilities in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.e. | Number of customers (including WUI and non-WUI) | [16 empty] | 3966386 | 2172 | 76068 | 29274 | 4088697 | 9 | 79518 | 29936 | 4101111 | 9 | 79843 | 29990 |  |  |  |  | Number of customers |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.f. | Number of customers in WUI | [16 empty] | 1165448 | 1943 | 66452 | 27165 | 1195814 | 7 | 68926 | 27751 | 1198356 | 7 | 69246 | 27792 |  |  |  |  | Number of customers in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | [16 empty] | 120605 | 45 | 2084 | 727 | 158034 |  | 3384 | 1198 | 163799 |  | 3561 | 1281 |  |  |  |  | Number of customers belonging to access and functional needs populations |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.h. | Number of customers belonging to access and functional needs populations in WUI | [16 empty] | 38384 | 39 | 1895 | 688 | 51034 |  | 3070 | 1121 | 52951 |  | 3225 | 1198 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | [16 empty] | 2178.8 | 0 | 226.8 | 62.3 | 2177.9 |  | 226.7 | 61.6 | 2163.9435 |  | 226.8274 | 61.5733 |  |  |  |  | Circuit miles of overhead transmission lines |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.j. | Circuit miles of overhead transmission lines in WUI | [16 empty] | 516.9 | 0 | 87.6 | 37.5 | 517 |  | 88.5 | 36.8 | 512.9365 |  | 88.5507 | 36.7859 |  |  |  |  | Circuit miles of overhead transmission lines in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | [16 empty] | 14141 | 0.5 | 840.6 | 326.9 | 14118 | 0.5 | 836.9 | 321.3 | 14110.188 | 0.51861 | 835.8478 | 318.2203 |  |  |  |  | Circuit miles of overhead distribution lines |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.l. | Circuit miles of overhead distribution lines in WUI | [16 empty] | 4278.7 | 0.4 | 664.1 | 288.2 | 4274.2 | 0.3 | 665.1 | 282.3 | 4270.816 | 0.34496 | 665.2275 | 279.9204 |  |  |  |  | Circuit miles of overhead distribution lines in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.m. | Number of substations (including WUI and non-WUI) | [16 empty] | 314 | 0 | 18 | 0 | 323 | - | 19 | - | 83 |  | 17 | 297 |  |  |  |  | Number of substations |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.n | Number of substations in WUI | [16 empty] | 94 | 0 | 14 | 0 | 93 | - | 13 | - | 34 |  | 11 | 85 |  |  |  |  | Number of substations in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.o. | Number of weather stations (including WUI and non-WUI) | [18 empty] | 8 | 4 | 16 | 0 | 19 | 8 | 18 |  | 17 | 8 |  |  |  |  | Number of weather stations |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.p. | Number of weather stations in WUI | [18 empty] | 4 | 3 | 13 |  | 10 | 5 | 12 |  | 10 | 6 |  |  |  |  | Number of weather stations in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
x | 2. State of service territory and equipment in rural areas | 2.a. | Circuit miles (including WUI and non-WUI) | [16 empty] | 45119 | 87 | 17020 | 7229 | 44489 | 8 | 17321 | 7262 | 44478.9174 | 8.3745 | 17303.2666 | 7241.5593 |  |  |  |  | Circuit miles |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.b. | Circuit miles in WUI | [16 empty] | 7962 | 57 | 9479 | 4671 | 7932 | 4 | 10846 | 4698 | 7926.7234 | 4.0336 | 9543.4406 | 4689.8885 |  |  |  |  | Circuit miles in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.c. | Number of critical facilities (including WUI and non-WUI) | [16 empty] | 10134 | 42 | 1857 | 1009 | 19815 | 4 | 5223 | 2683 | 19800 | 4 | 5219 | 2674 |  |  |  |  | Number of critical facilities |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.d. | Number of critical facilities in WUI | [16 empty] | 2532 | 29 | 1153 | 690 | 7228 | 3 | 3471 | 1945 | 7225 | 3 | 3484 | 1946 |  |  |  |  | Number of critical facilities in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.e. | Number of customers (including WUI and non-WUI) | [16 empty] | 1051321 | 3877 | 249888 | 130048 | 974331 | 401 | 250571 | 131232 | 977770 | 404 | 250950 | 131366 |  |  |  |  | Number of customers |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.f. | Number of customers in WUI | [16 empty] | 483462 | 3493 | 116821 | 210802 | 467317 | 368 | 211175 | 117920 | 467962 | 371 | 211663 | 118158 |  |  |  |  | Number of customers in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | [16 empty] | 37116 | 158 | 11161 | 5530 | 43594 | 4 | 14670 | 7127 | 44945 | 4 | 15099 | 7379 |  |  |  |  | Number of customers belonging to access and functional needs populations |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.h. | Number of customers belonging to access and functional needs populations in WUI | [16 empty] | 18815 | 149 | 10055 | 5217 | 23914 | 4 | 13219 | 6729 | 24692 | 5 | 13624 | 6972 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | [16 empty] | 8747.9 | 3 | 2962.8 | 1095.7 | 8748.4 | 3 | 2962.2 | 1095.5 | 8739.1794 | 3.0302 | 2962.6336 | 1095.4483 |  |  |  |  | Circuit miles of overhead transmission lines |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.j. | Circuit miles of overhead transmission lines in WUI | [16 empty] | 917.8 | 1.3 | 830 | 291 | 917.8 | 1.3 | 829.2 | 290.7 | 915.3254 | 1.3172 | 829.1236 | 290.7175 |  |  |  |  | Circuit miles of overhead transmission lines in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | [16 empty] | 35771.5 | 5.4 | 14469.7 | 6281.4 | 35740.8 | 5.3 | 14358.9 | 6166.4 | 35739.738 | 5.3443 | 14340.633 | 6146.111 |  |  |  |  | Circuit miles of overhead distribution lines |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.l. | Circuit miles of overhead distribution lines in WUI | [16 empty] | 7008.8 | 2.7 | 8724.8 | 4446.9 | 7013.6 | 2.7 | 8712.9 | 4407.6 | 7011.398 | 2.7164 | 8714.317 | 4399.171 |  |  |  |  | Circuit miles of overhead distribution lines in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.m. | Number of substations (including WUI and non-WUI) | [16 empty] | 289 | 0 | 35 | 7 | 351 | 1 | 68 | 26 | 41 | 70 | 37 | 300 |  |  |  |  | Number of substations |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.n | Number of substations in WUI | [16 empty] | 67 | 0 | 27 | 18 | 66 |  | 29 | 19 | 12 |  | 17 | 299 |  |  |  |  | Number of substations in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.o. | Number of weather stations (including WUI and non-WUI) | [16 empty] | 60 |  | 251 | 156 | 137 | 0 | 400 | 203 | 147 |  | 407 | 208 |  |  |  |  | Number of weather stations |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.p. | Number of weather stations in WUI | [16 empty] | 17 |  | 89 | 72 | 42 | 0 | 132 | 89 | 42 |  | 129 | 92 |  |  |  |  | Number of weather stations in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
x | 3. State of service territory and equipment in highly rural areas | 3.a. | Circuit miles (including WUI and non-WUI) | [16 empty] | 7302 | 39 | 4539 | 825 | 7216 | 12 | 4024 | 675 | 7210.8087 | 12.0666 | 4017.3925 | 673.9189 |  |  |  |  | Circuit miles |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.b. | Circuit miles in WUI | [16 empty] | 563 | 9 | 1035 | 331 | 498 | 1 | 942 | 274 | 499.1867 | 1.2012 | 945.5779 | 274.4058 |  |  |  |  | Circuit miles in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.c. | Number of critical facilities (including WUI and non-WUI) | [16 empty] | 649 | 8 | 326 | 104 | 1087 | 2 | 797 | 297 | 1086 | 2 | 803 | 293 |  |  |  |  | Number of critical facilities |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.d. | Number of critical facilities in WUI | [16 empty] | 108 | 4 | 144 | 60 | 250 | 1 | 385 | 185 | 250 | 1 | 386 | 185 |  |  |  |  | Number of critical facilities in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.e. | Number of customers (including WUI and non-WUI) | [16 empty] | 39611 | 1303 | 33739 | 9840 | 37193 | 93 | 30689 | 8545 | 37221 | 93 | 30681 | 8546 |  |  |  |  | Number of customers |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.f. | Number of customers in WUI | [16 empty] | 14576 | 1068 | 22200 | 7919 | 13629 | 45 | 20733 | 7059 | 13625 | 45 | 20809 | 7080 |  |  |  |  | Number of customers in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | [16 empty] | 878 | 7 | 1098 | 231 | 981 |  | 1287 | 263 | 1000 |  | 1298 | 279 |  |  |  |  | Number of customers belonging to access and functional needs populations |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.h. | Number of customers belonging to access and functional needs populations in WUI | [16 empty] | 475 | 4 | 813 | 188 | 456 |  | 961 | 215 | 461 |  | 968 | 229 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | [16 empty] | 1691.7 | 3.1 | 1039.3 | 135.5 | 1691.8 | 3.1 | 1039.2 | 135.4 | 1691.7656 | 3.1029 | 1039.1241 | 135.3815 |  |  |  |  | Circuit miles of overhead transmission lines |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.j. | Circuit miles of overhead transmission lines in WUI | [16 empty] | 40.8 | 0 | 83.9 | 24.3 | 40.8 | 0 | 83.9 | 24.2 | 40.8276 | 0 | 83.8505 | 24.2348 |  |  |  |  | Circuit miles of overhead transmission lines in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | [16 empty] | 5579.8 | 9 | 3032.4 | 546.9 | 5524.2 | 9 | 2984.8 | 540.1 | 5519.0431 | 8.9638 | 2978.2684 | 538.5374 |  |  |  |  | Circuit miles of overhead distribution lines |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.l. | Circuit miles of overhead distribution lines in WUI | [16 empty] | 458.8 | 1.2 | 855.3 | 254.4 | 457.4 | 1.2 | 858.5 | 249.7 | 458.3591 | 1.2012 | 861.7274 | 250.171 |  |  |  |  | Circuit miles of overhead distribution lines in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.m. | Number of substations (including WUI and non-WUI) | [16 empty] | 51 | 0 | 22 | 6 | 57 |  | 19 | 5 | 67 |  | 9 | 0 |  |  |  |  | Number of substations |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.n | Number of substations in WUI | [16 empty] | 3 | 0 | 7 | 3 | 4 |  | 7 | 2 | 4 |  | 3 | 0 |  |  |  |  | Number of substations in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.o. | Number of weather stations (including WUI and non-WUI) | [16 empty] | 14 |  | 23 | 23 | 33 | 0 | 76 | 25 | 39 |  | 167 | 27 |  |  |  |  | Number of weather stations |  | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.p. | Number of weather stations in WUI | [16 empty] | 3 |  | 7 | 7 | 5 | 0 | 17 | 7 | 5 |  | 29 | 8 |  |  |  |  | Number of weather stations in WUI |  | See section 6.5 for a note on why 2015-2018 data is not available
Comments for Table 8: Table 8 seeks information regarding the current baseline state of HFTD and non-HFTD service territory, as located in urban versus rural versus highly rural areas, including a subset with the Wildland-Urban Interface (WUI). The WUI is defined as areas where homes are built near or among lands prone to wildland fires. PG&E identifies WUI areas within PG&E’s service territory based upon data provided by the University of Wisconsin-Madison SILVIS Lab, available here: http://silvis.forest.wisc.edu/data/wui-change/, shows the WUI areas within California as of 2010. Note that in Table 8 data for 2015-2018 has not been provided for two reasons: (1) PG&E planned and executed a multi-year project starting in 2013 that included converting legacy sources of electric facility information into a single enterprise GIS database. The conversion started in 2014 and was completed in 2018. This conversion was executed, reviewed, and accepted in phases for the entire PG&E service territory during these project years. There is no historical database of the electric facilities during the requested years from 2015 to 2018 that would contain a complete and accurate inventory of all the electric facilities metrics requested in Table 8. (2) PG&E’s GIS system is a dynamic ‘real-time’ system that reflects the current assets in PG&E’s service territory, when old assets are removed or replaced they are removed from the GIS system. Therefore, snapshots of asset information at prior points in history, before the WMP process began in 2019, are not available. Substation count includes facility type: Distribution Switching station, Junction, Power House, Power Plant, Substation & Transmission Switching Station. PG&E is currently reviewing the number of weather stations installed in 2020 and will update this table if needed when the review is complete.

## Table 9 (hidden)
| Utility | Pacific Gas & Electric Company | Notes: |  |  |  |  | Make changes in PURPLE. Provide explanation for change in the "Notes on changes made" column
| Table No. | 9 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Report net additions using positive numbers and net removals and undergrounding using negative numbers for circuit miles and numbers of substations. Only report changes expected within the target year.
| Date Modified | 2021-05-03 | For example, if 20 net overhead circuit miles are planned for addition by 2023, with 15 being added by 2022 and 5 more added by 2023, then report “15” for 2022 and “5” for 2023. Do not report cumulative change across years. In this case, do not report “20” for 2023, but instead the number planned to be added for just that year, which is “5”.
|  |  |  | Actual |  |  |  | Projected
| Table 9: Location of actual and planned utility equipment additions or removal year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Notes on changes made | Internal Comments
x | 1. Planned utility equipment net addition (or removal) year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines | -0.9 | 0 | -0.1 | -0.7 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles |  | SME for 2020: Kassim Visram SME for 2021/2022: Michelle Sakamoto
|  | 1.b. | Circuit miles of overhead distribution lines | -23 | 0 | -3.7 | -5.6 | 0 | 0 | 0 | 0 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles |  | SME for 2020: Kassim Visram SME for 2021/2022: Trish Fabris / Amanda Miller
|  | 1.c. | Circuit miles of overhead transmission lines in WUI | 0.1 | 0 | 0.9 | -0.7 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI |  | SME for 2020: Kassim Visram SME for 2021/2022: Michelle Sakamoto
|  | 1.d. | Circuit miles of overhead distribution lines in WUI | -4.5 | -0.1 | 1 | -5.9 | 0 | 0 | 0 | 0 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI |  | SME for 2020: Kassim Visram SME for 2021/2022: Trish Fabris / Amanda Miller
|  | 1.e. | Number of substations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations |  | SME: Aster Mehari / Buba Jallow
|  | 1.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI |  | SME: Aster Mehari / Buba Jallow
|  | 1.g. | Number of weather stations | 16 | - | 9 | 6 | 10 | 0 | 21 | 2 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations |  | SME: Kathleen Gonos
|  | 1.h. | Number of weather stations in WUI | 12 | - | 5 | 4 | 1 | 0 | 1 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations in WUI |  | SME: Kathleen Gonos
x | 2. Planned utility equipment net addition (or removal) year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines | 0.5 | 0 | -0.6 | -0.2 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles |  | SME for 2020: Kassim Visram SME for 2021/2022: Michelle Sakamoto
|  | 2.b. | Circuit miles of overhead distribution lines | -30.7 | -0.1 | -110.8 | -115 | 0 | 0 | -2.4 | -0.5 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles |  | SME for 2020: Kassim Visram SME for 2021/2022: Trish Fabris / Amanda Miller
|  | 2.c. | Circuit miles of overhead transmission lines in WUI | 0 | 0 | -0.8 | -0.3 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI |  | SME for 2020: Kassim Visram SME for 2021/2022: Michelle Sakamoto
|  | 2.d. | Circuit miles of overhead distribution lines in WUI | 4.8 | 0 | -11.9 | -39.3 | 0 | 0 | -0.6 | -0.1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI |  | SME for 2020: Kassim Visram SME for 2021/2022: Trish Fabris / Amanda Miller
|  | 2.e. | Number of substations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | -1 | -1 | Number of substations |  | SME: Aster Mehari / Buba Jallow
|  | 2.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | Number of substations in WUI |  | SME: Aster Mehari / Buba Jallow
|  | 2.g. | Number of weather stations | 77 | 0 | 149 | 47 | 24 | 1 | 30 | 15 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations |  | SME: Kathleen Gonos
|  | 2.h. | Number of weather stations in WUI | 25 | 0 | 43 | 17 | 8 | 0 | 8 | 5 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations in WUI |  | SME: Kathleen Gonos
x | 3. Planned utility equipment net addition (or removal) year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines | 0.1 | 0 | -0.1 | -0.1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles |  | SME for 2020: Kassim Visram SME for 2021/2022: Michelle Sakamoto
|  | 3.b. | Circuit miles of overhead distribution lines | -55.6 | 0 | -47.6 | -6.8 | -0.8 | 0 | -3.3 | -0.8 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles |  | SME for 2020: Kassim Visram SME for 2021/2022: Trish Fabris / Amanda Miller
|  | 3.c. | Circuit miles of overhead transmission lines in WUI | 0 | 0 | 0 | -0.1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI |  | SME for 2020: Kassim Visram SME for 2021/2022: Michelle Sakamoto
|  | 3.d. | Circuit miles of overhead distribution lines in WUI | -1.4 | 0 | 3.2 | -4.7 | 0 | 0 | -2.12 | -0.2 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI |  | SME for 2020: Kassim Visram SME for 2021/2022: Trish Fabris / Amanda Miller
|  | 3.e. | Number of substations | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations |  | SME: Aster Mehari / Buba Jallow
|  | 3.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI |  | SME: Aster Mehari / Buba Jallow
|  | 3.g. | Number of weather stations | 20 | - | 140 | 2 | 7 | 0 | 0 | 1 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations |  | SME: Kathleen Gonos
|  | 3.h. | Number of weather stations in WUI | 7 | - | 21 | 0 | 3 | 0 | 0 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations in WUI |  | SME: Kathleen Gonos
Notes for Table 9:
The data presented in this table are based on the best knowledge that PG&E has as of January 2021. As better data becomes available, this will be updated in the quarterly updates.
Note 1: For transmission line additions and removals for 2021 and 2022, project prioritization and timing have not been fully determined or mapped.
Note 2: PG&E's weather station goal is to install 1,300 by the end of 2021 and then assess the need for further locations. Therefore, weather station additions for 2022 are undetermined at this time.
Other comments:
1) The data presented for 2021 Distribution removals/additions represents the work for removal of idle facilities. There are many other reasons that conductor may be added or removed.
2) The 2020 Actual data was derived by subtracting the 2019 data from the 2020 data in Table 8, and reflects the total net change in the system year-over-year.
3) The same layers used in Table 8 have been used to determine Population Density, HFTD, and WUI.
4) PG&E is currently reviewing the number of weather stations installed in 2020 and will update this table if needed when the review is complete.

## Table 10 (hidden)
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 10 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. |  |  |  |  | Make changes in PURPLE. Provide explanation for change in the "Notes on changes made" column
| Date Modified | 2021-02-05 | In future submissions update planned upgrade numbers with actuals
|  |  | In the comments column on the far-right, enter the relevant program target(s) associated | Actual |  |  |  | Projected
| Table 10: Location of actual and planned utility infrastructure upgrades year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comment | Notes on comments made | Internal Comments
x | 1. Planned utility infrastructure upgrades year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles | See Note 1 & Note 4 |  | SME for 2020: Michelle Sakomoto / FERC Form 1 SME for 2021/2022: Patsy Baynard
|  | 1.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 0.3 | 0 | 1.4 | 4.1 | 6.6 | 0 | 0 | 4.6 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles | See Note 3 & Note 5 |  | SME for 2020: Gary Long SME for 2021/2022: Jean Pierre Jodoin (Merih)
|  | 1.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles in WUI | See Note 1 & Note 4 |  | SME for 2020: Michelle Sakomoto / FERC Form 1 SME for 2021/2022: Patsy Baynard
|  | 1.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 0.3 | 0 | 1.4 | 4.1 | 6.6 | 0 | 0 | 4.6 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles in WUI | See Note 3 & Note 5 |  | SME for 2020: Gary Long SME for 2021/2022: Jean Pierre Jodoin
|  | 1.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Number of substations | PG&E is interpreting substation enhancements to be significant enhancement to substation buses. |  | SME: Aster Mehari / Buba Jallow
|  | 1.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Number of substations in WUI | PG&E is interpreting substation enhancements to be significant enhancement to substation buses. |  | SME: Aster Mehari / Buba Jallow
|  | 1.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations | See Note 2 |  | SME: Kathleen Gonos
x |  | 1.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | See Note 2 |  | SME: Kathleen Gonos
| 2. Planned utility infrastructure upgrades year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles | See Note 1 & Note 4 |  | SME for 2020: Michelle Sakomoto / FERC Form 1 SME for 2021/2022: Patsy Baynard
|  | 2.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 1 | 0 | 5.1 | 114.3 | 3.3 | 0 | 5.8 | 26.8 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles | See Note 3 & Note 5 |  | SME for 2020: Gary Long SME for 2021/2022: Jean Pierre Jodoin
|  | 2.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles in WUI | See Note 1 & Note 4 |  | SME for 2020: Michelle Sakomoto / FERC Form 1 SME for 2021/2022: Patsy Baynard
|  | 2.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 0.7 | 0 | 1.8 | 104.5 | 3.3 | 0 | 2.4 | 20 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles in WUI | See Note 3 & Note 5 |  | SME for 2020: Gary Long SME for 2021/2022: Jean Pierre Jodoin
|  | 2.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations | PG&E is interpreting substation enhancements to be significant enhancement to substation buses. |  | SME: Aster Mehari / Buba Jallow
|  | 2.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | PG&E is interpreting substation enhancements to be significant enhancement to substation buses. |  | SME: Aster Mehari / Buba Jallow
x |  | 2.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations | See Note 2 |  | SME: Kathleen Gonos
|  | 2.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | See Note 2 |  | SME: Kathleen Gonos
| 3. Planned utility infrastructure upgrades year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles | See Note 1 & Note 4 |  | SME for 2020: Michelle Sakomoto / FERC Form 1 SME for 2021/2022: Patsy Baynard
|  | 3.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 0 | 0 | 1.8 | 1.1 | 0 | 0 | 4.2 | 0.9 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles | See Note 3 & Note 5 |  | SME for 2020: Gary Long SME for 2021/2022: Jean Pierre Jodoin
|  | 3.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles in WUI | See Note 1 & Note 4 |  | SME for 2020: Michelle Sakomoto / FERC Form 1 SME for 2021/2022: Patsy Baynard
|  | 3.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 0 | 0 | 0.5 | 1.1 | 0 | 0 | 0.3 | 0.1 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles in WUI | See Note 3 & Note 5 |  | SME for 2020: Gary Long SME for 2021/2022: Jean Pierre Jodoin
|  | 3.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations | PG&E is interpreting substation enhancements to be significant enhancement to substation buses. |  | SME: Aster Mehari / Buba Jallow
|  | 3.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | PG&E is interpreting substation enhancements to be significant enhancement to substation buses. |  | SME: Aster Mehari / Buba Jallow
|  | 3.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations | See Note 2 |  | SME: Kathleen Gonos
|  | 3.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | See Note 2 |  | SME: Kathleen Gonos
Comments for Table 10: The data presented in Table 10 are based on the best knowledge that PG&E has as of January 2021. As better data becomes available, this will be updated in the quarterly updates. Note 1: PG&E reconductored approximately 103 HFTD and 127 Non-HFTD miles of transmission conductor across its service territory in 2020, but all jobs have not been mapped into the GIS system in order to break the data down as required by this table. Note 2: PG&E has no plans to upgrade or modify existing weather stations. Note 3: PG&E is in the process of replanning Distribution system hardening work for 2021 and 2022. 2021 data is shown as of the time of submission, but does not reflect all projects that will be completed in 2021 and will be revised in future submissions. Because of this replanning, 2022 planning is not yet complete. Note 4: PG&E does not have an equivalent "system hardening" program for transmission conductor, but PG&E is planning to reconductor 92 HFTD miles and 90 Non-HFTD miles in 2021. The preliminarily planned jobs have not been mapped in order to break the data down for this table. There will also be other upgrades during 2021 and 2022 to transmission lines in the normal course of PG&E’s business. Note 5: PG&E hardened 342 miles in 2020 but not all projects have been mapped as of January 2021 and therefore may not be included in this data. Other comments: 1) The same layers used in Table 8 have been used to determine Population Density, HFTD, and WUI.

## Table 11
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 11 | "PSPS" = Public Safety Power Shutoff
Date Modified | 2021-09-30
|  |  | Section 1: Historical Data (Event Actuals) | [10 empty] | Section 2: 2021 PSPS Protocols Forecasted data without 2021 Revised WMP Mitigations | [5 empty] | Section 3: 2021 PSPS Protocols Forecasted data with 2021 Revised WMP Mitigations
Table 11: Recent use of PSPS and other PSPS metrics | [7 empty] | Q1 | Q2 | Q3 | Q4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Baseline Forecast Comments
1. Recent use of PSPS | 1.a. | Frequency of PSPS events (total) | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 2 | 4 | 1 | 0 | 1 | 3.75 | 0 | 0 | 1 | 3.75 | 1 | 3.75 | 0 | 0 | 1 | 3.75 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per quarter or year. Only include events in which de-energization ultimately occurred | Base Forecast: 4-year average using backast re-analysis with 2021 criteria
| 1.b. | Scope of PSPS events (total) | 0 | 0 | 0 | 41 | 13122 | 0 | 0 | 408 | 1924 | 18 | 0 | 94.6924 | 597.3646 | 0 | 0 | 94.6924 | 597.3646 | 87.117 | 549.5754 | 0 | 0 | 87.117 | 549.5754 | Circuit-events, measured as the number of circuits de-energized in part or in whole by each PSPS event, summed across each quarter or year. | Base Forecast: 4-year average using backast re-analysis with 2021 criteria
| 1.c. | Duration of PSPS events (total), in customer-hours | 0 | 0 | 0 | 1517371 | 90740214 | 0 | 0 | 7540563.6175 | 14736124.6822 | 347470.136 | 0 | 2526801.9032 | 15941513.9692 | 0 | 0 | 2526801.9032 | 15941513.9692 | 2324657.7509 | 14666192.8517 | 0 | 0 | 2324657.7509 | 14666192.8517 | Customer hours of de-energization due to PSPS per quarter or year | Base Forecast: 4-year average using backast re-analysis with 2021 criteria
2. Customer hours of PSPS and other outages | 2.a. | Customer hours of planned outages including PSPS (total) | 1400185 | 1390308 | 1513383 | 4015315 | 101200587 | 508425 | 439423 | 8384809 | 15784931.2 | 919249 | 856249.5833 | 3127488.989 | 16788407.989 | 392564 | 507422.8 | 3127488.989 | 16788407.989 | 2873777.4509 | 15187749.8517 | 392564 | 507422.8 | 2873777.4509 | 15187749.8517 | Total customer hours of planned outages per quarter or year | Base Forecast: Non-PSPS outages (Historical Average) PSPS Planned Outages (4-year average backcast re-analysis with 2021 criteria)
| 2.b. | Customer hours of unplanned outages, not including PSPS (total) | 11961864 | 9745978 | 32897043 | 24589665 | 28791354 | 7070484 | 3075467 | 6303666 | 3370778.6 | 15076957 | 3569115.4833 | 3353012.2 | 7033480.7 | 7156787 | 3252816.4 | 3353012.2 | 7033480.7 | 3353012.2 | 7033480.7 | 7156787 | 3252816.4 | 3353012.2 | 7033480.7 | Total customer hours of unplanned outages per quarter or year | Base Forecast: Non-PSPS outages (Historical Average)
| 2.c. | System Average Interruption Duration Index (SAIDI) (including PSPS) | 147.2 | 121.9 | 374.3 | 309.3 | 1395.4 | 81.4 | 37.7 | 157.7 | 204.1 | 170.3 | 47.1 | 1.1817 | 4.3419 | 1.3767 | 0.685 | 1.1817 | 4.3419 | 1.1354 | 4.0501 | 1.3767 | 0.685 | 1.1354 | 4.0501 | SAIDI index value (hours) = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption in hours * # of customer interruptions) / Total number of customers served | Base Forecast: Non-PSPS outages (Historical Average) PSPS Planned Outages (4-year average backcast re-analysis with 2021 criteria)
| 2.d. | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | 147.2 | 121.9 | 374.3 | 292.9 | 334.4 | 81.4 | 37.7 | 73.6 | 44.8 | 167.1 | 47.1 | 0.71167 | 1.3767 | 1.3767 | 0.685 | 0.71167 | 1.3767 | 0.71167 | 1.3767 | 1.3767 | 0.685 | 0.71167 | 1.3767 | SAIDI index value (hours) = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption in hours * # of customer interruptions) / Total number of customers served | Base Forecast: Non-PSPS outages (Historical Average)
| 2.e. | System Average Interruption Frequency Index (SAIFI) (including PSPS) | 1.053 | 1.102 | 1.549 | 1.175 | 1.996 | 0.344 | 0.309 | 0.493 | 0.415 | 0.458 | 0.35 | 0.32861 | 0.44519 | 0.376 | 0.324 | 0.32861 | 0.44519 | 0.3276 | 0.43893 | 0.376 | 0.324 | 0.3276 | 0.43893 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | Base Forecast: Non-PSPS outages (Historical Average) PSPS Planned Outages (4-year average backcast re-analysis with 2021 criteria)
| 2.f. | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | 1.053 | 1.102 | 1.549 | 1.165 | 1.596 | 0.344 | 0.309 | 0.449 | 0.337 | 0.457 | 0.35 | 0.316 | 0.367 | 0.376 | 0.324 | 0.316 | 0.367 | 0.316 | 0.367 | 0.376 | 0.324 | 0.316 | 0.367 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | Base Forecast: Non-PSPS outages (Historical Average)
3. Critical infrastructure impacted by PSPS | 3.a. | Critical infrastructure outage customer-hours due to PSPS | 0 | 0 | 0 | 23257 | 810940.6833 | 0 | 0 | 139703.1325 | 282103.9075 | 2 | 0 | 41972.6472 | 258786.8831 | 0 | 0 | 41972.6472 | 258786.8831 | 37842.5387 | 233322.2538 | 0 | 0 | 37842.5387 | 233322.2538 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per quarter or year | Base Forecast: 4-year average using backast re-analysis with 2021 criteria
4. Community outreach of PSPS metrics | 4.a. | # of customers impacted by PSPS | 0 | 0 | 0 | 60806 | 2036019 | 0 | 0 | 232875 | 416810 | 5099 | 0 | 69189.0085 | 428929.2892 | 0 | 0 | 69189.0085 | 428929.2892 | 63653.8878 | 394614.946 | 0 | 0 | 63653.8878 | 394614.946 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | Base Forecast: 4-year average using backast re-analysis with 2021 criteria
| 4.b. | # of medical baseline customers impacted by PSPS | 0 | 0 | 0 | 2529 | 83333 | 0 | 0 | 14741 | 27065 | 274 | 0 | 5082.2535 | 30382.4579 | 0 | 0 | 5082.2535 | 30382.4579 | 4675.6732 | 27951.8612 | 0 | 0 | 4675.6732 | 27951.8612 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | Base Forecast: 4-year average using backast re-analysis with 2021 criteria
| 4.c. | # of customers notified prior to initiation of PSPS event | 0 | 0 | 0 | 69229 | 2517105 | 0 | 0 | 293681 | 735708 | 22433 | 0 | 91364.6491 | 566404.6188 | 0 | 0 | 91364.6491 | 566404.6188 | 84055.4771 | 521092.2493 | 0 | 0 | 84055.4771 | 521092.2493 | # of customers notified of PSPS event prior to initiation quarter or year. (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | Base Forecast: 4-year average using backast re-analysis with 2021 criteria
| 4.d. | # of medical baseline customers notified prior to initiation of PSPS event | 0 | 0 | 0 | 3610 | 105606 | 0 | 0 | 22927 | 47914 | 1174 | 0 | 7166.0184 | 42839.5108 | 0 | 0 | 7166.0184 | 42839.5108 | 6592.7369 | 39412.35 | 0 | 0 | 6592.7369 | 39412.35 | # of customers notified of PSPS event prior to initiation per quarter or year. (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | Base Forecast: 4-year average using backast re-analysis with 2021 criteria
| 4.e. | % of customers notified prior to a PSPS event impacting them | 0 | 0 | 0 | 1.1385 | 1.2363 | 0 | 0 | 1.2611 | 1.7651 | 4.3995 | 0 | 1.3205 | 1.3205 | 1.3205 | 1.3205 | 1.3205 | 1.3205 | 132.1% | 132.1% | 132.1% | 132.1% | 132.1% | 132.1% | =4.c. / 4.a. | Base Forecast: 2-year historical average. Kept the percentage fixed based on previous table
| 4.f. | % of medical baseline customers notified prior to a PSPS event impacting them | 0 | 0 | 0 | 1.4274 | 1.2673 | 0 | 0 | 1.5553 | 1.7703 | 4.2847 | 0 | 1.41 | 1.41 | 1.41 | 1.41 | 1.41 | 1.41 | 141% | 141% | 141% | 141% | 141% | 141% | =4.d. / 4.b. | Base Forecast: 2-year historical average. Kept the percentage fixed based on previous table
5. Other PSPS metrics | 5.a. | Number of PSPS events triggered where no de-energization occurred | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | Number of instances where utility notified the public of a potential PSPS event but no de-energization followed per quarter or year. | Base Forecast: 2-year historical average.
| 5.b. | Number of customers located on de-energized circuits | 0 | 0 | 0 | 60806 | 2831593 | 0 | 0 | 320057 | 929101 | 24021 | 0 | 166459.61 | 1126836.0328 | 0 | 0 | 166459.61 | 1126836.0328 | 153142.8412 | 1036689.1502 | 0 | 0 | 153142.8412 | 1036689.1502 | For the circuits de-energized for PSPS, the total customers served by the de-energized circuits. This is summed across all PSPS events per quarter or year. This customer count may be larger than the number of customers de-energized in each PSPS event, if only portions of circuits were de-energized due to sectionalization. | Base Forecast: 2-year historical average of % customers sectionalized * # of customers impacted by PSPS (4.a.)
| 5.c. | Customer hours of PSPS per RFW OH circuit mile day | 0 | 0 | 0 | 2.7985 | 195.9072 | 0 | 0 | 31.9665 | 40.353 | 6786.71 | 0 | 8.6211 | 23.5068 | 0 | 0 | 8.6211 | 23.5068 | 7.7727 | 21.1937 | 0 | 0 | 7.7727 | 21.1937 | =1.c. / RFW OH circuit mile days in time period | Base Forecast: 2-year historical average.
| 5.d. | Frequency of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | Events over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Base Forecast: 2-year historical average.
| 5.e. | Scope of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 365568 | 0 | 0 | 0 | 0 | 4696 | 0 | 0 | 112681.9929 | 0 | 0 | 0 | 112681.9929 | 0 | 101594.0848 | 0 | 0 | 0 | 101594.0848 | Estimated customers impacted over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Base Forecast: 4-year average sized event
| 5.f. | Duration of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 5749687 | 0 | 0 | 0 | 0 | 38.6 | 0 | 0 | 3858943.2726 | 0 | 0 | 0 | 3858943.2726 | 0 | 3479223.2546 | 0 | 0 | 0 | 3479223.2546 | Customer hours over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Base Forecast: 4-year average sized event
Updated comments for Table 11 (9/30/2021): 1. PG&E submits this updated Table 11 in connection with our response to Remedy PGE-21-29 from the OEIS Final Action Statement on the 2021 Wildfire Mitigation Plan (WMP). Updated comments for Table 11 (8/2/2021): 1. Replace Q2 projected with Q2 actuals data. Updated comments for Table 11 (6/3/2021): 1. PG&E submits this updated Table 11 in connection with our response to Critical Issue No. PGE-01 from the WSD. For further information on the data included in the revised Table 11, please reference our response to Critical Issue No. PGE-01 in our updated 2021 Wildfire Mitigation Plan provided on June 3, 2021. Updated comments for Table 11 (3/17/2020): 1. Removed whole number rounding for PSPS events which updated fields reliant on PSPS events per quarter. 2. Changed denominator of past PSPS lookback and event data from 11 to 10 to reflect the past 11 years of data (10 year lookback plus 2020 actuals) which updated fields reliant on duration, customer impact and scope. 3. Utilized actual event customer hours for 2020 which updated fields reliant on duration. 4. Changed denominator from 10-year average to 2-year average. 5. 2020 Q3 data for critical infrastructure updated. Original Comments for Table 11: PG&E has outlined the past and forecasted PSPS metrics in Table 11, which is utilizing historic recorded data for actuals and an analysis of the past ten years of weather data to provide the forecasted metrics. The forecasted numbers are largely weather dependent and do not include any event size or length reductions from the 2020 planned work. Further information historical lookback of the last ten years of weather data and its uses and limitations can be found in Section 8.1. PG&E projected PSPS metrics in 2021, and Table 11 keeps those values static for 2022. PG&E anticipates continued improvement from 2021 to 2022, but we do not yet have analysis on the value of those improvements. Thus, for the purposes of this table, no improvements have been assumed.

## Table 11 - Lookup (hidden)
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 11 | "PSPS" = Public Safety Power Shutoff | [9 empty] | REPLACE WITH Q1 ACTUALS HERE - make changes in PURPLE
Date Modified | 2021-05-03 | In future submissions update planned upgrade numbers with actuals
|  |  | Actual | [9 empty] | Projected (average of historical data) | [6 empty] | With Potential Reductions from 2021 work | With Potential Reductions from 2021 work | [7 empty] | With Potential Reductions from 2021 work and potential Judge Alsup tree overstrike criteria
Table 11: Recent use of PSPS and other PSPS metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | PMO NOTES | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 |  | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments | Draft Notes
1. Recent use of PSPS | 1.a. | Frequency of PSPS events (total) | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 2 | 4 | 1 | 0.18182 | 0.45455 | 2 | 0.3 | 0.18182 | 0.45455 | 2 | Frequency Multiplier | 0.27273 | 0.18182 | 0.45455 | 2 | 0.3 | 0.18182 | 0.45455 | 2 | 0.27273 | 0.18182 | 0.45455 | 2 | 0.3 | 0.18182 | 0.45455 | 2 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year. Only include events in which de-energization ultimately occurred | Base Forecast: 11-year average using backcast re-analysis
| 1.b. | Scope of PSPS events (total) | 0 | 0 | 0 | 41 | 13122 | 0 | 0 | 408 | 1924 | 18 | 3.2066 | 14.6281 | 550.7273 | 4.8099 | 3.2066 | 14.6281 | 550.7273 | Size Multiplier | 4.8099 | 3.2066 | 14.6281 | 550.7273 | 5 | 3.2066 | 14.6281 | 550.7273 | 4.8099 | 3.2066 | 14.6281 | 550.7273 | 5 | 3.2066 | 14.6281 | 550.7273 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | Base Forecast: 11-year average using backcast re-analysis
| 1.c. | Duration of PSPS events (total) | 0 | 0 | 0 | 1517371 | 90740214 | 0 | 0 | 7540563.6175 | 14736124.6822 | 347470.136 | 1140763.0455 | 947652.0561 | 22605223.0166 | 1168058 | 1140763.0455 | 947652.0561 | 22605223.0166 | Duration Multiplier | 1168057.8727 | 1140763.0455 | 947652.0561 | 22605223.0166 | 1168058 | 1140763.0455 | 947652.0561 | 22605223.0166 | 1168057.8727 | 1140763.0455 | 947652.0561 | 22605223.0166 | 1168058 | 1140763.0455 | 947652.0561 | 22605223.0166 | Customer hours per year | Base Forecast: 11-year average using backcast re-analysis | Input estimate for restoration time (1 hours of switching time and 9 with 10% improvement multiplier hours of restoration)
2. Customer hours of PSPS and other outages | 2.a. | Customer hours of planned outages including PSPS (total) | 1400185 | 1390308 | 1513383 | 4015315 | 101200587 | 508425 | 439423 | 8384809 | 15784931.2 | 919249 | 1648185.8455 | 1496771.7561 | 23126780.0166 | 1560622 | 1648185.8455 | 1496771.7561 | 23126780.0166 | PSPS portion only * duration multiplier * size multipliers | 1560621.8727 | 1648185.8455 | 1496771.7561 | 23126780.0166 | 1560622 | 1648185.8455 | 1496771.7561 | 23126780.0166 | 1560621.8727 | 1648185.8455 | 1496771.7561 | 23126780.0166 | 1560622 | 1648185.8455 | 1496771.7561 | 23126780.0166 | Total customer hours of planned outages per year | Base Forecast: 10-year historical average plus 11-year average using backcast re-analysis | Apply to only restoration portion of outage
| 2.b. | Customer hours of unplanned outages, not including PSPS (total) | 11961864 | 9745978 | 32897043 | 24589665 | 28791354 | 7070484 | 3075467 | 6303666 | 3370778.6 | 15076957 | 3252816.4 | 3353012.2 | 7033480.7 | 7156787 | 3252816.4 | 3353012.2 | 7033480.7 | N/A Same | 7156787 | 3252816.4 | 3353012.2 | 7033480.7 | 7156787 | 3252816.4 | 3353012.2 | 7033480.7 | 7156787 | 3252816.4 | 3353012.2 | 7033480.7 | 7156787 | 3252816.4 | 3353012.2 | 7033480.7 | Total customer hours of unplanned outages per year | Base Forecast: 10-year historical average
| 2.c. | System Average Interruption Duration Index (SAIDI) (including PSPS) | 147.2 | 121.9 | 374.3 | 309.3 | 1395.4 | 81.4 | 37.7 | 157.7 | 204.1 | 170.3 | 53.5768 | 53.0647 | 329.8391 | 95.4 | 53.5768 | 53.0647 | 329.8391 | PSPS portion only * duration multiplier | 95.3753 | 53.5768 | 53.0647 | 329.8391 | 95.4 | 53.5768 | 53.0647 | 329.8391 | 95.3753 | 53.5768 | 53.0647 | 329.8391 | 95.4 | 53.5768 | 53.0647 | 329.8391 | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | Base Forecast: 10-year historical average plus 11-year average using backcast re-analysis
| 2.d. | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | 147.2 | 121.9 | 374.3 | 292.9 | 334.4 | 81.4 | 37.7 | 73.6 | 44.8 | 167.1 | 41.1 | 42.7 | 82.6 | 82.6 | 41.1 | 42.7 | 82.6 | N/A Same | 82.6 | 41.1 | 42.7 | 82.6 | 82.6 | 41.1 | 42.7 | 82.6 | 82.6 | 41.1 | 42.7 | 82.6 | 82.6 | 41.1 | 42.7 | 82.6 | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | Base Forecast: 10-year historical average | OMT Team has provided 10-year average up to 2019. Need 2020 data once complete and to have it broken out by quarter.
| 2.e. | System Average Interruption Frequency Index (SAIFI) (including PSPS) | 1.053 | 1.102 | 1.549 | 1.175 | 1.996 | 0.344 | 0.309 | 0.493 | 0.415 | 0.458 | 0.324 | 0.34501 | 0.60141 | 0.4 | 0.324 | 0.34501 | 0.60141 | PSPS portion only * frequency multiplier | 0.376 | 0.324 | 0.34501 | 0.60141 | 0.4 | 0.324 | 0.34501 | 0.60141 | 0.376 | 0.324 | 0.34501 | 0.60141 | 0.4 | 0.324 | 0.34501 | 0.60141 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | Base Forecast: 10-year historical average plus 11-year average using backcast re-analysis
| 2.f. | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | 1.053 | 1.102 | 1.549 | 1.165 | 1.596 | 0.344 | 0.309 | 0.449 | 0.337 | 0.457 | 0.324 | 0.316 | 0.367 | 0.4 | 0.324 | 0.316 | 0.367 | N/A Same | 0.376 | 0.324 | 0.316 | 0.367 | 0.4 | 0.324 | 0.316 | 0.367 | 0.376 | 0.324 | 0.316 | 0.367 | 0.4 | 0.324 | 0.316 | 0.367 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | Base Forecast: 10-year historical average | OMT Team has provided 10-year average up to 2019. Need 2020 data once complete and to have it broken out by quarter.
3. Critical infrastructure impacted by PSPS | 3.a. | Critical infrastructure impacted by PSPS | 0 | 0 | 0 | 23257 | 810940.6833 | 0 | 0 | 139703.1325 | 282103.9075 | 2 | 11006.3909 | 18022.0757 | 225290.3007 | 9754 | 11006.3909 | 18022.0757 | 225290.3007 | Size Multiplier | 9754.3455 | 11006.3909 | 18022.0757 | 225290.3007 | 9754 | 11006.3909 | 18022.0757 | 225290.3007 | 9754.3455 | 11006.3909 | 18022.0757 | 225290.3007 | 9754 | 11006.3909 | 18022.0757 | 225290.3007 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per year | Base Forecast: 11-year average using backcast re-analysis | Asking team if there is a 10-year re-analysis on critical infrastructure How do we calculate duration? Currently using 2-year historical average Do we need a smaller PSPS metric multiplier?
4. Community outreach of PSPS metrics | 4.a. | # of customers impacted by PSPS | 0 | 0 | 0 | 60806 | 2036019 | 0 | 0 | 232875 | 416810 | 5099 | 25555 | 30103.1818 | 478502.2727 | 31453 | 25555 | 30103.1818 | 478502.2727 | Size Multiplier | 31453.4545 | 25555 | 30103.1818 | 478502.2727 | 31453 | 25555 | 30103.1818 | 478502.2727 | 31453.4545 | 25555 | 30103.1818 | 478502.2727 | 31453 | 25555 | 30103.1818 | 478502.2727 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | Base Forecast: 11-year average using backcast re-analysis
| 4.b. | # of medical baseline customers impacted by PSPS | 0 | 0 | 0 | 2529 | 83333 | 0 | 0 | 14741 | 27065 | 274 | 882.0909 | 1998.5455 | 16996.0909 | 922 | 882.0909 | 1998.5455 | 16996.0909 | Size Multiplier | 922.4545 | 882.0909 | 1998.5455 | 16996.0909 | 922 | 882.0909 | 1998.5455 | 16996.0909 | 922.4545 | 882.0909 | 1998.5455 | 16996.0909 | 922 | 882.0909 | 1998.5455 | 16996.0909 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | Base Forecast: 11-year average using backcast re-analysis
| 4.c. | # of customers notified prior to initiation of PSPS event | 0 | 0 | 0 | 69229 | 2517105 | 0 | 0 | 293681 | 735708 | 22433 | 33745.5856 | 39751.4967 | 631866.1473 | 41535 | 33745.5856 | 39751.4967 | 631866.1473 | Size Multiplier | 41534.5428 | 33745.5856 | 39751.4967 | 631866.1473 | 41535 | 33745.5856 | 39751.4967 | 631866.1473 | 41534.5428 | 33745.5856 | 39751.4967 | 631866.1473 | 41535 | 33745.5856 | 39751.4967 | 631866.1473 | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | Base Forecast: 11-year historical average of impacted customers multiplied by the 2-year historical average for customer notifications.
| 4.d. | # of medical baseline customers notified prior to initiation of PSPS event | 0 | 0 | 0 | 3610 | 105606 | 0 | 0 | 22927 | 47914 | 1174 | 1243.7553 | 2817.9652 | 23964.6254 | 1301 | 1243.7553 | 2817.9652 | 23964.6254 | Size Multiplier | 1300.6684 | 1243.7553 | 2817.9652 | 23964.6254 | 1301 | 1243.7553 | 2817.9652 | 23964.6254 | 1300.6684 | 1243.7553 | 2817.9652 | 23964.6254 | 1301 | 1243.7553 | 2817.9652 | 23964.6254 | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | Base Forecast: 2-year historical average
| 4.e. | % of customers notified prior to a PSPS event impacting them | 0 | 0 | 0 | 113.9% | 123.6% | 0 | 0 | 126.1% | 176.5% | 439.9% | 132.1% | 132.1% | 132.1% | 132% | 132.1% | 132.1% | 132.1% | Size Multiplier | 132.1% | 132.1% | 132.1% | 132.1% | 132% | 132.1% | 132.1% | 132.1% | 132.1% | 132.1% | 132.1% | 132.1% | 132% | 132.1% | 132.1% | 132.1% | =4.c. / 4.a. | Base Forecast: 2-year historical average
| 4.f. | % of medical baseline customers notified prior to a PSPS event impacting them | 0 | 0 | 0 | 142.7% | 126.7% | 0 | 0 | 155.5% | 177% | 428.5% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | Size Multiplier | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | =4.d. / 4.b. | Base Forecast: 2-year historical average
5. Other PSPS metrics | 5.a. | Number of PSPS events triggered where no de-energization occurred | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | - | 0 | 0 | 1 | Frequency Multiplier | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | - | 0 | 0 | 1 | Number of instances where utility notified the public of a potential PSPS event but no de-energization followed | Base Forecast: 2-year average
| 5.b. | Number of customers located on de-energized circuit | 0 | 0 | 0 | 60806 | 2831593 | 0 | 0 | 320057 | 929101 | 24021 | 38829.1457 | 45739.8095 | 727052.8055 | 47791 | 38829.1457 | 45739.8095 | 727052.8055 | Scope multiplier | 47791.4603 | 38829.1457 | 45739.8095 | 727052.8055 | 47791 | 38829.1457 | 45739.8095 | 727052.8055 | 47791.4603 | 38829.1457 | 45739.8095 | 727052.8055 | 47791 | 38829.1457 | 45739.8095 | 727052.8055 | Total customers on circuit (even if partial circuit de-energization due to sectionalizing) | Base Forecast: 2-year historical average
| 5.c. | Customer hours of PSPS per RFW OH circuit mile day | 0 | 0 | 0 | 2.7985 | 195.9072 | 0 | 0 | 31.9665 | 40.353 | 6786.71 | 3.6031 | 1.5843 | 16.3331 | 0 | 3.6031 | 1.5843 | 16.3331 | Duration Multiplier | 0 | 3.6031 | 1.5843 | 16.3331 | 0 | 3.6031 | 1.5843 | 16.3331 | 0 | 3.6031 | 1.5843 | 16.3331 | 0 | 3.6031 | 1.5843 | 16.3331 | =1.c. / RFW OH circuit mile days in time period | Base Forecast: 2-year historical average
| 5.d. | Frequency of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Frequency Multiplier then do the subtraction | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Events over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Base Forecast: 2-year historical average
| 5.e. | Scope of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 365568 | 0 | 0 | 0 | 0 | 4696 | 0 | 0 | 182784 | 0 | 0 | 0 | 182784 | Size multiplier then do the subtraction | 0 | 0 | 0 | 182784 | 0 | 0 | 0 | 182784 | 0 | 0 | 0 | 182784 | 0 | 0 | 0 | 182784 | Estimated customers impacted over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Base Forecast: 2-year historical average
| 5.f. | Duration of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 5749687 | 0 | 0 | 0 | 0 | 38.6 | 0 | 0 | 2874843.5 | 0 | 0 | 0 | 2874843.5 | Size multiplier then do the subtraction | 0 | 0 | 0 | 2874843.5 | 0 | 0 | 0 | 2874843.5 | 0 | 0 | 0 | 2874843.5 | 0 | 0 | 0 | 2874843.5 | Customer hours over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Base Forecast: 2-year historical average
Updated comments for Table 11 (3/17/2020): 1. Removed whole number rounding for PSPS events which updated fields reliant on PSPS events per quarter. 2. Changed denominator of past PSPS lookback and event data from 11 to 10 to reflect the past 11 years of data (10 year lookback plus 2020 actuals) which updated fields reliant on duration, customer impact and scope. 3. Utilized actual event customer hours for 2020 which updated fields reliant on duration. 4. Changed denominator from 10-year average to 2-year average. 5. 2020 Q3 data for critical infrastructure updated. Original Comments for Table 11: PG&E has outlined the past and forecasted PSPS metrics in Table 11, which is utilizing historic recorded data for actuals and an analysis of the past ten years of weather data to provide the forecasted metrics. The forecasted numbers are largely weather dependent and do not include any event size or length reductions from the 2020 planned work. Further information historical lookback of the last ten years of weather data and its uses and limitations can be found in Section 8.1. PG&E projected PSPS metrics in 2021, and Table 11 keeps those values static for 2022. PG&E anticipates continued improvement from 2021 to 2022, but we do not yet have analysis on the value of those improvements. Thus, for the purposes of this table, no improvements have been assumed.
Note on M22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Adjust for Broadnet notifications.

## Notes (hidden)
Notes
1 | Assumed that mitigation frequency is 1, reflecting no change from original submission.
2
3
4
5
|  | 2.7 | 4.7 | 2

## Sheet1 (hidden)
| Mitigations | Overstrike
Frequency | 1 | 1.74
Size | 0.92 | 0.932
Duration | 0.9145 | 0.975
Frequency | 1 | 1.74 | 74%
Duration | 1 | 1.5811 | 58.11%
Scope | 1 | 1.6217 | 62.17%
Do not multiply across substation. Do not multiply across transmission.
Transmission line - vegetation included in Q05.
Delta table 11 - apply 3% reduction to not overstate.
(Delta from JA - Baseline) * (Dx only benefits + baseline) * total reductions
Baseline * 8% + (JA - Baseline) * Dx benefits only
Baseline |  | Customers w/JA
100 | 92 | 158.1 | 148.357 | Actual Dx reduction is 2.7% not 3%.
6.163%