## 2022 Quarterly Submission Guide
| Yes | No | <-- for dropdowns
Office of Energy Infrastructure Safety Attachment 3
Wildifire Mitigation Plan Quarterly Data Report - non-spatial data template
Instructions for use |  |  |  | Relevant options for mitigations table: Table 12
1 | Fill out the tan cells (color represented here) starting with the cell below (D17: Utility). The Utility name will populate the Table tabs to follow. Date modified will vary by table.
2 | Cells will only accept valid entries. For most cells, this is positive numbers
3 | For each Table tab, after a modification is made, denote the date of the change in cell C4 for each Table tab. |  |  |  | Initiative categories | WMP Maturity model Categories | Driver options
4 | Some columns have an additional header in row 5 to serve as clarification for several columns. With the exception of projected data, row 5 will be highlighted in blue (color represented here) |  |  |  | Vegetation inspection | Risk Assessment & Mapping | 1. Ignitions | Contact with vegetation
5 | Some required metrics are future projections. For these, row 5, above the projections will be highlighted light green (color represented here) |  |  |  | Vegetation management project | Situational Awareness & Forecasting |  | Other contact with object
| In future submissions, report updated projected numbers if / when projections have changed, and report actuals once the quarter / year has passed. |  |  |  | Asset inspection | Grid Design & System Hardening |  | Equipment failure
6 | For data required annually rather than quarterly (see Tables 7.2 - 10, 12), report for entire year even if part of the year is projected. Once year has passed, update cell with actuals |  |  |  | Grid hardening | Asset Management & Inspections |  | Wire-to-wire contact
7 | Some tables will have additional instructions provided in a Notes box located in cells D2 - D4 |  |  |  | Other | Vegetation Management & Inspections |  | Contamination
| Notes will explain terms, signal where projections are required, and provide other useful information. |  |  |  |  | Grid Operations & Operating Protocols |  | Vandalism / Theft
8 | For the initial quarterly submission, utilities are required to submit data on annual metrics for 2015 - 2020, which should represent the most updated data from the 2020 WMP for years 2015-2019 |  |  |  |  | Data Governance | 2. PSPS | PSPS - for sectionalization, etc.
* | Do not add or manipulate the template for any of the tabs |  |  |  |  | Resource Allocation Methodology
Emergency Planning & Preparedness
Update the below table to establish which year, quarter of the WMP cycle this submission this represents. | [5 empty] | Stakeholder Cooperation & Community Engagement
Utility |  | Pacific Gas & Electric Company
First year of 3-year WMP cycle |  | 2020
Submission year |  | 2022
Submission quarter |  | Q1
Date Modified |  | 2022-05-02

## Table 1
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2022-05-02
Table 1: Recent performance on progress metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Progress metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Grid condition findings from inspection - Distribution lines in HFTD | 1.a. | Number of circuit miles inspected from patrol inspections in HFTD - Distribution lines | 14387.9332 | 14356.0438 | 13003.3088 | 26291.4698 | 12705.0356 | 4956.6152 | 6521.2204 | 6623.6717 | 1273.9693 | 9676 | 12532 | 3733 | 0 | 3777 |  |  |  | # circuit miles | Totals represent the number of poles patrolled in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the patrol program is measured by pole count only.
| 1.b. | Number of circuit miles inspected from detailed inspections in HFTD - Distribution lines | 5350.1353 | 5899.5323 | 6570.7741 | 6782.3004 | 25223 | 165.5898 | 6937.3393 | 5953.6485 | 61.3913 | 863 | 14062 | 1805 | 220 | 243 |  |  |  | # circuit miles | Totals represent the number of poles inspected in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the inspection program is measured by pole count only.
| 1.c. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Distribution lines | 1415.4965 | 3485.7618 | 3804.6946 | 1294.9429 | 1652.0647 | 259.5034 | 960.0238 | 180.1236 | 509.0795 | 122 | 632 | 1898 | 593 | 615 |  |  |  | # circuit miles | Totals represent the number of inspections from Pole Test and Treat program in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the program is measured by pole count only.
| 1.d. | Level 1 findings in HFTD for patrol inspections - Distribution lines | 0 | 0 | 0 | 0 | 50 | 5 | 15 | 20 | 2 | 21 | 13 | 6 | 9 | 9 |  |  |  | # findings
| 1.e. | Level 1 findings in HFTD for detailed inspections - Distribution lines | 0 | 0 | 0 | 0 | 270 | 16 | 192 | 125 | 16 | 25 | 395 | 137 | 20 | 37 |  |  |  | # findings
| 1.f. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 0 | 0 | 0 | 11 | 4632 | 831 | 1239 | 1065 | 965 | 961 | 1249 | 1244 | 970 | 995 |  |  |  | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.g. | Level 2 findings in HFTD for patrol inspections - Distribution lines | 0 | 0 | 2 | 136 | 520 | 43 | 90 | 61 | 7 | 59 | 70 | 15 | 7 | 22 |  |  |  | # findings
| 1.h. | Level 2 findings in HFTD for detailed inspections - Distribution lines | 149 | 154 | 368 | 6115 | 34045 | 1015 | 26976 | 21981 | 321 | 2757 | 42505 | 9816 | 987 | 1157 |  |  |  | # findings
| 1.i. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 12 | 10 | 131 | 2030 | 160743 | 1185 | 2880 | 2188 | 1536 | 1462 | 8302 | 2508 | 1818 | 2273 |  |  |  | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.j. | Level 3 findings in HFTD for patrol inspections - Distribution lines | 11 | 3 | 9 | 8 | 34 | 0 | 10 | 4 | 1 | 3 | 13 | 2 | 2 | 1 |  |  |  | # findings
| 1.k. | Level 3 findings in HFTD for detailed inspections - Distribution lines | 5775 | 7067 | 7945 | 3782 | 6647 | 194 | 7666 | 5500 | 147 | 604 | 10386 | 2348 | 170 | 230 |  |  |  | # findings
| 1.l. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 326 | 440 | 128 | 334 | 16576 | 97 | 264 | 215 | 182 | 174 | 527 | 500 | 327 | 252 |  |  |  | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
1. Grid condition findings from inspection - Distribution lines total | 1.a.ii. | Number of total circuit miles inspected from patrol inspections - Distribution lines | 41094.9594 | 39822.6237 | 39966.6637 | 55931.77 | 55583.0052 | 12536.2868 | 11649.4964 | 13067.4628 | 19631.0591 | 13022 | 21649 | 10123 | 259 | 8267 |  |  |  | # circuit miles | Totals represent the number of poles patrolled in relationship to total poles in Non-HFTD and converted to circuit miles. Note the circuit miles is an approximation since the patrol program is measured by pole count only.
| 1.b.ii. | Number of total circuit miles inspected from detailed inspections - Distribution lines | 14885.9002 | 15602.6283 | 15882.3415 | 16002.1839 | 35989.2651 | 162.5379 | 7700.9472 | 11401.9412 | 4203.1861 | 947 | 15346 | 4075 | 4964 | 782 |  |  |  | # circuit miles | Totals represent the number of poles patrolled in relationship to total poles in Non-HFTD and converted to circuit miles. Note the circuit miles is an approximation since the patrol program is measured by pole count only.
| 1.c.ii. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Distribution lines | 9772.36 | 9098.1252 | 7982.0498 | 4986.4074 | 6733.7729 | 1928.6223 | 1853.2088 | 1960.3699 | 2218.7724 | 1429 | 3516 | 782 | 564 | 1157 |  |  |  | # circuit miles | Totals represent the number of inspections from Pole Test and Treat program in relationship to total poles in Non-HFTD and converted to circuit miles. Note the circuit miles is an approximation since the program is measured by pole count only.
| 1.d.ii. | Level 1 findings for patrol inspections - Distribution lines | 0 | 0 | 0 | 2 | 244 | 44 | 49 | 80 | 137 | 55 | 61 | 70 | 65 | 40 |  |  |  | # findings | Non HFTD areas only
| 1.e.ii. | Level 1 findings for detailed inspections - Distribution lines | 0 | 0 | 0 | 12 | 714 | 37 | 277 | 407 | 210 | 71 | 625 | 721 | 487 | 131 |  |  |  | # findings | Non HFTD areas only
| 1.f.ii. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 0 | 0 | 5 | 275 | 18577 | 3706 | 5100 | 4513 | 4080 | 4076 | 5024 | 4635 | 4116 | 4221 |  |  |  | # findings | Non HFTD areas only. "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.g.ii. | Level 2 findings for patrol inspections - Distribution lines | 0 | 1 | 14 | 560 | 1953 | 370 | 320 | 373 | 426 | 223 | 270 | 206 | 208 | 245 |  |  |  | # findings | Non HFTD areas only
| 1.h.ii. | Level 2 findings for detailed inspections - Distribution lines | 977 | 1055 | 1267 | 20345 | 74539 | 3983 | 37690 | 56503 | 19153 | 6645 | 62540 | 47130 | 27266 | 8239 |  |  |  | # findings | Non HFTD areas only
| 1.i.ii. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 47 | 381 | 960 | 9663 | 182561 | 4806 | 5537 | 7232 | 5641 | 5067 | 12618 | 6894 | 5641 | 5315 |  |  |  | # findings | Non HFTD areas only. "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.j.ii. | Level 3 findings for patrol inspections - Distribution lines | 45 | 39 | 35 | 42 | 87 | 2 | 24 | 21 | 18 | 9 | 26 | 29 | 10 | 46 |  |  |  | # findings | Non HFTD areas only
| 1.k.ii. | Level 3 findings for detailed inspections - Distribution lines | 30966 | 36370 | 32973 | 17421 | 18033 | 955 | 11153 | 19803 | 10771 | 1670 | 14813 | 15557 | 11325 | 1836 |  |  |  | # findings | Non HFTD areas only
| 1.l.ii. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 3101 | 5287 | 1244 | 2553 | 19019 | 330 | 474 | 648 | 526 | 364 | 1000 | 1214 | 1041 | 964 |  |  |  | # findings | Non HFTD Areas only. "Other" inspection methods include Pole Test and Treat and overhead IR.
1. Grid condition findings from inspection - Transmission lines in HFTD | 1.a.iii. | Number of circuit miles inspected from patrol inspections in HFTD - Transmission lines | 2585 | 3696 | 3048 | 3251 | 0 | 663 | 1572 | 1259 | 1239 | 2140 | 1939 | 570 | 267 | 1029 |  |  |  | # circuit miles
| 1.b.iii. | Number of circuit miles inspected from detailed inspections in HFTD - Transmission lines | 2978 | 1867 | 2515 | 2312 | 5563 | 22 | 1048 | 1624 | 229 | 685 | 2520 | 34 | 7 | 348 |  |  |  | # circuit miles | Totals represent the number of poles inspected in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the inspection program is measured by pole count only.
| 1.c.iii. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Transmission lines | 1323 | 1323 | 1323 | 1323 | 1323 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 |  |  |  | # circuit miles | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.d.iii. | Level 1 findings in HFTD for patrol inspections - Transmission lines | 0 | 0 | 2 | 0 | 4 | 1 | 4 | 125 | 14 | 36 | 2 | 2 | 10 | 5 |  |  |  | # findings
| 1.e.iii. | Level 1 findings in HFTD for detailed inspections - Transmission lines | 2 | 2 | 4 | 18 | 23 | 2 | 3 | 4 | 2 | 3 | 7 | 2 | 0 | 17 |  |  |  | # findings
| 1.f.iii. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | 238 | 76 | 180 | 70 | 183 | 48 | 36 | 115 | 39 | 41 | 65 | 49 | 79 | 29 |  |  |  | # findings | Includes any notification not found by patrol or detailed inspection.
| 1.g.iii. | Level 2 findings in HFTD for patrol inspections - Transmission lines | 86 | 213 | 417 | 150 | 468 | 16 | 39 | 17 | 14 | 49 | 34 | 10 | 88 | 38 |  |  |  | # findings
| 1.h.iii. | Level 2 findings in HFTD for detailed inspections - Transmission lines | 1947 | 852 | 1054 | 3727 | 10466 | 164 | 641 | 2120 | 172 | 547 | 3076 | 105 | 24 | 2396 |  |  |  | # findings
| 1.i.iii. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | 635 | 770 | 960 | 1607 | 39172 | 569 | 3199 | 2607 | 783 | 535 | 6605 | 2522 | 222 | 173 |  |  |  | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.j.iii. | Level 3 findings in HFTD for patrol inspections - Transmission lines | 8 | 7 | 76 | 17 | 56 | 1 | 2 | 1 | 1 | 4 | 5 | 0 | 0 | 5 |  |  |  | # findings
| 1.k.iii. | Level 3 findings in HFTD for detailed inspections - Transmission lines | 387 | 261 | 567 | 427 | 613 | 62 | 388 | 1111 | 68 | 332 | 1139 | 34 | 24 | 833 |  |  |  | # findings
| 1.l.iii. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | 75 | 99 | 139 | 85 | 5284 | 143 | 2506 | 2503 | 600 | 202 | 3603 | 955 | 36 | 27 |  |  |  | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
1. Grid condition findings from inspection - Transmission lines total | 1.a.iv. | Number of total circuit miles inspected from patrol inspections - Transmission lines | 8385 | 11523 | 10015 | 11198 | 7671 | 2594 | 5742 | 4122 | 4208 | 3657 | 4546 | 1724 | 1884 | 1032 |  |  |  | # circuit miles | Totals represent the number of poles inspected in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the inspection program is measured by pole count only.
| 1.b.iv. | Number of total circuit miles inspected from detailed inspections - Transmission lines | 9944 | 6807 | 8315 | 7131 | 10658 | 36 | 1548 | 3847 | 1094 | 1063 | 3427 | 857 | 536 | 472 |  |  |  | # circuit miles
| 1.c.iv. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Transmission lines | 4393 | 4393 | 4393 | 4393 | 4393 | 1098 | 1098 | 1098 | 1098 | 1098 | 1098 | 1098 | 1098 | 1098 |  |  |  | # circuit miles | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.d.iv. | Level 1 findings for patrol inspections - Transmission lines | 5 | 7 | 15 | 3 | 14 | 5 | 9 | 149 | 16 | 56 | 8 | 17 | 17 | 7 |  |  |  | # findings
| 1.e.iv. | Level 1 findings for detailed inspections - Transmission lines | 11 | 5 | 29 | 47 | 45 | 3 | 7 | 16 | 12 | 6 | 23 | 9 | 3 | 24 |  |  |  | # findings
| 1.f.iv. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | 1992 | 1425 | 1623 | 1171 | 519 | 147 | 189 | 342 | 209 | 184 | 200 | 185 | 165 | 81 |  |  |  | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.g.iv. | Level 2 findings for patrol inspections - Transmission lines | 478 | 1240 | 1176 | 890 | 1284 | 86 | 199 | 218 | 169 | 103 | 195 | 164 | 154 | 118 |  |  |  | # findings
| 1.h.iv. | Level 2 findings for detailed inspections - Transmission lines | 5949 | 3735 | 4478 | 9286 | 15761 | 457 | 978 | 7548 | 759 | 1115 | 8022 | 1625 | 719 | 3751 |  |  |  | # findings
| 1.i.iv. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | 11053 | 11674 | 13211 | 14779 | 50307 | 1388 | 7560 | 7413 | 7307 | 1791 | 10005 | 10940 | 5784 | 798 |  |  |  | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.j.iv. | Level 3 findings for patrol inspections - Transmission lines | 25 | 30 | 151 | 68 | 136 | 5 | 8 | 7 | 16 | 13 | 33 | 12 | 0 | 8 |  |  |  | # findings
| 1.k.iv. | Level 3 findings for detailed inspections - Transmission lines | 684 | 577 | 1139 | 861 | 2190 | 199 | 612 | 3986 | 394 | 594 | 3533 | 670 | 467 | 1194 |  |  |  | # findings
| 1.l.iv. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | 299 | 587 | 947 | 455 | 6970 | 391 | 4801 | 5290 | 4114 | 462 | 5217 | 4920 | 2153 | 126 |  |  |  | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
2. Vegetation clearance findings from inspection - total | 2.a.i | Number of spans inspected where at least some vegetation was found in non-compliant condition - total | 2402 | 3010 | 3372 | 5072 | 37914 | 9637 | 11055 | 15783 | 15773 | 8543 | 10588 | 19,558 | 14125 | 10717 |  |  |  | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | See comments for this section.
| 2.a.ii | Number of spans inspected for vegetation compliance - total | 1443176 | 1562166 | 1458738 | 1496906 | 1525349 | 428110 | 417774 | 335799 | 468295 | 445641 | 419031 | 496,621 | 468082 | 499844 |  |  |  | # of spans inspected for vegetation compliance | See comments for this section.
2. Vegetation clearance findings from inspection - in HFTD | 2.b.i | Number of spans inspected where at least some vegetation was found in non-compliant condition in HFTD | 204 | 442 | 912 | 1919 | 14469 | 4385 | 6844 | 8078 | 5691 | 4307 | 5635 | 9,038 | 4291 | 6086 |  |  |  | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | See comments for this section.
| 2.b.ii | Number of spans inspected for vegetation compliance in HFTD | 170577 | 337899 | 323228 | 428070 | 457740 | 137694 | 165572 | 122804 | 120114 | 152931 | 163509 | 165,445 | 127861 | 194521 |  |  |  | # of spans inspected for vegetation compliance | See comments for this section.
3. Community outreach metrics | 3.a. | # Customers in an evacuation zone for utility-ignited wildfire | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 |  |  |  | # customers (if customer was in an evacuation zone for multiple wildfires, count the customer for each relevant wildfire) | See comments for this section.
| 3.b. | # Customers notified of evacuation orders | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 |  |  |  | # customers (count customer multiple times for each unique wildfire of which they were notified) | See comments for this section.
| 3.c. | % of customers notified of evacuation in evacuation zone of a utility-ignited wildfire | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 |  |  |  | Percentage of customers notified of evacuation | See comments for this section.
Comments for Table 1: Item 1. Description – Grid Condition Findings From Inspection – Distribution: · Level 1 findings are defined as Priority A tags. Level 2 findings are defined as Priority B and E tags. Level 3 findings are defined as priority F and H tags. · PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. · Inspection findings values were extracted utilizing the same filter criteria used to create PG&E's Compliance "repair tag" Plan Quarterly Update. · "Other" Inspections includes Pole Test & Treat and work verification work Item 1. Description – Grid Condition Findings From Inspection – Transmission: · Findings by inspection/patrol type are not available before 2019; all findings were assigned to Detailed Inspections. · Level 1 findings are defined as Priority A tags. Level 2 findings are defined as Priority B and E tags. Level 3 findings are defined as priority F tags. · PG&E does not track inspection data by circuit mile. If a structure/circuit was patrolled multiple times in a year, mileage is only counted once for that year. Fraction of total mileage was assumed proportional to the percentage of structures inspected. · Inspection findings values were extracted utilizing the same filter criteria used to create PG&E's Compliance "repair tag" Plan Quarterly Update. · "Other" Inspections includes Infrared Inspections, Pole Test & Treat and work verification work Item 2. Description – Vegetation Clearance Findings From Inspection: · The number of spans inspected with noncompliant clearance is based on applicable rules and regulations at the time of inspection. · PG&E does not track the precise data requested as PG&E’s vegetation management data is generally tracked by tree. Therefore, the closest available data has been provided with an estimated translation to the “Percentage of right-of-way with noncompliant clearance” data that was requested. PG&E vegetation management pre-inspectors identify a tree that is currently violating minimum clearance distances, or may violate minimum clearance in the near future, with a special designation of being a Hazard Notification (HN). Not all HNs represent actively non-compliant trees, as in many cases the tree is currently compliant but may be at risk of violating minimum clearances before the normal tree work cycle can be completed. Nonetheless, HNs are the best estimate PG&E has for the number of trees that were identified as being inside or near the minimum clearance requirements and have been provided above as the “Trees identified as being currently, or at risk in the near future, of being out of compliance” data. · This estimate for the number of electric overhead spans has been determined by assuming an average span length (distance between poles) of 275 feet. Item 3. Description – Community Outreach Metrics: # Customers in an Evacuation Zone for Utility-Ignited Wildfire; # Customers Notified of Evacuation Orders: · PG&E does not issue wildfire evacuation notices to customers and does not maintain metrics on the number of customers in an evacuation zone or the number of customers notified of evacuation orders. Because of this, PG&E is unable to report on evacuation related requirements in this table. PG&E anticipates this to be a recurring challenge going forward. Item 4. Assumptions for Inspection Data · See note below regarding Table 8 (historical grid data unavailable for 2014-2018); circuit mileage is assumed to be the same as our 2019 data for 2015-2018 for the purposes of Table 1 · Mileage was extrapolated using approximate unit counts of historical detailed inspection & Pole Test & Treat data & relative circuit mileage and asset counts in High Fire Threat District (HFTD) and Non HFTD

## Table 2
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2022-05-02 | HWW = High wind warning
RFW = Red flag warning
Note: These columns are placeholders for future QR submissions.
Table 2: Recent performance on outcome metrics | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | Wind Warning Status | HFTD Tier | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Risk events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | All | 1 | 15 | 23 | 31 | 7 | 15 | 0 | 0 | 0 | 1 | 5 | 3 | 6 | 1 | 2 |  |  |  | Number per year
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & not RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | All | 2 | 5609 | 5738 | 8352 | 4690 | 8359 | 1560 | 1296 | 1434 | 1190 | 2671 | 1529 | 1691 | 1681 | 962
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW | 2 | 19 | 3 | 385 | 137 | 74 | 0 | 8 | 229 | 76 | 7 | 31 | 68 | 29 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW | 2 | 36 | 63 | 391 | 3 | 432 | 0 | 0 | 0 | 0 | 323 | 0 | 194 | 8 | 8
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | 2 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 3 | 0 | 59 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & not RFW | 2 | 36 | 63 | 391 | 3 | 428 | 0 | 0 | 0 | 0 | 320 | 0 | 135 | 8 | 8
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | All | 3 | 3129 | 3237 | 5499 | 3265 | 5432 | 1480 | 719 | 1349 | 716 | 1973 | 715 | 734 | 1028 | 586
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW | 3 | 6 | 1 | 319 | 411 | 24 | 0 | 3 | 369 | 49 | 2 | 19 | 39 | 16 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW | 3 | 0 | 32 | 433 | 0 | 276 | 0 | 0 | 0 | 0 | 382 | 0 | 80 | 1 | 17
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 36 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & not RFW | 3 | 0 | 32 | 433 | 0 | 276 | 0 | 0 | 0 | 0 | 381 | 0 | 44 | 1 | 17
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | All | Non-HFTD | 26478 | 27239 | 35319 | 25168 | 30633 | 6125 | 6743 | 8142 | 7253 | 10718 | 8225 | 7776 | 13718 | 6839
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW | Non-HFTD | 111 | 38 | 976 | 479 | 960 | 0 | 56 | 980 | 449 | 14 | 221 | 210 | 646 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW | Non-HFTD | 94 | 142 | 793 | 22 | 1199 | 31 | 0 | 0 | 0 | 1108 | 3 | 877 | 55 | 12
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | Non-HFTD | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0
|  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & not RFW | Non-HFTD | 94 | 142 | 793 | 22 | 868 | 31 | 0 | 0 | 0 | 1108 | 3 | 681 | 55 | 12
1. Risk events | 1.b. | Number of wires down (total) | All | 1 | 0 | 1 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Number of wires down per year
|  | Number of wires down (total) | RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of wires down (total) | HWW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of wires down (total) | HWW & RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of wires down (total) | HWW & not RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of wires down (total) | All | 2 | 769 | 844 | 1582 | 551 | 1550 | 256 | 135 | 109 | 83 | 466 | 106 | 123 | 175 | 62
|  | Number of wires down (total) | RFW | 2 | 1 | 0 | 78 | 18 | 9 | 0 | 0 | 24 | 7 | 2 | 1 | 4 | 1 | 0
|  | Number of wires down (total) | HWW | 2 | 15 | 17 | 129 | 0 | 151 | 0 | 0 | 0 | 0 | 99 | 0 | 15 | 0 | 1
|  | Number of wires down (total) | HWW & RFW | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0
|  | Number of wires down (total) | HWW & not RFW | 2 | 15 | 17 | 129 | 0 | 151 | 0 | 0 | 0 | 0 | 99 | 0 | 11 | 1 | 1
|  | Number of wires down (total) | All | 3 | 476 | 641 | 1300 | 482 | 1088 | 385 | 94 | 144 | 78 | 550 | 62 | 64 | 151 | 52
|  | Number of wires down (total) | RFW | 3 | 1 | 0 | 62 | 22 | 3 | 0 | 0 | 49 | 8 | 1 | 3 | 2 | 2 | 0
|  | Number of wires down (total) | HWW | 3 | 0 | 9 | 173 | 0 | 102 | 0 | 0 | 0 | 0 | 207 | 0 | 6 | 0 | 4
|  | Number of wires down (total) | HWW & RFW | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
|  | Number of wires down (total) | HWW & not RFW | 3 | 0 | 9 | 173 | 0 | 102 | 0 | 0 | 0 | 0 | 207 | 0 | 4 | 0 | 4
|  | Number of wires down (total) | All | Non-HFTD | 2207 | 2440 | 3824 | 2174 | 3106 | 580 | 495 | 586 | 519 | 1037 | 519 | 529 | 2323 | 558
|  | Number of wires down (total) | RFW | Non-HFTD | 10 | 5 | 131 | 34 | 121 | 0 | 3 | 61 | 33 | 2 | 12 | 9 | 66 | 0
|  | Number of wires down (total) | HWW | Non-HFTD | 14 | 26 | 180 | 2 | 249 | 4 | 0 | 0 | 0 | 174 | 1 | 40 | 5 | 6
|  | Number of wires down (total) | HWW & RFW | Non-HFTD | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0
|  | Number of wires down (total) | HWW & not RFW | Non-HFTD | 14 | 26 | 180 | 2 | 206 | 4 | 0 | 0 | 0 | 174 | 1 | 31 | 5 | 6
1. Risk events | 1.c. | Number of outage events not caused by contact with vegetation (total) | All | 1 | 15 | 22 | 29 | 5 | 14 | 0 | 0 | 0 | 0 | 5 | 3 | 5 | 1 | 0 |  |  |  | Number of outage events per year
|  | Number of outage events not caused by contact with vegetation (total) | RFW | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events not caused by contact with vegetation (total) | HWW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events not caused by contact with vegetation (total) | HWW & RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events not caused by contact with vegetation (total) | HWW & not RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events not caused by contact with vegetation (total) | All | 2 | 4475 | 4538 | 6234 | 3881 | 5930 | 1167 | 1103 | 1249 | 1062 | 1980 | 1352 | 1495 | 1284 | 825
|  | Number of outage events not caused by contact with vegetation (total) | RFW | 2 | 17 | 2 | 341 | 121 | 61 | 0 | 7 | 196 | 63 | 5 | 30 | 58 | 23 | 0
|  | Number of outage events not caused by contact with vegetation (total) | HWW | 2 | 14 | 41 | 223 | 2 | 244 | 0 | 0 | 0 | 0 | 200 | 0 | 168 | 6 | 6
|  | Number of outage events not caused by contact with vegetation (total) | HWW & RFW | 2 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 49 | 0 | 0
|  | Number of outage events not caused by contact with vegetation (total) | HWW & not RFW | 2 | 14 | 41 | 223 | 2 | 241 | 0 | 0 | 0 | 0 | 197 | 0 | 119 | 6 | 6
|  | Number of outage events not caused by contact with vegetation (total) | All | 3 | 2232 | 2089 | 3345 | 2308 | 3195 | 714 | 506 | 1122 | 545 | 1128 | 581 | 617 | 660 | 420
|  | Number of outage events not caused by contact with vegetation (total) | RFW | 3 | 4 | 1 | 245 | 376 | 17 | 0 | 1 | 288 | 37 | 1 | 16 | 33 | 13 | 0
|  | Number of outage events not caused by contact with vegetation (total) | HWW | 3 | 0 | 17 | 199 | 0 | 122 | 0 | 0 | 0 | 0 | 171 | 0 | 68 | 1 | 13
|  | Number of outage events not caused by contact with vegetation (total) | HWW & RFW | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 30 | 0 | 0
|  | Number of outage events not caused by contact with vegetation (total) | HWW & not RFW | 3 | 0 | 17 | 199 | 0 | 122 | 0 | 0 | 0 | 0 | 170 | 0 | 38 | 1 | 13
|  | Number of outage events not caused by contact with vegetation (total) | All | Non-HFTD | 24765 | 25156 | 31411 | 23644 | 27134 | 5622 | 6330 | 7696 | 6880 | 9604 | 7858 | 7411 | 10913 | 6345
|  | Number of outage events not caused by contact with vegetation (total) | RFW | Non-HFTD | 106 | 37 | 853 | 453 | 772 | 0 | 48 | 896 | 386 | 10 | 203 | 196 | 519 | 0
|  | Number of outage events not caused by contact with vegetation (total) | HWW | Non-HFTD | 81 | 119 | 548 | 20 | 842 | 28 | 0 | 0 | 0 | 883 | 3 | 830 | 46 | 5
|  | Number of outage events not caused by contact with vegetation (total) | HWW & RFW | Non-HFTD | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0
|  | Number of outage events not caused by contact with vegetation (total) | HWW & not RFW | Non-HFTD | 81 | 119 | 548 | 20 | 577 | 28 | 0 | 0 | 0 | 883 | 3 | 648 | 46 | 5
1. Risk events | 1.d. | Number of outage events caused by contact with vegetation (total) | All | 1 | 0 | 1 | 2 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 |  |  |  | Number of outage events per year
|  | Number of outage events caused by contact with vegetation (total) | RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation (total) | HWW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation (total) | HWW & RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation (total) | HWW & not RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of outage events caused by contact with vegetation (total) | All | 2 | 1134 | 1200 | 2118 | 809 | 2429 | 393 | 193 | 185 | 128 | 691 | 177 | 196 | 397 | 137
|  | Number of outage events caused by contact with vegetation (total) | RFW | 2 | 2 | 1 | 44 | 16 | 13 | 0 | 1 | 33 | 13 | 2 | 1 | 10 | 6 | 0
|  | Number of outage events caused by contact with vegetation (total) | HWW | 2 | 22 | 22 | 168 | 1 | 188 | 0 | 0 | 0 | 0 | 123 | 0 | 26 | 2 | 2
|  | Number of outage events caused by contact with vegetation (total) | HWW & RFW | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
|  | Number of outage events caused by contact with vegetation (total) | HWW & not RFW | 2 | 22 | 22 | 168 | 1 | 187 | 0 | 0 | 0 | 0 | 123 | 0 | 16 | 2 | 2
|  | Number of outage events caused by contact with vegetation (total) | All | 3 | 897 | 1148 | 2154 | 957 | 2237 | 766 | 213 | 227 | 171 | 845 | 134 | 117 | 368 | 166
|  | Number of outage events caused by contact with vegetation (total) | RFW | 3 | 2 | 0 | 74 | 35 | 7 | 0 | 2 | 81 | 12 | 1 | 3 | 6 | 3 | 0
|  | Number of outage events caused by contact with vegetation (total) | HWW | 3 | 0 | 15 | 234 | 0 | 154 | 0 | 0 | 0 | 0 | 211 | 0 | 12 | 0 | 4
|  | Number of outage events caused by contact with vegetation (total) | HWW & RFW | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0
|  | Number of outage events caused by contact with vegetation (total) | HWW & not RFW | 3 | 0 | 15 | 234 | 0 | 154 | 0 | 0 | 0 | 0 | 211 | 0 | 6 | 0 | 4
|  | Number of outage events caused by contact with vegetation (total) | All | Non-HFTD | 1713 | 2083 | 3908 | 1524 | 3499 | 503 | 413 | 446 | 373 | 1114 | 367 | 365 | 2805 | 494
|  | Number of outage events caused by contact with vegetation (total) | RFW | Non-HFTD | 5 | 1 | 123 | 26 | 188 | 0 | 8 | 84 | 63 | 4 | 18 | 14 | 127 | 0
|  | Number of outage events caused by contact with vegetation (total) | HWW | Non-HFTD | 13 | 23 | 245 | 2 | 357 | 3 | 0 | 0 | 0 | 225 | 0 | 47 | 9 | 7
|  | Number of outage events caused by contact with vegetation (total) | HWW & RFW | Non-HFTD | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0
|  | Number of outage events caused by contact with vegetation (total) | HWW & not RFW | Non-HFTD | 13 | 23 | 245 | 2 | 291 | 3 | 0 | 0 | 0 | 225 | 0 | 33 | 9 | 7
2. Utility inspection findings - Distribution | 2.a. | Number of Level 1 findings (distribution - total) | N/A | 1 | 0 | 0 | 0 | 0 | 39 | 5 | 2 | 1 | 5 | 4 | 2 | 1 | 0 | 0 |  |  |  | # findings
|  | Number of Level 1 findings (distribution - total) | N/A | 2 | 0 | 0 | 0 | 11 | 3059 | 551 | 937 | 711 | 592 | 625 | 1044 | 897 | 597 | 657
|  | Number of Level 1 findings (distribution - total) | N/A | 3 | 0 | 0 | 0 | 14 | 1893 | 301 | 509 | 499 | 391 | 382 | 613 | 490 | 402 | 384
|  | Number of Level 1 findings (distribution - total) | N/A | Non- HFTD | 0 | 0 | 5 | 264 | 14544 | 2930 | 3978 | 3789 | 3439 | 3191 | 4051 | 4038 | 3669 | 3351
2. Utility inspection findings - Distribution | 2.b. | Number of Level 2 findings (distribution - total) | N/A | 1 | 1 | 2 | 0 | 15 | 455 | 4 | 7 | 38 | 9 | 5 | 120 | 55 | 2 | 0 |  |  |  | # findings
|  | Number of Level 2 findings (distribution - total) | N/A | 2 | 161 | 164 | 501 | 8281 | 136176 | 997 | 14087 | 11351 | 1096 | 2576 | 30520 | 8740 | 1809 | 2570
|  | Number of Level 2 findings (distribution - total) | N/A | 3 | 349 | 202 | 295 | 2648 | 59132 | 1246 | 15859 | 12879 | 768 | 1702 | 20357 | 3599 | 1003 | 882
|  | Number of Level 2 findings (distribution - total) | N/A | Non- HFTD | 513 | 1069 | 1445 | 19624 | 63290 | 6912 | 13594 | 39840 | 23347 | 7652 | 24431 | 41836 | 30301 | 10347
2. Utility inspection findings - Distribution | 2.c. | Number of Level 3 findings (distribution - total) | N/A | 1 | 75 | 27 | 12 | 18 | 33 | 1 | 2 | 12 | 16 | 2 | 14 | 8 | 3 | 1 |  |  |  | # findings
|  | Number of Level 3 findings (distribution - total) | N/A | 2 | 6112 | 7510 | 8082 | 4124 | 10311 | 123 | 3530 | 2429 | 157 | 476 | 6512 | 2028 | 354 | 351
|  | Number of Level 3 findings (distribution - total) | N/A | 3 | 3677 | 3480 | 3338 | 2911 | 12946 | 168 | 4410 | 3290 | 173 | 305 | 4414 | 822 | 145 | 132
|  | Number of Level 3 findings (distribution - total) | N/A | Non- HFTD | 24248 | 30679 | 22820 | 12963 | 13849 | 995 | 3709 | 14741 | 10969 | 1260 | 4899 | 13942 | 11874 | 2362
2. Utility inspection findings - Distribution | 2.d. | Number of distribution circuit miles inspected | N/A | Zone 1 | 13.3809 | 15.0178 | 14.7884 | 21.7402 | 25.0367 | 3.4042 | 9.1206 | 8.0698 | 1.1667 | 6.7437 | 17.222 | 4.7037 | 0.51427 | 0 |  |  |  | # circuit miles
|  | Number of distribution circuit miles inspected | N/A | 2 | 14420.9869 | 16185.1454 | 15937.9775 | 23430.1292 | 26982.8802 | 3668.8637 | 9829.5585 | 8697.1122 | 1257.4073 | 7267.9069 | 18560.7386 | 5069.3327 | 554.2452 | 4271
|  | Number of distribution circuit miles inspected | N/A | 3 | 6719.1972 | 7541.1749 | 7426.0115 | 10916.8436 | 12572.1835 | 1709.4405 | 4579.9044 | 4052.2617 | 585.8661 | 3386.3494 | 8648.0394 | 2361.9636 | 258.2405 | 363
|  | Number of distribution circuit miles inspected | N/A | Non- HFTD | 65753.2195 | 64523.3772 | 63831.055 | 76920.3613 | 98306.0432 | 14627.447 | 21203.6525 | 26429.7739 | 26053.0176 | 15398 | 40511 | 14980 | 5787 | 5029
2. Utility inspection findings - Transmission | 2.a.ii | Number of Level 1 findings (transmission - total) | N/A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # findings
|  | Number of Level 1 findings (transmission - total) | N/A | 2 | 240 | 78 | 186 | 88 | 134 | 24 | 28 | 65 | 30 | 54 | 34 | 28 | 41 | 23
|  | Number of Level 1 findings (transmission - total) | N/A | 3 | 45 | 17 | 36 | 63 | 76 | 27 | 15 | 179 | 25 | 26 | 40 | 25 | 48 | 28
|  | Number of Level 1 findings (transmission - total) | N/A | Non- HFTD | 1723 | 1342 | 1445 | 1070 | 368 | 104 | 162 | 263 | 182 | 166 | 157 | 158 | 96 | 61
2. Utility inspection findings - Transmission | 2.b.ii | Number of Level 2 findings (transmission - total) | N/A | 1 | 0 | 0 | 0 | 8 | 3 | 1 | 3 | 3 | 0 | 0 | 13 | 5 | 0 | 1 |  |  |  | # findings
|  | Number of Level 2 findings (transmission - total) | N/A | 2 | 2668 | 1835 | 2431 | 5484 | 39110 | 543 | 2035 | 3052 | 619 | 676 | 6130 | 1775 | 247 | 2167
|  | Number of Level 2 findings (transmission - total) | N/A | 3 | 726 | 543 | 563 | 2197 | 10996 | 206 | 1844 | 1692 | 350 | 455 | 3585 | 862 | 87 | 439
|  | Number of Level 2 findings (transmission - total) | N/A | Non- HFTD | 14086 | 14271 | 15871 | 17266 | 17243 | 1181 | 4855 | 10432 | 7266 | 1878 | 8494 | 10087 | 6323 | 2060
2. Utility inspection findings - Transmission | 2.c.ii | Number of Level 3 findings (transmission - total) | N/A | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 6 | 8 | 0 | 0 |  |  |  | # findings
|  | Number of Level 3 findings (transmission - total) | N/A | 2 | 470 | 367 | 782 | 529 | 4620 | 122 | 1338 | 2302 | 393 | 281 | 2862 | 668 | 40 | 736
|  | Number of Level 3 findings (transmission - total) | N/A | 3 | 208 | 194 | 187 | 174 | 1333 | 84 | 1558 | 1313 | 276 | 257 | 1885 | 321 | 20 | 129
|  | Number of Level 3 findings (transmission - total) | N/A | Non- HFTD | 330 | 633 | 1268 | 679 | 3343 | 389 | 2525 | 5666 | 3855 | 531 | 4030 | 4605 | 2560 | 463
2. Utility inspection findings - Transmission | 2.d.ii | Number of transmission circuit miles inspected | N/A | 1 | 30.3673 | 30.3673 | 30.3673 | 30.3673 | 30.3673 | 4.4806 | 13.0139 | 14.1737 | 7.9336 | 13.918 | 21.1239 | 4.1234 | 2.6681 | 0 |  |  |  | # circuit miles
|  | Number of transmission circuit miles inspected | N/A | 2 | 5317.4105 | 5317.4105 | 5317.4105 | 5317.4105 | 5317.4105 | 784.5613 | 2278.7799 | 2481.8701 | 1389.1986 | 2437.0821 | 3698.8667 | 722.0126 | 467.1846 | 826
|  | Number of transmission circuit miles inspected | N/A | 3 | 1538.2174 | 1538.2174 | 1538.2174 | 1538.2174 | 1538.2174 | 226.9574 | 659.2041 | 717.9539 | 401.8666 | 704.9977 | 1070.006 | 208.8634 | 135.1469 | 527
|  | Number of transmission circuit miles inspected | N/A | Non- HFTD | 15836 | 15837 | 15837 | 15836 | 15836 | 2712 | 5437 | 5853 | 4601 | 2662 | 4281 | 2744 | 2913 | 127
3. Utility ignited wildfire fatalities | 3.a. | Fatalities due to utility-ignited wildfire (total) | N/A | N/A | 2 | 0 | 22 | 85 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 |  |  |  | Number of fatalities per year
3. Utility ignited wildfire fatalities | 3.b. | Injuries due to utility-ignited wildfire (total) | N/A | N/A | 0 | 2 | 1 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Number of injuries per year
4. Value of assets destroyed by utility-ignited wildfire, listed by asset type | 4.a. | Value of assets destroyed by utility-ignited wildfire (total) | N/A | N/A | $911M | $2.4M | $25.5B | $1.49M | $35.448M | 0 | 0 | $198M | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Dollars of damage or destruction per year
5. Structures damaged or destroyed by utility-ignited wildfire | 5.a. | Number of structures destroyed by utility-ignited wildfire (total) | N/A | N/A | 965 | 0 | 2588 | 18806 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 1331 | 0 | 0 |  |  |  | Number of structures destroyed per year | Three structures have been added to the 2020 total since the last submittal
5. Structures damaged or destroyed by utility-ignited wildfire | 5.b. | Critical infrastructure damaged/destroyed by utility-ignited wildfire (total) | N/A | N/A | 2 | 0 | 20 | 33 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 |  |  |  | Number of critical infrastructure damaged/destroyed per year
6. Acreage burned by utility-ignited wildfire | 6.a. | Acreage burned by utility-ignited wildfire (total) | N/A | N/A | 72149 | 2727 | 206302 | 166282 | 82027 | 0 | 1545 | 57745 | 10 | 742 | 134 | 967609 | 457 | 0 |  |  |  | Acres burned per year
7. Number of utility-related ignitions | 7.a. | Number of ignitions (total) according to existing ignition data reporting requirement | N/A | N/A | 17 | 12 | 58 | 24 | 24 | 0 | 15 | 13 | 1 | 3 | 5 | 4 | 4 | 0 |  |  |  | Number per year | The total number of historical ignitions has risen since the initial submission due to ongoing audits of systems of records including FAS, the EIR database, and CAP. It is likely the number of historical ignitions will continue to increase as other systems of record are audited for potential missed ignitions.
7. Number of utility-related ignitions | 7.b. | Number of ignitions | All | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Number in HFTD Zone 1 per year
|  | Number of ignitions | RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & not RFW | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | All | 2 | 7 | 6 | 17 | 7 | 4 | 0 | 4 | 6 | 0 | 1 | 3 | 2 | 0 | 0 |  |  |  | Number in HFTD Tier 2 per year
|  | Number of ignitions | RFW | 2 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0
|  | Number of ignitions | HWW | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & RFW | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & not RFW | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | All | 3 | 2 | 2 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 |  |  |  | Number in HFTD Tier 3 per year
|  | Number of ignitions | RFW | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & RFW | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & not RFW | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | All | Non-HFTD | 8 | 4 | 31 | 15 | 20 | 0 | 11 | 7 | 1 | 1 | 2 | 1 | 4 | 0 |  |  |  | Number in non-HFTD per year
|  | Number of ignitions | RFW | Non-HFTD | 0 | 0 | 3 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0
|  | Number of ignitions | HWW | Non-HFTD | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & RFW | Non-HFTD | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Number of ignitions | HWW & not RFW | Non-HFTD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8. Fatalities resulting from utility wildfire mitigation initiatives | 8.a. | Fatalities due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | N/A | N/A | - | - | - | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 1 |  |  |  | Number of fatalities per year
9. OSHA-reportable injuries from utility wildfire mitigation initiatives | 9.a. | OSHA-reportable injuries due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | N/A | N/A | - | - | - | 2 | 1 | 0 | 1 | 1 | 1 | 0 | 2 | 0 | 1 | 3 |  |  |  | Number of OSHA-reportable injuries per year
Energy Safety’s template defined Transmission lines at or above 65kV, and distribution lines to all lines below 65kV, but PG&E uses 60kV as the threshold. The data in Table 2 is derived from ignitions that are linked to a wildfire, which is defined as a fire greater than 10 acres in size. - It should be noted that a small percentage of risk events do not have accurate Lat/Long coordinates assigned to it thus limiting the ability to determine the specified Wind Warning Status and HFTD Tier locations. As such, items 1.a., 1.b., 1.c., and 1.d. of the updated 2022 Table 2 have been populated to the extent of the available Lat/Long coordinate data. Furthermore, PG&E’s electric transmission outage reporting application (Transmission Operation Tracking & Logging) is not programmed to gather or report fault locations in terms of latitude/longitude and instead are reported by structure number or multiple structures as warranted. Data for 2021 were gathered as part of the newly established quarterly submittal process to OEIS by evaluating each 2021 unplanned “risk” event and retrieving the respective LAT/LONG of the reported structure(s) from PG&E’s Electric Transmission-Geographical Information System (ET-GIS). Given these limitations, PG&E was not able to include the information for every single risk event in this response - Items 2.a to 2.c and 2a.ii to 2c.ii · Inspection findings values were extracted utilizing the same filter criteria used to create PG&E's Compliance "repair tag" Plan Quarterly Update. · "Other" Inspections include Pole Test & Treat and work verification work - Items 2.d and 2d.ii · PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. · Items 3.a (Fatalities due to utility-ignited wildfire [total]) and 3.b (Injuries due to utility-ignited wildfire (total)): PG&E provides in the attached data table 2015 through 2019 for wildfires that the California Department of Forestry and Fire protection (CAL FIRE) concluded were caused by PG&E equipment. · Item 4a (Value of assets destroyed by utility-ignited wildfire [total]): PG&E provides in the attached data table all 2015-2020 wildfires that involve disputes regarding destroyed assets that have settled. These settlements are lump sum settlements that do not break out the settlement dollars by damage category. In addition, the settlements reached related to the 2017 North Bay Fires and the 2018 Camp Fire (other than the settlement with the cities and counties) do not break out the settlement dollars by fire. Any attempt to break out the dollars by fire and/or damage category would be speculative. The settlements are totaled based on the year of the fire. The one exception is the 2018 Camp Fire which is reported with the 2017 North Bay Fires for the reasons described above. The chart does not include wildfires that have not settled, which remain under investigation and/or civil discovery on causation issues, damages issues, or both. · Item 5b (Critical infrastructure damaged/destroyed by utility-ignited wildfire [total]): ‘Critical infrastructure’ is defined in accordance with the definition adopted in Decision (D.) 19-05-042 and modified in D.20-05-051. The number of critical infrastructure damaged/destroyed reflects the count of unique Service Point ID’s (meters) for red-tagged structures defined as critical infrastructure at the time of the wildfire. · Item 7a-b (Number of utility wildfire ignitions): The 2015 through 2018 ignition data is primarily based on fire incident reports filed with the California Public Utilities Commission (CPUC or Commission) annually in accordance with D.14-02-015. These reports include fire incidents that may be associated with PG&E facilities and meet the following conditions: (1) a self-propagating fire of material other than electrical and/or communication facilities (2) the resulting fire traveled greater than one linear meter from the ignition point, and (3) PG&E has knowledge that the fire occurred. Where not already included as part of the CPUC fire incidents report data, PG&E also included data for 2015 through 2018 wildfires that CAL FIRE concluded were caused by PG&E equipment.

## Table 3
Utility | Pacific Gas & Electric Company
Table No. | 3
Date Modified | 2022-02-11
Note: These columns are placeholders for future QR submissions.
Table 3: List and description of additional metrics | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
PG&E provided several metrics in the 2021 WMP for this section. With the update of the WMP template, all of these metrics were incorporated and included in other parts of the 2022 WMP. PG&E has no new or additional metrics to include to evaluate wildfire mitigation that are not already captured in other sections of the 2022 WMP. However, PG&E may analyze and look to reuse these metrics in ways not documented in the WMP as we continue to mature our data sets and modeling.

## Table 4
Utility | Pacific Gas & Electric Company
Table No. | 4
Date Modified | 2022-05-02
Note: These columns are placeholders for future QR submissions.
Table 4: Fatalities due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Fatalities - Full-time Employee | 1.a. | Fatalities due to utility inspection - Full-time employee | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 1.b. | Fatalities due to vegetation management - Full-time employee | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 1.c. | Fatalities due to utility fuel management - Full-time employee | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 1.d. | Fatalities due to grid hardening - Full-time employee | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 1.e. | Fatalities due to other - Full-time employee | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
2. Fatalities - Contractor | 2.a. | Fatalities due to utility inspection - Contractor | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | # fatalities
| 2.b. | Fatalities due to vegetation management - Contractor | - | - | - | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 2.c. | Fatalities due to utility fuel management - Contractor | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 2.d. | Fatalities due to grid hardening - Contractor | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 2.e. | Fatalities due to other - Contractor | - | - | - | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | # fatalities
3. Fatalities - Member of public | 3.a. | Fatalities due to utility inspection - Public | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 3.b. | Fatalities due to vegetation management - Public | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 3.c. | Fatalities due to utility fuel management - Public | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 3.d. | Fatalities due to grid hardening - Public | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # fatalities
| 3.e. | Fatalities due to other - Public | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  |  | # fatalities
Comments for Table 4: 1. Data for “Member of public” was derived from review of PG&E’s “Riskmaster” database, which tracks third party claims. 2. Please note that data in the "Riskmaster" database can be retroactively updated as more data is obtained. 3. PG&E’s Community Wildfire Safety Program (CWSP), under which PG&E tracks our wildfire mitigation activities, was developed in 2018, with the above activities implemented in late 2018. Therefore, the “Year 2018” data above represents data from late 2018.

## Table 5
Utility | Pacific Gas & Electric Company
Table No. | 5
Date Modified | 2022-05-02
Note: These columns are placeholders for future QR submissions.
Table 5: OSHA-reportable injuries due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. OSHA injuries - Full-time Employee | 1.a. | OSHA injuries due to utility inspection - Full-time employee | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
| 1.b. | OSHA injuries due to vegetation management - Full-time employee | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
| 1.c. | OSHA injuries due to utility fuel management - Full-time employee | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
| 1.d. | OSHA injuries due to grid hardening - Full-time employee | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  |  |  | # OSHA-reportable injuries
| 1.e. | OSHA injuries due to other - Full-time employee | - | - | - | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
2. OSHA injuries - Contractor | 2.a. | OSHA injuries due to utility inspection - Contractor | - | - | - | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
| 2.b. | OSHA injuries due to vegetation management - Contractor | - | - | - | 1 | 0 | 0 | 0 | 4 | 1 | 0 | 2 | 0 | 2 | 0 |  |  |  | # OSHA-reportable injuries
| 2.c. | OSHA injuries due to utility fuel management - Contractor | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
| 2.d. | OSHA injuries due to grid hardening - Contractor | - | - | - | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 2 |  |  |  | # OSHA-reportable injuries
| 2.e. | OSHA injuries due to other - Contractor | - | - | - | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
3. OSHA injuries - Member of public | 3.a. | OSHA injuries due to utility inspection - Public | - | - | - | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
| 3.b. | OSHA injuries due to vegetation management - Public | - | - | - | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
| 3.c. | OSHA injuries due to utility fuel management - Public | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
| 3.d. | OSHA injuries due to grid hardening - Public | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | # OSHA-reportable injuries
| 3.e. | OSHA injuries due to other - Public | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  |  | # OSHA-reportable injuries
Comments for Table 5: 1. PG&E has limited information regarding injuries to contractors and members of the public, and any related medical treatment, during wildfire mitigation initiatives because PG&E is not responsible for reporting those injuries to OSHA. Thus, the figures in Table 5 relating to OSHA-reportable injuries to contractors and members of the public due to wildfire mitigation initiatives are based on PG&E's best available data for injuries that, given their severity, would have likely been reported to OSHA by PG&E had the injuries occurred to a PG&E employee. 2. Please note that data in the "Riskmaster" database can be retroactively updated as more data is obtained. 3. PG&E’s CWSP, under which PG&E tracks our wildfire mitigation activities, was developed in 2018, with the above activities implemented in late 2018. Therefore, the “Year 2018” data above represents data from late 2018. 4. OSHA-reportable injuries resulting in fatalities due to wildfire mitigation activities are captured in Table 4 rather than Table 5 to avoid double-counting. 5. PG&E defines OSHA Reportable injuries if the fall within these criteria: a. Event that results in the loss of life b. Event that results in hospitalization due to a serious injury or illness means any injury or illness occurring in a place of employment or in connection with any employment that requires inpatient hospitalization for other than medical observation or diagnostic testing, or in which an employee suffers an amputation, the loss of body part, or any serious degree of permanent disfigurement, but does not include any injury or illness or death caused an accident on a public street or highway, unless the accident occurred in a construction zone. c. Event that results in hospitalization for more than 24 hours or more than observation

## Table 6
Utility | Pacific Gas & Electric Company
Table No. | 6
Date Modified | 2022-05-02
Note: These columns are placeholders for future QR submissions.
Table 6: Weather patterns | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Red Flag Warning Circuit Mile Days | 1.a. | Red Flag Warning overhead Circuit Mile days - entire utility territory | 148629.78 | 171642.81 | 594877.94 | 632033.39 | 577409.39 | 0 | 104375.13 | 285515.17 | 365180.7 | 6403.91 | 141547.28 | 160424.88 | 131870.87 | - |  |  |  | Sum of circuit miles of utility grid subject to Red Flag Warning each day within a given time period, calculated as the number of circuit miles that were under an RFW multiplied by the number of days those miles were under said RFW. For example, if 100 circuit miles were under an RFW for 1 day, and 10 of those miles were under RFW for an additional day, then the total RFW circuit mile days would be 110.
| 1.b. | Red Flag Warning overhead Circuit Mile days - HFTD Zone 1 | 87.81 | 8.42 | 65.48 | 347.77 | 164.27 | 0 | 0 | 154.46 | 163.51 | - | 1.36 | 40.74 | 0 | - |  |  |  | Red Flag Warning OH Circuit Mile days, see above for definition
| 1.c. | Red Flag Warning overhead Circuit Mile days - HFTD Tier 2 | 30101.21 | 48603.57 | 169935.61 | 166968.54 | 132579.98 | 0 | 14708.29 | 85128.14 | 105136.89 | 2673.32 | 43213.47 | 49293.94 | 21999.77 | - |  |  |  | Red Flag Warning OH Circuit Mile days, see above for definition
| 1.d. | Red Flag Warning overhead Circuit Mile days - HFTD Tier 3 | 12210.71 | 21835.32 | 89698.22 | 70654.04 | 56819.47 | 0 | 3346.08 | 29214.41 | 56324.3 | 516.29 | 14284.15 | 21200.88 | 6269.48 | - |  |  |  | Red Flag Warning OH Circuit Mile days, see above for definition
| 1.e. | Red Flag Warning overhead Circuit Mile days - Non-HFTD | 106230.05 | 101195.51 | 335178.62 | 394063.04 | 387845.67 | 0 | 86320.76 | 171018.16 | 203556 | 3214.31 | 84048.29 | 89889.29 | 103601.62 | - |  |  |  | Red Flag Warning OH Circuit Mile days, see above for definition
2. Wind conditions | 2.a. | High wind warning overhead circuit mile days | 2393.63 | 28023 | 140758.36 | 3996.58 | 83181.8 | 3142.43 | 581.79 | 0 | 1137.73 | 8415.73 | 779.31 | 0 | 2274.81 | 4989.23 |  |  |  | Sum of circuit miles of utility grid subject to High Wind Warnings (HWW, as defined by the National Weather Service) each day within a given time period, calculated as the number of circuit miles that were under an HWW multiplied by the number of days those miles were under said HWW. For example, if 100 circuit miles were under an HWW for 1 day, and 10 of those miles were under HWW for an additional day, then the total HWW circuit mile days would be 110.
3. Other | 3.a. | Other relevant weather pattern metrics tracked (add additional rows as needed) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Comments for Table 6: Table 6 shows the trends of National Weather Service (NWS) issued Red Flag Warnings (RFWs) and High Wind Warnings (HWWs) over the last 5 years impacting PG&E circuits across the territory through the metrics RFW Circuit Mile Days and HWW Circuit Mile Days. NWS RFWs are a proxy for high fire danger conditions, while HWWs are issued for solely high wind threats, regardless of humidity values and fire danger. These values have changed from previous reports, which calculated RFW Day Circuit miles based on Fire Index Areas. For these metrics, circuit miles are now calculated by the NWS RFW and HWW polygons to give a more accurate and precise values for RFW Circuit Mile Days and HWW Circuit Mile Days.

## Table 7.1
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 7.1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2022-05-02 | Data from 2015 - 2022 Q1 should be actual numbers. 2022 Q2 - 2024 should be projected. In future submissions update projected numbers with actuals
[6 empty] | Number of risk events | [13 empty] | Projected risk events
| Table 7.1: Key recent and projected drivers of risk events | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| Risk Event category | Cause category | # | Sub-cause category | Are risk events tracked for ignition driver? (yes / no) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | Unit(s) | Comments
x | Wire down event - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | Yes | 1387 | 1618 | 3566 | 1052 | 3267 | 665 | 238 | 270 | 176 | 1096 | 169 | 199 | 1621 | 206 | 203.5 | 234.5 | 898.5 | 651 | 186.25 | 216.75 | 1259.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 1.b. | Animal contact- Distribution | Yes | 99 | 96 | 93 | 107 | 100 | 35 | 28 | 24 | 31 | 22 | 25 | 24 | 21 | 20 | 26.5 | 24 | 26 | 21 | 25.75 | 24 | 23.5 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 1.c. | Balloon contact- Distribution | Yes | 38 | 36 | 32 | 53 | 35 | 6 | 20 | 14 | 7 | 7 | 17 | 8 | 6 | 4 | 18.5 | 11 | 6.5 | 5.5 | 17.75 | 9.5 | 6.25 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 1.d. | Vehicle contact- Distribution | Yes | 551 | 629 | 600 | 602 | 561 | 126 | 153 | 187 | 157 | 133 | 170 | 191 | 172 | 126 | 161.5 | 189 | 164.5 | 129.5 | 165.75 | 190 | 168.25 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 1.e. | Other contact from object - Distribution | Yes | 104 | 123 | 108 | 102 | 106 | 26 | 17 | 20 | 18 | 31 | 27 | 33 | 16 | 26 | 22 | 26.5 | 17 | 28.5 | 24.5 | 29.75 | 16.5 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 2. Equipment / facility failure - Distribution | 2.a. | Connector damage or failure- Distribution | Yes | 518 | 518 | 943 | 500 | 767 | 144 | 109 | 113 | 116 | 367 | 102 | 95 | 336 | 110 | 105.5 | 104 | 226 | 238.5 | 103.75 | 99.5 | 281 | # risk events (excluding ignitions) | Assumed this was meant to indicate conductor damage and not connector damage since these would be covered as splices. This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.b. | Splice damage or failure — Distribution | Yes | 231 | 262 | 320 | 225 | 245 | 64 | 47 | 48 | 54 | 86 | 58 | 43 | 65 | 42 | 52.5 | 45.5 | 59.5 | 64 | 55.25 | 44.25 | 62.25 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.c. | Crossarm damage or failure - Distribution | Yes | 36 | 50 | 86 | 46 | 69 | 13 | 10 | 6 | 19 | 27 | 7 | 11 | 35 | 7 | 8.5 | 8.5 | 27 | 17 | 7.75 | 9.75 | 31 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.d. | Insulator damage or failure- Distribution | Yes | 20 | 20 | 37 | 34 | 26 | 11 | 7 | 4 | 6 | 4 | 2 | 5 | 9 | 11 | 4.5 | 4.5 | 7.5 | 7.5 | 3.25 | 4.75 | 8.25 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.e. | Lightning arrestor damage or failure- Distribution | Yes | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0.75 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.f. | Tap damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Unclear what is requested and assumed this data detail is not readily available.
|  |  | 2.g. | Tie wire damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data detail is not readily available and jumper wire failures are included with the splice failure data.
|  |  | 2.h. | Other - Distribution | Yes | 118 | 151 | 319 | 141 | 208 | 38 | 16 | 23 | 35 | 97 | 28 | 26 | 98 | 31 | 22 | 24.5 | 66.5 | 64 | 25 | 25.25 | 82.25 | # risk events (excluding ignitions) | Includes ignition events since this detail is not readily available to be excluded.
|  | 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Generally not applicable to wire down events.
|  | 4. Contamination - Distribution | 4.a. | Contamination - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Not applicable. PG&E uses contamination more as a condition of the equipment and not normally as a basic cause.
|  | 5. Utility work / Operation | 5.a. | Utility work / Operation | No | 8 | 22 | 9 | 12 | 15 | 3 | 2 | 6 | 3 | 5 | 8 | 6 | 4 | 0 | 5 | 6 | 3.5 | 2.5 | 6.5 | 6 | 3.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | Yes | 4 | 2 | 2 | 6 | 4 | 0 | 0 | 1 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 1.5 | 1 | 1 | 0 | 1.75 | 0.5 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 7. Other- Distribution | 7.a. | All Other- Distribution | Yes | 100 | 72 | 264 | 69 | 97 | 22 | 23 | 78 | 8 | 35 | 10 | 18 | 153 | 16 | 16.5 | 48 | 80.5 | 25.5 | 13.25 | 33 | 116.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 8. Unknown- Distribution | 8.a. | Unknown - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Generally not applicable to wire down events.
x | Wire down event - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | Yes | 20 | 10 | 35 | 5 | 18 | 5 | 0 | 0 | 1 | 11 | 0 | 0 | 14 | 2 | 0 | 0 | 7.5 | 6.5 | 0 | 0 | 10.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.b. | Animal contact- Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.c. | Balloon contact- Transmission | Yes | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.d. | Vehicle contact- Transmission | Yes | 8 | 5 | 8 | 10 | 9 | 4 | 1 | 0 | 2 | 3 | 3 | 1 | 2 | 2 | 2 | 0.5 | 2 | 2.5 | 2.5 | 0.75 | 2 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.e. | Other contact from object - Transmission | Yes | 5 | 4 | 4 | 4 | 1 | 0 | 3 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 0.5 | 0 | 0 | 1.5 | 0.75 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 10. Equipment / facility failure - Transmission | 10.a. | Connector damage or failure- Transmission | Yes | 7 | 14 | 8 | 7 | 28 | 6 | 1 | 1 | 3 | 23 | 1 | 2 | 13 | 4 | 1 | 1.5 | 8 | 13.5 | 1 | 1.75 | 10.5 | # risk events (excluding ignitions) | Assume OEIS meant "Conductor"; does not exclude events that led to CPUC reportable ignition
|  |  | 10.b. | Splice damage or failure — Transmission | Yes | 5 | 3 | 7 | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0 | 0 | 0.25 | 0.5 | 0 | # risk events (excluding ignitions) | Includes "Connector" failures; does not exclude events that led to CPUC reportable ignition
|  |  | 10.c. | Crossarm damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | 0.5 | 2 | 0 | 0 | 0.75 | 3 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.d. | Insulator damage or failure- Transmission | Yes | 3 | 0 | 2 | 2 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0.5 | 0 | 0 | 0.5 | 0.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.e. | Lightning arrestor damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.f. | Tap damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.g. | Tie wire damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.h. | Other - Transmission | Yes | 5 | 2 | 15 | 2 | 3 | 2 | 0 | 1 | 0 | 4 | 1 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 2 | 0.75 | 0.25 | 0 | # risk events (excluding ignitions) | Pole & Line Switch failures; does not exclude events that led to CPUC reportable ignition
|  | 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 12. Contamination - Transmission | 12.a. | Contamination - Transmission | Yes | 2 | 0 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0.5 | 0 | 1 | 0 | 0.25 | 0 | 1 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 13. Utility work / Operation | 13.a. | Utility work / Operation | No | 1 | 0 | 1 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | Yes | 1 | 3 | 4 | 2 | 4 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0.5 | 0 | 0.25 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 15. Other- Transmission | 15.a. | All Other- Transmission | Yes | 7 | 4 | 11 | 7 | 6 | 1 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 3 | 0 | 0.5 | 0 | 3 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 16. Unknown- Transmission | 16.a. | Unknown - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
x | Outage - Distribution | 17. Contact from object - Distribution | 17.a. | Veg. contact- Distribution | Yes | 3760 | 4432 | 8277 | 3361 | 8198 | 1665 | 823 | 863 | 674 | 2629 | 680 | 684 | 3535 | 795 | 1172.9551 | 1229.9638 | 960.5975 | 741.9433 | 1094.6743 | 1147.8784 | 896.4891 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 17.b. | Animal contact- Distribution | Yes | 2354 | 2242 | 2197 | 2448 | 2071 | 402 | 648 | 632 | 757 | 495 | 784 | 765 | 628 | 525 | 671.3227 | 654.7468 | 784.2458 | 522.1983 | 667.7401 | 651.2527 | 780.0606 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 17.c. | Balloon contact- Distribution | Yes | 476 | 526 | 526 | 647 | 465 | 105 | 214 | 158 | 129 | 152 | 303 | 174 | 102 | 124 | 219.9014 | 162.3571 | 132.5574 | 121.8126 | 216.0222 | 159.4931 | 130.219 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 17.d. | Vehicle contact- Distribution | Yes | 1819 | 2041 | 1917 | 1917 | 1837 | 418 | 592 | 567 | 544 | 463 | 577 | 624 | 556 | 504 | 594.3642 | 569.2644 | 546.1725 | 495.1091 | 583.8793 | 559.2222 | 536.5377 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 17.e. | Other contact from object - Distribution | Yes | 729 | 645 | 629 | 693 | 735 | 158 | 184 | 181 | 185 | 185 | 222 | 189 | 176 | 168 | 201.21 | 197.9294 | 202.3035 | 165.0364 | 197.6605 | 194.4378 | 198.7348 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 18. Equipment / facility failure - Distribution | 18.a. | Capacitor bank damage or failure- Distribution | Yes | 57 | 65 | 83 | 55 | 70 | 7 | 22 | 17 | 21 | 20 | 20 | 23 | 17 | 18 | 22.4946 | 17.3822 | 21.4721 | 17.866 | 22.3271 | 17.2528 | 21.3122 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.b. | Conductor damage or failure — Distribution | Yes | 1281 | 1359 | 2063 | 1238 | 1926 | 384 | 281 | 297 | 322 | 807 | 340 | 331 | 767 | 333 | 347.3245 | 367.101 | 398.0017 | 330.5203 | 344.7381 | 364.3673 | 395.038 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 18.c. | Fuse damage or failure - Distribution | Yes | 373 | 352 | 479 | 305 | 341 | 48 | 84 | 190 | 125 | 171 | 153 | 123 | 222 | 190 | 73.286 | 165.766 | 109.0566 | 188.5851 | 72.7403 | 164.5316 | 108.2445 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.d. | Lightning arrestor damage or failure- Distribution | Yes | 144 | 145 | 139 | 135 | 131 | 26 | 42 | 31 | 46 | 36 | 29 | 23 | 53 | 27 | 42.4769 | 31.352 | 46.5223 | 26.7989 | 42.1606 | 31.1185 | 46.1758 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.e. | Switch damage or failure- Distribution | Yes | 141 | 156 | 178 | 188 | 188 | 30 | 50 | 44 | 35 | 53 | 54 | 65 | 60 | 36 | 60.0283 | 52.8249 | 42.0198 | 35.7319 | 59.5813 | 52.4315 | 41.7069 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.f. | Pole damage or failure - Distribution | Yes | 502 | 628 | 1111 | 665 | 1149 | 193 | 210 | 173 | 247 | 403 | 228 | 342 | 538 | 213 | 240.0816 | 197.7815 | 282.3817 | 211.4139 | 238.2938 | 196.3087 | 280.2789 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.g. | Insulator and brushing damage or failure - Distribution | Yes | 253 | 295 | 384 | 272 | 375 | 74 | 86 | 66 | 84 | 132 | 83 | 63 | 107 | 81 | 94.7279 | 72.6982 | 92.525 | 80.3968 | 94.0225 | 72.1568 | 91.836 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.h. | Crossarm damage or failure - Distribution | Yes | 573 | 717 | 777 | 771 | 995 | 207 | 190 | 179 | 253 | 296 | 254 | 275 | 437 | 189 | 212.21 | 199.9241 | 282.5743 | 187.5926 | 210.6297 | 198.4354 | 280.4701 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 59 | 62 | 59 | 52 | 59 | 13 | 22 | 17 | 16 | 12 | 25 | 28 | 15 | 18 | 20.6631 | 15.967 | 15.0277 | 17.866 | 20.5093 | 15.8481 | 14.9158 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.j. | Recloser damage or failure - Distribution | Yes | 61 | 60 | 102 | 90 | 112 | 12 | 10 | 19 | 15 | 36 | 20 | 23 | 76 | 28 | 16.4385 | 31.2331 | 24.6577 | 27.7915 | 16.316 | 31.0005 | 24.4741 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.k. | Anchor / guy damage or failure - Distribution | Yes | 36 | 41 | 47 | 47 | 57 | 14 | 9 | 19 | 14 | 23 | 10 | 12 | 22 | 9 | 9.175 | 19.3693 | 14.2721 | 8.933 | 9.1066 | 19.2251 | 14.1659 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.l. | Sectionalizer damage or failure - Distribution | Yes | 4 | 3 | 2 | 4 | 3 | 0 | 0 | 2 | 0 | 3 | 2 | 2 | 0 | 0 | 0 | 3.2112 | 0 | 0 | 0 | 3.1873 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.m. | Connection device damage or failure - Distribution | Yes | 1210 | 1250 | 1687 | 1095 | 1386 | 322 | 264 | 264 | 325 | 558 | 368 | 257 | 433 | 315 | 293.0904 | 293.0904 | 360.812 | 312.6543 | 290.9079 | 290.9079 | 358.1252 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 18.n. | Transformer damage or failure - Distribution | Yes | 4224 | 3947 | 4977 | 3136 | 3969 | 728 | 1104 | 1856 | 1088 | 1206 | 1289 | 1403 | 1327 | 992 | 979.912 | 1647.3883 | 965.7104 | 984.6129 | 972.615 | 1635.1208 | 958.5191 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.o. | Other - Distribution | Yes | 2241 | 2426 | 2612 | 2094 | 2242 | 376 | 529 | 640 | 448 | 650 | 655 | 585 | 672 | 458 | 599.3946 | 725.1655 | 507.6158 | 454.5894 | 594.9311 | 719.7654 | 503.8358 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  | 19. Wire-to-wire contact - Distribution | 19.a. | Wire-to-wire contact / contamination- Distribution | Yes | 4900 | 5239 | 6731 | 5276 | 6732 | 1700 | 1178 | 1087 | 1383 | 2408 | 1250 | 1071 | 2217 | 1448 | 1385.6939 | 1278.6496 | 1626.8375 | 1422.4564 | 1361.2494 | 1256.0934 | 1598.1391 | # risk events (excluding ignitions) | PG&E uses contamination more as a condition of the equipment and not normally as a basic cause. Assumed this cause refers to a Basic Cause of "Unknown" and a Fault Type of "Line to Line". This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  | 20. Contamination - Distribution | 20.a. | Contamination - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | PG&E typically uses contamination as a condition of the equipment and not normally as a basic cause.
|  | 21. Utility work / Operation | 21.a. | Utility work / Operation | No | 431 | 650 | 793 | 680 | 886 | 185 | 240 | 240 | 204 | 293 | 249 | 297 | 299 | 192 | 254.7208 | 254.7208 | 216.5127 | 190.802 | 253.1315 | 253.1315 | 215.1618 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 22. Vandalism / Theft - Distribution | 22.a. | Vandalism / Theft - Distribution | Yes | 45 | 26 | 26 | 58 | 44 | 10 | 13 | 17 | 16 | 13 | 12 | 14 | 13 | 22 | 12.4641 | 16.2993 | 15.3405 | 21.9639 | 12.4437 | 16.2725 | 15.3153 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 23. Other- Distribution | 23.a. | All Other- Distribution | Yes | 1818 | 752 | 1488 | 1232 | 978 | 111 | 255 | 1402 | 95 | 181 | 188 | 249 | 388 | 147 | 202.0717 | 1110.9981 | 75.2816 | 144.4068 | 198.507 | 1091.3994 | 73.9536 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  | 24. Unknown- Distribution | 24.a. | Unknown - Distribution | Yes | 7974 | 8185 | 12158 | 6726 | 9503 | 1978 | 1715 | 1971 | 2137 | 3809 | 2407 | 2343 | 3400 | 1376 | 1898.5228 | 2181.9175 | 2365.6812 | 1367.5417 | 1886.8526 | 2168.5052 | 2351.1394 | # risk events (excluding ignitions) | Omits the outages reported with an unknown cause that are shown in the row above for wire-to-wire contacts. This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
x | Outage - Transmission | 25. Contact from object - Transmission | 25.a. | Veg. contact- Transmission | Yes | 57 | 50 | 141 | 27 | 76 | 21 | 1 | 0 | 3 | 36 | 0 | 2 | 39 | 5 | 0.5 | 1 | 21 | 20.5 | 0.25 | 1.5 | 30 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.b. | Animal contact- Transmission | Yes | 56 | 58 | 65 | 58 | 44 | 15 | 8 | 11 | 13 | 0 | 14 | 4 | 9 | 8 | 11 | 7.5 | 11 | 4 | 12.5 | 5.75 | 10 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.c. | Balloon contact- Transmission | Yes | 13 | 8 | 14 | 20 | 12 | 4 | 5 | 6 | 1 | 2 | 6 | 2 | 1 | 2 | 5.5 | 4 | 1 | 2 | 5.75 | 3 | 1 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.d. | Vehicle contact- Transmission | Yes | 61 | 66 | 69 | 79 | 49 | 18 | 14 | 17 | 24 | 23 | 23 | 18 | 10 | 20 | 18.5 | 17.5 | 17 | 21.5 | 20.75 | 17.75 | 13.5 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.e. | Other contact from object - Transmission | Yes | 34 | 22 | 20 | 14 | 26 | 2 | 5 | 19 | 2 | 9 | 3 | 8 | 2 | 3 | 4 | 13.5 | 2 | 6 | 3.5 | 10.75 | 2 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 26. Equipment / facility failure - Transmission | 26.a. | Capacitor bank damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.b. | Conductor damage or failure — Transmission | Yes | 14 | 29 | 23 | 24 | 53 | 16 | 3 | 5 | 15 | 26 | 4 | 1 | 14 | 7 | 3.5 | 3 | 14.5 | 16.5 | 3.75 | 2 | 14.25 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0.25 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.d. | Lightning arrestor damage or failure- Transmission | Yes | 0 | 2 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.5 | 0.5 | 0 | 0.5 | 0.25 | 0.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.e. | Switch damage or failure- Transmission | Yes | 67 | 24 | 25 | 17 | 34 | 8 | 6 | 5 | 3 | 4 | 7 | 1 | 4 | 0 | 6.5 | 3 | 3.5 | 2 | 6.75 | 2 | 3.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.f. | Pole damage or failure - Transmission | Yes | 27 | 15 | 53 | 42 | 68 | 7 | 7 | 8 | 5 | 19 | 4 | 2 | 18 | 1 | 5.5 | 5 | 11.5 | 10 | 4.75 | 3.5 | 14.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.g. | Insulator and brushing damage or failure - Transmission | Yes | 51 | 75 | 78 | 86 | 65 | 19 | 40 | 26 | 33 | 11 | 16 | 11 | 9 | 3 | 28 | 18.5 | 21 | 7 | 22 | 14.75 | 15 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.h. | Crossarm damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 5 | 7 | 8 | 1 | 6 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.75 | 0.25 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.j. | Recloser damage or failure - Transmission | Yes | 36 | 30 | 44 | 29 | 29 | 10 | 4 | 12 | 9 | 5 | 8 | 2 | 2 | 3 | 6 | 7 | 5.5 | 4 | 7 | 4.5 | 3.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.k. | Anchor / guy damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0.5 | 0.5 | 1 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.l. | Sectionalizer damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.m. | Connection device damage or failure - Transmission | Yes | 19 | 37 | 32 | 18 | 51 | 3 | 16 | 24 | 8 | 3 | 2 | 1 | 0 | 0 | 9 | 12.5 | 4 | 1.5 | 5.5 | 6.75 | 2 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.n. | Transformer damage or failure - Transmission | Yes | 1 | 6 | 0 | 2 | 9 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0.5 | 0.5 | 1 | 0 | 0.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.o. | Other - Transmission | Yes | 63 | 45 | 56 | 40 | 49 | 12 | 19 | 7 | 9 | 13 | 4 | 7 | 2 | 3 | 11.5 | 7 | 5.5 | 8 | 7.75 | 7 | 3.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 27. Wire-to-wire contact - Transmission | 27.a. | Wire-to-wire contact / contamination- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 28. Contamination - Transmission | 28.a. | Contamination - Transmission | Yes | 22 | 18 | 25 | 51 | 17 | 6 | 13 | 9 | 6 | 4 | 16 | 14 | 9 | 4 | 14.5 | 11.5 | 7.5 | 4 | 15.25 | 12.75 | 8.25 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 29. Utility work / Operation | 29.a. | Utility work / Operation | No | 51 | 36 | 50 | 76 | 451 | 25 | 56 | 70 | 109 | 77 | 122 | 76 | 72 | 56 | 89 | 73 | 90.5 | 66.5 | 105.5 | 74.5 | 81.25 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 30. Vandalism / Theft - Transmission | 30.a. | Vandalism / Theft - Transmission | Yes | 7 | 10 | 9 | 5 | 21 | 2 | 2 | 4 | 1 | 1 | 1 | 6 | 2 | 0 | 1.5 | 5 | 1.5 | 0.5 | 1.25 | 5.5 | 1.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 31. Other- Transmission | 31.a. | All Other- Transmission | Yes | 436 | 138 | 388 | 168 | 314 | 93 | 57 | 163 | 25 | 115 | 26 | 72 | 141 | 34 | 41.5 | 117.5 | 83 | 74.5 | 33.75 | 94.75 | 112 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 32. Unknown- Transmission | 32.a. | Unknown - Transmission | Yes | 158 | 158 | 168 | 187 | 162 | 26 | 34 | 36 | 34 | 45 | 25 | 16 | 31 | 32 | 29.5 | 26 | 32.5 | 38.5 | 27.25 | 21 | 31.75 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
Updated comments for Table 7.1 (5/2/2022): Projected Risk events were updated based on the Q1 2022 actuals and revisions to 2021 data, if applicable. Comments for Table 7.1: 2022 and 2023 HFTD Distribution outages: Values show impact of implementation of EPSS based on preliminary modeling
Comments for Table 7.1: Key Recent and Projected Drivers of Ignition Probability, Last 5 Years (Distribution System): To the extent available, PG&E’s Integrated Logging Information System – Operations Data Base (ILIS-ODB) was used to provide the level of detail contained in Table 7.1 (Distribution) that includes both sustained and momentary outages experienced on our distribution system. When reviewing this data, the following should be noted: · Based on PG&E’s standard definition, a distribution wire down event results in a reportable outage event and occurs when a normally energized electric primary distribution conductor is broken, or stays intact, and falls from its intended position to rest on the ground or a foreign object. PG&E used this standard definition in this year’s report and thus it does not include any secondary related wire down events. However, it should also be noted that any primary or secondary wire down condition that resulted in an outage event is also reported in the distribution outage results. · In our 2020 WMP, PG&E utilized a different data extraction method attempting to identify a larger number of distribution wire down event conditions. However, it was subsequently determined this method resulted in an erroneously higher number of distribution wire down events due to various data issues such as momentary outages resulting from the same wire down event/condition that was also reported as a sustained outage. · For sub-cause category 2.a.”Connector damage or failure – Distribution,” it was assumed that the word “Connector” was meant to indicate “Conductor” since connector damage would typically be reported as splice damage. · For sub-cause category 8.a. “Unknown – Distribution,” this generally does not apply to distribution wire down events. · PG&E was unsure what was intended by the use of the term “Fuse damage or failure” because when a fuse isolates a fault condition, it will become permanently damaged and by design will no longer conduct electricity. For this subcategory, PG&E has interpreted it as only those outage events when a fuse was reported as the actual failed equipment. · PG&E does not have an outage cause classification that specifically matches the terms, “Tap damage or failure – Distribution” and “Tie wire damage or failure – Distribution” and thus did not use these categories in this report. · For “Wire-to-wire contact/Contamination,” PG&E typically does not use this term for distribution wire down events. In addition, PG&E typically uses contamination more as a condition of the equipment and not normally as a basic cause. For this category under the Distribution outages, PG&E assumed this cause refers to a Basic Cause of “Unknown” and a Fault Type of “Line to Line.” · For “Contamination – Distribution,” PG&E uses contamination more as a condition of the equipment and not as a basic cause. As such, PG&E does not have an outage classification that matches this term. · For “Unknown – Distribution” outages, this category omits outages reported with a Basic Cause of “Unknown” and a Fault Type of “Line to Line” covered as “Wire-to-wire contact/Contamination” outages noted in the above bullet item. · Due to their relatively small contribution, the Commission does not require transformer-only outages be reported in the annual electric system reliability metrics. However, transformer-only outages are reported within PG&E’s Field Automation System (FAS) and most were also reported in PG&E’s ILIS-ODB outage data base. PG&E is including these transformer-only outages in the WMP reporting to reflect the full picture of outage incidents which could have represented ignition potential. PG&E also further enhanced our reporting process/controls in September 2020 to ensure future transformer-only outages are fully reported in our ILIS-ODB outage data base and is working to improve outage cause reporting. · In Table 7.1 (Distribution), columns under the category ‘Projected risk events’ depict the projections in the respective years. Projections are based on forecasts submitted in the 2020 RAMP Report.
Comments for Table 7.1: Key Recent and Projected Drivers of Ignition Probability, Last 5 Years (Transmission System): PG&E’s Transmission Operations Tracking & Logging (TOTL) application was used as the primary data source for Table 7.1 (Transmission) which includes unplanned outages experienced on the transmission (i.e., >50 kV) system. Unplanned outages include those due to an “automatic” operation (i.e., the transmission line relayed automatically by a protective device (typically a circuit breaker) and either automatically tested OK, tested no good, or was set up not to test (e.g., automatics disabled or cut out for wildfire risk mitigation)). Unplanned outages also include those where the line was manually removed from service by Operations on an “emergency” basis, usually to repair or replace an imminent failure of an asset. Such emergency forced outages (EFOs) are taken without securing approval from the California Independent System Operator (CAISO). Planned or “scheduled” outages are not included. Scheduled outages differ from EFOs in that PG&E garnered CAISO approval prior to the line being removed from service. Based on PG&E’s standard definition, a transmission wire down event (similar to distribution) results in a reportable outage event (note: customers may or may not have been de-energized) and occurs when a normally energized electric transmission conductor fails in service and falls from its intended position to rest on the ground or a foreign object. • Sub-cause category 10.a. “Connector damage or failure – Transmission,” PG&E assumed that the word “Connector” was meant to indicate “Conductor” since connector damage would be reported separately in 10.b. • Sub-cause category 10.f. “Tap damage or failure – Transmission,” PG&E does not have an outage cause classification that specifically matches such. • Sub-cause category 10.g. “Tie wire damage or failure – Transmission” does not exist in PG&E outage reporting. • Sub-cause category 11.a. and 27.a. “Wire-to-wire contact/Contamination-Transmission” does not exist in PG&E transmission outage reporting and therefore has no data entries. • Unlike distribution outage reporting, cause category “Contamination – Transmission” is tracked and reported accordingly. • Every effort is made to minimize the number of outages assigned a cause category “Unknown – Transmission” for automatic type outages. At least one and sometimes more patrols are conducted after the outage to determine cause and certainly to find and correct any damaged equipment, usually with the help of fault location data provided by System Protection to help focus on the failure point. It’s also important to note that any outage due to animal contact is one where the patrol found a carcass to support the cause of animal, otherwise the choice “Unknown” is used. • Sub-cause category 26.c. “Fuse damage or failure” has no meaning for unplanned transmission outages. • Sub-cause category 26.h. “Crossarm damage or failure – Transmission” is not separately reported but included as part of reporting in the Sub-cause category “Pole damage or failure – Transmission,” if applicable. • Sub-cause category 26.j. “Recloser damage or failure – Transmission” represents outages where a circuit breaker failed in service and led to an outage. • Sub-cause category 26.l. “Sectionalizer damage or failure – Transmission” has no entries; rather, transmission lines are sectionalized using line switches, hence such failures are captured in cause Category 26.e. “Switch damage or failure- Transmission.” • In Table 7.1 (Transmission), columns under the category ‘Projected risk events’ depict the projections in the respective years. Projections are based on forecasts submitted in the 2020 RAMP Report.

## Table 7.2
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 7.2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2022-05-02 | Data from 2015 - 2021 should be actual numbers. 2022 and 2023 should be projected. In future submissions update projected numbers with actuals
| Table 7.2: Key recent and projected drivers of ignitions | [5 empty] | Number of ignitions | [7 empty] | Projected ignitions
| Metric type | # | Ignition driver | Line Type | HFTD tier | Are ignitions tracked for ignition driver? (yes / no) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Unit(s) | Comments
x | 1. Contact from object | 1.a.i | Veg. contact | Distribution | Non-HFTD | Yes | 45 | 45 | 76 | 57 | 76 | 63 | 75 | 2 | 67.6667 | # ignitions
|  | 1.a.ii | Veg. contact | Distribution | HFTD Zone 1 | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.71 | # ignitions
|  | 1.a.iii | Veg. contact | Distribution | HFTD Tier 2 | Yes | 38 | 40 | 61 | 32 | 46 | 38 | 42 | 3 | 28.4 | # ignitions
|  | 1.a.iv | Veg. contact | Distribution | HFTD Tier 3 | Yes | 24 | 23 | 40 | 36 | 16 | 27 | 24 | 1 | 17.04 | # ignitions
|  | 1.a.v | Veg. contact | Distribution | System | Yes | 108 | 108 | 177 | 125 | 138 | 128 | 142 | 6 | 113.8167 | # ignitions
|  | 1.a.vi | Veg. contact | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.a.vii | Veg. contact | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.a.viii | Veg. contact | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0.66667 | # ignitions
|  | 1.a.ix | Veg. contact | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.44444 | # ignitions
|  | 1.a.x | Veg. contact | Transmission | System | Yes | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 1.1111 | # ignitions
|  | 1.b.i | Animal contact | Distribution | Non-HFTD | Yes | 49 | 34 | 54 | 37 | 56 | 37 | 28 | 6 | 45.4444 | # ignitions
|  | 1.b.ii | Animal contact | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.b.iii | Animal contact | Distribution | HFTD Tier 2 | Yes | 7 | 6 | 10 | 12 | 10 | 9 | 8 | 1 | 5.68 | # ignitions
|  | 1.b.iv | Animal contact | Distribution | HFTD Tier 3 | Yes | 2 | 2 | 1 | 5 | 1 | 0 | 1 | 0 | 0.71 | # ignitions
|  | 1.b.v | Animal contact | Distribution | System | Yes | 58 | 42 | 65 | 54 | 67 | 46 | 37 | 7 | 51.8344 | # ignitions
|  | 1.b.vi | Animal contact | Transmission | Non-HFTD | Yes | 3 | 5 | 5 | 6 | 7 | 3 | 0 | 1 | 2.1111 | # ignitions
|  | 1.b.vii | Animal contact | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.b.viii | Animal contact | Transmission | HFTD Tier 2 | Yes | 4 | 4 | 4 | 4 | 1 | 3 | 1 | 0 | 1.8889 | # ignitions
|  | 1.b.ix | Animal contact | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 2 | 3 | 0 | 2 | 0 | 0 | 0.88889 | # ignitions
|  | 1.b.x | Animal contact | Transmission | System | Yes | 7 | 9 | 11 | 13 | 8 | 8 | 1 | 1 | 4.8889 | # ignitions
|  | 1.c.i | Balloon contact | Distribution | Non-HFTD | Yes | 20 | 11 | 11 | 10 | 15 | 14 | 15 | 2 | 14 | # ignitions
|  | 1.c.ii | Balloon contact | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.c.iii | Balloon contact | Distribution | HFTD Tier 2 | Yes | 4 | 2 | 0 | 3 | 0 | 0 | 1 | 0 | 0.71 | # ignitions
|  | 1.c.iv | Balloon contact | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  | 1.c.v | Balloon contact | Distribution | System | Yes | 24 | 13 | 11 | 13 | 15 | 14 | 16 | 3 | 14.71 | # ignitions
|  | 1.c.vi | Balloon contact | Transmission | Non-HFTD | Yes | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | # ignitions
|  | 1.c.vii | Balloon contact | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.c.viii | Balloon contact | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.44444 | # ignitions
|  | 1.c.ix | Balloon contact | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.c.x | Balloon contact | Transmission | System | Yes | 0 | 1 | 1 | 0 | 1 | 2 | 1 | 0 | 1.4444 | # ignitions
|  | 1.d.i | Vehicle contact | Distribution | Non-HFTD | Yes | 38 | 23 | 40 | 18 | 31 | 42 | 28 | 5 | 34.4444 | # ignitions
|  | 1.d.ii | Vehicle contact | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.d.iii | Vehicle contact | Distribution | HFTD Tier 2 | Yes | 9 | 13 | 11 | 8 | 5 | 10 | 7 | 0 | 4.97 | # ignitions
|  | 1.d.iv | Vehicle contact | Distribution | HFTD Tier 3 | Yes | 1 | 0 | 4 | 2 | 0 | 3 | 2 | 0 | 0.71 | # ignitions
|  | 1.d.v | Vehicle contact | Distribution | System | Yes | 48 | 36 | 55 | 28 | 36 | 55 | 37 | 5 | 40.1244 | # ignitions
|  | 1.d.vi | Vehicle contact | Transmission | Non-HFTD | Yes | 0 | 1 | 1 | 3 | 4 | 2 | 3 | 1 | 2.6667 | # ignitions
|  | 1.d.vii | Vehicle contact | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.d.viii | Vehicle contact | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.d.ix | Vehicle contact | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.d.x | Vehicle contact | Transmission | System | Yes | 0 | 1 | 1 | 3 | 4 | 2 | 3 | 1 | 2.6667 | # ignitions
|  | 1.e.i | Other contact from object | Distribution | Non-HFTD | Yes | 7 | 3 | 3 | 33 | 16 | 17 | 12 | 1 | 18.2222 | # ignitions
|  | 1.e.ii | Other contact from object | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.e.iii | Other contact from object | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 3 | 9 | 5 | 6 | 2 | 0 | 1.42 | # ignitions
|  | 1.e.iv | Other contact from object | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  | 1.e.v | Other contact from object | Distribution | System | Yes | 7 | 3 | 6 | 49 | 21 | 23 | 14 | 2 | 19.6422 | # ignitions
|  | 1.e.vi | Other contact from object | Transmission | Non-HFTD | Yes | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0.11111 | # ignitions
|  | 1.e.vii | Other contact from object | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.e.viii | Other contact from object | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 1.3333 | # ignitions
|  | 1.e.ix | Other contact from object | Transmission | HFTD Tier 3 | Yes | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0.11111 | # ignitions
|  | 1.e.x | Other contact from object | Transmission | System | Yes | 0 | 1 | 1 | 3 | 2 | 3 | 0 | 0 | 1.5556 | # ignitions
| 2. Equipment / facility failure | 2.a.i | Capacitor bank damage or failure | Distribution | Non-HFTD | Yes | 12 | 10 | 11 | 5 | 7 | 7 | 4 | 2 | 6.7778 | # ignitions
|  | 2.a.ii | Capacitor bank damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.iii | Capacitor bank damage or failure | Distribution | HFTD Tier 2 | Yes | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.iv | Capacitor bank damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.v | Capacitor bank damage or failure | Distribution | System | Yes | 14 | 12 | 13 | 8 | 7 | 7 | 4 | 2 | 6.7778 | # ignitions
|  | 2.a.vi | Capacitor bank damage or failure | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.vii | Capacitor bank damage or failure | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.viii | Capacitor bank damage or failure | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.ix | Capacitor bank damage or failure | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.x | Capacitor bank damage or failure | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.b.i | Conductor damage or failure | Distribution | Non-HFTD | Yes | 36 | 43 | 57 | 27 | 61 | 49 | 51 | 5 | 51.4444 | # ignitions
|  | 2.b.ii | Conductor damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.b.iii | Conductor damage or failure | Distribution | HFTD Tier 2 | Yes | 11 | 8 | 15 | 11 | 10 | 7 | 6 | 0 | 3.55 | # ignitions
|  | 2.b.iv | Conductor damage or failure | Distribution | HFTD Tier 3 | Yes | 3 | 6 | 4 | 2 | 3 | 0 | 4 | 1 | 2.84 | # ignitions
|  | 2.b.v | Conductor damage or failure | Distribution | System | Yes | 50 | 57 | 76 | 40 | 74 | 56 | 61 | 6 | 57.8344 | # ignitions
|  | 2.b.vi | Conductor damage or failure | Transmission | Non-HFTD | Yes | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0.88889 | # ignitions
|  | 2.b.vii | Conductor damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.b.viii | Conductor damage or failure | Transmission | HFTD Tier 2 | Yes | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.b.ix | Conductor damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.55556 | # ignitions
|  | 2.b.x | Conductor damage or failure | Transmission | System | Yes | 1 | 3 | 3 | 0 | 0 | 2 | 1 | 0 | 1.4444 | # ignitions
|  | 2.c.i | Fuse damage or failure | Distribution | Non-HFTD | Yes | 4 | 7 | 8 | 2 | 5 | 7 | 7 | 0 | 5.5556 | # ignitions
|  | 2.c.ii | Fuse damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.c.iii | Fuse damage or failure | Distribution | HFTD Tier 2 | Yes | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | # ignitions
|  | 2.c.iv | Fuse damage or failure | Distribution | HFTD Tier 3 | Yes | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | # ignitions
|  | 2.c.v | Fuse damage or failure | Distribution | System | Yes | 7 | 7 | 10 | 2 | 5 | 11 | 7 | 0 | 5.5556 | # ignitions
|  | 2.c.vi | Fuse damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.c.vii | Fuse damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.c.viii | Fuse damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.c.ix | Fuse damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.c.x | Fuse damage or failure | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.i | Lightning arrestor damage or failure | Distribution | Non-HFTD | Yes | 6 | 3 | 6 | 1 | 3 | 1 | 1 | 1 | 2.3333 | # ignitions
|  | 2.d.ii | Lightning arrestor damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.iii | Lightning arrestor damage or failure | Distribution | HFTD Tier 2 | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.iv | Lightning arrestor damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.v | Lightning arrestor damage or failure | Distribution | System | Yes | 7 | 3 | 6 | 1 | 3 | 1 | 1 | 1 | 2.3333 | # ignitions
|  | 2.d.vi | Lightning arrestor damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.vii | Lightning arrestor damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.viii | Lightning arrestor damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.ix | Lightning arrestor damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.x | Lightning arrestor damage or failure | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.i | Switch damage or failure | Distribution | Non-HFTD | Yes | 3 | 3 | 5 | 1 | 1 | 3 | 4 | 0 | 1.4444 | # ignitions
|  | 2.e.ii | Switch damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.iii | Switch damage or failure | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0.71 | # ignitions
|  | 2.e.iv | Switch damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  | 2.e.v | Switch damage or failure | Distribution | System | Yes | 3 | 3 | 5 | 1 | 2 | 4 | 5 | 0 | 2.1544 | # ignitions
|  | 2.e.vi | Switch damage or failure | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.vii | Switch damage or failure | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.viii | Switch damage or failure | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.ix | Switch damage or failure | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.x | Switch damage or failure | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.f.i | Pole damage or failure | Distribution | Non-HFTD | Yes | 4 | 5 | 11 | 7 | 6 | 8 | 8 | 0 | 7 | # ignitions
|  | 2.f.ii | Pole damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.f.iii | Pole damage or failure | Distribution | HFTD Tier 2 | Yes | 1 | 2 | 2 | 4 | 0 | 1 | 2 | 0 | 1.42 | # ignitions
|  | 2.f.iv | Pole damage or failure | Distribution | HFTD Tier 3 | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.f.v | Pole damage or failure | Distribution | System | Yes | 6 | 7 | 13 | 11 | 6 | 9 | 10 | 0 | 8.42 | # ignitions
|  | 2.f.vi | Pole damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.f.vii | Pole damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.f.viii | Pole damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.f.ix | Pole damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.11111 | # ignitions
|  | 2.f.x | Pole damage or failure | Transmission | System | Yes | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0.11111 | # ignitions
|  | 2.g.i | Insulator and brushing damage or failure | Distribution | Non-HFTD | Yes | 6 | 4 | 8 | 4 | 3 | 4 | 2 | 0 | 3.5556 | # ignitions
|  | 2.g.ii | Insulator and brushing damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.g.iii | Insulator and brushing damage or failure | Distribution | HFTD Tier 2 | Yes | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | # ignitions
|  | 2.g.iv | Insulator and brushing damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0.71 | # ignitions
|  | 2.g.v | Insulator and brushing damage or failure | Distribution | System | Yes | 7 | 4 | 9 | 5 | 4 | 6 | 3 | 0 | 4.2656 | # ignitions
|  | 2.g.vi | Insulator and brushing damage or failure | Transmission | Non-HFTD | Yes | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0.44444 | # ignitions
|  | 2.g.vii | Insulator and brushing damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.g.viii | Insulator and brushing damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 0.66667 | # ignitions
|  | 2.g.ix | Insulator and brushing damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.g.x | Insulator and brushing damage or failure | Transmission | System | Yes | 1 | 1 | 2 | 1 | 2 | 2 | 0 | 0 | 1.1111 | # ignitions
|  | 2.h.i | Crossarm damage or failure | Distribution | Non-HFTD | Yes | 5 | 7 | 5 | 1 | 1 | 2 | 3 | 0 | 1.4444 | # ignitions
|  | 2.h.ii | Crossarm damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.h.iii | Crossarm damage or failure | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 5 | 1 | 1 | 0 | 1 | 0 | 0.71 | # ignitions
|  | 2.h.iv | Crossarm damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0.71 | # ignitions
|  | 2.h.v | Crossarm damage or failure | Distribution | System | Yes | 5 | 7 | 13 | 2 | 2 | 2 | 5 | 0 | 2.8644 | # ignitions
|  | 2.h.vi | Crossarm damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.h.vii | Crossarm damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.h.viii | Crossarm damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.h.ix | Crossarm damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.h.x | Crossarm damage or failure | Transmission | System | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.i.i | Voltage regulator / booster damage or failure | Distribution | Non-HFTD | Yes | 2 | 0 | 5 | 0 | 1 | 3 | 3 | 0 | 1.7778 | # ignitions
|  | 2.i.ii | Voltage regulator / booster damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.i.iii | Voltage regulator / booster damage or failure | Distribution | HFTD Tier 2 | Yes | 4 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | # ignitions
|  | 2.i.iv | Voltage regulator / booster damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.i.v | Voltage regulator / booster damage or failure | Distribution | System | Yes | 6 | 1 | 5 | 0 | 2 | 4 | 3 | 0 | 1.7778 | # ignitions
|  | 2.i.vi | Voltage regulator / booster damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.i.vii | Voltage regulator / booster damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.i.viii | Voltage regulator / booster damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.44444 | # ignitions
|  | 2.i.ix | Voltage regulator / booster damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.i.x | Voltage regulator / booster damage or failure | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.44444 | # ignitions
|  | 2.j.i | Recloser damage or failure | Distribution | Non-HFTD | Yes | 0 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 1.3333 | # ignitions
|  | 2.j.ii | Recloser damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.iii | Recloser damage or failure | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  | 2.j.iv | Recloser damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.v | Recloser damage or failure | Distribution | System | Yes | 0 | 3 | 3 | 0 | 3 | 1 | 3 | 0 | 1.3333 | # ignitions
|  | 2.j.vi | Recloser damage or failure | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.vii | Recloser damage or failure | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.viii | Recloser damage or failure | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.ix | Recloser damage or failure | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.x | Recloser damage or failure | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.i | Anchor / guy damage or failure | Distribution | Non-HFTD | Yes | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0.55556 | # ignitions
|  | 2.k.ii | Anchor / guy damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.iii | Anchor / guy damage or failure | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.iv | Anchor / guy damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.v | Anchor / guy damage or failure | Distribution | System | Yes | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0.55556 | # ignitions
|  | 2.k.vi | Anchor / guy damage or failure | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.vii | Anchor / guy damage or failure | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.viii | Anchor / guy damage or failure | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.ix | Anchor / guy damage or failure | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.x | Anchor / guy damage or failure | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.i | Sectionalizer damage or failure | Distribution | Non-HFTD | Yes | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.ii | Sectionalizer damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.iii | Sectionalizer damage or failure | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.iv | Sectionalizer damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.v | Sectionalizer damage or failure | Distribution | System | Yes | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.vi | Sectionalizer damage or failure | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.vii | Sectionalizer damage or failure | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.viii | Sectionalizer damage or failure | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.ix | Sectionalizer damage or failure | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.x | Sectionalizer damage or failure | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.m.i | Connection device damage or failure | Distribution | Non-HFTD | Yes | 40 | 20 | 29 | 2 | 0 | 29 | 33 | 1 | 12.6667 | # ignitions
|  | 2.m.ii | Connection device damage or failure | Distribution | HFTD Zone 1 | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.m.iii | Connection device damage or failure | Distribution | HFTD Tier 2 | Yes | 2 | 3 | 8 | 2 | 0 | 8 | 9 | 0 | 6.39 | # ignitions
|  | 2.m.iv | Connection device damage or failure | Distribution | HFTD Tier 3 | Yes | 2 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0.71 | # ignitions
|  | 2.m.v | Connection device damage or failure | Distribution | System | Yes | 45 | 24 | 39 | 4 | 0 | 37 | 43 | 1 | 19.7667 | # ignitions
|  | 2.m.vi | Connection device damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.44444 | # ignitions
|  | 2.m.vii | Connection device damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.m.viii | Connection device damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.m.ix | Connection device damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.m.x | Connection device damage or failure | Transmission | System | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0.44444 | # ignitions
|  | 2.n.i | Transformer damage or failure | Distribution | Non-HFTD | Yes | 14 | 11 | 18 | 12 | 19 | 15 | 10 | 1 | 16.3333 | # ignitions
|  | 2.n.ii | Transformer damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.n.iii | Transformer damage or failure | Distribution | HFTD Tier 2 | Yes | 4 | 2 | 3 | 2 | 1 | 6 | 2 | 0 | 1.42 | # ignitions
|  | 2.n.iv | Transformer damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.n.v | Transformer damage or failure | Distribution | System | Yes | 18 | 13 | 23 | 18 | 20 | 21 | 12 | 1 | 17.7533 | # ignitions
|  | 2.n.vi | Transformer damage or failure | Transmission | Non-HFTD | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.n.vii | Transformer damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.n.viii | Transformer damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.n.ix | Transformer damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.n.x | Transformer damage or failure | Transmission | System | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.o.i | Other | Distribution | Non-HFTD | Yes | 31 | 22 | 24 | 26 | 22 | 20 | 29 | 2 | 21.1111 | # ignitions
|  | 2.o.ii | Other | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.o.iii | Other | Distribution | HFTD Tier 2 | Yes | 4 | 3 | 4 | 9 | 3 | 2 | 5 | 0 | 2.84 | # ignitions
|  | 2.o.iv | Other | Distribution | HFTD Tier 3 | Yes | 5 | 2 | 3 | 7 | 1 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.o.v | Other | Distribution | System | Yes | 40 | 27 | 31 | 42 | 26 | 22 | 34 | 2 | 23.9511 | # ignitions
|  | 2.o.vi | Other | Transmission | Non-HFTD | Yes | 3 | 0 | 1 | 0 | 2 | 1 | 3 | 0 | 2.4444 | # ignitions
|  | 2.o.vii | Other | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.o.viii | Other | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 1 | 3 | 1 | 1 | 1 | 0 | 1 | # ignitions
|  | 2.o.ix | Other | Transmission | HFTD Tier 3 | Yes | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0.88889 | # ignitions
|  | 2.o.x | Other | Transmission | System | Yes | 3 | 1 | 3 | 3 | 3 | 3 | 5 | 0 | 4.3333 | # ignitions
| 3. Wire-to-wire contact | 3.a.i | Wire-to-wire contact / contamination | Distribution | Non-HFTD | Yes | 3 | 4 | 3 | 1 | 10 | 20 | 0 | 0 | 13.4444 | # ignitions
|  | 3.a.ii | Wire-to-wire contact / contamination | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 3.a.iii | Wire-to-wire contact / contamination | Distribution | HFTD Tier 2 | Yes | 1 | 2 | 1 | 3 | 1 | 7 | 0 | 0 | 0 | # ignitions
|  | 3.a.iv | Wire-to-wire contact / contamination | Distribution | HFTD Tier 3 | Yes | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 3.a.v | Wire-to-wire contact / contamination | Distribution | System | Yes | 5 | 6 | 4 | 5 | 11 | 27 | 0 | 0 | 13.4444 | # ignitions
|  | 3.a.vi | Wire-to-wire contact / contamination | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 3.a.vii | Wire-to-wire contact / contamination | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 3.a.viii | Wire-to-wire contact / contamination | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 3.a.ix | Wire-to-wire contact / contamination | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 3.a.x | Wire-to-wire contact / contamination | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
| 4. Contamination | 4.a.i | Contamination | Distribution | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 1 | 1.3333 | # ignitions
|  | 4.a.ii | Contamination | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 4.a.iii | Contamination | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 1 | 1 | 0 | 2 | 3 | 0 | 2.13 | # ignitions
|  | 4.a.iv | Contamination | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1.42 | # ignitions
|  | 4.a.v | Contamination | Distribution | System | Yes | 0 | 0 | 1 | 1 | 0 | 5 | 15 | 1 | 4.8833 | # ignitions
|  | 4.a.vi | Contamination | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.44444 | # ignitions
|  | 4.a.vii | Contamination | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 4.a.viii | Contamination | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 4.a.ix | Contamination | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 4.a.x | Contamination | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.44444 | # ignitions
| 5. Utility work / Operation | 5.a.i | Utility work / Operation | Distribution | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | # ignitions
|  | 5.a.ii | Utility work / Operation | Distribution | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 5.a.iii | Utility work / Operation | Distribution | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 5.a.iv | Utility work / Operation | Distribution | HFTD Tier 3 | No | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.71 | # ignitions
|  | 5.a.v | Utility work / Operation | Distribution | System | No | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 0.71 | # ignitions
|  | 5.a.vi | Utility work / Operation | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 5.a.vii | Utility work / Operation | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 5.a.viii | Utility work / Operation | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.44444 | # ignitions
|  | 5.a.ix | Utility work / Operation | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 5.a.x | Utility work / Operation | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.44444 | # ignitions
| 6. Vandalism / Theft | 6.a.i | Vandalism / Theft | Distribution | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 0 | 0.88889 | # ignitions
|  | 6.a.ii | Vandalism / Theft | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6.a.iii | Vandalism / Theft | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  | 6.a.iv | Vandalism / Theft | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6.a.v | Vandalism / Theft | Distribution | System | Yes | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0.88889 | # ignitions
|  | 6.a.vi | Vandalism / Theft | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6.a.vii | Vandalism / Theft | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6.a.viii | Vandalism / Theft | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6.a.ix | Vandalism / Theft | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6.a.x | Vandalism / Theft | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
| 7. Other | 7.a.i | All Other | Distribution | Non-HFTD | Yes | 0 | 4 | 1 | 4 | 3 | 3 | 0 | 5 | 3.4444 | # ignitions
|  | 7.a.ii | All Other | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 7.a.iii | All Other | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 0 | 2.13 | # ignitions
|  | 7.a.iv | All Other | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | # ignitions
|  | 7.a.v | All Other | Distribution | System | Yes | 0 | 4 | 1 | 5 | 4 | 6 | 2 | 5 | 5.5744 | # ignitions
|  | 7.a.vi | All Other | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 7.a.vii | All Other | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 7.a.viii | All Other | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.44444 | # ignitions
|  | 7.a.ix | All Other | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 7.a.x | All Other | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.44444 | # ignitions
| 8. Unknown | 8.a.i | Unknown | Distribution | Non-HFTD | Yes | 2 | 1 | 2 | 18 | 12 | 0 | 2 | 1 | 7.7778 | # ignitions
|  | 8.a.ii | Unknown | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 8.a.iii | Unknown | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 1 | 6 | 2 | 0 | 1 | 0 | 2.13 | # ignitions
|  | 8.a.iv | Unknown | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0.71 | # ignitions
|  | 8.a.v | Unknown | Distribution | System | Yes | 2 | 1 | 4 | 25 | 14 | 0 | 3 | 1 | 10.6178 | # ignitions
|  | 8.a.vi | Unknown | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0.11111 | # ignitions
|  | 8.a.vii | Unknown | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 8.a.viii | Unknown | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0.11111 | # ignitions
|  | 8.a.ix | Unknown | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 8.a.x | Unknown | Transmission | System | Yes | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 0.22222 | # ignitions
Comments for Table 7.2: The fire ignition data provided in this table is based on fire incident reports filed with the CPUC annually in accordance with D.14-02-015. The ignition data provided in these tables was pulled from PG&E’s systems in mid-January 2022 and reflects preliminary data for two reasons: first, PG&E’s final 2021 fire ignition report is due on April 1, 2022 and 2021 data will be further reviewed in advance of that filing. Second, in late 2020 PG&E self-identified a data omission regarding prior year’s fire ignition data in the annual reports submitted and notified the CPUC of this issue on December 23, 2020. More detail is provided in WMP Section 6.7 discussion. PG&E’s Ignition Investigation team is conducting a system of record audit for ignition events. The updated counts in Table 7.2 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. The System HFTD Tier metric is the sum of Non HFTD, HFTD Zone 1, HFTD Tier 2, and HFTD Tier 3. 2022 and 2023 HFTD Distribution: Values show decreases as compared to 2021 HFTD distribution based on preliminary EPSS modeling forecasted against 2018-2020 data.

## Table 8
| Utility | Pacific Gas & Electric Company
| Table No. | 8
| Date Modified | 2022-05-02
| Table 8: State of service territory and utility equipment |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | Unit(s) | Comments
x | 1. State of service territory and equipment in urban areas | 1.a. | Circuit miles (including WUI and non-WUI) | [16 empty] | 15604 | 9 | 996 | 395 | 16296 | 1 | 1064 | 383 | 16259.2883 | 0.55426 | 1063.523 | 376.5677 | 34852.9143 | 0.55424 | 1396.2077 | 485.3435 |  |  |  |  | Circuit miles | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.b. | Circuit miles in WUI | [16 empty] | 4195 | 8 | 721 | 340 | 4791 | 0 | 754 | 319 | 4779.3583 | 0.34495 | 755.1437 | 313.6694 | 10698.8046 | 0.34485 | 1029.6495 | 415.008 |  |  |  |  | Circuit miles in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.c. | Number of critical facilities (including WUI and non-WUI) | [16 empty] | 17009 | 7 | 442 | 204 | 51008 |  | 1356 | 477 | 51952 | 0 | 1369 | 484 | 52464 |  | 1358 | 483 |  |  |  |  | Number of critical facilities | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.d. | Number of critical facilities in WUI | [16 empty] | 4213 | 5 | 402 | 172 | 13782 |  | 1051 | 421 | 13890 | 0 | 1058 | 427 | 14202 |  | 1052 | 422 |  |  |  |  | Number of critical facilities in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.e. | Number of customers (including WUI and non-WUI) | [16 empty] | 3966386 | 2172 | 76068 | 29274 | 4088697 | 9 | 79518 | 29936 | 4119512 | 9 | 80309 | 30166 | 4183633 | 9 | 79911 | 30886 |  |  |  |  | Number of customers | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.f. | Number of customers in WUI | [16 empty] | 1165448 | 1943 | 66452 | 27165 | 1195814 | 7 | 68926 | 27751 | 1201785 | 7 | 69646 | 27968 | 1237700 | 7 | 69186 | 28635 |  |  |  |  | Number of customers in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | [16 empty] | 120605 | 45 | 2084 | 727 | 158034 |  | 3384 | 1198 | 169094 | 0 | 3724 | 1340 | 173514 |  | 3757 | 1366 |  |  |  |  | Number of customers belonging to access and functional needs populations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.h. | Number of customers belonging to access and functional needs populations in WUI | [16 empty] | 38384 | 39 | 1895 | 688 | 51034 |  | 3070 | 1121 | 54746 | 0 | 3360 | 1252 | 57130 |  | 3370 | 1276 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | [16 empty] | 2178.8 | 0 | 226.8 | 62.3 | 2177.9 |  | 226.7 | 61.6 | 2169.0193 | 0 | 228.0265 | 60.942 | 2187.3145 |  | 218.9499 | 58.1292 |  |  |  |  | Circuit miles of overhead transmission lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.j. | Circuit miles of overhead transmission lines in WUI | [16 empty] | 516.9 | 0 | 87.6 | 37.5 | 517 |  | 88.5 | 36.8 | 515.0593 | 0 | 89.4019 | 36.1546 | 532.9372 |  | 85.2227 | 32.1786 |  |  |  |  | Circuit miles of overhead transmission lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | [16 empty] | 14141 | 0.5 | 840.6 | 326.9 | 14118 | 0.5 | 836.9 | 321.3 | 14090.269 | 0.51859 | 835.4965 | 315.6257 | 14065.2275 | 0.51858 | 804.81 | 307.4459 |  |  |  |  | Circuit miles of overhead distribution lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.l. | Circuit miles of overhead distribution lines in WUI | [16 empty] | 4278.7 | 0.4 | 664.1 | 288.2 | 4274.2 | 0.3 | 665.1 | 282.3 | 4264.299 | 0.34495 | 665.7418 | 277.5148 | 4348.5699 | 0.34485 | 647.0469 | 271.6586 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.m. | Number of substations (including WUI and non-WUI) | [16 empty] | 314 | 0 | 18 | 0 | 323 | - | 19 | - | 297 | 0 | 17 | 0 | 303 | 0 | 16 | 0 |  |  |  |  | Number of substations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.n | Number of substations in WUI | [16 empty] | 94 | 0 | 14 | 0 | 93 | - | 13 | - | 33 | 0 | 11 | 0 | 87 | 0 | 11 | 0 |  |  |  |  | Number of substations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.o. | Number of weather stations (including WUI and non-WUI) | [16 empty] | 1 | 0 | 7 | 3 | 17 | 0 | 17 | 8 | 22 | 0 | 18 | 9 | 22 | 0 | 18 | 9 |  |  |  |  | Number of weather stations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.p. | Number of weather stations in WUI | [16 empty] | 0 | 0 | 4 | 3 | 12 | 0 | 10 | 6 | 15 | 0 | 10 | 6 | 15 | 0 | 10 | 6 |  |  |  |  | Number of weather stations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
x | 2. State of service territory and equipment in rural areas | 2.a. | Circuit miles (including WUI and non-WUI) | [16 empty] | 45119 | 87 | 17020 | 7229 | 44489 | 8 | 17321 | 7262 | 44455.4291 | 8.3415 | 17272.8818 | 7199.1238 | 50869.7207 | 11.0337 | 18447.46 | 7638.8849 |  |  |  |  | Circuit miles | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.b. | Circuit miles in WUI | [16 empty] | 7962 | 57 | 9479 | 4671 | 7932 | 4 | 10846 | 4698 | 7920.3851 | 4.0674 | 9535.6348 | 4666.1777 | 10339.9197 | 6.4684 | 10527.247 | 5051.946 |  |  |  |  | Circuit miles in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.c. | Number of critical facilities (including WUI and non-WUI) | [16 empty] | 10134 | 42 | 1857 | 1009 | 19815 | 4 | 5223 | 2683 | 20283 | 4 | 5259 | 2669 | 19845 | 4 | 5242 | 2652 |  |  |  |  | Number of critical facilities | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.d. | Number of critical facilities in WUI | [16 empty] | 2532 | 29 | 1153 | 690 | 7228 | 3 | 3471 | 1945 | 7309 | 3 | 3516 | 1943 | 7062 | 3 | 3534 | 1926 |  |  |  |  | Number of critical facilities in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.e. | Number of customers (including WUI and non-WUI) | [16 empty] | 1051321 | 3877 | 249888 | 130048 | 974331 | 401 | 250571 | 131232 | 985685 | 407 | 251690 | 131471 | 932472 | 408 | 252184 | 127018 |  |  |  |  | Number of customers | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.f. | Number of customers in WUI | [16 empty] | 483462 | 3493 | 116821 | 210802 | 467317 | 368 | 211175 | 117920 | 470194 | 374 | 212392 | 118361 | 438023 | 375 | 213743 | 114610 |  |  |  |  | Number of customers in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | [16 empty] | 37116 | 158 | 11161 | 5530 | 43594 | 4 | 14670 | 7127 | 46432 | 4 | 15586 | 7570 | 43672 | 4 | 15711 | 7509 |  |  |  |  | Number of customers belonging to access and functional needs populations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.h. | Number of customers belonging to access and functional needs populations in WUI | [16 empty] | 18815 | 149 | 10055 | 5217 | 23914 | 4 | 13219 | 6729 | 25468 | 4 | 14077 | 7162 | 23983 | 4 | 14192 | 7115 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | [16 empty] | 8747.9 | 3 | 2962.8 | 1095.7 | 8748.4 | 3 | 2962.2 | 1095.5 | 8717.0691 | 3.0302 | 2959.9748 | 1090.2248 | 8815.8744 | 3.0302 | 2919.8947 | 1065.1915 |  |  |  |  | Circuit miles of overhead transmission lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.j. | Circuit miles of overhead transmission lines in WUI | [16 empty] | 917.8 | 1.3 | 830 | 291 | 917.8 | 1.3 | 829.2 | 290.7 | 909.9251 | 1.3172 | 826.8608 | 287.3427 | 887.7087 | 1.3171 | 835.8007 | 293.3891 |  |  |  |  | Circuit miles of overhead transmission lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | [16 empty] | 35771.5 | 5.4 | 14469.7 | 6281.4 | 35740.8 | 5.3 | 14358.9 | 6166.4 | 35738.36 | 5.3113 | 14312.907 | 6108.899 | 35979.8252 | 5.2263 | 14067.2418 | 5960.3285 |  |  |  |  | Circuit miles of overhead distribution lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.l. | Circuit miles of overhead distribution lines in WUI | [16 empty] | 7008.8 | 2.7 | 8724.8 | 4446.9 | 7013.6 | 2.7 | 8712.9 | 4407.6 | 7010.46 | 2.7502 | 8708.774 | 4378.835 | 6957.1301 | 2.7078 | 8693.1045 | 4297.583 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.m. | Number of substations (including WUI and non-WUI) | [16 empty] | 289 | 0 | 35 | 7 | 351 | 1 | 68 | 26 | 374 | 2 | 104 | 50 | 372 | 1 | 99 | 46 |  |  |  |  | Number of substations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.n | Number of substations in WUI | [16 empty] | 67 | 0 | 27 | 18 | 66 |  | 29 | 19 | 76 | 1 | 35 | 18 | 67 | 0 | 35 | 18 |  |  |  |  | Number of substations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.o. | Number of weather stations (including WUI and non-WUI) | [16 empty] | 59 | 0 | 250 | 157 | 135 | 0 | 399 | 205 | 197 | 0 | 527 | 253 | 198 | 0 | 529 | 253 |  |  |  |  | Number of weather stations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.p. | Number of weather stations in WUI | [16 empty] | 18 | 0 | 85 | 73 | 41 | 0 | 125 | 92 | 57 | 0 | 174 | 114 | 57 | 0 | 174 | 114 |  |  |  |  | Number of weather stations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
x | 3. State of service territory and equipment in highly rural areas | 3.a. | Circuit miles (including WUI and non-WUI) | [16 empty] | 7302 | 39 | 4539 | 825 | 7216 | 12 | 4024 | 675 | 7225.2123 | 12.001 | 4009.2344 | 678.617 | 7073.4227 | 21.154 | 4538.3243 | 905.6532 |  |  |  |  | Circuit miles | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.b. | Circuit miles in WUI | [16 empty] | 563 | 9 | 1035 | 331 | 498 | 1 | 942 | 274 | 501.1773 | 1.1918 | 941.7548 | 274.8566 | 525.3076 | 1.2989 | 1031.7915 | 376.3993 |  |  |  |  | Circuit miles in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.c. | Number of critical facilities (including WUI and non-WUI) | [16 empty] | 649 | 8 | 326 | 104 | 1087 | 2 | 797 | 297 | 1130 | 2 | 803 | 301 | 1035 | 2 | 834 | 323 |  |  |  |  | Number of critical facilities | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.d. | Number of critical facilities in WUI | [16 empty] | 108 | 4 | 144 | 60 | 250 | 1 | 385 | 185 | 258 | 1 | 386 | 185 | 231 | 1 | 365 | 210 |  |  |  |  | Number of critical facilities in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.e. | Number of customers (including WUI and non-WUI) | [16 empty] | 39611 | 1303 | 33739 | 9840 | 37193 | 93 | 30689 | 8545 | 37383 | 94 | 30602 | 8592 | 35682 | 94 | 30870 | 12448 |  |  |  |  | Number of customers | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.f. | Number of customers in WUI | [16 empty] | 14576 | 1068 | 22200 | 7919 | 13629 | 45 | 20733 | 7059 | 13613 | 45 | 20810 | 7129 | 11876 | 45 | 20134 | 10357 |  |  |  |  | Number of customers in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | [16 empty] | 878 | 7 | 1098 | 231 | 981 |  | 1287 | 263 | 1034 | 0 | 1319 | 276 | 974 |  | 1292 | 404 |  |  |  |  | Number of customers belonging to access and functional needs populations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.h. | Number of customers belonging to access and functional needs populations in WUI | [16 empty] | 475 | 4 | 813 | 188 | 456 |  | 961 | 215 | 480 | 0 | 982 | 223 | 472 |  | 955 | 334 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | [16 empty] | 1691.7 | 3.1 | 1039.3 | 135.5 | 1691.8 | 3.1 | 1039.2 | 135.4 | 1704.1571 | 3.1029 | 1038.9408 | 141.384 | 1586.8821 | 3.1029 | 1089.1296 | 168.4528 |  |  |  |  | Circuit miles of overhead transmission lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.j. | Circuit miles of overhead transmission lines in WUI | [16 empty] | 40.8 | 0 | 83.9 | 24.3 | 40.8 | 0 | 83.9 | 24.2 | 40.8271 | 0 | 83.8322 | 24.89 | 45.105 | 0 | 79.0616 | 22.8332 |  |  |  |  | Circuit miles of overhead transmission lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | [16 empty] | 5579.8 | 9 | 3032.4 | 546.9 | 5524.2 | 9 | 2984.8 | 540.1 | 5521.0552 | 8.8982 | 2970.2936 | 537.233 | 5278.7664 | 8.9625 | 3249.5388 | 686.2241 |  |  |  |  | Circuit miles of overhead distribution lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.l. | Circuit miles of overhead distribution lines in WUI | [16 empty] | 458.8 | 1.2 | 855.3 | 254.4 | 457.4 | 1.2 | 858.5 | 249.7 | 460.3502 | 1.1918 | 857.9226 | 249.9666 | 426.5629 | 1.2561 | 888.9491 | 333.3048 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.m. | Number of substations (including WUI and non-WUI) | [16 empty] | 51 | 0 | 22 | 6 | 57 |  | 19 | 5 | 69 | 0 | 65 | 16 | 65 | 0 | 71 | 20 |  |  |  |  | Number of substations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.n | Number of substations in WUI | [16 empty] | 3 | 0 | 7 | 3 | 4 |  | 7 | 2 | 7 | 0 | 17 | 4 | 4 | 0 | 17 | 4 |  |  |  |  | Number of substations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.o. | Number of weather stations (including WUI and non-WUI) | [16 empty] | 13 | 0 | 113 | 24 | 32 | 0 | 166 | 26 | 50 | 0 | 206 | 36 | 50 | 0 | 208 | 36 |  |  |  |  | Number of weather stations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.p. | Number of weather stations in WUI | [16 empty] | 3 | 0 | 18 | 8 | 5 | 0 | 29 | 8 | 7 | 0 | 31 | 13 | 7 | 0 | 31 | 13 |  |  |  |  | Number of weather stations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
| 1. State of service territory and equipment in urban areas | 1.q | Circuit miles of underground transmission lines (including WUI and non-WUI) | [28 empty] | 123.2748 | 0 | 1.8023 | 0 |  |  |  |  | Circuit miles of underground transmission lines | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 1. State of service territory and equipment in urban areas | 1.r | Circuit miles of underground transmission lines in WUI | [28 empty] | 20.8916 | 0 | 1.3204 | 0 |  |  |  |  | Circuit miles of underground transmission lines in WUI | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 1. State of service territory and equipment in urban areas | 1.s | Circuit miles of underground distribution lines (including WUI and non-WUI) | [28 empty] | 18477.0976 | 0.035661 | 370.6455 | 119.7684 |  |  |  |  | Circuit miles of underground distribution lines | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 1. State of service territory and equipment in urban areas | 1.t | Circuit miles of underground distribution lines in WUI | [28 empty] | 5796.4058 | 0 | 296.0595 | 111.1707 |  |  |  |  | Circuit miles of underground distribution lines in WUI | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 2. State of service territory and equipment in rural areas | 2.q | Circuit miles of underground transmission lines (including WUI and non-WUI) | [28 empty] | 47.1943 | 0 | 8.9804 | 0.93404 |  |  |  |  | Circuit miles of underground transmission lines | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 2. State of service territory and equipment in rural areas | 2.r | Circuit miles of underground transmission lines in WUI | [28 empty] | 8.1396 | 0 | 0.49677 | 0.548 |  |  |  |  | Circuit miles of underground transmission lines in WUI | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 2. State of service territory and equipment in rural areas | 2.s | Circuit miles of underground distribution lines (including WUI and non-WUI) | [28 empty] | 6026.8268 | 2.7772 | 1451.343 | 612.4308 |  |  |  |  | Circuit miles of underground distribution lines | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 2. State of service territory and equipment in rural areas | 2.t | Circuit miles of underground distribution lines in WUI | [28 empty] | 2486.9413 | 2.4434 | 997.8451 | 460.4259 |  |  |  |  | Circuit miles of underground distribution lines in WUI | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 3. State of service territory and equipment in highly rural areas | 3.q | Circuit miles of underground transmission lines (including WUI and non-WUI) | [28 empty] | 0 | 0 | 0 | 0 |  |  |  |  | Circuit miles of underground transmission lines | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 3. State of service territory and equipment in highly rural areas | 3.r | Circuit miles of underground transmission lines in WUI | [28 empty] | 0 | 0 | 0 | 0 |  |  |  |  | Circuit miles of underground transmission lines in WUI | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 3. State of service territory and equipment in highly rural areas | 3.s | Circuit miles of underground distribution lines (including WUI and non-WUI) | [28 empty] | 207.7741 | 9.0887 | 199.656 | 50.9763 |  |  |  |  | Circuit miles of underground distribution lines | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
| 3. State of service territory and equipment in highly rural areas | 3.t | Circuit miles of underground distribution lines in WUI | [28 empty] | 53.6397 | 0.04285 | 63.7808 | 20.2613 |  |  |  |  | Circuit miles of underground distribution lines in WUI | Added per data request from Energy Safety requesting Table 8 total circuit miles to include underground data
Updated comments for Table 7.1 (5/2/2022): Please note that we added Undergrounding mileage starting with our Q1 2022 submission. There are 5 weather stations, although installed by 12/31/21, should not be counted towards the 2021 WMP commitment as they were installed to support other PG&E programs. Thus, the total count of stations is 1323 with 1318 counted towards the WMP commitment. PG&E is using 2020 Census data and which has impacted the Urban, Rural and Highly Rural layers starting with our Q1 2022 submission. Comments for Table 8: Table 8 seeks information regarding the current baseline state of HFTD and non-HFTD service territory, as located in urban versus rural versus highly rural areas, including a subset with the Wildland-Urban Interface (WUI). The WUI is defined as areas where homes are built near or among lands prone to wildland fires. PG&E identifies WUI areas within PG&E’s service territory based upon data provided by the University of Wisconsin-Madison SILVIS Lab, available here: http://silvis.forest.wisc.edu/data/wui-change/, shows the WUI areas within California as of 2010. Note that in Table 8 data for 2015-2018 has not been provided for two reasons: (1) PG&E planned and executed a multi-year project starting in 2013 that included converting legacy sources of electric facility information into a single enterprise GIS database. The conversion started in 2014 and was completed in 2018. This conversion was executed, reviewed, and accepted in phases for the entire PG&E service territory during these project years. There is no historical database of the electric facilities during the requested years from 2015 to 2018 that would contain a complete and accurate inventory of all the electric facilities metrics requested in Table 8. (2) PG&E’s GIS system is a dynamic ‘real-time’ system that reflects the current assets in PG&E’s service territory, when old assets are removed or replaced, they are removed from the GIS system. Therefore, snapshots of asset information at prior points in history, before the WMP process began in 2019, are not available. Customers belonging to AFN (Access and Functional Needs) population dataset is based on Medical Baseline Customers only and does not reflect the revision of AFN definition in the 2021 WMP. This is due to the system limitation of the data within the various systems that are not currently connected to the enterprise GIS database. Substation count includes facility type: Distribution Switching station, Junction, Power House, Power Plant, Substation & Transmission Switching Station. PG&E’s GIS system is a dynamic ‘real-time’ system that reflects the current assets in PG&E’s service territory, hence data will continue to change as our system evolves.

## Table 9
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 9 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Report net additions using positive numbers and net removals and undergrounding using negative numbers for circuit miles and numbers of substations. Only report changes expected within the target year.
| Date Modified | 2022-02-11 | For example, if 20 net overhead circuit miles are planned for addition by 2023, with 15 being added by 2022 and 5 more added by 2023, then report “15” for 2022 and “5” for 2023. Do not report cumulative change across years. In this case, do not report “20” for 2023, but instead the number planned to be added for just that year, which is “5”.
|  |  |  | Actual | [7 empty] | Projected
| Table 9: Location of actual and planned utility equipment additions or removal year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | Unit(s)
x | 1. Planned utility equipment net addition (or removal) year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines | -0.9 | 0 | -0.1 | -0.7 | -8.8807 | 0 | 1.3265 | -0.65797 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 1.b. | Circuit miles of overhead distribution lines | -23 | 0 | -3.7 | -5.6 | -27.731 | 0.018595 | -1.4035 | -5.6743 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 1.c. | Circuit miles of overhead transmission lines in WUI | 0.1 | 0 | 0.9 | -0.7 | -1.9407 | 0 | 0.90192 | -0.64538 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 1.d. | Circuit miles of overhead distribution lines in WUI | -4.5 | -0.1 | 1 | -5.9 | -9.901 | 0.044946 | 0.6418 | -4.7852 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 1.e. | Number of substations | 0 | 0 | 0 | 0 | Note 4 | Note 4 | Note 4 | Note 4 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Number of substations
|  | 1.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | Note 4 | Note 4 | Note 4 | Note 4 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Number of substations in WUI
|  | 1.g. | Number of weather stations | 16 | 0 | 10 | 5 | 5 | 0 | 1 | 1 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations
|  | 1.h. | Number of weather stations in WUI | 12 | 0 | 6 | 3 | 3 | 0 | 0 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations in WUI
x | 2. Planned utility equipment net addition (or removal) year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines | 0.5 | 0 | -0.6 | -0.2 | -31.3309 | 0.030205 | -2.2252 | -5.2752 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 2.b. | Circuit miles of overhead distribution lines | -30.7 | -0.1 | -110.8 | -115 | -2.44 | 0.011291 | -45.993 | -57.501 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 2.c. | Circuit miles of overhead transmission lines in WUI | 0 | 0 | -0.8 | -0.3 | -7.8749 | 0.01715 | -2.3392 | -3.3573 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 2.d. | Circuit miles of overhead distribution lines in WUI | 4.8 | 0 | -11.9 | -39.3 | -3.14 | 0.050205 | -4.126 | -28.765 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 2.e. | Number of substations | 0 | 0 | 0 | 0 | Note 4 | Note 4 | Note 4 | Note 4 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Number of substations
|  | 2.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | Note 4 | Note 4 | Note 4 | Note 4 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Number of substations in WUI
|  | 2.g. | Number of weather stations | 76 | 0 | 149 | 48 | 62 | 0 | 128 | 48 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations
|  | 2.h. | Number of weather stations in WUI | 23 | 0 | 40 | 19 | 16 | 0 | 49 | 22 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations in WUI
x | 3. Planned utility equipment net addition (or removal) year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines | 0.1 | 0 | -0.1 | -0.1 | 12.3571 | 0.002873 | -0.25919 | 5.984 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 3.b. | Circuit miles of overhead distribution lines | -55.6 | 0 | -47.6 | -6.8 | -3.1448 | -0.10182 | -14.5064 | -2.867 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 3.c. | Circuit miles of overhead transmission lines in WUI | 0 | 0 | 0 | -0.1 | 0.02712 | 0 | -0.06779 | 0.69 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 3.d. | Circuit miles of overhead distribution lines in WUI | -1.4 | 0 | 3.2 | -4.7 | 2.9502 | -0.008219 | -0.5774 | 0.2666 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 3.e. | Number of substations | 0 | 0 | 0 | 0 | Note 4 | Note 4 | Note 4 | Note 4 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Number of substations
|  | 3.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | Note 4 | Note 4 | Note 4 | Note 4 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Number of substations in WUI
|  | 3.g. | Number of weather stations | 19 | 0 | 53 | 2 | 18 | 0 | 40 | 10 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations
|  | 3.h. | Number of weather stations in WUI | 2 | 0 | 11 | 0 | 2 | 0 | 2 | 5 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations in WUI
Comments for Table 9: The 2021 Actual data was derived by subtracting the 2020 data from the 2021 data in Table 8, and reflects the total net change in the system year-over-year. This logic is also applied for 2020 actual data were it’s a derived by subtracting the 2019 data from the 2020 data in Table 8 . The data presented for 2020 and 2021 Transmission and Distribution removals/additions represents the work for removal of idle facilities. There are many other reasons that conductor may be added or removed. The same layers used in Table 8 have been used to determine Population Density, HFTD, and WUI. Notes for Table 9: The data presented in this table are based on the best knowledge that PG&E has as of January 31, 2022. As better data becomes available, this will be updated in the quarterly updates. Note 1: For transmission & distribution line additions and removals for 2022 and 2023, project prioritization and timing have not been fully determined or mapped. Note 2: PG&E's has reached its weather station goal of the installation of 1,300 by the end of 2021. For Weather Station additional and removals for 2022, project prioritization and timing have not been fully determined or mapped. Note 3: For substation additional and removals for 2022 and 2023, project prioritization and timing have not been fully determined or mapped. Note 4: The substation count was refined after the submission of our May 5, 2021 self-identification letter relating to substation inspections. Since substations are facilities in which significant amounts of equipment is installed, a single installation date for this field cannot be provided. As a result, PG&E is unable to provide year-over-year data for 2021 because the dataset used in 2021 is different than that from 2020 and would cause discrepancies in the data set. However, PG&E will be able to report the year-over-year data for 2022 and all future years since this standardized counting method will allow for an accurate comparison of annual substation data going forward.

## Table 10
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 10 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2022-02-11 | In future submissions update planned upgrade numbers with actuals
|  |  | In the comments column on the far-right, enter the relevant program target(s) associated | Actual | [7 empty] | Projected
| Table 10: Location of actual and planned utility infrastructure upgrades year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | Unit(s) | Comment
x | 1. Planned utility infrastructure upgrades year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles | See Note 1 & Note 4
|  | 1.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles | See Note 3 & Note 5
|  | 1.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles in WUI | See Note 1 & Note 4
|  | 1.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles in WUI | See Note 3 & Note 5
|  | 1.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Number of substations | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
|  | 1.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
|  | 1.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | 0 | 0 | 0 | 0 | Number of weather stations | See Note 2
x |  | 1.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | See Note 2
| 2. Planned utility infrastructure upgrades year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles | See Note 1 & Note 4
|  | 2.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles | See Note 3 & Note 5
|  | 2.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles in WUI | See Note 1 & Note 4
|  | 2.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles in WUI | See Note 3 & Note 5
|  | 2.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | Number of substations | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
|  | 2.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Number of substations in WUI | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
x |  | 2.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | 0 | 0 | 0 | 0 | Number of weather stations | See Note 2
|  | 2.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | See Note 2
| 3. Planned utility infrastructure upgrades year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles | See Note 1 & Note 4
|  | 3.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles | See Note 3 & Note 5
|  | 3.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles in WUI | See Note 1 & Note 4
|  | 3.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles in WUI | See Note 3 & Note 5
|  | 3.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
|  | 3.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
|  | 3.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | 0 | 0 | 0 | 0 | Number of weather stations | See Note 2
|  | 3.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | See Note 2
Comments for Table 10: The data presented in this table are based on the best knowledge that PG&E has as of January 31, 2022. As better data becomes available, this will be updated in the quarterly updates. Note 1: PG&E reconducted approximately 119 miles of transmission conductor in 2020 and approximately 103 HFTD and 38 Non-HFTD miles of transmission conductor across its service territory in 2021, but all jobs have not been mapped into the GIS system in order to break the data down as required by this table. Note 2: PG&E plans to do some power upgrades on some weather stations in 2022, but projects have not been mapped as of January 2022 therefore its' projection will not be included in this dataset. Note 3: PG&E is in the process of replanning Distribution system hardening work for 2022 and 2023. PG&E will submit maps of the projected work in Section 7.1H of our 2022 WMP. Note 4: PG&E does not have an equivalent "system hardening" program for transmission conductor, but PG&E is planning to reconductor 32 HFTD miles and 0 Non-HFTD miles in 2022. The preliminarily planned jobs have not been mapped in order to break the data down for this table. There will also be other upgrades during 2022 and 2023 to transmission lines in the normal course of PG&E’s business. PG&E will submit maps of the projected work in Section 7.1H of our 2022 WMP. Note 5: PG&E hardened 342 miles in 2020 and 210 miles in 2021, but not all projects have been mapped as of January 2022 and therefore may not be included in this data. The deteriorated conductor program replaced 29 miles in 2020 and approximately 35 miles in 2021, but not all projects have been mapped as of January 2022 and therefore may not be included in this data. Other comments: 1) The same layers used in Table 8 have been used to determine Population Density, HFTD, and WUI.

## Table 11
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 11 | "PSPS" = Public Safety Power Shutoff
Date Modified | 2022-05-02 | In future submissions update planned upgrade numbers with actuals
|  |  | Section 1: Historical Data (Event Actuals) | [13 empty] | Section 2: Forecasted Data (average of historical data)
Table 11: Recent use of PSPS and other PSPS metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | Q2 | Q3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | Unit(s)
1. Recent use of PSPS | 1.a. | Frequency of PSPS events (total) | 0 | 0 | 0 | 1 | 8 | 0 | 0 | 2 | 4 | 1 | 0 | 2 | 2 | 0 | 0 | 1.5 | 3.25 | 0 | 0 | 1.5 | 3.25 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per quarter or year. Only include events in which de-energization ultimately occurred
| 1.b. | Scope of PSPS events (total) | 0 | 0 | 0 | 43 | 1842 | 0 | 0 | 270 | 547 | 18 | 0 | 115 | 104 | 0 | 0 | 109.5 | 518.75 | 0 | 0 | 109.5 | 518.75 | Circuit-events, measured as the number of circuits de-energized in part or in whole by each PSPS event, summed across each quarter or year.
| 1.c. | Duration of PSPS events (total), in customer-hours | 0 | 0 | 0 | 1464637.9833 | 91887334.1667 | 0 | 0 | 7540563.6175 | 14736124.6822 | 347470.1364 | 0 | 1449211.0494 | 666779.8167 | 0 | 0 | 2787408.4425 | 12887075.8975 | 0 | 0 | 2787408.4425 | 12887075.8975 | Customer hours of de-energization due to PSPS per quarter or year
2. Customer hours of PSPS and other outages | 2.a. | Customer hours of planned outages including PSPS (total) | 1400185 | 1390308.15 | 1513382.5 | 3962582.7167 | 94246224.0167 | 508424.8667 | 439422.5833 | 8090408.8342 | 15567600.0156 | 950774.7031 | 842778.35 | 2290835.1994 | 1357350.9 | 802882.3 | 641100.4667 | 3483143.1258 | 13648099.1058 | 555864.7167 | 641100.4667 | 3483143.1258 | 13648099.1058 | Total customer hours of planned outages per quarter or year
| 2.b. | Customer hours of unplanned outages, not including PSPS (total) | 11961863.95 | 9745978.4833 | 32897043 | 24589664.7833 | 28791354.15 | 7070480.5667 | 3078995.3833 | 6373922.6667 | 3371555.75 | 14960641.4833 | 3560095.9 | 11353792.55 | 22575109.6167 | 3108761.05 | 3319545.6417 | 8863857.6083 | 12973332.6833 | 11015561.025 | 3319545.6417 | 8863857.6083 | 12973332.6833 | Total customer hours of unplanned outages per quarter or year
| 2.c. | System Average Interruption Duration Index (SAIDI) (including PSPS) | 2.4533 | 2.0317 | 6.2383 | 5.1465 | 22.0128 | 1.3458 | 0.62476 | 2.5684 | 3.363 | 2.8036 | 0.77578 | 2.4042 | 4.2169 | 0.69 | 0.7 | 2.1803 | 4.694 | 2.0442 | 0.7 | 2.1803 | 4.694 | SAIDI index value (hours) = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption in hours * # of customer interruptions) / Total number of customers served
| 2.d. | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | 2.4533 | 2.0317 | 6.2383 | 4.8817 | 5.5733 | 1.345 | 0.625 | 1.23 | 0.74667 | 2.7433 | 0.775 | 2.1483 | 4.1 | 0.69 | 0.7 | 1.6892 | 2.4233 | 2.0442 | 0.7 | 1.6892 | 2.4233 | SAIDI index value (hours) = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption in hours * # of customer interruptions) / Total number of customers served
| 2.e. | System Average Interruption Frequency Index (SAIFI) (including PSPS) | 1.053 | 1.102 | 1.549 | 1.1749 | 1.9575 | 0.342 | 0.307 | 0.48935 | 0.41101 | 0.45291 | 0.348 | 0.46708 | 0.57029 | 0.268 | 0.3275 | 0.46662 | 0.50831 | 0.397 | 0.3275 | 0.46662 | 0.50831 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served)
| 2.f. | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | 1.053 | 1.102 | 1.549 | 1.165 | 1.596 | 0.342 | 0.307 | 0.448 | 0.337 | 0.452 | 0.348 | 0.458 | 0.566 | 0.268 | 0.3275 | 0.453 | 0.4515 | 0.397 | 0.3275 | 0.453 | 0.4515 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served)
3. Critical infrastructure impacted by PSPS | 3.a. | Critical infrastructure outage customer-hours due to PSPS | 0 | 0 | 0 | 23257 | 810940.6833 | 0 | 0 | 139703.1325 | 282103.9075 | 8142.3697 | 0 | 25001.15 | 18007.2833 | 0 | 0 | 49869.908 | 219598.5705 | 0 | 0 | 49869.908 | 219598.5705 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per quarter or year
4. Community outreach of PSPS metrics | 4.a. | # of customers impacted by PSPS | 0 | 0 | 0 | 55864 | 2036019 | 0 | 0 | 232875 | 416810 | 5099 | 0 | 51122 | 24170 | 0 | 0 | 77307.504 | 322447.404 | 0 | 0 | 77307.504 | 322447.404 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer)
| 4.b. | # of medical baseline customers impacted by PSPS | 0 | 0 | 0 | 2529 | 83333 | 0 | 0 | 14741 | 27065 | 274 | 0 | 4090 | 1772 | 0 | 0 | 5906.9955 | 23235.3945 | 0 | 0 | 5906.9955 | 23235.3945 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer)
| 4.c. | # of customers notified prior to initiation of PSPS event | 0 | 0 | 0 | 69229 | 2517105 | 0 | 0 | 288351 | 580825 | 22433 | 0 | 82921 | 75954 | 0 | 0 | 111235.4002 | 463959.6956 | 0 | 0 | 111235.4002 | 463959.6956 | # of customers notified of PSPS event prior to initiation quarter or year. (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer)
| 4.d. | # of medical baseline customers notified prior to initiation of PSPS event | 0 | 0 | 0 | 3610 | 105606 | 0 | 0 | 18649 | 36420 | 1146 | 0 | 6539 | 5599 | 0 | 0 | 8421.8611 | 33127.7152 | 0 | 0 | 8421.8611 | 33127.7152 | # of customers notified of PSPS event prior to initiation per quarter or year. (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer)
| 4.e. | % of customers notified prior to a PSPS event impacting them | 0 | 0 | 0 | 123.9% | 123.6% | 0 | 0 | 123.8% | 139.4% | 439.9% | 0% | 162.2% | 314.2% | 0 | 0 | 143.9% | 143.9% | 143.9% | 143.9% | 143.9% | 143.9% | =4.c. / 4.a.
| 4.f. | % of medical baseline customers notified prior to a PSPS event impacting them | 0 | 0 | 0 | 142.7% | 126.7% | 0 | 0 | 126.5% | 134.6% | 418.2% | 0% | 159.9% | 316% | 0 | 0 | 142.6% | 142.6% | 142.6% | 142.6% | 142.6% | 142.6% | =4.d. / 4.b.
5. Other PSPS metrics | 5.a. | Number of PSPS events triggered where no de-energization occurred | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Number of instances where utility notified the public of a potential PSPS event but no de-energization followed per quarter or year.
| 5.b. | Number of customers located on de-energized circuits | 0 | 0 | 0 | 75373 | 2912790 | 0 | 0 | 320937 | 937032 | 29125 | 0 | 179032 | 146890 | 0 | 0 | 181095.75 | 710769.75 | 0 | 0 | 181095.75 | 710769.75 | For the circuits de-energized for PSPS, the total customers served by the de-energized circuits. This is summed across all PSPS events per quarter or year. This customer count may be larger than the number of customers de-energized in each PSPS event, if only portions of circuits were de-energized due to sectionalization.
| 5.c. | Customer hours of PSPS per RFW OH circuit mile day | 0 | 0 | 0 | 2.7985 | 195.9072 | 0 | 0 | 31.9665 | 40.353 | 6786.71 | 0 | 0 | 5.0563 | 0 | 0 | 15.9832 | 22.7047 | 0 | 0 | 15.9832 | 22.7047 | =1.c. / RFW OH circuit mile days in time period
| 5.d. | Frequency of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0.5 | Events over time period that overlapped with a High Wind Warning as defined by the National Weather Service
| 5.e. | Scope of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 365568 | 0 | 0 | 0 | 0 | 4696 | 0 | 0 | 615 | 0 | 0 | 0 | 307.5 | 0 | 0 | 0 | 307.5 | Estimated customers impacted over time period that overlapped with a High Wind Warning as defined by the National Weather Service
| 5.f. | Duration of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 5749687 | 0 | 0 | 0 | 0 | 38.6 | 0 | 0 | 6326 | 0 | 0 | 0 | 3163 | 0 | 0 | 0 | 3163 | Customer hours over time period that overlapped with a High Wind Warning as defined by the National Weather Service
Comments for Table 11: PG&E has outlined the past and forecasted PSPS metrics in Table 11, which is utilizing historic recorded data for actuals and an analysis of the past ten years of weather data to provide the forecasted metrics. The forecasted numbers are largely weather dependent and do not include any event size or length reductions from the 2021 planned work. Further information historical lookback of the last ten years of weather data and its uses and limitations can be found in Section 8.1. PG&E projected PSPS metrics in 2022, and Table 11 keeps those values static for 2022. PG&E anticipates continued improvement from 2022 to 2023, but we do not yet have analysis on the value of those improvements. Thus, for the purposes of this table, no improvements have been assumed.

## Table 12
Utility |  | Pacific Gas & Electric Company | Notes:
Table No. |  | 12 | Risk-Spend-Efficiency (RSE) is defined as "An estimate of the cost-effectiveness of initiative, calculated by dividing the mitigation risk reduction benefit by the mitigation cost estimate based on the full set of risk reduction benefits estimated from the incurred costs."
Date Modified |  | 2022-05-02 | CAPEX = Capital expenditure; OPEX = Operating expenditure. In future submissions update planned spend, line miles treated, RSE, etc. with updated projections and actuals. Additional instructions can be found in QR information.
[18 empty] | Actual | [20 empty] | Projected
Table 12: Mitigation initiatives financials | [17 empty] | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | Line miles treated |  | Alternative units (if used) | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | Line miles treated |  | Alternative units (if used) | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | Line miles treated |  | Alternative units (if used) | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | Line miles treated |  | Alternative units (if used) | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | Line miles treated |  | Alternative units (if used)
[18 empty] | Territory | HFTD | Territory | HFTD | Line Miles - Territory | Line Miles - HFTD |  | Territory | HFTD | Territory | HFTD | Line Miles - Territory | Line Miles - HFTD |  | Territory | HFTD | Territory | HFTD | Line Miles - Territory | Line Miles - HFTD |  | Territory | HFTD | Territory | HFTD | Line Miles - Territory | Line Miles - HFTD |  | Territory | HFTD | Territory | HFTD | Line Miles - Territory | Line Miles - HFTD
Metric type | WMP Table # / Category | WMP Initiative # | Initative Activity | Primary driver targeted | Secondary driver targeted | Year initiated | Estimated RSE territory-wide | Estimated RSE in non-HFTD region | Estimated RSE in HFTD Zone 1 | Estimated RSE in HFTD Tier 2 | Estimated RSE in HFTD Tier 3 | If existing: most recent proceeding that has reviewed program | If new: memorandum account | Current compliance status - In / exceeding compliance with regulations | Associated rule(s) - if multiple, separate by semi-colon - ";" | If spend not disaggregated by category, note spend category or mark general operations | Comments | 2019 | [6 empty] | 2020 | [6 empty] | 2021 | [6 empty] | 2022 | [6 empty] | 2023
Other | Risk Assessment & Mapping | 7.3.1.1 | A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment | All Drivers | All Drivers | 2018 | 2227.7163 | 0 | 42.3222 | 2600.8227 | 1271.2675 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 100.3542 | 31.3384 | 0 | 0 | N/A | N/A |  | 1039.5227 | 324.6196 | 0 | 0 | N/A | N/A |  | 1006.5347 | 314.3182 | 0 | 0 | N/A | N/A |  | 909.8101 | 284.1132 | 0 | 0 | 0 | 0 | N/A | 1061.1252 | 331.3655 | 0 | 0 | 0 | 0 | N/A
Other | Risk Assessment & Mapping | 7.3.1.2 | Climate-driven risk map and modeling based on various relevant weather scenarios | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | N/A | N/A |  | 0 | 0 | 770 | 241.8156 | N/A | N/A |  | 0 | 0 | 1623 | 509.697 | N/A | N/A |  | 0 | 0 | 1572 | 493.6807 | 0 | 0 | N/A | 0 | 0 | 1297 | 407.3179 | 0 | 0 | N/A
Other | Risk Assessment & Mapping | 7.3.1.3 | Ignition probability mapping showing the probability of ignition along the electric lines and equipment | All Drivers | All Drivers | 2018 | 2227.7163 | 0 | 42.3222 | 2600.8227 | 1271.2675 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 100.3542 | 31.3384 | 0 | 0 | N/A | N/A |  | 1039.5227 | 324.6196 | 0 | 0 | N/A | N/A |  | 1006.5347 | 314.3182 | 0 | 0 | N/A | N/A |  | 909.8101 | 284.1132 | 0 | 0 | 0 | 0 | N/A | 1061.1252 | 331.3655 | 0 | 0 | 0 | 0 | N/A
Other | Risk Assessment & Mapping | 7.3.1.4 | Initiative mapping and estimation of wildfire and PSPS risk-reduction impact | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 23.1064 | 7.2156 | N/A | N/A |  | 0 | 0 | 15.5357 | 4.8514 | N/A | N/A |  | 0 | 0 | 171.1056 | 53.432 | 54.2068 | N/A |  | 0 | 0 | 168.4643 | 52.608 | 53.3708 | 0 | N/A | 0 | 0 | 173.5182 | 54.186 | 54.9717 | 0 | N/A
Other | Risk Assessment & Mapping | 7.3.1.5 | Match drop simulations showing the potential wildfire consequence of ignitions that occur along the electric lines and equipment | N/A - Foundational | N/A - Foundational | 2019 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 2100 | 2100 | N/A | N/A |  | 0 | 0 | 3000 | 3000 | N/A | N/A |  | 1194 | 1194 | 3800 | 3800 | N/A | N/A |  | 1194 | 1194 | 3200 | 3200 | 0 | 0 | N/A | 1229.82 | 1229.82 | 3296 | 3296 | 0 | 0 | N/A
Other | Risk Assessment & Mapping | 7.3.1.6 | Weather-Driven Risk Map and Modelling Based on Various Relevant Weather Scenarios | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | N/A | N/A |  | 0 | 0 | 0 | 0 | N/A | N/A |  | 0 | 0 | 0 | 0 | N/A | N/A |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.1.1 | Advanced weather monitoring and weather stations, Numerical Weather Prediction | Consequence - PSPS | No other consequences reflected | <2018 | 189.3603 | 0 | 189.3603 | 189.3603 | 189.3603 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | N/A | N/A |  | 0 | 0 | 650.8331 | 650.8331 | N/A | N/A |  | 0 | 0 | 718.9587 | 718.9587 | 0 | 0 | N/A | 0 | 0 | 789.075 | 789.075 | 0 | 0 | N/A | 0 | 0 | 806.8874 | 806.8874 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.1.2 | Advanced weather monitoring and weather stations, Fuel Moisture Sampling and Modeling | Consequence - PSPS | No other consequences reflected | 2018 | 74.9475 | 0 | 74.9475 | 74.9475 | 74.9475 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 413.3169 | 129.8006 | N/A | N/A |  | 0 | 0 | 571.1528 | 179.3684 | N/A | N/A |  | 0 | 0 | 571.796 | 179.5704 | 0 | 0 | N/A | 0 | 0 | 598.0965 | 187.8299 | 0 | 0 | N/A | 0 | 0 | 616.6032 | 193.6419 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.1.3 | Advanced weather monitoring and weather stations, Weather Stations | Consequence - PSPS | No other consequences reflected | 2018 | 21.6596 | 0 | 21.6596 | 21.6596 | 21.6596 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 6933.6763 | 5699.898 | 605.6783 | 497.9039 | 627 | 515.4316 | # of Weather Stations | 8314.9397 | 6835.3793 | 111.2093 | 91.4207 | 9624 | 9624 |  | 7719.7701 | 6346.1142 | 145.2292 | 119.3871 | 1313 | 1079.3648 | # of Weather Stations | 6181.3442 | 5081.4358 | 1595.2679 | 1311.4059 | 1650 | 1356.399 | # of Weather Stations | 3156.22 | 2594.6022 | 1714.7949 | 1409.6643 | 1550 | 1274.193 | # of Weather Stations
Other | Situational Awareness & Forecasting | 7.3.2.1.4 | Advanced weather monitoring and weather stations, Wildfire Cameras | All Drivers | All Drivers | 2018 | 122.8516 | 0 | 7.9164 | 140.5841 | 75.2795 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 2063.3694 | 1748.5046 | 124 | 105.0779 | # of HD Cameras | 0 | 0 | 6955.7637 | 5894.3323 | 11148 | 11148 |  | 0 | 0 | 8050.7839 | 6822.2552 | 153 | 129.6526 | # of HD Cameras | 0 | 0 | 11211.216 | 9500.4135 | 133 | 112.7045 | # of HD Cameras | 0 | 0 | 8002.0207 | 6780.9331 | 10 | 8.474 | # of HD Cameras
Other | Situational Awareness & Forecasting | 7.3.2.1.5 | Advanced weather monitoring and weather stations, Fire Detection & Alerting | All Drivers | All Drivers | 2019 | 175.9289 | 2.5211 | 35.7727 | 635.3427 | 340.2102 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | N/A | N/A |  | 0 | 0 | 0 | 0 | 81004 | 25439 |  | 0 | 0 | 195.207 | 61.304 | 0 | 0 | N/A | 0 | 0 | 341.3279 | 107.1927 | 0 | 0 | N/A | 0 | 0 | 351.8894 | 110.5095 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.1.6 | Advanced weather monitoring and weather stations, Other Meteorology Tools and Upgrades | N/A - Foundational | N/A - Foundational | 2019 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 289.3218 | 90.8604 | N/A | N/A |  | 0 | 0 | 887.9318 | 278.8516 | N/A | N/A |  | 0 | 0 | 939.4762 | 295.039 | 0 | 0 | N/A | 0 | 0 | 1020 | 320.3271 | 0 | 0 | N/A | 0 | 0 | 1050.6 | 329.937 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.2.1 | Continuous monitoring sensors, Electric Transmission SEL T400L | N/A - Pilot | N/A - Pilot | 2019 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | Transmission Owner | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 39627.9794 | 12062.3022 | 0 | 0 | 0 | 0 | Relays | 47015.4914 | 14310.9761 | 0 | 0 | 0 | 0 | Relays | 35312.5456 | 10748.7337 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.2.2 | Continuous monitoring sensors, SmartMeter™ Partial Voltage Detection (Formerly Known as Enhanced Wires Down Detection) |  |  | 2019 | [6 empty] | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 390.5367 | 390.5367 | 0.17818 | 0.17818 | 0 | 0 | SmartMeters | 1215.5724 | 1215.5724 | 3.6572 | 3.6572 | 0 | 0 | SmartMeters | 607.6568 | 607.6568 | 2.1919 | 2.1919 | 0 | 0 | SmartMeters enabled | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.2.3 | Continuous monitoring sensors, Distribution Fault Anticipation Technology and Early Fault Detection | Equipment / facility failure, Vegetation Contact, Contact from object, Other, Vandalism / Theft, | No other drivers addressed | 2019 | 4.5183 | 0 | 0.14208 | 5.3571 | 2.3672 | WMCE | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 815.6914 | 815.6914 | 7.5 | 7.5 | # of DFA Sensors | 0 | 0 | 338.2566 | 338.2566 | 1 | 1 | # of DFA Sensors | 5274.7005 | 5274.7005 | 158.6605 | 158.6605 | 16 | 16 | # of DFA Sensors | 14579.4178 | 14579.4178 | 2573.4993 | 2573.4993 | 42 | 42 | # of DFA Sensors | 13965.4892 | 13965.4892 | 3425.8093 | 3425.8093 | 43 | 43 | # of DFA Sensors
Other | Situational Awareness & Forecasting | 7.3.2.2.4 | Continuous monitoring sensors, Sensor IQ | N/A - Foundational | N/A - Foundational | 2020 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | WMCE | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 29.212 | 9.2923 | 23.5013 | 7.4758 | N/A | N/A |  | -30.0251 | -9.551 | 1870.7814 | 595.0956 | N/A | N/A |  | 0.01217 | 0.0038713 | 1247.9865 | 396.9845 | 551 | 175.2731 | SmartMeters enabled | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 10507 | 3342.2767 | 3676.2309 | 1169.4091 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.2.5 | Continuous monitoring sensors, Line Sensor Devices | All Drivers, All Consequences | All Drivers, All Consequences | 2019 | 72.5033 | 0 | 1.4867 | 84.8118 | 40.9492 | N/A | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 2764.5835 | 2764.5835 | 455.1574 | 455.1574 | 14 | 14 | # of Circuits | 2720.7288 | 2720.7288 | 924.254 | 924.254 | 38 | 38 | # of Circuits | 3234.4113 | 3234.4113 | 1115.8787 | 1115.8787 | 67 | 67 | # of Circuits | 7812.786 | 7812.786 | 0 | 0 | 40 | 40 | # of Circuits | 8005.572 | 8005.572 | 0 | 0 | 40 | 40 | # of Circuits
Other | Situational Awareness & Forecasting | 7.3.2.2.6 | Continuous monitoring sensors, Distribution Arcing Fault Signature Library | N/A - Pilot | N/A - Pilot | 2020 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | WMCE | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | N/A |  | 0 | 0 | 563.4847 | 563.4847 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.2.7 | Continuous monitoring sensors, DTS FAST | N/A - Pilot | N/A - Pilot | 2020 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot |  |  | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 9.08 | 9.08 |  |  |  | 4220.2594 | 4220.2594 | 137.1107 | 137.1107 |  |  |  | 19452 | 19452 | 600 | 600 |  |  |  | 20542.5 | 20542.5 | 800 | 800
Other | Situational Awareness & Forecasting | 7.3.2.3 | Fault indicators for detecting faults on electric lines and equipment | All Drivers, All Consequences | All Drivers, All Consequences | <2018 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 84.5536 | 26.5537 | 0 | 0 | 0 | 0 | N/A | 52.5431 | 16.501 | 0 | 0 | 0 | 0 | N/A | 19.6899 | 6.1835 | 0 | 0 | 0 | 0 | Fault Indicators | 0 | 0 | 0 | 0 | 0 | 0 | Fault Indicators | 0 | 0 | 0 | 0 | 0 | 0 | Fault Indicators
Other | Situational Awareness & Forecasting | 7.3.2.4 | Forecast of a fire risk index, fire potential index, or similar | Consequence - PSPS | No other consequences reflected | <2018 | 49.965 | 0 | 49.965 | 49.965 | 49.965 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 198.2271 | 198.2271 | 1416.3562 | 1416.3562 | 0 | 0 | N/A | 898.8112 | 898.8112 | 1833.7554 | 1833.7554 | 0 | 0 | N/A | 14.032 | 14.032 | 1080.0589 | 1080.0589 | 0 | 0 | N/A | 0 | 0 | 1867.1707 | 1867.1707 | 0 | 0 | N/A | 0 | 0 | 1927.7466 | 1927.7466 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.5 | Personnel monitoring areas of electric lines and equipment in elevated fire risk conditions | N/A | N/A | 2018 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 128.4705 | 128.4705 | 2583.6528 | 2583.6528 |  | N/A |  | 250.785 | 250.785 | 3068.3805 | 3068.3805 | N/A | N/A |  | 11.7078 | 11.7078 | 3422.4025 | 3422.4025 |  |  |  | 230.0126 | 230.0126 | 4841.3383 | 4841.3383 |  |  |  | 47.8332 | 47.8332 | 5027.7593 | 5027.7593
Other | Situational Awareness & Forecasting | 7.3.2.6 | Weather forecasting and estimating impacts on electric lines and equipment | Consequence - PSPS | No other consequences reflected | <2018 | 140.251 | 0 | 140.251 | 140.251 | 140.251 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 488.1249 | 488.1249 | 0 | 0 | N/A | 975.1272 | 975.1272 | 718.7264 | 718.7264 | 0 | 0 | N/A | 1022.9234 | 1022.9234 | 1107.8211 | 1107.8211 | 0 | 0 | N/A | 1045.0294 | 1045.0294 | 1030.3787 | 1030.3787 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.7 | Other, Wildfire Safety Operations Center (WSOC) | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 2120.9695 | 2120.9695 | 5678.2011 | 5678.2011 | 0 | 0 | N/A | -34.0887 | -34.0887 | 4117.327 | 4117.327 | 0 | 0 | N/A | 140.5808 | 140.5808 | 4847.3841 | 4847.3841 | 0 | 0 | N/A | 124.6707 | 124.6707 | 6981.0461 | 6981.0461 | 0 | 0 | N/A | 0 | 0 | 7138.6341 | 7138.6341 | 0 | 0 | N/A
Other | Situational Awareness & Forecasting | 7.3.2.8 | Other, Meteorology Analytics/Operations Center | N/A - Foundational | N/A - Foundational | 2020 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - to be removed, no financials after 2021 | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 920.104 | 920.104 | 0 | 0 | N/A | 0 | 0 | 49.4055 | 49.4055 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Grid hardening | Grid Design & System Hardening | 7.3.3.1 | Capacitor maintenance and replacement program | Equipment / facility failure | No other drivers addressed | <2018 | 238.1338 | 2.6423 |  | 1033.92 | 202.7749 | 2020 GRC | N/A | In Compliance | GO 95 |  | RSEs presented are for the year 2022. | 6426.3172 | 2018.1606 | 2034.6632 | 638.9783 | 81004 | 25439 |  | 8246.664 | 2589.8337 | 2383.3797 | 748.4914 | 81004 | 25439 |  | 10931.5542 | 3433.0133 | 2959.1761 | 929.3181 | 81004 | 25439 |  | 10549.2358 | 3312.9476 | 2369.2363 | 744.0497 | 81004 | 25439 |  | 11964.7222 | 3757.4758 | 2436.1597 | 765.0668 | 81004 | 25439
Grid hardening | Grid Design & System Hardening | 7.3.3.2-D | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Distribution | Equipment / facility failure |  | <2018 | 0 | 0 | 0 | 0 | 0 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 1511.585 | 474.7076 | 1947 | 611.448 | Circuit Breakers | 0 | 0 | 2368.31 | 743.7588 | 2253 | 707.5461 | Circuit Breakers | 0 | 0 | 2638.202 | 828.5174 | 2067 | 649.1335 | Circuit Breakers | 0 | 0 | 2585.9803 | 812.1174 | 2817 | 884.6682 | Circuit Breakers | 0 | 0 | 2411.392 | 757.2885 | 2817 | 884.6682 | Circuit Breakers
Grid hardening | Grid Design & System Hardening | 7.3.3.2-T | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Transmission | Equipment / facility failure |  | <2018 | 0 | 0 | 0 | 0 | 0 | Transmission Owner | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 1772.44 | 539.5104 | 4095 | 1246.471 | Circuit Breakers | 0 | 0 | 2414.211 | 734.8581 | 4639 | 1412.0584 | Circuit Breakers | 0 | 0 | 2088.398 | 635.6844 | 3572 | 1087.2758 | Circuit Breakers | 0 | 0 | 2444.5316 | 744.0874 | 3416 | 1039.7912 | Circuit Breakers | 0 | 0 | 2444.5316 | 744.0874 | 3687 | 1122.2805 | Circuit Breakers
Grid hardening | Grid Design & System Hardening | 7.3.3.3 | Covered conductor installation | See initiative 7.3.3.17.1 | See initiative 7.3.3.17.1 | 2018 | See initiative 7.3.3.17.1 | See initiative 7.3.3.17.1 | See initiative 7.3.3.17.1 | See initiative 7.3.3.17.1 | See initiative 7.3.3.17.1 | See 7.3.3.17.1 | N/A | Exceeds | GO 95 | 7.3.3.17.1 Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 171 | 171 |  | 0 | 0 | 0 | 0 | 339.3 | 339.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Grid hardening | Grid Design & System Hardening | 7.3.3.4 | Covered conductor maintenance | Equipment / facility failure | No other drivers addressed | 2018 | 1670.0685 | 4.3235 | 6.6812 | 2903.9408 | 935.5143 | 2020 GRC | FRMMA / WMPMA | In Compliance | GO 95 |  | RSEs presented are for the year 2022. | 24674.9144 | 8110.2403 | 17159.8071 | 5983.6764 | 6554.5715 | 2409.4104 | Tags | 18576.5561 | 7135.1861 | 17027.1357 | 9990.2317 | 6183.0734 | 3514.6289 | Tags | 29052.1113 | 8749.5237 | 15281.3978 | 9723.6746 | 6323 | 3564 | Tags | 44386.3098 | 25367.0235 | 9013.3054 | 7470.0681 | 7829 | 5554 | Tags | 44386.3098 | 25367.0235 | 9013.3054 | 7470.0681 | 7829 | 5554 | Tags
Grid hardening | Grid Design & System Hardening | 7.3.3.5 | Crossarm maintenance, repair, and replacement | Equipment / facility failure | No other drivers addressed | <2018 | 102.684 | 0.67149 | 19.5661 | 291.1802 | 98.1179 | 2020 GRC, Transmission Owners | FRMMA / WMPMA | Exceeds | GO 95; GO 165; FERC TPL Standards |  | RSEs presented are for the year 2022. | 75781.991 | 37223.8565 | 1443.2985 | 845.1408 | 6236.8444 | 2723.7009 | Tags | 52085.7144 | 26213.3011 | 966.639 | 592.122 | 4798.0915 | 2345.6171 | Tags | 80299.6185 | 32933.4025 | 2820.1257 | 1843.5114 | 7043 | 2874 | Tags | 71788.1646 | 32920.0287 | 2567.1658 | 1728.7875 | 7326 | 3410 | Tags | 68996.6128 | 31322.5064 | 2760.6981 | 1858.7698 | 7341 | 3420 | Tags
Grid hardening | Grid Design & System Hardening | 7.3.3.6 | Distribution pole replacement and reinforcement, including with composite poles | Equipment / facility failure | No other drivers addressed | <2018 | 140.7824 | 0.82055 | 1.7852 | 237.7257 | 66.6294 | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 347133.1356 | 105777.9113 | 3764.3247 | 1080.3612 | 17834 | 8157.432 | Tags | 238929.563 | 129004.8389 | 4783.4683 | 1372.8554 | 14033 | 8605.374 | Tags | 390886.8857 | 330359.7864 | 2800.1469 | 803.6422 | 19269 | 14705.477 | Tags | 419170.185 | 337801.8772 | 3460.0221 | 993.0263 | 22345 | 16269.4 | Tags | 434217.5427 | 368822.4335 | 3911.4241 | 1122.5787 | 20734 | 14602.5 | Tags
Grid hardening | Grid Design & System Hardening | 7.3.3.7 | Expulsion fuse replacement | Equipment / facility failure | No other drivers addressed | <2018 | 24.7226 | 0 | 0 | 33.0214 | 12.6693 | 2020 GRC | N/A | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 9130.3359 | 9130.3359 | 0 | 0 | 405 | 405 | # of fuses | 7846.551 | 7846.551 | 0 | 0 | 643 | 643 | # of fuses | 11295.1645 | 11295.1645 | 0 | 0 | 1429 | 1429 | # of fuses | 35000 | 35000 | 0 | 0 | 3000 | 3000 | # of fuses | 35000 | 35000 | 0 | 0 | 3000 | 3000 | # of fuses
Grid hardening | Grid Design & System Hardening | 7.3.3.8.1 | Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Sectionalizing | Consequence - PSPS | No other consequences reflected | 2019 | 4.2542 | 0 | 4.2542 | 4.2542 | 4.2542 | 2020 GRC | N/A | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 25591.6764 | 25591.6764 | 0 | 0 | 298 | 298 | # of distribution sectionalizing devices | 34977.9909 | 34977.9909 | 0 | 0 | 603 | 603 | # of distribution sectionalizing devices | 14912.7556 | 14912.7556 | 44.0336 | 44.0336 | 269 | 269 | # of distribution sectionalizing devices | 10452.1989 | 10452.1989 | 0 | 0 | 100 | 100 | # of distribution sectionalizing devices | 5948.7598 | 5948.7598 | 0 | 0 | 100 | 100 | # of distribution sectionalizing devices
Grid hardening | Grid Design & System Hardening | 7.3.3.8.2 | Grid topology improvements to mitigate or reduce PSPS events, Transmission Line Sectionalizing | Consequence - PSPS | No other consequences reflected | 2020 | 3.4138 | 0 | 3.4138 | 3.4138 | 3.4138 | Transmission Owner | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 33100 | 28491.1392 | 0 | 0 | 54 | 46.481 | # of switches | 44700 | 38475.9494 | 0 | 0 | 79 | 68 | # of switches | 24700 | 21260.7595 | 0 | 0 | 43 | 37.0127 | # of switches | 54247.7608 | 49727.1141 | 0 | 0 | 36 | 33 | # of switches | 55295.487 | 50687.5298 | 0 | 0 | 36 | 33 | # of switches
Grid hardening | Grid Design & System Hardening | 7.3.3.8.3 | Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Motorized Switch Operator Pilot | N/A - Foundational | N/A - Foundational | 2020 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 25591.6764 | 25591.6764 | 0 | 0 | 0 | 0 | N/A | 34977.9909 | 34977.9909 | 0 | 0 | 0 | 0 | # of MSOs | 14912.7556 | 14912.7556 | 0 | 0 | 50 | 50 | # of MSOs | 10452.1989 | 10452.1989 | 0 | 0 | 50 | 50 | # of MSOs | 5948.7598 | 5948.7598 | 0 | 0 | 100 | 100 | # of MSOs
Grid hardening | Grid Design & System Hardening | 7.3.3.9.1 | Installation of system automation equipment | Equipment Failure, All Consequence | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | N/A | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 47562.0695 | 19539.6813 | 0 | 0 | 0 | 0 | N/A | 20215.7585 | 7328.4392 | 0 | 0 | 20 | 20 | # of reclosers | 17206.8303 | 10504.4378 | 0 | 0 | 81 | 81 | # of reclosers | 15598.7243 | 6284.347 | 0 | 0 | 65 | 32.0742 | # of reclosers | 12710.0163 | 3991.5326 | 0 | 0 | 18 | 5.6528 | # of reclosers
Grid hardening | Grid Design & System Hardening | 7.3.3.9.2 | Installation of system automation equipment, Single phase reclosers | Contact from object, Vegetation Contact, Equipment / facility failure, Vandalism / Theft | No other drivers addressed | 2019 | 34.5818 | 0 | 0.74089 | 39.7479 | 21.3439 | 2020 GRC | N/A | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | # of fuse saver sets | 0 | 0 | 0 | 0 | 0 | 0 | # of fuse saver sets | 6730.3359 | 6730.3359 | 0 | 0 | 71 | 71 | # of fuse saver sets | 4400 | 4400 | 0 | 0 | 80 | 80 | # of fuse saver sets | 4400 | 4400 | 0 | 0 | 80 | 80 | # of fuse saver sets
Grid hardening | Grid Design & System Hardening | 7.3.3.10 | Maintenance, repair, and replacement of connectors, including hotline clamps | Equipment / facility failure | No other drivers addressed | <2018 | 2110.5075 | 4.761 | 170.4384 | 2768.9373 | 1064.0456 | 2020 GRC, Transmission Owners | FRMMA / WMPMA | Exceeds | GO 95; GO 165; PRC 4292; FERC TPL Standards |  | RSEs presented are for the year 2022. | 1483.4945 | 1263.9381 | 17568.445 | 13317.6256 | 6039.528 | 4698.5749 | Tags | 1223.835 | 1072.1854 | 24792.9007 | 22172.6126 | 8541.0148 | 7700.9728 | Tags | 1583.8682 | 1314.7676 | 23651.4136 | 21507.2985 | 8216 | 7527 | Tags | 3134.7231 | 2960.8996 | 14596.8005 | 13431.1838 | 6481 | 5975 | Tags | 3134.7231 | 2960.8996 | 14597.6988 | 13431.7494 | 6481 | 5975 | Tags
Grid hardening | Grid Design & System Hardening | 7.3.3.11.1 | Mitigation of impact on customers and other residents affected during PSPS event, Generation for PSPS Mitigation | Consequence - PSPS | No other consequences reflected | 2019 | 0.37111 | 0 | 0.37111 | 0.37111 | 0.37111 | 2020 GRC | Microgrid Memo Account FRMMA, WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 3283.1713 | 3283.1713 | 210.7776 | 210.7776 | 1 | 1 | # of PIHs | 20800.889 | 20800.889 | 176496.497 | 176496.497 | 2 | 2 | # of PIHs | 16661.6908 | 16661.6908 | 160389.6555 | 160389.6555 | 6 | 6 | # of PIHs | 23324.9089 | 23324.9089 | 112689.5805 | 112689.5805 | 5 | 5 | # of PIHs | 5515 | 5515 | 106552.3851 | 106552.3851 | 0 | 0 | # of PIHs
Grid hardening | Grid Design & System Hardening | 7.3.3.11.2 | Mitigation of impact on customers and other residents affected during PSPS event, Substation activities to enable reduction of PSPS impacts | Consequence - PSPS | No other consequences reflected | 2020 | 66.5629 | 0 | 66.5629 | 66.5629 | 66.5629 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 4086 | 1283.1929 | 0 | 0 | 18 | 5.6528 | # of fuses | 3845.8212 | 1207.7656 | 0 | 0 | 4 | 1.2562 | # of fuses | 11630.0472 | 3652.3724 | 0 | 0 | 2 | 0.62809 | # of fuses | 681 | 213.8655 | 0 | 0 | 0 | 0 | # of fuses | 0 | 0 | 0 | 0 | 0 | 0 | # of fuses
Grid hardening | Grid Design & System Hardening | 7.3.3.11.3 | Mitigation of impact on customers and other residents affected during PSPS event, Emergency Back-up Generation – PG&E Service Centers & Materials Distribution Centers | N/A - Foundational | N/A - Foundational | 2021 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | WMCE | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 37100 | 37100 | 0 | 0 | 0 | 0 | N/A | 39600 | 39600 | 0 | 0 | 0 | 0 | N/A | 18000 | 18000 | 0 | 0 | 15 | 15 | # of sites | 3000 | 3000 | 0 | 0 | 6 | 6 | # of sites
Grid hardening | Grid Design & System Hardening | 7.3.3.11.4 | Fixed Power Solutions | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 7800 | 7800 | 150 | 150 | Customer Systems | 0 | 0 | 12066.21 | 12066.21 | 500 | 500 | Customer systems
Grid hardening | Grid Design & System Hardening | 7.3.3.12.1 | Other corrective action, Distribution Substation | Contact from object | No other drivers addressed | <2018 | 0 | 0 | 0 | 0 | 0 | 2020 GRC | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 1306.7098 | 410.3673 | 5248.1172 | 5246.8212 | 543 | 543 | Corrective Notifications | 4960.8901 | 1557.9488 | 2445.1287 | 2085.6017 | 532 | 308 | Corrective Notifications | 4739.2217 | 1488.3347 | 2792.2492 | 2792.2492 | 1308 | 1308 | Corrective Notifications | 0 | 0 | 976.9113 | 976.9113 | 584 | 584 | Corrective Notifications | 0 | 0 | 4626.1392 | 4626.1392 | 0 | 0 | Corrective Notifications
Grid hardening | Grid Design & System Hardening | 7.3.3.12.2 | Other corrective action, Transmission Substation | Contact from object | No other drivers addressed | <2018 | 0 | 0 | 0 | 0 | 0 | Transmission Owner | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 402.2633 | 122.4443 | 2830.6898 | 2824.2018 | 261 | 261 | Corrective Notifications | 958.5485 | 291.7712 | 2014.4506 | 1749.5156 | 420 | 208 | Corrective Notifications | 1390.5826 | 423.2774 | 2882.8844 | 2882.8844 | 1294 | 1294 | Corrective Notifications | 0 | 0 | 504.1428 | 504.1428 | 300 | 300 | Corrective Notifications | 0 | 0 | 1186.6132 | 1186.6132 | 0 | 0 | Corrective Notifications
Grid hardening | Grid Design & System Hardening | 7.3.3.12.3 | Other corrective action, Maintenance, Transmission | Equipment / facility failure | No other drivers addressed | <2018 | 8.6993 | 0.23923 | 26.8768 | 26.8768 | 31.8235 | Transmission Owner | N/A | In Compliance | GO 95; GO 165; FERC TPL Standards |  | RSEs presented are for the year 2022. | 365319.6504 | 111199.1095 | 347117.5879 | 105658.6105 | 29322 | 8925.2803 | Corrective Notifications | 449179.0138 | 136724.9374 | 99945.9642 | 30422.4046 | 15877 | 4832.7766 | Corrective Notifications | 360362.224 | 109690.1258 | 89135.5812 | 27131.8481 | 15001 | 4566.1323 | Corrective Notifications | 412054.6501 | 125424.7071 | 127975.5381 | 38954.2853 | 15169 | 4617.2695 | Corrective Notifications | 381315.7334 | 116068.1336 | 139107.312 | 42342.6695 | 19098 | 5813.212 | Corrective Notifications
Grid hardening | Grid Design & System Hardening | 7.3.3.12.4 | Other corrective action, Maintenance, Distribution | Equipment / facility failure | No other drivers addressed | <2018 | 395.5788 | 1.6005 | 2.6868 | 779.669 | 238.7884 | 2020 GRC | FRMMA / WMPMA | In Compliance | GO 95 |  | RSEs presented are for the year 2022. | 233861.3126 | 120626.7514 | 75112.7333 | 40250.6338 | 79416.7946 | 52993.8445 | Corrective Notifications | 236372.8788 | 116324.8261 | 75248.474 | 49008.5383 | 0 | 0 | Corrective Notifications | 295107.9589 | 149538.0917 | 74702.949 | 48599.3991 | N/A | N/A | Corrective Notifications | 196540.8369 | 110480.7735 | 93704.4326 | 72464.987 | N/A | N/A | Corrective Notifications | 329592.6125 | 194791.8113 | 73465.8102 | 47353.6213 | N/A | N/A | Corrective Notifications
Grid hardening | Grid Design & System Hardening | 7.3.3.12.5 | Other corrective action, Generation Substation | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | FRMMA / WMPMA | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | Corrective Actions | 0 | 0 | 0 | 0 | 0 | 0 | Corrective Actions | 0 | 0 | 905.9398 | 905.9398 | 53 | 53 | Corrective Actions | 0 | 0 | 2839.3903 | 2839.3903 | 51 | 51 | Corrective Actions | 0 | 0 | 516.6667 | 516.6667 | 51 | 51 | Corrective Actions
Grid hardening | Grid Design & System Hardening | 7.3.3.13 | Pole loading infrastructure hardening and replacement program based on pole loading assessment program | Equipment / facility failure | No other drivers addressed | <2018 | 61.6932 | 0.32153 | 0.69952 | 93.1517 | 26.1084 | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 8200.8693 | 6806.7215 | 228.0798 | 189.3062 | 167.08 | 63.08 | Poles | 13793.3459 | 11448.4771 | 61.0715 | 50.6893 | 263.69 | 118.69 | Poles | 19998.0899 | 16598.4146 | 0.41075 | 0.34092 | 492.53 | 324.53 | Poles | 9236.196 | 7666.0427 | 154.455 | 128.1977 | 269.27 | 223.27 | Poles | 9220.919 | 7653.3628 | 158.91 | 131.8953 | 262.46 | 217.46 | Poles
Grid hardening | Grid Design & System Hardening | 7.3.3.14 | Transformers maintenance and replacement | Equipment / facility failure | No other drivers addressed | <2018 | 14.9196 | 0.13781 | 0 | 28.6747 | 8.3421 | 2020 GRC, Transmission Owner | FRMMA / WMPMA | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 41206.9431 | 22054.9637 | 170.8347 | 20.838 | 2534.0569 | 1467.3339 | Tags | 32920.1029 | 19691.6578 | 129.2342 | 34.7907 | 2043.0982 | 1308.268 | Tags | 48102.8368 | 24629.1037 | 108.4535 | 33.8624 | 2898 | 1614 | Tags | 22485.2165 | 15708.2682 | 1335.0436 | 1310.7454 | 1488 | 963 | Tags | 27558.7165 | 20781.7682 | 1372.5436 | 1348.2454 | 1688 | 1163 | Tags
Grid hardening | Grid Design & System Hardening | 7.3.3.15 | Transmission tower maintenance and replacement | Equipment / facility failure | No other drivers addressed | <2018 | 30.2769 | 0.39379 | 0 | 44.2413 | 54.5776 | Transmission Owner | N/A | Exceeds | GO95; GO165 |  | RSEs presented are for the year 2022. | 9135.9949 | 5800.8696 | 96300.0848 | 61145.4189 | 13241 | 8407.329 | Structures | 40848.31 | 25936.4987 | 51008.4425 | 32387.6411 | 8066 | 5121.4799 | Structures | 60006.7976 | 38101.1168 | 57675.5552 | 36620.9022 | 7466 | 4740.5119 | Structures | 154981 | 98404.671 | 50261.2325 | 31913.2026 | 6220 | 3949.3683 | Structures | 175000 | 111115.6686 | 53422.01 | 33920.1278 | 6512.9445 | 4135.3725 | Structures
Grid hardening | Grid Design & System Hardening | 7.3.3.16 | Undergrounding of electric lines and/or equipment | See initiative 7.3.3.17.1 | See initiative 7.3.3.17.1 | <2018 | See initiative 7.3.3.17.1 | See initiative 7.3.3.17.1 | See initiative 7.3.3.17.1 | See initiative 7.3.3.17.1 | See initiative 7.3.3.17.1 | N/A | N/A | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | # of circuit miles | 0 | 0 | 0 | 0 | 0 | 0 | # of circuit miles | 0 | 0 | 0 | 0 | 0 | 0 | # of circuit miles
Grid hardening | Grid Design & System Hardening | 7.3.3.17.1 | Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution | Contact from object, Vegetation Contact, Contamination, Equipment / facility failure, Other, Unknown, Wire-to-wire contact, Vandalism / Theft, Utility work / Operation, CC - Seismic Scenario | No other drivers addressed | 2018 | 5.5351 | 0 | 0.061721 | 5.8004 | 4.1463 | 2020 GRC | N/A | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 281066.4254 | 281066.4254 | 0 | 0 | 171 | 171 |  | 460142.0956 | 460142.0956 | 0 | 0 | 342 | 342 |  | 280421.7066 | 280421.7066 | 0 | 0 | 210.5855 | 210.5855 |  | 977250 | 977250 | 0 | 0 | 470 | 470 |  | 1457954.875 | 1457954.875 | 0 | 0 | 527.3 | 527.3
Grid hardening | Grid Design & System Hardening | 7.3.3.17.2 | Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Transmission | N/A | No other drivers addressed | 2019 | N/A | N/A | N/A | N/A | N/A | Transmission Owner | N/A | Exceeds | GO 95; GO 165; FERC TPL Standards |  | RSEs presented are for the year 2022. | 508.0346 | 508.0346 | 0 | 0 | 0 | 0 | N/A | 1060.154 | 1060.154 | 0 | 0 | 0 | 0 | N/A | 24817.0913 | 24817.0913 | 0 | 0 | 0 | 0 | # of circuit miles | 19050.876 | 19050.876 | 0 | 0 | 32.58 | 32.58 | # of circuit miles | 19622.4022 | 19622.4022 | 0 | 0 | 32.58 | 32.58 | # of circuit miles
Grid hardening | Grid Design & System Hardening | 7.3.3.17.3 | Updates to grid topology to minimize risk of ignition in HFTDs, Surge Arrestor | Equipment / facility failure | No other drivers addressed | <2018 | 4.4597 | 0.1445 | 0 | 7.427 | 1.9172 | 2020 GRC | N/A | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 21767.3506 | 16242.3826 | 0 | 0 | 3404 | 2540 | # of Surge Arrestors | 63497.9953 | 45387.9005 | 0 | 0 | 14372 | 10273 | # of Surge Arrestors | 74190.9391 | 74190.9391 | 0 | 0 | 15477 | 15477 | # of Surge Arrestors | 33172.1158 | 21401.365 | 0 | 0 | 7750 | 5000 | # of Surge Arrestors | 17706.3611 | 0 | 0 | 0 | 4396 | 0 | # of Surge Arrestors
Grid hardening | Grid Design & System Hardening | 7.3.3.17.4 | Updates to grid topology to minimize risk of ignition in HFTDs, Rapid Earth Current Fault Limiter | N/A | No other drivers addressed | 2019 | N/A | N/A | N/A | N/A | N/A | EPIC | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 56.6213 | 56.6213 | 0 | 0 | 0 | 0 | N/A | 4798.2197 | 4798.2197 | 0 | 0 | 0 | 0 | N/A | -2022.3511 | -2022.3511 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Grid hardening | Grid Design & System Hardening | 7.3.3.17.5 | Updates to grid topology to minimize risk of ignition in HFTDs, Remote Grid | N/A | No other drivers addressed | 2020 | N/A | N/A | N/A | N/A | N/A | WMCE | FRMMA / WMPMA | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 0 | 0 | 30.5914 | 30.5914 |  | N/A |  | 0 | 0 | 755.2311 | 755.2311 | N/A | N/A |  | 0 | 0 | 4857.1281 | 4857.1281 | 1 | 1 | # of Remote Grids | 0 | 0 | 14824.2289 | 14824.2289 | 6 | 6 | # of Remote Grids | 0 | 0 | 15166.0821 | 15166.0821 | 6 | 6 | # of Remote Grids
Grid hardening | Grid Design & System Hardening | 7.3.3.17.6 | Updates to grid topology to minimize risk of ignition in HFTDs, Butte County Rebuild | All Drivers | All Drivers | 2019 | 1.1633 | 0.012507 | 0.031868 | 1.6293 | 1.5161 | N/A | N/A | Exceeds | GO 95 |  | RSEs presented are for the year 2022. | 38549.4114 | 28912.0586 | 0 | 0 | 0.4 | 0 |  | 64587.0231 | 48440.2673 | 0 | 0 | 36.6 | 26.4 |  | 98429.0159 | 73821.7619 | 0 | 0 | 31.5 | 22.4 |  | 138750 | 104062.5 | 0 | 0 | 55 | 32.8 |  | 142521.925 | 114017.54 | 0 | 0 | 70 | 56
Asset inspection | Asset Management & Inspections | 7.3.4.1 | Detailed inspections of distribution electric lines and equipment | Equipment / facility failure | No other drivers addressed | <2018 | 214.356 | 1.0272 | 1.6793 | 487.3024 | 149.2456 | 2020 GRC | FRMMA / WMPMA | In Compliance | GO 165 |  | RSEs presented are for the year 2022. | 0 | 0 | 143845.2604 | 135655.8362 | N/A | 25597 |  | 0 | 0 | 100485.3167 | 52079.6486 | 24263 | 13265.7 |  | 0 | 0 | 95920.6026 | 50048.7923 | 24264 | 13151 |  | 0 | 0 | 100378.9799 | 51876.3511 | 24264 | 13151 |  | 0 | 0 | 101781.9707 | 53372.639 | 24264 | 13151
Asset inspection | Asset Management & Inspections | 7.3.4.2 | Detailed inspections of transmission electric lines and equipment | Equipment / facility failure | No other drivers addressed | <2018 | 9.1825 | 0.0079059 | 24.0528 | 3.9055 | 32.3295 | Transmission Owner | N/A | In Compliance | GO 165 |  | RSEs presented are for the year 2022. | 0 | 0 | 72520.882 | 67601.1067 | N/A | 5710 |  | 0 | 0 | 92826.651 | 9442.9715 | 5235 | 2862 |  | 0 | 0 | 85681.5605 | 28378.4479 | 5473 | 2862 |  | 0 | 0 | 86707.253 | 56022.0741 | 5473 | 2862 |  | 0 | 0 | 89308.4706 | 57702.7363 | 5473 | 2862
Asset inspection | Asset Management & Inspections | 7.3.4.3 | Improvement of inspections | N/A - Foundational | No other drivers addressed | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | N/A |  | 0 | 0 | 0 | 0 | N/A | N/A |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Asset inspection | Asset Management & Inspections | 7.3.4.4 | Infrared inspections of distribution electric lines and equipment | Equipment / facility failure | No other drivers addressed | <2018 | 45.5994 | 0.19162 | 0.32167 | 93.3446 | 28.5885 | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 165 |  | RSEs presented are for the year 2022. | 0 | 0 | 1918.7773 | 952.1643 | 14608 | 7249 |  | 0 | 0 | 1561.3355 | 879.1485 | 5450 | 5450 |  | 0 | 0 | 2118.1083 | 1651.2346 | 12948 | 10094 |  | 0 | 0 | 2225.8927 | 2114.5981 | 10600 | 10070 |  | 0 | 0 | 2290.0949 | 2175.5902 | 10600 | 10070
Asset inspection | Asset Management & Inspections | 7.3.4.5 | Infrared inspections of transmission electric lines and equipment | Equipment / facility failure | No other drivers addressed | <2018 | 0.50745 | 0.0020873 | 0.78938 | 0.88523 | 1.0663 | Transmission Owner | N/A | In Compliance | GO 95; GO 165 |  | RSEs presented are for the year 2022. | 0 | 0 | 222.5848 | 0 |  | N/A |  | 0 | 0 | 1443.6 | 711.148 | 5280 | 2601.04 |  | 0 | 0 | 2534.5113 | 1407.327 | 7591.34 | 4215.21 |  | 0 | 0 | 2220 | 912.418 | 7844.47 | 3224.07 |  | 0 | 0 | 2220 | 912.418 | 7844.47 | 3224.07
Asset inspection | Asset Management & Inspections | 7.3.4.6.1 | Intrusive pole inspections, Distribution | Equipment / facility failure | No other drivers addressed | <2018 | 379.7853 | 5.7482 | 12.5058 | 1665.3441 | 466.7604 | 2020 GRC, Transmission Owner | FRMMA / WMPMA | Exceeds | GO 165; GO 95 rule 44.3 |  | RSEs presented are for the year 2022. | 0 | 0 | 17848.7066 | 5122.5788 |  | 2559.7 |  | 0 | 0 | 17446.6652 | 628.3732 | 8100 | 2559.7 |  | 0 | 0 | 17628.5321 | 3691.7164 | 8100 | 2544 |  | 0 | 0 | 21239.442 | 6095.7199 | 8100 | 2544 |  | 0 | 0 | 19247.0471 | 5523.9025 | 8100 | 2544
Asset inspection | Asset Management & Inspections | 7.3.4.6.2 | Intrusive pole inspections, Transmission | N/A | N/A | <2018 | N/A | N/A | N/A | N/A | N/A |  |  | Exceeds | GO 165; GO 95 |  | RSEs presented are for the year 2022. | 0 | 0 | 1958.5373 | 312.1908 |  | 587 |  | 0 | 0 | 1450.5177 | 231.2125 | 1892 | 587 |  | 0 | 0 | 1323.8431 | 211.0206 | 1892 | 587 |  | 0 | 0 | 2150 | 342.71 | 1892 | 587 |  | 0 | 0 | 2150 | 342.71 | 1892 | 587
Asset inspection | Asset Management & Inspections | 7.3.4.7 | LiDAR Inspections of Distribution Electric Lines and Equipment | N/A - Pilot | N/A - Pilot | <2018 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A | N/A | Exceeds | GO 165 |  | RSEs presented are for the year 2022. | 0 | 0 | 15061 | 3012.2 |  |  |  | 0 | 0 | 5404 | 1080.8 | 3000 | 3000 |  | 0 | 0 | 10312 | 2062.4 | 0 | 0 | N/A | 0 | 0 | 10500 | 2100 | N/A | 158 |  | 0 | 0 | 10000 | 2000 | N/A | N/A
Asset inspection | Asset Management & Inspections | 7.3.4.8 | LiDAR Inspections of Transmission Electric Lines and Equipment | N/A | N/A | See Initiative 7.3.5.8 | N/A | N/A | N/A | N/A | N/A | Transmission Owner | N/A | See Initiative 7.3.5.8 | See Initiative 7.3.5.8 |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 398 | 358.2 | N/A | N/A |  | 0 | 0 | 355 | 319.5 | 0 | 0 | N/A | 11003 | 9902.7 | 5030 | 4527 | N/A | 269 |  | 3000 | 2700 | 3000 | 2700 | N/A | N/A
Asset inspection | Asset Management & Inspections | 7.3.4.9 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations | N/A - Complementary | N/A - Complementary | See Initiatives 7.3.4.1 and 7.3.4.4 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 2287.3577 | 718.336 |  | 25597 |  | 0 | 0 | 2729.9172 | 857.3202 | 24643 | 7739.041 | Inspections | 0 | 0 | 2964.3061 | 930.9291 | 25007 | 7853.3538 | Inspections | 0 | 0 | 3257.6179 | 1023.0426 | 27884 | 8756.8648 | Inspections | 0 | 0 | 3351.5785 | 1052.5505 | 27884 | 8756.8648 | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.10 | Other discretionary inspection of transmission electric lines and equipment, beyond inspections mandated by rules and regulations | N/A - Pilot | N/A - Pilot | <2018 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | Transmission Owner | N/A | In Compliance | GO 95; GO 165 |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 5710 |  | 0 | 0 | 131 | 39.8749 | 0 | 0 | N/A | 579.433 | 176.3728 | 1127 | 343.0459 | 318 | 96.7956 | Inspections | 3700 | 1126.2375 | 4300 | 1308.8707 | 1001 | 304.6929 | Inspections | 4070 | 1238.8613 | 4429 | 1348.1368 | 1101.1 | 335.1622 | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.11 | Patrol inspections of distribution electric lines and equipment | Equipment / facility failure | No other drivers addressed | <2018 | 68.4054 | 0.63187 | 1.0607 | 307.8012 | 94.2699 | 2020 GRC | N/A | In Compliance | GO 165 |  | RSEs presented are for the year 2022. | 0 | 0 | 6151.5771 | 1931.8795 |  | 2238.5449 |  | 0 | 0 | 7737.2502 | 2429.8542 | 56541 | 12089 |  | 0 | 0 | 6097.237 | 1914.8142 | 56541 | 12089 |  | 0 | 0 | 6062.9179 | 1284.0581 | 56541 | 12089 |  | 0 | 0 | 6237.7928 | 1321.0946 | 56541 | 12089
Asset inspection | Asset Management & Inspections | 7.3.4.12 | Patrol inspections of transmission electric lines and equipment | Equipment / facility failure | No other drivers addressed | <2018 | 1092.8532 | 12.6633 | 4382.7663 | 4914.9156 | 0 | Transmission Owner | N/A | In Compliance | GO 95; GO 167 |  | RSEs presented are for the year 2022. | 0 | 0 | 18.1944 | 0 |  | N/A |  | 0 | 0 | 170.4886 | 0 | 13400 | 2956 |  | 0 | 0 | 59.6549 | 0 | 13400 | 2956 |  | 0 | 0 | 83.6831 | 24.6165 | 13400 | 2956 |  | 0 | 0 | 83.6831 | 24.6165 | 13400 | 2956
Asset inspection | Asset Management & Inspections | 7.3.4.13 | Pole loading assessment program to determine safety factor | N/A | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | N/A | N/A | FRMMA / WMPMA | Exceeds | GO 165 |  | RSEs presented are for the year 2022. | 0 | 0 | 55 | 55 |  | N/A |  | 0 | 0 | 13652 | 13652 | 134899 | 134899 | Calculations | 0 | 0 | 10162 | 10162 | 61723 | 61723 | Calculations | 0 | 0 | 9122.83 | 9122.83 | 180000 | 180000 | Calculations | 0 | 0 | 10237.025 | 10237.025 | 200000 | 200000 | Calculations
Asset inspection | Asset Management & Inspections | 7.3.4.14 | Quality assurance / quality control of inspections | N/A | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 165 |  | RSEs presented are for the year 2022. | 0 | 0 | 38509.9606 | 32511.4787 |  | N/A |  | 0 | 0 | 40700.2842 | 33846.7053 | 0 | 0 | N/A | 0 | 0 | 27309.1184 | 14190.742 | 0 | 0 | N/A | 0 | 0 | 6015.9077 | 3214.3418 | 0 | 0 | N/A | 0 | 0 | 6189.4267 | 3307.0542 | 0 | 0 | N/A
Asset inspection | Asset Management & Inspections | 7.3.4.15-T | Substation inspections, Enhanced Transmission, Substation | Equipment / facility failure | All Drivers | 2018 | 0.55924 | 0.014362 | 0.83444 | 0.83444 | 0.83444 | Transmission Owner | N/A | Exceeds | GO 174 |  | RSEs presented are for the year 2022. | 0 | 0 | 13495.198 | 5410.8105 | 212 | 85 | Substation Inspections | 0 | 0 | 9667.808 | 5012.9375 | 54 | 28 | Substation Inspections | 0 | 0 | 4164.357 | 4105.7041 | 71 | 70 | Substation Inspections | 0 | 0 | 1757.465 | 1757.465 | 43 | 43 | Substation Inspections | 0 | 0 | 1757.465 | 1757.465 | 43 | 43 | Substation Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.15-D | Substation inspections, Enhanced Distribution, Substation | Equipment / facility failure | All Drivers | 2018 | 73.5862 | 1.5544 | 174.634 | 174.634 | 174.634 | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 174 |  | RSEs presented are for the year 2022. | 0 | 0 | 8147.582 | 2060.1743 | 700 | 177 | Substation Inspections | 0 | 0 | 6888.384 | 3308.2371 | 152 | 73 | Substation Inspections | 0 | 0 | 3251.776 | 3205.9763 | 71 | 70 | Substation Inspections | 0 | 0 | 4397.3044 | 4397.3044 | 86 | 86 | Substation Inspections | 0 | 0 | 4397.3044 | 4397.3044 | 86 | 86 | Substation Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.16 | Other, Substation inspections, Generation | N/A | N/A | 2019 | N/A | N/A | N/A | N/A | N/A | N/A | FRMMA / WMPMA | Exceeds | CAISO Transmission Control Agreement |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | # of Hydroelectric Substations and Powerhouses | 0 | 0 | 0 | 0 | 0 | 0 | # of Hydroelectric Substations and Powerhouses | 0 | 0 | 1483.8958 | 1483.8958 | 53 | 53 | # of Hydroelectric Substations and Powerhouses | 0 | 0 | 1141.3333 | 1141.3333 | 51 | 51 | # of Hydroelectric Substations and Powerhouses | 0 | 0 | 991.6667 | 991.6667 | 51 | 51 | # of Hydroelectric Substations and Powerhouses
Vegetation management project | Vegetation Management & Inspections | 7.3.5.1 | Additional efforts to manage community and environmental impacts | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - no forecast | N/A - no forecast | In Compliance | GO 95 Rule 35; PRC 4293 |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.2 | Detailed inspections and management practices for vegetation clearances around distribution electrical lines and equipment | Vegetation Contact | No other drivers addressed | <2018 | 4763.5214 | 54.0791 |  | 11252.802 | 3506.954 | 2020 GRC | N/A | In Compliance | GO 95 Rule 35; PRC 4293 |  | RSEs presented are for the year 2022. | 0 | 0 | 806068.9253 | 253142 |  | 25597 |  | 0 | 0 | 1134778.924 | 356373 | 81004 | 25439 |  | 0 | 0 | 1379387.0157 | 433191 | 81004 | 25439 |  | 0 | 0 | 1370788.1352 | 430490.8322 | 81004 | 25439 |  | 0 | 0 | 958671.3201 | 301067.1042 | 81004 | 25439
Vegetation management project | Vegetation Management & Inspections | 7.3.5.3 | Detailed inspections and management practices for vegetation clearances around transmission electrical lines and equipment | See initiative 7.3.5.8 | See initiative 7.3.5.8 | <2018 | See initiative 7.3.5.8 | See initiative 7.3.5.8 | See initiative 7.3.5.8 | See initiative 7.3.5.8 | See initiative 7.3.5.8 | Transmission Owner | N/A | In Compliance | GO 95; PRC 4293 |  | RSEs presented are for the year 2022. | 39737.215 | 12095.5523 | 98910.881 | 30107.3372 |  | 5710 |  | 45622.191 | 13886.8714 | 114443.617 | 34835.3238 | 18161 | 5869 |  | 36682.458 | 11165.7193 | 157375.864 | 47903.4071 | 18161 | 5869 |  | 78701 | 23955.6813 | 111609.484 | 33972.6462 | 18161 | 5869 |  | 63180 | 19231.267 | 115556.208 | 35173.9837 | 18161 | 5869
Vegetation management project | Vegetation Management & Inspections | 7.3.5.4 | Emergency response vegetation management due to red flag warning or other urgent climate conditions | N/A | N/A | <2018 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | N/A | In Compliance | GO 95 Rule 35; PRC 4293 |  | RSEs presented are for the year 2022. | 0 | 0 | 3097.6429 | 967.324 |  | 31307 |  | 0 | 0 | 4441.7621 | 1387.062 | 0 | 0 | N/A | 0 | 0 | 5880 | 1836.066 | 0 | 0 | N/A | 0 | 0 | 3126.977 | 976.4846 | 0 | 0 | N/A | 0 | 0 | 3382.4606 | 1056.2664 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.5 | Fuel management (including all wood management) and reduction of “slash” from vegetation management activities | N/A - Pilot | N/A - Pilot | <2018 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | 2020 GRC | N/A | Exceeds | GO 95 Rule 35; PRC 4293; PRC 4292 |  | RSEs presented are for the year 2022. | 0 | 0 | 69216.4957 | 69216.4957 |  | 25597 |  | 0 | 0 | 95380.2828 | 95380.2828 | N/A | N/A |  | 0 | 0 | 61101.1196 | 61101.1196 | 0 | 0 | N/A | 0 | 0 | 92609.6675 | 92609.6675 | 0 | 0 | N/A | 0 | 0 | 14447.1723 | 14447.1723 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.6 | Improvement of inspections | N/A | N/A | <2018 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | N/A | In Compliance | GO 95 Rule 35; PRC 4293; PRC 4295 |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 31307 |  | 0 | 0 | 0 | 0 | N/A | N/A |  | 0 | 0 | 65429 | 20432.027 | 0 | 0 | N/A | 0 | 0 | 143138.4921 | 44698.9329 | 0 | 0 | N/A | 0 | 0 | 52133.0295 | 16279.973 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.7 | Remote sensing inspections of vegetation around distribution electric lines and equipment | N/A - Pilot | N/A - Pilot | <2018 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | 2020 GRC | N/A | In Compliance | GO 95 Rule 35; PRC 4293; PRC 4295 |  | RSEs presented are for the year 2022. | 0 | 0 | 27034.3666 | 27034.3666 | N/A | 2533 |  | 0 | 0 | 4775.2336 | 4775.2336 | 0 | 0 |  | 0 | 0 | 437.9922 | 437.9922 | 0 | 0 | # of circuit miles | 0 | 0 | 37090.1758 | 37090.1758 | 2000 | 2000 |  | 0 | 0 | 14568.8925 | 14568.8925 | 4000 | 4000
Vegetation management project | Vegetation Management & Inspections | 7.3.5.8 | Remote sensing inspections of vegetation around transmission electric lines and equipment | Vegetation Contact | No other drivers addressed | <2018 | 2164.8804 | 0 | 10324.0754 | 6321.644 | 9406.2576 | Transmission Owner | N/A | In Compliance | GO95; PRC 4293; FAC 003-4 |  | RSEs presented are for the year 2022. | 0 | 0 | 7287.753 | 2218.3084 | N/A | 5710 |  | 0 | 0 | 9927.717 | 3021.8831 | 18161 | 5869 |  | 0 | 0 | 10120.589 | 3080.5912 | 17759 | 5869 |  | 0 | 0 | 13000 | 3957.0508 | 17759 | 5869 |  | 0 | 0 | 13390 | 4075.7623 | 17759 | 5869
Vegetation management project | Vegetation Management & Inspections | 7.3.5.9 | Other discretionary inspections of vegetation around distribution electric lines and equipment | Vegetation Contact | No other drivers addressed | <2018 See Initiative 7.3.5.3 | 2828.8503 | 0 | 0 | 3140.5168 | 2031.3959 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | Exceeds | GO 95 Rule 35; PRC 4292; PRC 4293; PRC 4295 | 7.3.5.2 Detailed inspections of vegetation around distribution electric lines and equipment | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 25597 |  | 0 | 0 | 0 | 0 | 81004 | 25439 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.10 | Other discretionary inspections of vegetation around transmission electric lines and equipment | N/A - Complementary | N/A - Complementary | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | 7.3.5.3 Detailed inspections and management practices for vegetation clearances around transmission electrical lines and equipment | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 5710 |  | 0 | 0 | 0 | 0 | 18161 | 5869 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.11 | Patrol inspections of vegetation around distribution electric lines and equipment | N/A - Complementary | N/A - Complementary | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | 7.3.5.2 Detailed inspections of vegetation around distribution electric lines and equipment | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 25597 |  | 0 | 0 | 0 | 0 | 81004 | 25439 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.12 | Patrol inspections of vegetation around transmission electric lines and equipment | N/A - Complementary | N/A - Complementary | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | 7.3.5.3 Detailed inspections and management practices for vegetation clearances around transmission electrical lines and equipment | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 8243 |  | 0 | 0 | 0 | 0 | 20724 | 7510 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.13 | Quality assurance / quality control of vegetation inspections | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | In Compliance | GO 95 Rule 35; PRC 4293 | 7.3.5.2 Detailed inspections and management practices for vegetation clearances around distribution electrical lines and equipment | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 31307 |  | 0 | 0 | 0 | 0 | 99165 | 31307 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.14 | Recruiting and training of vegetation management personnel | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | N/A | N/A | 7.3.5.2 Detailed inspections and management practices for vegetation clearances around distribution electrical lines and equipment | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 31307 |  | 0 | 0 | 0 | 0 | N/A | N/A |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.15 | Identification and remediation of "at-risk species" | Vegetation Contact | No other drivers addressed | 2018 | 2.1828 | 0 | 1.7489e-05 | 2.3933 | 1.6446 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | Exceeds | GO 95 Rule 35; PRC 4293 |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 2533 |  | 0 | 0 | 0 | 0 | 1878 | 1878 |  | 0 | 0 | 0 | 0 | 1800 | 1800 |  | 0 | 0 | 0 | 0 | 1890 | 1890 |  | 0 | 0 | 0 | 0 | 1890 | 1890
Vegetation management project | Vegetation Management & Inspections | 7.3.5.16 | Removal and remediation of trees with strike potential to electric lines and equipment | N/A - Complementary | N/A - Complementary | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | 7.3.5.2 Detailed inspections of vegetation around distribution electric lines and equipment, and 7.3.5.3 Detailed inspections of vegetation around transmission electric lines and equipment | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 141 |  | 0 | 0 | 0 | 0 | N/A | N/A |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.17.1 | Substation inspection , Distribution substation | N/A | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | N/A | Exceeds | GO 95 Rule 35; PRC 4293; NERC Standard FAC-003-4 |  | RSEs presented are for the year 2022. | 0 | 0 | 211.8192 | 66.5479 | 0 | 0 | # of Distribution Substations | 0 | 0 | 207.8645 | 65.3055 | 0 | 0 | # of Distribution Substations | 0 | 0 | 536.678 | 536.678 | 0 | 0 | # of Distribution Substations | 0 | 0 | 552.779 | 552.779 | 133 | 132 | # of Distribution Substations | 0 | 0 | 569.363 | 569.363 | 133 | 132 | # of Distribution Substations
Vegetation management project | Vegetation Management & Inspections | 7.3.5.17.2 | Substation inspection, Transmission substation | N/A | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | N/A | Transmission Owner | N/A | Exceeds | GO 95 Rule 35; PRC 4293; NERC Standard FAC-003-4 |  | RSEs presented are for the year 2022. | 0 | 0 | 104.68 | 31.8634 | 0 | 0 | # of Transmission Substations | 0 | 0 | 147.654 | 44.9442 | 0 | 0 | # of Transmission Substations | 0 | 0 | 226.153 | 226.153 | 0 | 0 | # of Transmission Substations | 0 | 0 | 232.938 | 232.938 | 55 | 55 | # of Transmission Substations | 0 | 0 | 239.926 | 239.926 | 55 | 55 | # of Transmission Substations
Vegetation management project | Vegetation Management & Inspections | 7.3.5.17.3 | Substation inspection, Generation substation | N/A | N/A | 2019 | N/A | N/A | N/A | N/A | N/A | N/A | FRMMA / WMPMA | In Compliance | NERC Standard FAC-003-3 |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | # of Hydroelectric Substations and Powerhouses | 0 | 0 | 0 | 0 | 0 | 0 | # of Hydroelectric Substations and Powerhouses | 0 | 0 | 2158.6661 | 2158.6661 | 62 | 62 | # of Hydroelectric Substations and Powerhouses | 0 | 0 | 1766.3333 | 1766.3333 | 60 | 60 | # of Hydroelectric Substations and Powerhouses | 0 | 0 | 1786.6667 | 1786.6667 | 60 | 60 | # of Hydroelectric Substations and Powerhouses
Vegetation management project | Vegetation Management & Inspections | 7.3.5.18.1 | Substation vegetation management, Maintenance substation distribution | N/A | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 95 Rule 35; PRC 4293; NERC Standard FAC-003-4 |  | RSEs presented are for the year 2022. | 0 | 0 | 2727.533 | 1709.384 |  | N/A |  | 0 | 0 | 2676.609 | 1677.469 | N/A | N/A |  | 0 | 0 | 2314.258 | 2314.258 | 0 | 0 | Tags | 0 | 0 | 1265.501 | 1265.501 | 0 | 0 | Tags | 0 | 0 | 1302.003 | 1302.003 | 0 | 0 | Tags
Vegetation management project | Vegetation Management & Inspections | 7.3.5.18.2 | Substation vegetation management, Maintenance substation transmission | N/A | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | N/A | Transmission Owner | N/A | In Compliance | GO 95 Rule 35; PRC 4293; NERC Standard FAC-003-3 |  | RSEs presented are for the year 2022. | 0 | 0 | 1217.6491 | 856.4361 |  | N/A |  | 0 | 0 | 1717.5268 | 1208.0268 | N/A | N/A |  | 0 | 0 | 1670.4913 | 1670.4913 | 0 | 0 | Tags | 0 | 0 | 1252.9987 | 1252.9987 | 0 | 0 | Tags | 0 | 0 | 1252.9987 | 1252.9987 | 0 | 0 | Tags
Vegetation management project | Vegetation Management & Inspections | 7.3.5.18.3 | Substation vegetation management, Maintenance substation Generation | N/A | N/A | 2019 | N/A | N/A | N/A | N/A | N/A | See initiative 7.3.5.17.3 | See initiative 7.3.5.17.3 | In Compliance | GO 95 Rule 35; PRC 4293; NERC Standard FAC-003-3 |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 62 | 62 | Tags | 0 | 0 | 0 | 0 | 61 | 61 | Tags | 0 | 0 | 0 | 0 | 61 | 61 | Tags
Vegetation management project | Vegetation Management & Inspections | 7.3.5.19 | Vegetation management system | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | 25597 |  | 0 | 0 | 0 | 0 | 99165 | 31307 |  | 0 | 0 | 8962.0837 | 2814.5085 | 0 | 0 | N/A | 0 | 0 | 92516.1157 | 29054.3364 | 0 | 0 | N/A | 0 | 0 | 8792.936 | 2761.3883 | 0 | 0 | N/A
Vegetation management project | Vegetation Management & Inspections | 7.3.5.20 | Additional vegetation management practices beyond regulatory requirements and recommendations | N/A | N/A | 2021 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 13363.3195 | 4173.0642 |  | 31307 |  | 0 | 0 | 7971.0423 | 2489.1773 | 99165 | 31307 |  | 0 | 0 | 18784.8196 | 5866.0768 | 0 | 0 | # of distribution poles | 0 | 0 | 32353.9608 | 10103.4146 | 0 | 0 | # of distribution poles | 0 | 0 | 7076.6439 | 2209.8768 | 0 | 0 | # of distribution poles
Vegetation management project | Vegetation Management & Inspections | 7.3.5.21 | Vegetation management activities post-fire | N/A | N/A | See Initiative 7.3.5.2 | N/A | N/A | N/A | N/A | N/A | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.1 | Automatic recloser operations | N/A | N/A | 2018 | N/A | N/A | N/A | N/A | N/A | N/A - no forecast | N/A - no forecast | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.2 | Crew-accompanying ignition prevention and suppression resources and services | Consequence - Financial | No other consequences reflected | 2018 | 0.71408 | 0 | 0.066674 | 0.81573 | 0.44133 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 385.4115 | 385.4115 | 7750.9584 | 7750.9584 | 0 | 0 | N/A | 752.3551 | 752.3551 | 9205.1416 | 9205.1416 | 0 | 0 | N/A | 35.1233 | 35.1233 | 10267.2076 | 10267.2076 | 0 | 0 | N/A | 690.0377 | 690.0377 | 14524.0149 | 14524.0149 | 0 | 0 | N/A | 143.4995 | 143.4995 | 15083.2779 | 15083.2779 | 0 | 0 | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.3 | Personnel work procedures and training in conditions of elevated fire risk | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 1384.7294 | 1384.7294 | 0 | 0 | N/A | 0 | 0 | 839.8231 | 839.8231 | 0 | 0 | N/A | 0 | 0 | 966.4419 | 966.4419 | 0 | 0 | N/A | 0 | 0 | 1000 | 1000 | 0 | 0 | N/A | 0 | 0 | 1030 | 1030 | 0 | 0 | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.4-D | Protocols for PSPS re-energization, Distribution | Consequence - PSPS | No other consequences reflected | 2018 | 1.7858 | 0 | 1.7858 | 1.7858 | 1.7858 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 756.8257 | 756.8257 | 739.8956 | 739.8956 | 0 | 0 | N/A | 1376.1542 | 1376.1542 | 7610.4654 | 7610.4654 | 0 | 0 | N/A | 1215.9062 | 1215.9062 | 8794.8573 | 8794.8573 | 0 | 0 | N/A | 4940.315 | 4940.315 | 10093.2135 | 10093.2135 | 0 | 0 | N/A | 3250.143 | 3250.143 | 8620.9611 | 8620.9611 | 0 | 0 | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.4-T | Protocols for PSPS re-energization, Transmission | Consequence - PSPS | No other consequences reflected | 2018 | 3.1359 | 0 | 3.1359 | 3.1359 | 3.1359 | Transmission Owner | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 1774.2242 | 1774.2242 | 0 | 0 | N/A | 0 | 0 | 1208.096 | 1208.096 | 0 | 0 | N/A | 0 | 0 | 1349.7304 | 1349.7304 | 0 | 0 | N/A | 0 | 0 | 2000 | 2000 | 0 | 0 | N/A | 0 | 0 | 2000 | 2000 | 0 | 0 | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.5-D | PSPS events and mitigation of PSPS impacts , Distribution | Equipment Failure, Vegetation | No other drivers addressed | 2018 | N/A | N/A | N/A | N/A | N/A | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 178868.2005 | 178868.2005 | 0 | 0 | N/A | 0 | 0 | 80703.3268 | 80703.3268 | 0 | 0 | N/A | 0 | 0 | 35313.6331 | 35313.6331 | 0 | 0 | N/A | 0 | 0 | 68814.333 | 68814.333 | 0 | 0 | N/A | 0 | 0 | 70943.6296 | 70943.6296 | 0 | 0 | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.5-T | PSPS events and mitigation of PSPS impacts , Transmission | Equipment Failure, Vegetation | No other drivers addressed | 2018 | N/A | N/A | N/A | N/A | N/A | Transmission Owner | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 16255.2054 | 16255.2054 | 0 | 0 | N/A | 0 | 0 | 2406.708 | 2406.708 | 0 | 0 | N/A | 0 | 0 | 1209.142 | 1209.142 | 0 | 0 | N/A | 0 | 0 | 1807.925 | 1807.925 | 0 | 0 | N/A | 0 | 0 | 1807.925 | 1807.925 | 0 | 0 | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.6 | Stationed and on-call ignition prevention and suppression resources and services | Consequence - Financial | No other consequences reflected | 2018 | 0.71408 | 0 | 0.066674 | 0.81573 | 0.44133 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 128.4705 | 128.4705 | 2583.6528 | 2583.6528 | 0 | 0 | N/A | 250.785 | 250.785 | 3068.3805 | 3068.3805 | 0 | 0 | N/A | 11.7078 | 11.7078 | 3422.4025 | 3422.4025 | 0 | 0 | N/A | 230.0126 | 230.0126 | 4841.3383 | 4841.3383 | 0 | 0 | N/A | 47.8332 | 47.8332 | 5027.7593 | 5027.7593 | 0 | 0 | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.7 | Other, Aviation Support | Consequence - PSPS | No other consequences reflected | <2018 | 32.2052 | 0 | 32.2052 | 32.2052 | 32.2052 | 2020 GRC | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  | N/A |  | 0 | 0 | 5398 | 5398 | 0 | 0 | N/A | 285 | 285 | 3349 | 3349 | 0 | 0 | N/A | 325 | 325 | 6142 | 6142 | 0 | 0 | N/A | 24500 | 24500 | 5723 | 5723 | 0 | 0 | N/A
Other | Grid Operations & Operating Protocols | 7.3.6.8 | Protective equipment and device settings | All Drivers | No other drivers addressed | 2021 | 75.967 | 0 | 1.685 | 88.284 | 44.398 | N/A | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2742.1862 | 2742.1862 | 18211.1575 | 18211.1575 | 0 | 0 | N/A | 21900 | 21900 | 142592.2 | 142592.2 | 25734 | 25734 | N/A | 22557 | 22557 | 140510.67 | 140510.67 | 25734 | 25734 | N/A
Other | Data Governance | 7.3.7.1 | Centralized repository for data | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 758.3188 | 758.3188 | 0 | 0 | N/A | 0 | 0 | 666.2762 | 666.2762 | 0 | 0 | N/A | 0 | 0 | 779.4454 | 779.4454 | 0 | 0 | N/A | 0 | 0 | 857.7958 | 857.7958 | 0 | 0 | N/A | 0 | 0 | 883.5297 | 883.5297 | 0 | 0 | N/A
Other | Data Governance | 7.3.7.2 | Collaborative research on utility ignition and/or wildfire | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC, EPIC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 695.354 | 695.354 | 0 | 0 | N/A | 0 | 0 | 985.249 | 985.249 | 0 | 0 | N/A | 0 | 0 | 994.427 | 994.427 | 0 | 0 | N/A | 0 | 0 | 866 | 866 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Other | Data Governance | 7.3.7.3 | Documentation and disclosure of wildfire-related data and algorithms | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 947.943 | 947.943 | 0 | 0 | N/A | 0 | 0 | 931.0686 | 931.0686 | 0 | 0 | N/A | 0 | 0 | 995.7826 | 995.7826 | 0 | 0 | N/A | 0 | 0 | 1047.3536 | 1047.3536 | 0 | 0 | N/A | 0 | 0 | 1078.7742 | 1078.7742 | 0 | 0 | N/A
Other | Data Governance | 7.3.7.4 | Tracking and analysis of near miss data | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 153.3257 | 153.3257 | 0 | 0 | N/A | 0 | 0 | 631.7019 | 631.7019 | 0 | 0 | N/A | 0 | 0 | 650.6529 | 650.6529 | 0 | 0 | N/A | 0 | 0 | 670.1725 | 670.1725 | 0 | 0 | N/A
Other | Data Governance | 7.3.7.5 | Other, IT projects to support wildfire mitigation work | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | WMCE and Transmission Owner | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 27283.5563 | 27283.5563 | 9316.7949 | 9316.7949 | 0 | 0 | N/A | 32178.3272 | 32178.3272 | 23179.6683 | 23179.6683 | 0 | 0 | N/A | 51741.0219 | 51741.0219 | 40129.2822 | 40129.2822 | 0 | 0 | N/A | 49300.0264 | 49300.0264 | 45100.0056 | 45100.0056 | 0 | 0 | N/A | 35300 | 35300 | 36700 | 36700 | 0 | 0 | N/A
Other | Resource allocation methodology | 7.3.8.1 | Allocation methodology development and application | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 921.4123 | 287.7363 | 0 | 0 | N/A | 0 | 0 | 5710.4034 | 1783.2306 | 0 | 0 | N/A | 1776.0833 | 554.6309 | 6208.3813 | 1938.7379 | 0 | 0 | N/A | 4382.394 | 1368.5231 | 3485.7611 | 1088.5248 | 0 | 0 | N/A | 0 | 0 | 564.2835 | 176.213 | 0 | 0 | N/A
Other | Resource allocation methodology | 7.3.8.2 | Risk reduction scenario development and analysis | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 100.3542 | 31.3384 | 53.729 | 16.7784 | 0 | 0 | N/A | 1039.5227 | 324.6196 | 77.5158 | 24.2064 | 0 | 0 | N/A | 1006.5347 | 314.3182 | 53.3266 | 16.6527 | 0 | 0 | N/A | 909.8101 | 284.1132 | 62.1916 | 19.421 | 0 | 0 | N/A | 1061.1252 | 331.3655 | 64.0574 | 20.0037 | 0 | 0 | N/A
Other | Resource allocation methodology | 7.3.8.3 | Risk spend efficiency analysis (RSE) | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 103.9062 | 32.4476 | 0 | 0 | N/A | 0 | 0 | 263.9438 | 82.4237 | 0 | 0 | N/A | 0 | 0 | 956.594 | 298.7228 | 0 | 0 | N/A | 0 | 0 | 933.7633 | 291.5933 | 0 | 0 | N/A | 0 | 0 | 783.7633 | 244.7517 | 0 | 0 | N/A
Other | Emergency planning and preparedness | 7.3.9.1 | Adequate and trained workforce for service restoration | All Consequences | All Consequences | <2018 | 68.9708 | 0 | 4.6405 | 78.9126 | 42.2983 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 9204.2186 | 9204.2186 | 0 | 0 | N/A | 0 | 0 | 8674.0874 | 8674.0874 | 0 | 0 | N/A | 0 | 0 | 7947.3524 | 7947.3524 | 0 | 0 | N/A | 0 | 0 | 7666.0593 | 7666.0593 | 0 | 0 | N/A | 0 | 0 | 7896.041 | 7896.041 | 0 | 0 | N/A
Other | Emergency planning and preparedness | 7.3.9.2 | Community outreach, public awareness, and communications efforts | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | 2020 GRC | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 20394.114 | 20394.114 | 0 | 0 | N/A | 0 | 0 | 22942.9399 | 22942.9399 | 0 | 0 | N/A | 0 | 0 | 20751.9809 | 20751.9809 | 0 | 0 | N/A | 0 | 0 | 21739.4284 | 21739.4284 | 0 | 0 | N/A | 0 | 0 | 21374.1553 | 21374.1553 | 0 | 0 | N/A
Other | Emergency planning and preparedness | 7.3.9.3 | Customer support in emergencies | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | Emergency Consumer Protections | ECPMA FRMMA / WMPMA | In Compliance | Gas & Electric Rule 1; Gas & Electric Rule 6; Gas & Electric Rule 11; Gas & Electric Rule 19.1; Gas & Electric Rule 19.2; Gas & Electric Rule 19.3; Electric Rule 12; Electric Rule 13; Electric Rule 15; Electric Rule 16; Electric Rule 21 |  | RSEs presented are for the year 2022. | 0 | 0 | 2578.7053 | 2578.7053 | 0 | 0 | N/A | 0 | 0 | 3938.9336 | 3938.9336 | 0 | 0 | N/A | 0 | 0 | 2442.1174 | 2442.1174 | 0 | 0 | N/A | 0 | 0 | 3413.3412 | 3413.3412 | 0 | 0 | N/A | 0 | 0 | 3582.8169 | 3582.8169 | 0 | 0 | N/A
Other | Emergency planning and preparedness | 7.3.9.4 | Disaster and emergency preparedness plan | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | 2020 GRC | FRMMA / WMPMA | In Compliance | GO 166 Standards 1-13 |  | RSEs presented are for the year 2022. | 0 | 0 | 1289.0715 | 1289.0715 | 0 | 0 | N/A | 0 | 0 | 1557.0173 | 1557.0173 | 0 | 0 | N/A | 0 | 0 | 5643.612 | 5643.612 | 0 | 0 | N/A | 0 | 0 | 6843.4437 | 6843.4437 | 0 | 0 | N/A | 0 | 0 | 7048.747 | 7048.747 | 0 | 0 | N/A
Other | Emergency planning and preparedness | 7.3.9.5 | Preparedness and planning for service restoration | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 189.1269 | 189.1269 | 0 | 0 | N/A | 0 | 0 | 16156.1589 | 16156.1589 | 0 | 0 | N/A | 0 | 0 | 16467.4266 | 16467.4266 | 0 | 0 | N/A | 0 | 0 | 15794.469 | 15794.469 | 0 | 0 | N/A | 0 | 0 | 16716.448 | 16716.448 | 0 | 0 | N/A
Other | Emergency planning and preparedness | 7.3.9.6 | Protocols in place to learn from wildfire events | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 552.4592 | 552.4592 | 0 | 0 | N/A | 0 | 0 | 667.2931 | 667.2931 | 0 | 0 | N/A | 0 | 0 | 1148.3742 | 1148.3742 | 0 | 0 | N/A | 0 | 0 | 1235.8906 | 1235.8906 | 0 | 0 | N/A | 0 | 0 | 1272.9673 | 1272.9673 | 0 | 0 | N/A
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.1 | Community engagement | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 19980.6211 | 19980.6211 | 0 | 0 | # of meetings | 0 | 0 | 21811.6767 | 21811.6767 | 0 | 0 | # of meetings | 0 | 0 | 19643.3108 | 19643.3108 | 0 | 0 | # of meetings | 0 | 0 | 20615.9564 | 20615.9564 | 0 | 0 | # of meetings | 0 | 0 | 20216.9795 | 20216.9795 | 0 | 0 | # of meetings
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.2 | Cooperation and best practice sharing with agencies outside CA | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 134.745 | 134.745 | 0 | 0 | N/A | 0 | 0 | 225 | 225 | 0 | 0 | N/A | 0 | 0 | 193.2407 | 193.2407 | 0 | 0 | N/A | 0 | 0 | 204.6708 | 204.6708 | 0 | 0 | N/A
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.3 | Cooperation with suppression agencies | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 1337.9408 | 1337.9408 | 0 | 0 | N/A | 0 | 0 | 3858.6212 | 3858.6212 | 0 | 0 | N/A | 0 | 0 | 4258.2642 | 4258.2642 | 0 | 0 | N/A | 0 | 0 | 4532.2125 | 4532.2125 | 0 | 0 | N/A | 0 | 0 | 4668.1789 | 4668.1789 | 0 | 0 | N/A
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.4 | Forest service and fuel reduction cooperation and joint roadmap | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC, Transmission Owner | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 2357.4014 | 728.5419 | 0 | 0 | N/A | 0 | 0 | 5114.9445 | 1581.0027 | 0 | 0 | N/A | 0 | 0 | 4420.1345 | 1366.2406 | 0 | 0 | N/A | 0 | 0 | 5132.6675 | 1586.4693 | 0 | 0 | N/A | 0 | 0 | 5136.6475 | 1587.6808 | 0 | 0 | N/A
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.5 | Other, PMO and General Wildfire Support | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | FRMMA / WMPMA | N/A | N/A |  | RSEs presented are for the year 2022. | 0 | 0 | 21505.3579 | 21505.3579 | 0 | 0 | N/A | 0 | 0 | 24849.4976 | 24849.4976 | 0 | 0 | N/A | 0 | 0 | 26581.8864 | 26581.8864 | 0 | 0 | N/A | 0 | 0 | 24192.6411 | 24192.6411 | 0 | 0 | N/A | 0 | 0 | 17473.2686 | 17473.2686 | 0 | 0 | N/A
Updated comments for Table 12 (5/2/2022): 7.3.6.8 Protective equipment and device settings – the forecast has been updated to include capital work underway to replace/upgrade substation equipment (e.g., circuit breakers) so that EPSS (Enhanced Powerline Safety Settings) settings can be enabled. No changes to the financials at this time for all other initiatives Table 12 comments: Initiatives showing "Line Miles Treated" measured in "Alternative Units" are derived from the annual forecasted budget for that initiative which can include the costs of new installations as well as the forecasted costs for ongoing Operations & Maintenance and Repairs. Detailed notes on Table 12 data can be found in the Section 7.3.a in the 2022 Wildfire Mitigation Plan.