## READ ME FIRST
Quarterly Initiative Update - WMP Initiative Status Updates
Instructions for use
1 | Update progress on WMP Initiatives on "Initiatives" sheet by populating columns A through AB. Progress currently filled in is an example. Yellow cells indicate information that needs to be filled out or confirmed by utility. WMP initiatives that are not already listed in the "Initiatives" sheet shall be added as separate line items on the "Initiatives" sheet. Quantitative information, included initiative targets, the units of said targets and subsequent progress are reported in columns L through U with qualitative targets and progress described in columns V through Z.
2 | WSD Compliance will reach out to follow up on which Initiatives require documentation for auditing, indicated in columns AD and AE in the "Initiatives" sheet. For those initiatives requiring audit documentation, please fill out columns AF through AH. Please be sure to link to a Kiteworks folder in column AF.
3 | Definitions for each field are provided in the table below starting in row 17 - READ BEFORE INPUTTING DATA
4 | WSD Compliance will contact the electrical corporation with any follow-up questions regarding audits
Update the below table to establish which year, quarter, month of the WMP cycle this submission represents
Utility |  | SCE
Report Year |  | 2022
Report Quarter |  | q1
Submission Date |  | 2022-06-06
Definition of fields
| Column | Column name | Definition | Input type | Submission in which to be completed
| A | UtilityID | Standardized ID of utility (PGE, SCE, SDGE, BVES, LU, PC, HWT, or TBC) - auto populated by utility field above | Text | Q1
| B | Submission Date | Autogenerated based on submission date field above | Date | Q1
| C | WMPInitiativeCategory | One of the 10 initiative categories in the WMP | Text | Q1
| D | WMPInitiativeCategory# | Autogenerated based on initiative category | Numeric | Q1
| E | WMPInitiativeActivity | The relevant WMP activity classification for the initiative. If this initiative applies to an activity not presented, mark "other" | Text | Q1
| F | ActivityNameifOther | If activity was "other", then provide the name of the appropriate activity. Should match an activity name in utility's WMP (Table 12) | Text | Q1
| G | WMPInitiativeActivity# | Autogenerated based on initiative activity. Will be number or name of activity if activity was marked as "other" | Numeric/Text | Q1
| H | UtilityInitiativeName | Utility name for initiative | Text | Q1
| I | InitiativeActivityID | ID for the utility initiative. Must be unique to a utility's Initiative activity across submissions. If this initiative is also reported in the initiatives feature class for Grid hardening, Asset inspections, or vegetation management and inspections, then this ID should also connect to the ID in the corresponding initiative feature class (Fields "GhlogID", "AiLogID", "VmiLogID", "VmpLogID", and "OiLogID") | Text | Q1
| J | WMPInitiativeCode | Unique ID of the initiative. Must be unique for each initiative for each utility for each year. Follows the format “[UtilityID]_ [WMPInitiativeCategory]_[ WMPInitiativeActivity]_[InitiativeActivityID]_[Year four digit number (e.g., “2021”)]”. For example the code “PGE_Vegetation Management & Inspections_Substation vegetation management _001_2021” would be where utility is PG&E, Initiative category is Vegetation Management & Inspections, activity is Substation vegetation management, unique initiative ID is 001 and the year is 2021 | Text | Q1
| K | WMPPageNumber | Page of most recent WMP where initiative is detailed. If the initiative is detailed on multiple pages, put the first page | Numeric | Q1
| L | QuantTargetUnits | If initiative has a quantitative target, then report the units for the target. For example, if the initiative is installing covered conductors, then the unit would be "# of covered conductors installed" | Text | Q1
| M | AnnualQuantTarget | Quantitative target for year | Numeric | Q1
| N | ProjectedQuantProgressQ1 | Quantitative projected progress by end of Q1: Jan 1 - Mar 31 | Numeric | Q1
| O | ProjectedQuantProgressQ1-2 | Cumulative quantitative projected progress by end of Q2: Jan 1 - June 30. Q1 projected progress + Q2 projected progress | Numeric | Q1
| P | ProjectedQuantProgressQ1-3 | Cumulative quantitative projected progress by end of Q3: Jan 1 - Sep 30. Q1 projected progress + Q2 projected progress + Q3 projected progress | Numeric | Q1
| Q | ProjectedQuantProgressQ1-4 | Cumulative quantitative projected progress by end of Q4: Jan 1 - Dec 31. Equal to total annual target | Numeric | Q1
| R | QuantActualProgressQ1 | Quantitative progress by end of Q1: Jan 1 - Mar 31 | Numeric | Q1
| S | QuantActualProgressQ1-2 | Cumulative quantitative progress by end of Q2: Jan 1 - June 30. Q1 progress + Q2 progress | Numeric | Q2
| T | QuantActualProgressQ1-3 | Cumulative quantitative progress by end of Q3: Jan 1 - Sep 30. Q1 progress + Q2 progress + Q3 progress | Numeric | Q3
| U | QuantActualProgressQ1-4 | Cumulative quantitative progress by end of Q4: Jan 1 - Dec 31. Total annual progress | Numeric | Q4
| V | QualTargetAnnual | If initiative has a qualitative target, then detail the target. For example, if the initiative is building a centralized data lake, then the target may be "Developing a centralized data lake by end of year" | Text | Q1
| W | QualProgressQ1 | Qualitative progress by end of Q1: Jan 1 - Mar 31 | Text | Q1
| X | QualProgressQ1-2 | Qualitative progress by end of Q2: Jan 1 - June 30 | Text | Q2
| Y | QualProgressQ1-3 | Qualitative progress by end of Q3: Jan 1 - Sep 30 | Text | Q3
| Z | QualProgressQ1-4 | Qualitative progress by end of Q4: Jan 1 - Dec 31. Total annual progress | Text | Q4
| AA | Status | Status of initiative, can be one of the following: Completed/In Progress/Planned/Delayed/Cancelled | Text | Q1, Q2, Q3, Q4
| AB | CorrectiveActionsIfDelayed | If initiative is delayed based on reported target vs progress (e.g., reported QuantProgress for Q1 was significantly below the ProjectedQuantProgress for Q1), detail corrective actions | Text | As needed
AC-onwards is managed by WSD; columns AF-AH will only be completed by utility upon WSD request

## Initiatives
UtilityID | Submission Date | WMPInitiativeCategory | WMPInitiativeCategory# | WMPInitiativeActivity | ActivityNameifOther | WMPInitiativeActivity# | UtilityInitiativeName | InitiativeActivityID | WMPInitiativeCode | WMPPageNumber | QuantTargetUnits | AnnualQuantTarget | ProjectedQuantProgressQ1 | ProjectedQuantProgressQ1-2 | ProjectedQuantProgressQ1-3 | ProjectedQuantProgressQ1-4 | QuantActualProgressQ1 | QuantActualProgressQ1-2 | QuantActualProgressQ1-3 | QuantActualProgressQ1-4 | AnnualQualTarget | QualActualProgressQ1 | QualActualProgressQ1-2 | QualActualProgressQ1-3 | QualActualProgressQ1-4 | Status | CorrectiveActionsIfDelayed | REFERENCE: Compliance Branch Requirements --> | Audit | Audit File Documentation Requested | FolderLink | PersonInChargeName | PersonInChargeEmail
SCE | 2022-05-02 | Situational Awareness & Forecasting | 7.3.2 | Advanced weather monitoring and weather stations |  | 1 | Weather Stations | SA-1 | SCE_Situational Awareness & Forecasting_Advanced weather monitoring and weather stations _SA-1_2022 | 265 | # of weather stations installed | Install 150 weather stations in SCE's HFRA. SCE will strive to install up to 175 weather stations in SCE's HFRA, subject to resource and execution constraints | 0 | 50 | 110 | 150 | 26 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Situational Awareness & Forecasting | 7.3.2 | Continuous monitoring sensors |  | 9 | Distribution Fault Anticipation (DFA) | SA-9 | SCE_Situational Awareness & Forecasting_Continuous monitoring sensors _SA-9_2022 | 269 | Qualitative Initiative | [9 empty] | SCE will evaluate the performance of installed fault anticipation technology and develop recommendations for future use by year-end 2022 | Distribution Fault Anticipation (DFA) events reviewed internal to SCE in Q1 and 4 events reviewed external with the vendor. 50% of the first draft report is complete. |  |  |  | On Track
SCE | 2022-05-02 | Situational Awareness & Forecasting | 7.3.2 | Continuous monitoring sensors |  | 10 | High -Definition (HD) Cameras | SA-10 | SCE_Situational Awareness & Forecasting_Continuous monitoring sensors _SA-10_2022 | 272 | # HD cameras installed | Install 10 HD Cameras. SCE will strive to install up 20 HD Cameras, subject to resource and execution constraints. | 0 | 4 | 6 | 0 | Worked with local Fire Management Officers and Alert Wildfire PI to identify and validate intallation location. Installations to begin in Q2. | [8 empty] | On Track
SCE | 2022-05-02 | Situational Awareness & Forecasting | 7.3.2 | Forecast of a fire risk index, fire potential index, or similar |  | 8 | Fire Science Enhancements | SA-8 | SCE_Situational Awareness & Forecasting_Forecast of a fire risk index, fire potential index, or similar _SA-8_2022 | 275 | Qualitative Initiative | Qualitative Initiative | [8 empty] | Calibrate FPI 2.0 and evaluate its performance over the 2022 fire season. Improve fire spread modeling applications (i.e., FireSim and FireCast) to include 1) fire suppression and 2) buildings destroyed by fire | Calibration of FPI 2.0 by Fire Climate Zones using historical fire occurrence data continues. The calibration has been completed for the Fuels Index component. The Purchase Order (PO) to support fire spread modeling application work was issued and signed in Q1. Coordination with vendor to draft a project plan to support development of the Building Loss Factor metric for evaluation has begun. |  |  |  | On Track
SCE | 2022-05-02 | Situational Awareness & Forecasting | 7.3.2 | Weather forecasting and estimating impacts on electric lines and equipment |  | 3 | Weather and Fuels Modeling | SA-3 | SCE_Situational Awareness & Forecasting_Weather forecasting and estimating impacts on electric lines and equipment _SA-3_2022 | 283 | Qualitative Initiative | Qualitative Initiative | [8 empty] | Equip 400 weather station locations with machine learning capabilities. SCE will strive to equip up to 500 weather station locations with machine learning capabilities, subject to resource and execution constraints. | Point locations were provided to vendor to asess data quality and sutiability to build new machine learning models. Vendor began training new maching learning models across SCE territory and performed new model verifications. . Machine learning to be operationalized in Q3. |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault |  | 6 | Circuit Breaker Relay Hardware for Fast Curve | SH-6 | SCE_Grid Design & System Hardening_Circuit breaker maintenance and installation to de-energize lines upon detecting a fault _SH-6_2022 | 292 | # of installations and placed into service | Replace/upgrade 104 relay units in SCE’s HFRA. SCE will strive to replace/ upgrade up to 125 relay units in SCE’s HFRA, subject to resource constraints and other execution risks | 0 | 21 | 90 | 113 | Design completed in Q1 with installations to begin in Q2. Procurement delays have shifted some projects into later quarters in 2022 but still expect to meet year end target. |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Covered conductor installation |  | 1 | Covered Conductor | SH-1 | SCE_Grid Design & System Hardening_Covered conductor installation _SH-1_2022 | 294 | # of circuit miles in HFRA | Install 1,100 circuit miles of covered conductor in SCE’s HFRA. SCE will strive to install up to as many as 1,250 circuit miles of covered conductor in SCE’s HFRA, subject to resource constraints and other execution risks. | 250 | 555 | 855 | 1100 | 278 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Covered conductor installation |  | 10 | Tree Attachment Remediation | SH-10 | SCE_Grid Design & System Hardening_Covered conductor installation _SH-10_2022 | 301 | # of tree attachment remediations | Remediate 500 tree attachments in SCE’s HFRA. SCE will strive to complete up to 700 tree attachment remediations in SCE’s HFRA, subject to resource constraints and other execution risks. | 20 | 184 | 480 | 500 | 257 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Covered conductor installation |  | 16 | Vibration Damper Retrofit | SH-16 | SCE_Grid Design & System Hardening_Covered conductor installation _SH-16_2022 | 303 | # structures | Retrofit vibration dampers on 100 structures where covered conductor is already installed in SCE’s HFRA. SCE will strive to retrofit vibration dampers on up to 115 structures where covered conductor is already installed in SCE’s HFRA. | 0 | 15 | 50 | 100 | Construction began in Q1, completed 33 installations. There are some back-office activities continuing to be addressed including monitoring material availability. |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Expulsion fuse replacement |  | 4 | Branch Line Protection Strategy | SH-4 | SCE_Grid Design & System Hardening_Expulsion fuse replacement _SH-4_2022 | 308 | # of locations with installed / replaced fuses | Install or replace fusing at 350 fuse locations that serve HFRA circuitry. SCE will strive to install or replace fusing at up to 483 locations that serve HFRA circuitry, subject to resource constraints and other execution risks. | 45 | 175 | 350 | 350 | 69 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Grid topology improvements to mitigate or reduce PSPS events |  | 7 | PSPS-Driven Grid Hardening Work | SH-7 | SCE_Grid Design & System Hardening_Grid topology improvements to mitigate or reduce PSPS events _SH-7_2022 | 310 | # of highly impacted circuits evaluated | Evaluate approximately 70 highly impacted circuits including 2021 PSPS events to determine additional deployment of PSPS mitigations | 72 | 72 | 72 | 72 | 104 |  |  |  | Quantitative Initiative |  |  |  |  | Complete
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Grid topology improvements to mitigate or reduce PSPS events |  | 12 | Microgrid Assessment | SH-12 | SCE_Grid Design & System Hardening_Grid topology improvements to mitigate or reduce PSPS events _SH-12_2022 | 311 | Qualitative Initiative | Qualitative Initiative | [8 empty] | SCE will actively attempt to obtain approval of easement with the landowner of the microgrid site, and if approval is received, SCE will move forward with microgrid project. If an approval is not received by June 30, 2022, or rejected, SCE will start to pursue other microgrid opportunities | SCE continues to discuss with land owner approval of easement for microgrid site. The site location requires a vote and approval to grant easement. Vote was postponed from Q1 to Q2. |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Installation of system automation equipment |  | 5 | Installation of System Automation Equipment - RAR / RCS | SH-5 | SCE_Grid Design & System Hardening_Installation of system automation equipment _SH-5_2022 | 313 | # of RARs / RCSs installed and operationalized | Install 15 sectionalizing devices such as RARs/RCSs driven by the results of evaluations / assessments conducted under SH-6 and SH-7. SCE will strive to install up to 31 sectionalizing devices such as RARs/RCSs driven by the results of evaluations / assessments conducted under SH-6 and SH-7, subject to resource constraints and other execution risks | 0 | 3 | 12 | 15 | Scope and design have been recived. Installations to begin in Q2 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Other corrective action |  | 14 | Long Span Initiative | SH-14 | SCE_Grid Design & System Hardening_Other corrective action _SH-14_2022 | 321 | # of assessments | Remediate 1,400 spans in SCE’s HFRA. SCE will strive to remediate up to 1,800 spans in SCE’s HFRA, subject to resource constraints and other execution risks. | 210 | 490 | 980 | 1400 | 935 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Other corrective action |  | 17 | Rapid Earth Fault Current Limiter | SH-17 | SCE_Grid Design & System Hardening_Other corrective action _SH-17_2022 | 323 | Qualitative Initiative | SCE will produce a report summarizing performance and lessons learned from previous REFCL installations. SCE will also initiate engineering and material purchase for the ground fault neutralizers (GFNs) to be constructed in 2023 at Acton and Phelan Substations. | [8 empty] | SCE will produce a report summarizing performance and lessons learned from previous REFCL installations. SCE will also initiate engineering and material purchase for the ground fault neutralizers (GFNs) to be constructed in 2023 at Acton and Phelan Substations. | Ground fault neutralizer is in service, and performance continues to be monitored. Finalized specifications and material order to initiate engineering and material purchase for ground neutralizers, and. engineering design contract awarded. |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Transmission tower maintenance and replacement |  | 13 | C-Hooks | SH-13 | SCE_Grid Design & System Hardening_Transmission tower maintenance and replacement _SH-13_2022 | 331 | # of C-hooks | SCE will replace C‐Hooks on 10 structures in SCE’s HFRA and strive to replace up to 21 C‐Hooks, subject to execution risks such as environmental clearance | 0 | 0 | 21 | 21 | Statement of work for bid in progress; and expect to award by late Q2. Installations to begin in Q3. |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Undergrounding of electric lines and/or equipment |  | 2 | Undergrounding Overhead Conductor | SH-2 | SCE_Grid Design & System Hardening_Undergrounding of electric lines and/or equipment _SH-2_2022 | 334 | # of circuit miles in HFRA | Install 11 circuit miles of targeted undergrounding in SCE’s HFRA. SCE will strive to install up to 13 miles of targeted undergrounding in SCE’s HFRA, subject to resource constraints and other execution risks. | 0 | 8 | 9 | 11 | Currently 3 underground miles are in construction and will be completed in Q2. 9 underground miles have been authorized to proceed with an overall year end target of 11. |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Updates to grid topology to minimize risk of ignition in HFTDs |  | 8 | Transmission Open Phase Detection | SH-8 | SCE_Grid Design & System Hardening_Updates to grid topology to minimize risk of ignition in HFTDs _SH-8_2022 | 337 | # of installations | Deploy open phase logic on five transmission lines. SCE will strive to deploy open phase logic on up to 11 transmission lines, subject to resource constraints and other execution risks. | 0 | 0 | 0 | 6 | Preliminary settings review completed. Currently developing finalized design packages and relay setting plans with field activities commencing in Q3. Deployment to occur in Q4. |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Updates to grid topology to minimize risk of ignition in HFTDs |  | 11 | Legacy Facilities | SH-11 | SCE_Grid Design & System Hardening_Updates to grid topology to minimize risk of ignition in HFTDs _SH-11_2022 | 340 | # sites | Hydro Control Circuits: Based on 2021 assessments, perform grid hardening on three control circuits at three legacy facility sites. Low Voltage Site Hardening: Based on 2021 assessment, perform one grid hardening project at a legacy facility site Grounding Studies/Lightning Arrestor Assessments and Remediations: Based on 2021 assessments perform four remediation projects at legacy facility sites. Additionally, complete 13 assessments. | 2 0 0 | 7 0 0 | 22 0 0 | 32 0 0 | 0 0 0 |  |  |  | Quantitative Initiative |  |  |  |  | Off Track | Hydro Control Circuits: Currently behind plan due to COVID-related resource constraints. Expect to return to on track performance by end of Q2 Low Voltage Site Hardening: Currently behind plan to finalize the project plan and scope due to COVID-related resource constraints. Expect to return to on track performance by end of Q2 Grounding Studies/Lightning Arrestor Assessments and Remediations: Currently behind plan against the original plan to finalize the project plan and scope due to project management resource constraints. Expect to return to on track performance in Q2
SCE | 2022-05-02 | Grid Design & System Hardening | 7.3.3 | Updates to grid topology to minimize risk of ignition in HFTDs |  | 15 | Vertical Switches | SH-15 | SCE_Grid Design & System Hardening_Updates to grid topology to minimize risk of ignition in HFTDs _SH-15_2022 | 341 | # of switches | Install 15 vertical switches in SCE’s HFRA. SCE will strive to install 25 vertical switches in SCE’s HFRA | 4 | 7 | 11 | 15 | 4 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Asset Management & Inspections | 7.3.4 | Improvement of inspections |  | 8 | Inspection Work Management Tools | IN-8 | SCE_Asset Management & Inspections_Improvement of inspections _IN-8_2022 | 347 | Qualitative Initiative | Qualitative Initiative | [8 empty] | Design capability for the legacy Distribution Ground inspection application in 2022 to transition to a single digital inspection platform in a future year In support of remediation efforts, conduct assessment to identify enhancements for Field Crew application, and evaluate applicability of enhancements by yearend 2022 | InspectForce Transmission Ground was implemented in February and released in Q1, which included new survey questions and updates to notification validation logic and google maps. Completed production upgrade of the field crew iPad application with capabilities; and planning deployment of distribution activities for Q2 and Q3. |  |  |  | On Track
SCE | 2022-05-02 | Asset Management & Inspections | 7.3.4 | Infrared inspections of distribution electric lines and equipment |  | 3 | Infrared Inspection of Energized Overhead Distribution Facilities and Equipment | IN-3 | SCE_Asset Management & Inspections_Infrared inspections of distribution electric lines and equipment _IN-3_2022 | 352 | # of distribution circuit miles in HFRA | Inspect 4,408 distribution overhead circuit miles in HFRA | 3480 | 4408 | 4408 | 4408 | 4114 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Asset Management & Inspections | 7.3.4 | Infrared inspections of transmission electric lines and equipment |  | 4 | Infrared Inspection, Corona Scanning, and High-Definition Imagery of Energized Overhead Transmission facilitites and Equipment | IN-4 | SCE_Asset Management & Inspections_Infrared inspections of transmission electric lines and equipment _IN-4_2022 | 354 | # of transmission circuit miles in HFRA | Inspect 1,000 transmission overhead circuit miles in HFRA | 150 | 600 | 900 | 1000 | 176 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Asset Management & Inspections | 7.3.4 | Infrared inspections of transmission electric lines and equipment |  | 9 | Transmission Conductor and Splice Assessment | IN-9 | SCE_Asset Management & Inspections_Infrared inspections of transmission electric lines and equipment _IN-9_2022 | 356 | # Spans/splices Inspections | Will inspect 75 spans with Line Vue, inspect 50 splices with X-Ray and obtain 5 Conductor Samples; SCE will strive to inspect up to 150 spans with Line Vue, inspect up to 70 splices with XRay, and obtain up to 15 Conductor Samples, subject to execution constraints. | Line Vue: 0 Splices w/X-ray: 5 Conductor Samples: 0 | Line Vue: 30 Splices w/X-ray: 35 Conductor Samples: 1 | Line Vue: 30 Splices w/X-ray: 50 Conductor Samples: 4 | Line Vue: 75 Splices w/X-ray: 50 Conductor Samples: 5 | Line Vue: 0 Splices w/X-ray: 19 Conductor Samples: 0 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Asset Management & Inspections | 7.3.4 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations |  | 1 | Distribution High Fire Risk Informed Inspections in HFRA | IN-1.1 | SCE_Asset Management & Inspections_Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations _IN-1.1_2022 | 362 | # of structures in HFRA | Inspect 150,000 structures in HFRA via both ground and aerial inspections.Subject to resource constraints and other factors. SCE will strive to inspect up to 180,000 structures in HFRA via both ground and aerial inspections. This target includes HFRI inspections, compliance due structures in HFRA and emergent risks identified during the fire season | Ground: 77179 Aerial: 43917 | Ground: 150000 Aerial: 120726 | Ground: 150000 Aerial: 142285 | Ground: 150000 Aerial: 150000 | Ground: 71822 Aerial: 46446 |  |  |  | Quantitative Initiative |  |  |  |  | Off Track | Vendor has been onboarded and issued equipment, which has aided in returning to planned throughput. Vendor is also learning SCE processes. To narrow the gap between planned and actual work completed, the vendor created a get-well-plan involving onboarding a sub-contractor to increase overall throughput.
SCE | 2022-05-02 | Asset Management & Inspections | 7.3.4 | Generation High Fire Risk-Informed inspections and remediations in HFRA |  | 5 | Generation High Fire Risk Informed Inspections in HFRA | IN-5 | SCE_Asset Management & Inspections_Generation High Fire Risk-Informed inspections and remediations in HFRA_IN-5_2022 | 373 | # of structures in HFRA | Inspect 190 generation-related assets in HFRA | 0 | 70 | 190 | 190 | 36 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Asset Management & Inspections | 7.3.4 | Other discretionary inspection of transmission electric lines and equipment, beyond inspections mandated by rules and regulations |  | 1 | Transmission High Fire Risk Informed Inspections in HFRA | IN-1.2 | SCE_Asset Management & Inspections_Other discretionary inspection of transmission electric lines and equipment, beyond inspections mandated by rules and regulations_IN-1.2_2022 | 375 | # of structures in HFRA | Inspect 16,000 structures in HFRA via both ground and aerial inspections. Subject to resource constraints and other factors SCE will strive to inspect up to 19,000 structures in HFRA via both ground and aerial inspections. This target includes HFRI inspections, compliance due structures in HFRA and emergent risks identified during the fire season | Ground: 2947 Aerial: 4915 | Ground: 10526 Aerial: 12723 | Ground: 15579 Aerial: 14965 | Ground: 16000 Aerial: 16000 | Ground: 3138 Aerial: 6461 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Detailed inspections of vegetation around distribution electric lines and equipment | Detailed inspections and management practices for vegetation clearances around distribution electrical lines, and equipment | Other | Detailed inspections and management practices for vegetation clearances around distribution electrical lines, and equipment | N/A | SCE_Vegetation Management & Inspections_Detailed inspections of vegetation around distribution electric lines and equipment _N/A_2022 | 396 | # of trees inspected | In its HFRA for 2022, SCE plans to inspect approximately 600,000 trees adjacent to distribution lines, based on current unique tree inventory count. Tree inventory is subject to fluctuations based on actual field conditions. | 140365 | 346966 | 532922 | 600000 | 238022 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Detailed inspections of vegetation around transmission electric lines and equipment | Detailed inspections and management practices for vegetation clearances around transmission infrastructure lines, and equipment | Other | Detailed inspections and management practices for vegetation clearances around transmission infrastructure lines, and equipment | N/A | SCE_Vegetation Management & Inspections_Detailed inspections of vegetation around transmission electric lines and equipment _N/A_2022 | 396 | # of trees inspected | In its HFRA for 2022, SCE plans to inspect approximately 100,000 trees adjacent to transmission lines, based on current unique tree inventory count. Tree inventory is subject to fluctuations based on actual field conditions. | 7053 | 71462 | 97316 | 100000 | 17523 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Emergency response vegetation management due to red flag warning or other urgent conditions | Emergency response vegetation management due to red flag warning or other urgent climate condition | Other | Emergency response vegetation management due to red flag warning or other urgent climate condition | N/A | SCE_Vegetation Management & Inspections_Emergency response vegetation management due to red flag warning or other urgent conditions _N/A_2022 | 400 | # poles brushed | SCE will inspect and clear (where clearance is needed) approximately 26,400 poles in identified Areas of Concern (AOC), with the exception of poles for which there are customer access or environmental constraints. These poles are included in the count of the Expanded Pole Brushing (VM-2) goal. | 15050 | 20903 | 27870 | 0 |  |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Fuel management and reduction of “slash” from vegetation management activities |  | 2 | Pole Brushing | VM-2 | SCE_Vegetation Management & Inspections_Fuel management and reduction of “slash” from vegetation management activities _VM-2_2022 | 404 | # of poles cleared | SCE will inspect and clear (where clearance is needed) 78,700 poles in HFRA, with the exception of poles for which there are customer access or environmental constraints. SCE will strive to inspect and clear (where clearance is needed) up to 170,000 distribution poles in HFRA. These poles are in addition to poles subject to PRC 4292. | 29906 | 47220 | 66108 | 78700 | 31198 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Fuel management and reduction of “slash” from vegetation management activities |  | 3 | Expanded Clearances for Legacy Facilities | VM-3 | SCE_Vegetation Management & Inspections_Fuel management and reduction of “slash” from vegetation management activities _VM-3_2022 | 407 | # of sites treated | Perform expanded clearances at 32 legacy facility location | 2 | 8 | 28 | 32 | 2 |  |  |  | Quantitative Initiative | Completed expanded clearance at 2 sites. The majority of expanded clearances are scheduled in the summertime to capture all new growth and avoid snow and weather issues. |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Fuel management and reduction of “slash” from vegetation management activities | Poles Brushed per PRC 4292 | Other | Poles Brushed per PRC 4292 | N/A | SCE_Vegetation Management & Inspections_Fuel management and reduction of “slash” from vegetation management activities _N/A_2022 | 407 | # of poles brushed (cleared) | SCE will inspect and clear (where clearance is needed) 55,100 poles in State Responsibility Area with the equipment identified by PRC 4292, with the exception of poles for which there are customer access or environmental constraints, or poles that are exempt under 14 Cal. Code of Regulations 1255 (e.g., poles in fruit orchards that are plowed or cultivated). | 20938 | 44080 | 55100 | 0 | 22281 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | LiDAR inspections of vegetation around distribution electric lines and equipment | LiDAR Vegetation Inspections – Distribution | Other | LiDAR Vegetation Inspections – Distribution | N/A | SCE_Vegetation Management & Inspections_LiDAR inspections of vegetation around distribution electric lines and equipment _N/A_2022 | 410 | # of Circuit Miles | SCE will inspect at least 500 HFRA circuit miles | 0 | 317 | 500 | 500 | 0 |  |  |  | Quantitative Initiative | Completed inspection of 0 HFRA circuit miles. Inspections planned to begin in May and be completed in Q3 |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | LiDAR inspections of vegetation around transmission electric lines and equipment | LiDAR Vegetation Inspections – Transmission | Other | LiDAR Vegetation Inspections – Transmission | N/A | SCE_Vegetation Management & Inspections_LiDAR inspections of vegetation around transmission electric lines and equipment _N/A_2022 | 412 | # of Circuit Miles | SCE will inspect at least 1600 HFRA circuit miles | 708 | 1386 | 1539 | 1600 | 747 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Quality assurance / quality control of inspections | Vegetation Inspections Audited Annually | Other | Vegetation Inspections Audited Annually | N/A | SCE_Vegetation Management & Inspections_Quality assurance / quality control of inspections_N/A_2022 | 416 | % of vegetation inspections audited | SCE plans to perform risk-based circuit mile Quality Control (QC) inspections on approximately 15% of SCEs total tree inventory. | 63000 | 126000 | 189000 | 252000 | 111729 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Recruiting and training of vegetation management personnel | Recruiting and training of vegetation management personnel | Other | Recruiting and training of vegetation management personnel | N/A | SCE_Vegetation Management & Inspections_Recruiting and training of vegetation management personnel_N/A_2022 | 420 | # ISA Certified Arborists | Maintain the current staffing levels of 95 International Society of Arboriculture (ISA) certified arborists performing work within SCEs service territory. Inclusive of SCE personnel and contractors. | 95 | 95 | 95 | 95 | 148 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Removal and remediation of trees with strike potential to electric lines and equipment |  | 1 | Hazard Tree Management Program | VM-1 | SCE_Vegetation Management & Inspections_Removal and remediation of trees with strike potential to electric lines and equipment _VM-1_2022 | 425 | # of circuits | Inspect 330 circuits and assess any trees with strike potential along those circuits. | 103 | 103 | 279 | 330 | 119 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Removal and remediation of trees with strike potential to electric lines and equipment |  | 4 | Dead and Dying Tree Removal | VM-4 | SCE_Vegetation Management & Inspections_Removal and remediation of trees with strike potential to electric lines and equipment _VM-4_2022 | 427 | # of circuits | Inspect 900 unique circuits and prescribe mitigation for dead and dying trees with strike potential along those circuits. | 334 | 676 | 805 | 900 | 325 |  |  |  | Quantitative Initiative |  |  |  |  | Off Track | Currently behind plan by 3% against the original plan of 334 due to weather conditions and some circuits having longer mileage average. Monitoring and tracking assessor vendors and performing Bi-Weekly status meetings. Assessors are working in other areas until snow melts and area is safe to return and continue work.Expect to return to on track performance in Q2.
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Substation inspections | Substation Inspections | Other | Substation Inspections | N/A | SCE_Vegetation Management & Inspections_Substation inspections_N/A_2022 | 428 | # of inspections | SCE performs substation inspections on 169 substations in HFRA. SCE plans to inspect all 169 substations, 5 times a year for GO174 Substations (146 Substations) and ISO & FERC Substations (23 Substations), for a total of 845 inspections. | 277 | 553 | 772 | 845 | 294 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Substation vegetation management | Substation vegetation inspections | Other | Substation vegetation inspections | N/A | SCE_Vegetation Management & Inspections_Substation vegetation management _N/A_2022 | 429 | # of inspections | SCE will perform Vegetation Management substation inspections in Tier 2 & Tier 3 totaling 169 substations. | 25 | 97 | 169 | 169 | 26 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Vegetation Management & Inspections | 7.3.5 | Vegetation inventory system |  | 6 | VM Work Management Tool | VM-6 | SCE_Vegetation Management & Inspections_Vegetation inventory system _VM-6_2022 | 430 | Qualitative Initiative | Qualitative Initiative | [8 empty] | SCE will implement the following programs within the VM Work Management Tool, Arbora: (1) Hazardous Tree Program (HTP) (including: Dead & Dying Tree Removal and Hazard Tree Mitigation) and (2) Routine Line Clearing | HTP pilot launch in Q1 was successful. HTP full roll out is on track and expected to completed in Q2 |  |  |  | On Track
SCE | 2022-05-02 | Grid Operations & Operating Protocols | 7.3.6 | PSPS events and mitigation of PSPS impacts |  | 2 | Customer Care Programs | PSPS-2 | SCE_Grid Operations & Operating Protocols_PSPS events and mitigation of PSPS impacts _PSPS-2_2022 | 448 | # of enrollments # of rebates | Customer Resiliency Equipment: CCBB: Enroll 2,750 customers in the CCBB program (35% of forecasted eligible population). Continue to identify new eligible customers each month to offer program. Portable Power Station Rebates and Portable Generator Rebates: SCE to issue 3,000 rebates and will strive to issue 4,000 rebates. | CCBB: 659 Rebates: 487 | CCBB: 1719 Rebates: 1369 | CCBB: 2427 Rebates: 2281 | CCBB: 2720 Rebates: 3000 | CCBB: 478 Rebates: 380 |  |  |  | Quantitative Initiative |  |  |  |  | Off Track | Currently behind plan due to 2022 forecast baselined to 2021 rebates which included a large PSPS event January 2021. Updates will be made to marketing material based on key customer survey feedback; customers weren't aware battery was free. Adjusting data pull dates so mailers can go out earlier in the month and contractors may contact customers earlier Pamphlet insert coming with the April bill to increase program awareness; social media ad retargeting will also begin in May and will run through November. 10 virtual community outreach and engagement sessions scheduled between May and June
SCE | 2022-05-02 | Data Governance | 7.3.7 | Centralized repository for data |  | 1 | Wildfire Safety Data Mart and Data Management (WiSDM / Ezy) | DG-1 | SCE_Data Governance_Centralized repository for data _DG-1_2022 | 462 | Qualitative Initiative | Qualitative Initiative | [8 empty] | Ezy Data: 1) Expand cloud Artificial Intelligence (AI) platform 2) Enable LIDAR data storage capability WiSDM: 1) Complete wildfire data repository design 2) Consolidate wildfire data storage onto wildfire data repository platform | Ezy Data deployed the Digital Accelerator (DA) image quality model integration on cloud platform and working to refine model capabilities, and finalizing LiDAR business capability definition. WiSDM: Process revalidation and data mapping continues. Common data repository design in progress to baseline system requirements for OEIS data reporting in Q2. |  |  |  | On Track
SCE | 2022-05-02 | Emergency Planning & Preparedness | 7.3.9 | Adequate and trained workforce for service restoration |  | 2 | SCE Emergency Response Training | DEP-2 | SCE_Emergency Planning & Preparedness_Adequate and trained workforce for service restoration _DEP-2_2022 | 477 | # trained | IMT – Have all PSPS IMT and Task Force members fully trained and qualified or requalified by July 1, 2022 UAS – SCE plans to expand the program by technically qualifying 50 UAS Operators that have passed the FAA 107 exam. | IMT: PSPS IMT Training and Exercise Kick-off UAS: 20 | IMT: PSPS IMT Trained in all Requalification Training Requirements & conduct readiness exercise UAS: 35 | IMT: 0 UAS: 50 | IMT: 0 UAS: 50 | IMT:Training and IMT Exercise kicked-off in Q1. Training to begin in Q2. UAS: 21 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Emergency Planning & Preparedness | 7.3.10 | Community engagement |  | 1 | Customer Education and Engagement - Community Meetings | DEP-1.2 | SCE_Emergency Planning & Preparedness_Community engagement_DEP-1.2_2022 | 491 | # of meetings | SCE will host at least nine wildfire community safety meetings in targeted communities based on the impact of 2021 PSPS events and ongoing wildfire mitigation activities. | 0 | 9 | 9 | 9 | 0 YTD; 9 meetings currently scheduled for Q2 |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Emergency Planning & Preparedness | 7.3.10 | Community engagement |  | 1 | Customer Education and Engagement, Marketing Campaign | DEP-1.3 | SCE_Emergency Planning & Preparedness_Community engagement_DEP-1.3_2022 | 502 | % PSPS awareness | PSPS Awareness goal: 50% | 50% | 50% | 50% | 50% | 55% |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Emergency Planning & Preparedness | 7.3.10 | Community engagement |  | 4 | Customer Research and Education | DEP-4 | SCE_Emergency Planning & Preparedness_Community engagement_DEP-4_2022 | 507 | # of surveys | SCE plans to conduct at least six PSPS‐related surveys in 2022, including the PSPS Tracker survey, wildfire safety community meeting feedback survey, CRC/CCV feedback survey, In‐Language Wildfire Mitigation Communications Effectiveness Surveys, PSPS Working Group and Advisory Board Surveys, and the Voice of Customer surveys. | Begin PSPS Tracker data collection | Administer community meeting feedback surveys (contingent upon meeting dates) | 0 | Administer community meeting feedback surveys (contingent upon PSPS event) | PSPS tracker questionnaire was finalized, and data collection has begun. Residential and Non-Residential customers will be contacted via phone and web-based surveys. |  |  |  | Quantitative Initiative |  |  |  |  | On Track
SCE | 2022-05-02 | Emergency Planning & Preparedness | 7.3.10 | Cooperation with suppression agencies |  | 5 | Aerial Suppression (DEP-5) | DEP-5 | SCE_Emergency Planning & Preparedness_Cooperation with suppression agencies_DEP-5_2022 | 512 | # of MOU | Will enter into a Memorandum of Understanding (MOU) with local county fire departments to provide standby cost funding for up to five aerial suppression resources strategically placed around the SCE service area | 0 | 6 | 6 | 6 | Draft MOUs were sent to Los Angeles County Fire Department, Orange County Fire Association and Ventura County Fire Department; and all three counties provided MOU draft comments in late Q1. |  |  |  | Quantitative Initiative |  |  |  |  | On Track
Notes:
In this QIU, SCE reports on progress in the 39 2021 WMP activities which were initiated to primarily address wildfire risks and/or PSPS impacts and which have specific 2021 program targets. SCE considers Non-WMP programs to be programs which are not initiated to primarily address wildfire risks and/or PSPS impacts. These programs are implemented for purposes primarily outside of wildfire / PSPS impact mitigation (e.g., for reliability), though they may provide indirect wildfire / PSPS impact mitigation benefits. Therefore, these programs would continue even if wildfire and/or PSPS risk did not exist.
Reported numbers are subject to revision upon data validation
NOTE: To add more rows, highlight the current last row of the table, copy, and paste directly below the last row
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See notes at end of table below
Note on H1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SCE focuses its QIU on reporting on WMP activities which are initiated to primarily address wildfire risks and/or PSPS impacts and have specific program targets. SCE considers Non-WMP programs to be programs which are not initiated to primarily address wildfire risks and/or PSPS impacts. These programs are implemented for purposes primarily outside of wildfire / PSPS impact mitigation (e.g., for reliability), though they may provide indirect wildfire / PSPS impact mitigation benefits. Therefore, these programs would continue even if wildfire and/or PSPS risk did not exist. These programs can also include work SCE is doing as part of standard operations. Discussion on these programs were included in SCE’s 2020-2022 WMP.

## Initiative mapping-DO NOT EDIT
WMP Table # / Category | WMP Initiative # | Initative activity | WMP category | WMP code | Utility
Risk Assessment and Mapping | 7.3.1.1 | A summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment | Risk Assessment & Mapping | 7.3.1 | PGE
Risk Assessment and Mapping | 7.3.1.2 | Climate-driven risk map and modelling based on various relevant weather scenarios | Situational Awareness & Forecasting | 7.3.2 | SCE
Risk Assessment and Mapping | 7.3.1.3 | Ignition probability mapping showing the probability of ignition along the electric lines and equipment | Grid Design & System Hardening | 7.3.3 | SDGE
Risk Assessment and Mapping | 7.3.1.4 | Initiative mapping and estimation of wildfire and PSPS risk-reduction impact | Asset Management & Inspections | 7.3.4 | BVES
Risk Assessment and Mapping | 7.3.1.5 | Match drop simulations showing the potential wildfire consequence of ignitions that occur along the electric lines and equipment | Vegetation Management & Inspections | 7.3.5 | LU
Situational Awareness and Forecasting | 7.3.2.1 | Advanced weather monitoring and weather stations: | Grid Operations & Operating Protocols | 7.3.6 | PC
Situational Awareness and Forecasting | 7.3.2.2 | Continuous monitoring sensors | Data Governance | 7.3.7 | TBC
Situational Awareness and Forecasting | 7.3.2.3 | Fault indicators for detecting faults on electric lines and equipment | Resource Allocation Methodology | 7.3.8 | HWT
Situational Awareness and Forecasting | 7.3.2.4 | Forecast of a fire risk index, fire potential index, or similar | Emergency Planning & Preparedness | 7.3.9
Situational Awareness and Forecasting | 7.3.2.5 | Personnel monitoring areas of electric lines and equipment in elevated fire risk conditions | Stakeholder Cooperation & Community Engagement | 7.3.10
Situational Awareness and Forecasting | 7.3.2.6 | Weather forecasting and estimating impacts on electric lines and equipment
Situational Awareness and Forecasting | 7.3.2.7 | Forecast of a fire risk index, fire potential index, or similar
Situational Awareness and Forecasting | 7.3.2.8 | Personnel monitoring areas of electric lines and equipment in elevated fire risk conditions
Situational Awareness and Forecasting | 7.3.2.9 | Weather forecasting and estimating impacts on electric lines and equipment:
Situational Awareness and Forecasting | 7.3.2.10 | Weather forecasting and estimating impacts on electric lines and equipment:
Grid Design and System Hardening | 7.3.3.1 | Capacitor maintenance and replacement program
Grid Design and System Hardening | 7.3.3.2 | Circuit breaker maintenance and installation to de-energize lines upon detecting a fault
Grid Design and System Hardening | 7.3.3.3 | Covered conductor installation
Grid Design and System Hardening | 7.3.3.4 | Covered conductor maintenance
Grid Design and System Hardening | 7.3.3.5 | Crossarm maintenance, repair, and replacement
Grid Design and System Hardening | 7.3.3.6 | Distribution pole replacement and reinforcement, including with composite poles
Grid Design and System Hardening | 7.3.3.7 | Expulsion fuse replacement
Grid Design and System Hardening | 7.3.3.8 | Grid topology improvements to mitigate or reduce PSPS events
Grid Design and System Hardening | 7.3.3.9 | Installation of system automation equipment
Grid Design and System Hardening | 7.3.3.10 | Maintenance, repair, and replacement of connectors, including hotline clamps
Grid Design and System Hardening | 7.3.3.11 | Mitigation of impact on customers and other residents affected during PSPS event
Grid Design and System Hardening | 7.3.3.12 | Other corrective action
Grid Design and System Hardening | 7.3.3.13 | Pole loading infrastructure hardening and replacement program based on pole loading assessment program
Grid Design and System Hardening | 7.3.3.14 | Transformers maintenance and replacement
Grid Design and System Hardening | 7.3.3.15 | Transmission tower maintenance and replacement
Grid Design and System Hardening | 7.3.3.16 | Undergrounding of electric lines and/or equipment
Grid Design and System Hardening | 7.3.3.17 | Updates to grid topology to minimize risk of ignition in HFTDs
Asset Management and Inspections | 7.3.4.1 | Detailed inspections of distribution electric lines and equipment
Asset Management and Inspections | 7.3.4.2 | Detailed inspections of Transmission electric lines and equipment
Asset Management and Inspections | 7.3.4.3 | Improvement of Inspections
Asset Management and Inspections | 7.3.4.4 | Infrared inspections of distribution electric lines and equipment:
Asset Management and Inspections | 7.3.4.5 | Infrared inspections of transmission electric lines and equipment:
Asset Management and Inspections | 7.3.4.6 | Intrusive pole inspections (IPI)
Asset Management and Inspections | 7.3.4.7 | LiDAR inspections of distribution electric lines and equipment
Asset Management and Inspections | 7.3.4.8 | LiDAR inspections of transmission electric lines and equipment
Asset Management and Inspections | 7.3.4.9 | Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations
Asset Management and Inspections | 7.3.4.10 | Generation High Fire Risk-Informed inspections and remediations in HFRA
Asset Management and Inspections | 7.3.4.11 | Other discretionary inspection of transmission electric lines and equipment, beyond inspections mandated by rules and regulations
Asset Management and Inspections | 7.3.4.12 | Patrol inspections of distribution electric lines and equipment
Asset Management and Inspections | 7.3.4.13 | Patrol inspections of transmission electric lines and equipment
Asset Management and Inspections | 7.3.4.14 | Pole loading assessment program to determine safety factor
Asset Management and Inspections | 7.3.4.15 | Quality assurance / quality control of inspections
Asset Management and Inspections | 7.3.4.16 | Substation inspections
Veg Management & Inspections | 7.3.5.1 | Additional efforts to manage community and environmental impacts
Veg Management & Inspections | 7.3.5.2 | Detailed inspections and management practices for vegetation clearances around distribution electrical lines and equipment
Veg Management & Inspections | 7.3.5.3 | Detailed inspections and management practices for vegetation clearances around transmission electrical lines and equipment
Veg Management & Inspections | 7.3.5.4 | Emergency response vegetation management due to red flag warning or other urgent climate conditions
Veg Management & Inspections | 7.3.5.5 | Fuel management (including all wood management) and reduction of “slash” from vegetation management activities
Veg Management & Inspections | 7.3.5.6 | Improvement of Inspections
Veg Management & Inspections | 7.3.5.7 | Remote sensing inspections of vegetation around distribution electrical lines and equipment
Veg Management & Inspections | 7.3.5.8 | Remote sensing inspections of vegetation around transmission electrical lines and equipment
Veg Management & Inspections | 7.3.5.9 | Other discretionary inspection of vegetation around distribution electric lines and equipment, beyond inspections mandated by rules and regulations
Veg Management & Inspections | 7.3.5.10 | Other discretionary inspection of vegetation around transmission electric lines and equipment, beyond inspections mandated by rules and regulations
Veg Management & Inspections | 7.3.5.11 | Patrol inspections of vegetation around distribution electric lines and equipment
Veg Management & Inspections | 7.3.5.12 | Patrol inspections of vegetation around transmission electric lines and equipment
Veg Management & Inspections | 7.3.5.13 | Quality assurance / quality control of vegetation management
Veg Management & Inspections | 7.3.5.14 | Recruiting and training of vegetation management personnel
Veg Management & Inspections | 7.3.5.15 | Identification and remediation of "at-risk species"
Veg Management & Inspections | 7.3.5.16 | Removal and remediation of trees with strike potential to electric lines and equipment
Veg Management & Inspections | 7.3.5.17 | Substation inspections
Veg Management & Inspections | 7.3.5.18 | Substation vegetation management
Veg Management & Inspections | 7.3.5.19 | Vegetation inventory system
Veg Management & Inspections | 7.3.5.20 | Vegetation management to achieve clearances around electric lines and equipment
Veg Management & Inspections | 7.3.5.21 | Vegetation management activities post-fire
Grid Operations & Protocols | 7.3.6.1 | Automatic recloser operations
Grid Operations & Protocols | 7.3.6.2 | Protective equipment and device settings
Grid Operations & Protocols | 7.3.6.3 | Crew-accompanying ignition prevention and suppression resources and services
Grid Operations & Protocols | 7.3.6.4 | Personnel work procedures and training in conditions of elevated fire risk
Grid Operations & Protocols | 7.3.6.5 | Protocols for PSPS re-energization
Grid Operations & Protocols | 7.3.6.6 | PSPS events and mitigation of PSPS impacts
Grid Operations & Protocols | 7.3.6.7 | Stationed and on-call ignition prevention and suppression resources and services
Data Governance | 7.3.7.1 | Centralized repository for data
Data Governance | 7.3.7.2 | Collaborative research on utility ignition and/or wildfire
Data Governance | 7.3.7.3 | Documentation and disclosure of wildfire-related data and algorithms
Data Governance | 7.3.7.4 | Tracking and analysis of risk event & near miss data
Resource Allocation Methodology | 7.3.8.1 | Allocation methodology development and application
Resource Allocation Methodology | 7.3.8.2 | Risk reduction scenario development and analysis
Resource Allocation Methodology | 7.3.8.3 | Risk spend efficiency analysis - not to include PSPS
Emergency Planning & Preparedness | 7.3.9.1 | Adequate and trained workforce for service restoration: SCE Emergency Response Training
Emergency Planning & Preparedness | 7.3.9.2 | Community outreach, public awareness, and communications efforts
Emergency Planning & Preparedness | 7.3.9.3 | Customer support in emergencies
Emergency Planning & Preparedness | 7.3.9.4 | Disaster and emergency preparedness plan
Emergency Planning & Preparedness | 7.3.9.5 | Preparedness and planning for service restoration
Emergency Planning & Preparedness | 7.3.9.6 | Protocols in place to learn from wildfire events
Stakeholder Cooperation & Community Engagement | 7.3.10.1 | Community engagement
Stakeholder Cooperation & Community Engagement | 7.3.10.2 | Cooperation and best practice sharing with agencies outside CA
Stakeholder Cooperation & Community Engagement | 7.3.10.3 | Cooperation with suppression agencies
Stakeholder Cooperation & Community Engagement | 7.3.10.4 | Forest service and fuel reduction cooperation and joint roadmap