## Discovery Log
**This Discovery Log reflects Data Requests completed as of 12:00PM each Thursday
Count | Party Name | DR Set # | Data Request | Question No. | Question ID | Question | Responses | Requestor | Date Rec'd | Final Due Date | Date Sent | Links | Number of Atchs | NDA required | WMP Section | Category | Subcategory | Confidential (Yes)
1 | CalAdvocates | CalAdvocates-SCE-2022WMP-15 | CalAdvocates-SCE-2022WMP-15 | 1 | CalAdvocates-SCE-2022WMP-15-01 | Fast Curve Settings for 2022 Please provide the protective device settings that SCE plans on using during high fire-risk weather in 2022, including the following parameters: a) The minimum to trip current; b) Definite time delay; c) Time curve; and d) Coordination parameters. | a. SCE currently has both Fast Curve settings that are set according to a prior practice, created in 2018, and set according to a newer Fast Curve practice. SCE’s prior phase Fast Curve pickup is equal to or greater than 4x the phase minimum trip at the circuit breaker and 5x the phase minimum trip at the recloser. SCE’s prior ground Fast Curve pickup is equal to or greater than 4x the ground minimum trip at the circuit breaker, with no ground Fast Curve added to the recloser. If a circuit has Fast Curve enabled reclosers or branch line fuses (BLFs) installed, the substation Fast Curve phase and ground pickup may be set higher than the typical 4x in order to reach past the furthest downstream recloser or BLF with some margin (called overreach), as long as it also provides the standard fault current/minimum trip multiple on all other unprotected branches. Increasing the pickup will prevent excessive overreach of downstream fast tripping devices. SCE’s new phase Fast Curve pickup is equal to or greater than 2.3x the protective device minimum trip. SCE’s ground Fast Curve pickup is equal to or greater than 5x the protective device minimum trip. If a circuit has Fast Curve enabled reclosers or branch line fuses (BLFs) installed, the substation or recloser Fast Curve phase and ground pickup may be set higher than the typical 2.3x or 5x in order to overreach the furthest downstream recloser or BLF with some margin, as long as it also provides the standard fault current/minimum trip multiple on all other unprotected branches. b. SCE’s old phase and ground Fast Curve definite time delays are set to either 0 cycles or 2 cycles (0.033 seconds) at the circuit breaker and 0 cycles at the recloser. SCE’s new phase and ground Fast Curve definite time delays are set at 4 cycles (0.066 seconds) at the circuit breaker and recloser. c. SCE uses a definite time delay for both phase and ground Fast Curves. SCE’s old definite time delay will operate in 0 or 2 cycles, and the new definite time delay will operate in 4 cycles. Both the old and new definite times operate at the set 0, 2 or 4 cycle time for any current exceeding the Fast Curve pickup value and do not vary as fault currents increase. d. SCE’s Fast Curve parameters are set to selectively coordinate with downstream (i.e., further from the substation) protective device pickup magnitudes to avoid excessive overreach of downstream reclosers or BLFs. The Fast Curve time delay will be set at 0, 2 or 4 cycles to provide selective coordination time interval with downstream main line or branch line fuses. | CalAdvocates | 2022-06-29 | 2022-07-14 | 2022-07-14 | CalAdvocates-SCE-2022WMP-15 |  |  | Section 7.3.3.2 | Grid Design & System Hardening | Fast Curve
2 | CalAdvocates | CalAdvocates-SCE-2022WMP-15 | CalAdvocates-SCE-2022WMP-15 | 2 | CalAdvocates-SCE-2022WMP-15-02 | If any of the parameters identified in question 1 depend on the normal operating parameters for its protective devices (i.e., device settings such as the minimum to trip during ordinary weather), please describe how SCE determines those normal operating parameters | SCE’s phase and ground Fast Curve pickup values are set to a multiple greater than the normal operating minimum trip setpoints. The normal distribution circuit operating minimum trip values are described below. Phase minimum trip: The minimum trip will typically be set to 150% of maximum projected downstream load of the protective device. 1. For 12kV and 16kV distribution circuits, the typical pickup setting for the substation protection device is 720 amps, or 130% of maximum load. Ground minimum trip: The minimum trip will typically be set to about 20-30% of the phase minimum trip. 1. Typical pickup setting is 180 amps for 12kV and 16kV distribution circuits, which allows the ground function to coordinate, in 4-wire systems, with the largest standard fuse used on branch line fusing and underground fuse dips. 2. SCE validates at the issuance of the setting that the unbalance current does not exceed the ground minimum trip setting. | CalAdvocates | 2022-06-29 | 2022-07-14 | 2022-07-14 | CalAdvocates-SCE-2022WMP-15 |  |  | Section 7.3.3.2 | Grid Design & System Hardening | Fast Curve
3 | CalAdvocates | CalAdvocates-SCE-2022WMP-15 | CalAdvocates-SCE-2022WMP-15 | 3 | CalAdvocates-SCE-2022WMP-15-03 | a) Please state whether (in 2022) SCE plans to coordinate protective devices with fuses’ time overcurrent curves, or plans on operating protective devices in a fuse-saving mode (i.e. the recloser/circuit breaker trips before the fuse operates) while fast curve settings are in effect. b) Please explain the reasoning for SCE’s choice(s) in part (a) of this question | a. SCE’s phase and ground Fast Curves are set to provide selective coordination time interval with downstream main line or branch line fuses. b. The reason SCE has elected to coordinate with downstream fuses is to provide better circuit reliability. By allowing the fuse to operate first before the next upstream protective device, fewer customers will be deenergized. The use of Current Limiting Fuses also reduce the fault energy for short circuits downstream of the fuse. When the fault current is greater than the current limiting rating, the fuse design will actively limit the current and the fuse can clear the fault quickly. This limits the overall energy of a fault, which causes less damage to the conductors and line equipment and provides for a fast clearing of the fault. Current Limiting Fuses are also designed to prevent the release of hot or burning material when clearing a fault. The fast clearing times and current limiting capabilities can provide coordination with upstream Fast Curve settings to provide customer electric service reliability. | CalAdvocates | 2022-06-29 | 2022-07-14 | 2022-07-14 | CalAdvocates-SCE-2022WMP-15 |  |  | Section 7.3.3.2 | Grid Design & System Hardening | Fast Curve
4 | CalAdvocates | CalAdvocates-SCE-2022WMP-15 | CalAdvocates-SCE-2022WMP-15 | 4 | CalAdvocates-SCE-2022WMP-15-04 | Please provide: a) Any studies that show how SCE determined that the protective device settings identified in question 1 are the best settings to use during high fire-risk weather; and b) Any studies of the impact to reliability due to the settings identified in question 1 | CONFIDENTIAL The Attachment(s) Are Marked Confidential In Accordance With D. 16-08-024 and D.17-09-023. Basis for Confidentiality In Accompanying Confidentiality Declaration. Public Disclosure Restricted. a. SCE completed a study in 2021 that analyzed a total of 15 HFRA circuits using both the existing Fast Curve practice (“philosophy”) first applied in 2018 and the revised philosophy. The goal of the study was to evaluate the revised philosophy’s ability to operate correctly for fault induced low voltage events that impact AC motor stalling when compared to the 2018 philosophy. The 15 circuits were first modeled in MATLAB/Simulink to study the effects of AC motor stalling caused by low voltage events due to faults on adjacent circuits or the subtransmission system. Using relay event records from an AC motor stalling event, the study verified that the revised Fast Curve philosophy would have operated correctly (meaning that it would not have tripped) for this event. In addition, SCE benchmarked its Fast Curve philosophy with several other electric utilities’ fast trip philosophies. The results of these studies are included in the attached “Fast Curve Protection Philosophy Review, Revision 0_CONFIDENTIAL”, dated August 9, 2021. SCE also compared the fire ignition rates for electric faults which occurred with Fast Curves enabled and without Fast Curves enabled. By calculating the fault to ignition ratio on circuits in HFRA when fast curve settings were activated in 2020 and 2021 versus circuits in HFRA over the same period where fast curve was not enabled, SCE found that an estimated 40% relative reduction in the fault to ignition ratio was achieved when Fast Curve was enabled. b. SCE minimizes the impact to reliability by studying the appropriate settings applied to each protective device installed on every circuit. The setting philosophy is to help ensure, to the extent possible, that each protective device coordinates so that the nearest device upstream of a fault operates before other upstream devices in order to minimize the number of customers impacted. For example, if a fault occurs downstream of a branch line fuse at the end of a circuit, the fuse should operate before the upstream recloser or circuit breaker so only that section of the circuit is interrupted from service. SCE reviews this type of coordination and deploys its settings accordingly based on the configuration of each circuit. | CalAdvocates | 2022-06-29 | 2022-07-14 | 2022-07-14 | CalAdvocates-SCE-2022WMP-15 | 2 |  | Section 7.3.3.2 | Grid Design & System Hardening | Fast Curve | yes
5 | CalAdvocates | CalAdvocates-SCE-2022WMP-15 | CalAdvocates-SCE-2022WMP-15 | 5 | CalAdvocates-SCE-2022WMP-15-05 | Please provide the protective device settings that SCE normally uses (i.e., outside of HFTD areas or outside of high fire-risk weather) in 2022, including the following parameters: a) The minimum to trip current; b) Definite time delay; c) Time curve; and d) Coordination parameters. | a. During normal operating conditions SCE’s distribution circuit phase and ground minimum trip values are described below. Phase minimum trip: The minimum trip will typically be set to 150% of maximum projected downstream load of the protective device. For 12kV and 16kV distribution circuits, the typical pickup setting for the substation protection device is 720 amps, or 130% of maximum load. Ground minimum trip: The minimum trip will typically be set to about 20-30% of the phase minimum trip. 1. Typical pickup setting is 180 amps for 12kV and 16kV distribution circuits, which allows the ground function to coordinate, in 4-wire systems, with the largest standard fuse used on branch line fusing and underground fuse dips. 2. SCE validates at the issuance of the setting that the unbalance current does not exceed the ground minimum trip setting. b. SCE doesn’t typically use a definite time delay during normal operating conditions. c. SCE typically uses Inverse or Very Inverse time current curves during normal operating conditions. d. SCE performs coordination studies on distribution circuits to provide circuit-optimized settings to the protective devices on that circuit. The maximum available fault current at the substation with any allowed switching configuration should be used for coordination. Coordination parameters between CBs and RARs follow a timing interval generally known at the Coordinating Time Interval (CTI). The minimum CTI is 0.3 seconds with the ideal CTI being 0.5 seconds. A 0.3 second CTI is usually required when there are three or more devices to coordinate, to avoid clearing timing from becoming excessive. If more than three devices in a series need to be coordinated, other options may be considered | CalAdvocates | 2022-06-29 | 2022-07-14 | 2022-07-14 | CalAdvocates-SCE-2022WMP-15 |  |  | Section 7.3.3.2 | Grid Design & System Hardening | Fast Curve
6 | CalAdvocates | CalAdvocates-SCE-2022WMP-15 | CalAdvocates-SCE-2022WMP-15 | 6 | CalAdvocates-SCE-2022WMP-15-06 | Fast Curve Settings in 2021 Please provide the remaining data (i.e. after 9/23/2021) from “04_CalAdvocates-SCE-NonCaseTYH-10122021_Response_Q4” for 2021, including whether the furthest upstream protective device operating was a fuse | Please see the attached spreadsheet entitled “04_CalAdvocates-SCE-NonCase-TYH10122021_Response_Q4_UPDATED_FUSE.xlsx” that contains the requested information. Please note that SCE utilized outage information to provide the answer. Column L indicates if the first restoration step indicated a fuse, it is assumed that the furthest upstream protective device that operated was a fuse. Column M indicates that the outage was an “area out” and possibly could have been a fuse that operated. Column N is the same as column M, but removes only transformer outages. | CalAdvocates | 2022-06-29 | 2022-07-14 | 2022-07-14 | CalAdvocates-SCE-2022WMP-15 | 1 |  | Section 7.3.3.2 | Grid Design & System Hardening | Fast Curve