## Instructions
Version | 2.2 | Format Guide
Published On | 4453600% | Description |  | Format
Tabs contained within this workbook |  | Input cell (Manual) - user input required (Data used by Model or Description mandated to have) |  | Font
This workbook is a companion input to the Risk Model Input file. For more information on that file, see the Risk Model User Guide. |  | Input cell (Manual) - user input required (Not used by Model / For information only - Optional) |  | Font
Below are the workbook tab names along with a description and instructions. |  | Input cell - Not applicable / Not be used by the model for specific scenarios
|  | Calculated cell - formula that should not be touched |  | Font
Tab | Description + Instructions | Error checking cell - formula that should not be touched / Not be used by the model |  | OK/True | Error/False
Summary of Programs | Using one row per program, include a program description, Mitigation or Control specification, high-level justification/explanation for program characterization.
1-Program Exposure | This includes the scope of each program - how much of the risk exposure (in term of exposure unit or % of tranche exposure) or work units are covered.
2-Program Cost | This includes 2 tables. 1) TableProgSpend - The total costs (CapEX and OoEx) oer each program distributing across time. PPVR multipliers are applicable when CapEX exists. 2) TableTrancheSpend - The total cost allocation across tranches accross time. Need to specify the allocation method (i.e., prorate by Program Exposure or % of Total Cost)
3-Eff - Freq Programs | Combined with the tranche exposure and spend specified in tabs 1 and 2, this constitutes all information needed to compute an RSE for a Program affecting event Frequency. Detailed instructions are in the section below. This table can accommodate quantitative effectiveness, or, facilitates use of the qualitative effectiveness methodology. For each program based on quantitative information, add the supporting worksheet. For each control program using the qualitative methodology, add a Maturity Factor - XX worksheet.
4-Eff - Conseq Programs | Combined with the tranche exposure and spend specified in tabs 1 and 2, this constitutes all information needed to compute an RSE for a Program affecting Consequence. Detailed instructions are in the section below. This table can accommodate quantitative effectiveness, or, facilitates use of the qualitative effectiveness methodology. For each program based on quantitative information, add the supporting worksheet. For each control program using the qualitative methodology, add a Maturity Factor - XX worksheet.
RSE Lite | Tool to compute the RSE for a single program specified within this workbook. 1. Within the worksheet, specify the location and filename for the RSE Lite datafile (a workbook output from the Enterprise Risk Model using a Risk Model Input File with RSE Lite Run = TRUE in the 0-Global Parameters tab). 2. Select the Program. 3. Press Run to call an executable file which will return Risk Reduction and RSE information over time.
RSE Results | Tool to compute the batch RSE run for all listed programs specified within this workbook.
Maturity Factor - XX | Maturity factor calculation for <Control XX>, which is qualitatively evaluated
Match esc definition | For advanced users: Specify custom effectiveness escalation ('match'-type escalation). See the User Guide for additional information about parameter escalation, including the 'match' method.
Data Dictionary | Do not edit. Input Table column information (Input Cell Type, Formula, Validation Formula, Conditional Formatting)
Data & Validation | Do not edit. Data supporting the Control Maturity Factor calculations and Lists for drop down menus
TablePVRR | Do not edit. Reference lookup table for generic PVRR multipliers
BowTie | Do not edit. Reference lookup tables for tranches, drivers, subdrivers, outcomes
Instructions on how to complete the Effectiveness by Model Element tables on tabs 3 and 4:
Column | Instructions
ID | Do not modify. This looks up the Program ID from the Summary of Programs tab. Future enhancement will link this to the Master Control and Mitigation Cost File.
Type | Do not modify. This looks up the Program Type from the Summary of Programs tab, and determines whether a Maturity Factor is necessary (if Control and Qualitative). Future enhancement will link this to the Master Control and Mitigation Cost File.
Program | Each program should be listed at least once in this table. Repeat the program name as many times as is necessary. | Quantitative Measure
Tranche | Include the names of the tranches over which the effectiveness and/or benefit length will differ. | Effectiveness - Quantitative | Either link via cell reference to the quantitatively-derived effectiveness value or copy+paste from an external effectiveness workpaper. List the reference to the external workpaper in the row.
Outcome | Include the names of the outcomes over which the effectiveness and/or benefit length will differ. | Effectiveness | The effectiveness of the program per unit of program exposure in the first year of deployment. The existing formula will compute the effectiveness so do not overwrite this column.
Driver / Subdriver / Attribute | Include the names of the driver/subdriver/attribute over which the effectiveness and/or benefit length will differ.
Does this use qualitative measure? | Specify TRUE or FALSE. If TRUE, fill out columns 'Category?' and 'Risk driver primarily due to…' | Qualitative Measure
… | … | Category? | Select the appropriate category for the program.
Benefit Length (yrs) | List the number of years the program provides benefit for. This may or may not be the same over all Program rows in this table. | Risk driver primarily due to… / Consequence develops… | Select the appropriate driver type for frequency mitigation OR select the appropriate consequence type for consequence mitigation. If previously specified that the effectiveness does not vary by Driver/Subdriver, consider revisiting that specification.
Effectiveness Degradation Rate | If the benefits provided by the program degrade with time, specify the rate (%) at which the effectiveness of the program degrades. A blank value is treats as 0% reduction over time. | Explanation of Categorization | Include the rationale behind the selection of program category as well as driver or consequence type.
Effectiveness Degradation Method | Specify the method by which the degradation rate should be applied. The default is 'esc'; see the User Guide for additional information about parameter escalation, including the 'match' method. | Effectiveness Cap | The value which matches the category and driver/outcome type selected.
Explanation of Benefit Length | If the benefit length, effectiveness degradation rate, and/or degradation method vary within the program, include the rationale behind the specified information. Otherwise, include the program-level explanation only in the Summary of Programs tab. | Maturity Factor | This is necessary for control programs using the qualitative methodology. Duplicate the 'Maturity Factor - XX' worksheet as many times as is necessary, updating responses after duplication. Update 'XX' in the tab name with the Program ID. Each control should have one corresponding worksheet. The existing formula will look up the discount factor so do not overwrite this column.
|  | Effectiveness | The effectiveness of the program per unit of program exposure in the first year of deployment. The existing formula will compute the effectiveness so do not overwrite this column.
See 'Qualitative Program Effectiveness Guidance' documentation for more details on qualitative methodology.
TRUE
FALSE
Necessary cells are highlighted in green

## Data Dictionary
RSE Lite Template Data Dictionary
formula | formula |  | formula | input | formula | formula | formula | input | input | input | input | input | formula
# | Col# | Sheet Name | Table Name | Type | Column Name | Col | Formula | Data Validation | Conditional Formatting Criteria | Conditional Formatting Application | Sheet Name | Table Name | Columns
1 | 1 | Summary of Programs | TableSummary | Input | Program ID | A |  |  |  |  | Summary of Programs | TableSummary | 14
1 | 2 | Summary of Programs | TableSummary | Input | Program | B |  |  |  |  | 1-Program Exposure | TableExposure | 27
1 | 3 | Summary of Programs | TableSummary | Input | Mitigation or Control? | C |  | =INDIRECT("TableProgTypeDropdown[Program Type Options]") |  |  | 2-Program Cost | TableProgSpend | 28
1 | 4 | Summary of Programs | TableSummary | Input | MAT or MWC | D |  |  |  |  | 2-Program Cost | TableTranchSpend | 13
1 | 5 | Summary of Programs | TableSummary | Input | Program Description | E |  |  |  |  | 3-Eff - Freq Programs | TableFreqPrograms | 22
1 | 6 | Summary of Programs | TableSummary | Input | Modifying Likelihood of Failure (LOF) or Consequence of Failure (COF) | F |  | =INDIRECT("TableBowtieDropdown[Bow Tie Element]") |  |  | 4-Eff - Conseq Programs | TableConseqPrograms | 21
1 | 7 | Summary of Programs | TableSummary | Input | Risk Drivers and/or Consequences being addressed by Program | G |  |  |  |  | Total Input Table Columns |  | 125
1 | 8 | Summary of Programs | TableSummary | Input | Year(s) of Implementation | H |  |  |  |  | RSE Lite | TableRSESummary | 18
1 | 9 | Summary of Programs | TableSummary | Input | Justification for Effectiveness % | I |  |  |  |  | RSE Lite | TableRSE | 35
1 | 10 | Summary of Programs | TableSummary | Input | Benefit Length | J |  |  |  |  | RSE Lite | TableProgramRR | 44
1 | 11 | Summary of Programs | TableSummary | Input | Justification for Benefit Length | K |  |  |  |  | RSE Lite | Table_LoRECalc | 29
1 | 12 | Summary of Programs | TableSummary | Optional Input | Assumptions / Comments | L |  |  |  |  | RSE Lite | Table_CoRECalc | 28
1 | 13 | Summary of Programs | TableSummary | Formula | Mitigation Program Count | M | =IF(ISNUMBER(#REF!),IF(AND(LEFT(C10,1)="M",B10<>#REF!),#REF!+1,#REF!),IF(LEFT(C10,1)="M",1,0)) |  |  |  | RSE Result | TableAllRSEs | 21
1 | 14 | Summary of Programs | TableSummary | Formula | Control Program Count | N | =IF(ISNUMBER(#REF!),IF(AND(LEFT(C10,1)="C",B10<>#REF!),#REF!+1,#REF!),IF(LEFT(C10,1)="C",1,0)) |  |  |  | RSE Result | TableRSEbatch | #REF!
2 | 1 | 1-Program Exposure | TableExposure | Formula | Program ID | B | =IFERROR(INDEX('Summary of Programs'!A:A,MATCH([@Program],'Summary of Programs'!B:B,0)),"No match in Summary of Programs tab") |  |  |  | RSE Result | TableProgramRRbatch | #REF!
2 | 2 | 1-Program Exposure | TableExposure | Formula | Type | C | =IFERROR(INDEX('Summary of Programs'!C:C,MATCH([@Program],'Summary of Programs'!B:B,0)),"No match in Summary of Programs tab")
2 | 3 | 1-Program Exposure | TableExposure | Input | Program | D |  | =INDIRECT("TableSummary[Program]")
2 | 4 | 1-Program Exposure | TableExposure | Input | Risk (for Cross Cutter only) | E |  | =INDIRECT("Table_RiskNameLookup[Risk/Cross Cutting Factor Name]")
2 | 5 | 1-Program Exposure | TableExposure | Input | Tranche | F |  | =INDIRECT("TableTranche[Tranche]")
2 | 6 | 1-Program Exposure | TableExposure | Formula | Tranche Exposure | G | =INDEX(TableTranche[[#All],[Exposure]], MATCH([@Tranche], TableTranche[[#All],[Tranche]], 0))
2 | 7 | 1-Program Exposure | TableExposure | Formula | Tranche Exposure Unit | H | =INDEX(TableTranche[[#All],[Unit]], MATCH([@Tranche], TableTranche[[#All],[Tranche]], 0))
2 | 8 | 1-Program Exposure | TableExposure | Input | Program Exposure 2020 | I
2 | 9 | 1-Program Exposure | TableExposure | Input | Program Exposure 2021 | J
2 | 10 | 1-Program Exposure | TableExposure | Input | Program Exposure 2022 | K
2 | 11 | 1-Program Exposure | TableExposure | Input | Program Exposure 2023 | L
2 | 12 | 1-Program Exposure | TableExposure | Input | Program Exposure 2024 | M
2 | 13 | 1-Program Exposure | TableExposure | Input | Program Exposure 2025 | N
2 | 14 | 1-Program Exposure | TableExposure | Input | Program Exposure 2026 | O
2 | 15 | 1-Program Exposure | TableExposure | Input | Unit for Program Exposure | P |  | =INDIRECT("TableProgExpDropdown[Program Exposure Options]")
2 | 16 | 1-Program Exposure | TableExposure | Optional Input | Work Units 2020 | Q
2 | 17 | 1-Program Exposure | TableExposure | Optional Input | Work Units 2021 | R
2 | 18 | 1-Program Exposure | TableExposure | Optional Input | Work Units 2022 | S
2 | 19 | 1-Program Exposure | TableExposure | Optional Input | Work Units 2023 | T
2 | 20 | 1-Program Exposure | TableExposure | Optional Input | Work Units 2024 | U
2 | 21 | 1-Program Exposure | TableExposure | Optional Input | Work Units 2025 | V
2 | 22 | 1-Program Exposure | TableExposure | Optional Input | Work Units 2026 | W
2 | 23 | 1-Program Exposure | TableExposure | Optional Input | Unit for work units | X
2 | 24 | 1-Program Exposure | TableExposure | Optional Input | Explanation of relationship between different units | Y
2 | 25 | 1-Program Exposure | TableExposure | Optional Input | Other Note | Z
2 | 26 | 1-Program Exposure | TableExposure | Error Check | Flag for modeler | AA | =IF(AND(MAX(TableExposure[@[Program Exposure 2020]:[Program Exposure 2026]])>1,[@[Unit for Program Exposure]]="% of tranche exposure"),"Format not percent","") |  | No Blank | Red font if there is Error
2 | 27 | 1-Program Exposure | TableExposure | Formula | Risk ID | AB | =IFERROR(INDEX(Table_RiskNameLookup[RISK ID],MATCH([@[Risk (for Cross Cutter only)]],Table_RiskNameLookup[Risk/Cross Cutting Factor Name],0)),RiskID)
3 | 1 | 2-Program Cost | TableProgSpend | Formula | Program ID | B | =IFERROR(INDEX('Summary of Programs'!A:A,MATCH([@Program],'Summary of Programs'!B:B,0)),"No match in Summary of Programs")
3 | 2 | 2-Program Cost | TableProgSpend | Formula | Type | C | =IFERROR(INDEX('Summary of Programs'!C:C,MATCH([@Program],'Summary of Programs'!B:B,0)),"No match in Summary of Programs tab")
3 | 3 | 2-Program Cost | TableProgSpend | Input | Program | D |  | =INDIRECT("TableSummary[Program]")
3 | 4 | 2-Program Cost | TableProgSpend | Input | MAT (optional) | E
3 | 5 | 2-Program Cost | TableProgSpend | Input | CapEx USD 2020 | F
3 | 6 | 2-Program Cost | TableProgSpend | Input | CapEx USD 2021 | G
3 | 7 | 2-Program Cost | TableProgSpend | Input | CapEx USD 2022 | H
3 | 8 | 2-Program Cost | TableProgSpend | Input | CapEx USD 2023 | I
3 | 9 | 2-Program Cost | TableProgSpend | Input | CapEx USD 2024 | J
3 | 10 | 2-Program Cost | TableProgSpend | Input | CapEx USD 2025 | K
3 | 11 | 2-Program Cost | TableProgSpend | Input | CapEx USD 2026 | L
3 | 12 | 2-Program Cost | TableProgSpend | Input | OpEx USD 2020 | M
3 | 13 | 2-Program Cost | TableProgSpend | Input | OpEx USD 2021 | N
3 | 14 | 2-Program Cost | TableProgSpend | Input | OpEx USD 2022 | O
3 | 15 | 2-Program Cost | TableProgSpend | Input | OpEx USD 2023 | P
3 | 16 | 2-Program Cost | TableProgSpend | Input | OpEx USD 2024 | Q
3 | 17 | 2-Program Cost | TableProgSpend | Input | OpEx USD 2025 | R
3 | 18 | 2-Program Cost | TableProgSpend | Input | OpEx USD 2026 | S
3 | 19 | 2-Program Cost | TableProgSpend | Input | Asset Type | T
3 | 20 | 2-Program Cost | TableProgSpend | Formula | Generic Capital PVRR Multiplier | U | =IF(SUM(TableProgSpend[@[CapEx USD 2020]:[CapEx USD 2026]])>0,INDEX(TablePVRR[PVRR Multiplier (no O&M)],MATCH([@[Asset Type]],TablePVRR[Asset Group],0)),"") |  | =SUM($F9:$L9)=0 | Condition on if there is CapEX. If CapEX exists, then PVRR Multipliers are applicable. Otherwise, not applicable.
3 | 21 | 2-Program Cost | TableProgSpend | Input | Custom Capital PVRR Multiplier | V |  |  | =SUM($F9:$L9)=0 =$T9<>"Custom" | Condition on if there is CapEX and if the Asset Type is "Custom". If so, then PVRR Multipliers are applicable. Otherwise, not applicable.
3 | 22 | 2-Program Cost | TableProgSpend | Formula | Generic Lifetime Incremental O&M PVRR Multiplier | W | =IF(SUM(TableProgSpend[@[CapEx USD 2020]:[CapEx USD 2026]])>0,INDEX(TablePVRR[Lifetime O&M as % of PVRR],MATCH([@[Asset Type]],TablePVRR[Asset Group],0)),"") |  | =SUM($F9:$L9)=0 | Condition on if there is CapEX. If CapEX exists, then PVRR Multipliers are applicable. Otherwise, not applicable.
3 | 23 | 2-Program Cost | TableProgSpend | Input | Custom Lifetime Incremental O&M PVRR Multiplier (optional; specify if 0) | X |  |  | =SUM($F9:$L9)=0
3 | 24 | 2-Program Cost | TableProgSpend | Formula | Lifetime Incremental O&M PVRR Multiplier | Y | =IF([@[Custom Lifetime Incremental O&M PVRR Multiplier (optional; specify if 0)]]<>"",[@[Custom Lifetime Incremental O&M PVRR Multiplier (optional; specify if 0)]],[@[Generic Lifetime Incremental O&M PVRR Multiplier]]) |  | =SUM($F9:$L9)=0
3 | 25 | 2-Program Cost | TableProgSpend | Formula | PVRR Multiplier | Z | =IFERROR(IF([@[Asset Type]]="Custom",[@[Custom Capital PVRR Multiplier]],[@[Generic Capital PVRR Multiplier]])+[@[Lifetime Incremental O&M PVRR Multiplier]],0) |  | =SUM($F9:$L9)=0
3 | 26 | 2-Program Cost | TableProgSpend | Error Check | In Exposure tab? | AA | =ISNUMBER(MATCH([@Program],TableExposure[Program],0)) |  | FALSE | Red font if FALSE
3 | 27 | 2-Program Cost | TableProgSpend | Error Check | In Allocation table | AB | =ISNUMBER(MATCH([@Program],TableTranchSpend[Program],0)) |  | FALSE | Red font if FALSE
3 | 28 | 2-Program Cost | TableProgSpend | Error Check | In Eff Table | AC | =OR(ISNUMBER(MATCH([@Program],TableFreqPrograms[Program],0)),ISNUMBER(MATCH([@Program],TableConseqPrograms[Program],0))) |  | FALSE | Red font if FALSE
4 | 1 | 2-Program Cost | TableTranchSpend | Formula | Program ID | B | =IFERROR(INDEX('Summary of Programs'!A:A,MATCH([@Program],'Summary of Programs'!B:B,0)),"No match in Summary of Programs")
4 | 2 | 2-Program Cost | TableTranchSpend | Formula | Type | C | =IFERROR(INDEX('Summary of Programs'!C:C,MATCH([@Program],'Summary of Programs'!B:B,0)),"No match in Summary of Programs tab")
4 | 3 | 2-Program Cost | TableTranchSpend | Input | Program | D |  | =INDIRECT("TableSummary[Program]")
4 | 4 | 2-Program Cost | TableTranchSpend | Input | MAT (optional) | E
4 | 5 | 2-Program Cost | TableTranchSpend | Input | Allocation method | F |  | =INDIRECT("TableProgCostDropdown[Program Cost Options]")
4 | 6 | 2-Program Cost | TableTranchSpend | Input | Tranche | G |  | =INDIRECT("TableTranche[Tranche]") | =$F52="% of Total Cost (specify to the right)" | Condition on if Allocation method is set as "% of Total Cost". If it is, need to input the Tranche and allocation % across the years.
4 | 7 | 2-Program Cost | TableTranchSpend | Input | Spend USD 2020 | H |  |  | =$F52="% of Total Cost (specify to the right)"
4 | 8 | 2-Program Cost | TableTranchSpend | Input | Spend USD 2021 | I |  |  | =$F52="% of Total Cost (specify to the right)"
4 | 9 | 2-Program Cost | TableTranchSpend | Input | Spend USD 2022 | J |  |  | =$F52="% of Total Cost (specify to the right)"
4 | 10 | 2-Program Cost | TableTranchSpend | Input | Spend USD 2023 | K |  |  | =$F52="% of Total Cost (specify to the right)"
4 | 11 | 2-Program Cost | TableTranchSpend | Input | Spend USD 2024 | L |  |  | =$F52="% of Total Cost (specify to the right)"
4 | 12 | 2-Program Cost | TableTranchSpend | Input | Spend USD 2025 | M |  |  | =$F52="% of Total Cost (specify to the right)"
4 | 13 | 2-Program Cost | TableTranchSpend | Input | Spend USD 2026 | N |  |  | =$F52="% of Total Cost (specify to the right)"
5 | 1 | 3-Eff - Freq Programs | TableFreqPrograms | Formula | ID | B | =IFERROR(INDEX('Summary of Programs'!A:A,MATCH([@Program],'Summary of Programs'!B:B,0)),"No match in Program Cost tab")
5 | 2 | 3-Eff - Freq Programs | TableFreqPrograms | Formula | Type | C | =IFERROR(INDEX('Summary of Programs'!C:C,MATCH([@Program],'Summary of Programs'!B:B,0)),"No match in Summary of Programs tab")
5 | 3 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Program | D |  | =INDIRECT("TableSummary[Program]")
5 | 4 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Risk (for Cross Cutter only) | E |  | =INDIRECT("Table_RiskNameLookup[Risk/Cross Cutting Factor Name]")
5 | 5 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Tranche | F |  | =INDIRECT("TableTranche[Tranche]")
5 | 6 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Driver | G |  | =INDIRECT("TableDriverSubdriver[Driver]")
5 | 7 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Subdriver | H |  | =INDIRECT("TableDriverSubdriver[Subdriver]")
5 | 8 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Outcome | I |  | =INDIRECT("TableOutcome[Outcome]")
5 | 9 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Does this use qualitative measure? | J
5 | 10 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Effectiveness - Quantitative | K |  |  | =NOT($J8) | If not use qualitative measure, need to input effective rate.
5 | 11 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Category | L |  | =INDIRECT("TableQualFreqEff[Program Category]") | =$J8 | If use qualitative measure, need to input Category and Risk driver primarily due to …
5 | 12 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Risk driver primarily due to… | M |  | =$Z$7:$AC$7 | =$J8
5 | 13 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Explanation of Program Category and Risk Driver type | N |  |  | =$J8
5 | 14 | 3-Eff - Freq Programs | TableFreqPrograms | Formula | Effectiveness Cap (Ec) | O | =IF([@[Does this use qualitative measure?]],INDEX(TableQualFreqEff,MATCH([@Category],TableQualFreqEff[Program Category],0),MATCH([@[Risk driver primarily due to…]],TableQualFreqEff[#Headers],0)),"") |  | =$J8
5 | 15 | 3-Eff - Freq Programs | TableFreqPrograms | Formula | Maturity Factor (Mf) | P | =IFERROR(@IF(AND([@[Does this use qualitative measure?]],[@Type]="Control"),INDIRECT("'Maturity Factor - " & [@ID] & "'!EffFactor"),""),"Cannot find Maturity Factor - " & [@ID] & " tab.") |  | =$J8
5 | 16 | 3-Eff - Freq Programs | TableFreqPrograms | Formula | Effectiveness (Ec * Mf) | Q | =IFERROR(IF([@[Does this use qualitative measure?]],[@[Effectiveness Cap (Ec)]]*MIN([@[Maturity Factor (Mf)]],1),[@[Effectiveness - Quantitative]]),0)
5 | 17 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Benefit Length (yrs) | R
5 | 18 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Effectiveness Degradation Rate | S
5 | 19 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Effectiveness Degradation Method | T
5 | 20 | 3-Eff - Freq Programs | TableFreqPrograms | Input | Explanation of Benefit Length | U
5 | 21 | 3-Eff - Freq Programs | TableFreqPrograms | Formula | Same benefit set across program? | V | =SUMPRODUCT((([Program]=[@Program]))/COUNTIFS([Program],[Program]&"",[Benefit Length (yrs)],[Benefit Length (yrs)]&"",[Effectiveness Degradation Rate],[Effectiveness Degradation Rate]&"",[Effectiveness Degradation Method],[Effectiveness Degradation Method]&""))=1
5 | 22 | 3-Eff - Freq Programs | TableFreqPrograms | Formula | Risk ID | W | =IFERROR(INDEX(Table_RiskNameLookup[RISK ID],MATCH([@[Risk (for Cross Cutter only)]],Table_RiskNameLookup[Risk/Cross Cutting Factor Name],0)),RiskID)
6 | 1 | 4-Eff - Conseq Programs | TableConseqPrograms | Formula | ID | B | =IFERROR(INDEX('Summary of Programs'!A:A,MATCH([@Program],'Summary of Programs'!B:B,0)),"No match in Program Cost tab")
6 | 2 | 4-Eff - Conseq Programs | TableConseqPrograms | Formula | Type | C | =IFERROR(INDEX('Summary of Programs'!C:C,MATCH([@Program],'Summary of Programs'!B:B,0)),"No match in Summary of Programs tab")
6 | 3 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Program | D |  | =INDIRECT("TableSummary[Program]")
6 | 4 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Risk (for Cross Cutter only) | E |  | =INDIRECT("Table_RiskNameLookup[Risk/Cross Cutting Factor Name]")
6 | 5 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Tranche | F |  | =INDIRECT("TableTranche[Tranche]")
6 | 6 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Outcome | G |  | =INDIRECT("TableOutcome[Outcome]")
6 | 7 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Attribute | H
6 | 8 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Does this use qualitative measure? | I
6 | 9 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Effectiveness - Quantitative | J |  |  | =NOT($I8) | If not use qualitative measure, need to input effective rate.
6 | 10 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Category | K |  | =INDIRECT("TableQualConseqEff[Control Program Category]") | =$I8 | If use qualitative measure, need to input Category and Consequence develops …
6 | 11 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Consequence develops… | L |  | =$AA$7:$AB$7 | =$I8
6 | 12 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Explanation of Program Category and Consequence type | M |  |  | =$I8
6 | 13 | 4-Eff - Conseq Programs | TableConseqPrograms | Formula | Effectiveness Cap (Ec) | N | =IF([@[Does this use qualitative measure?]],INDEX(TableQualConseqEff,MATCH([@Category],TableQualConseqEff[Control Program Category],0),MATCH([@[Consequence develops…]],TableQualConseqEff[#Headers],0)),"") |  | =$I8
6 | 14 | 4-Eff - Conseq Programs | TableConseqPrograms | Formula | Maturity Factor (Mf) | O | =IFERROR(@IF(AND([@[Does this use qualitative measure?]],ISNUMBER(SEARCH("control",[@Type]))),INDIRECT("'Maturity Factor - " & RIGHT([@ID],4) & "'!EffFactor"),""),"Cannot fine Maturity Factor - " & [@ID]& " tab.") |  | =$I8
6 | 15 | 4-Eff - Conseq Programs | TableConseqPrograms | Formula | Effectiveness (Ec * Mf) | P | =IFERROR(IF([@[Does this use qualitative measure?]],[@[Effectiveness Cap (Ec)]]*MIN([@[Maturity Factor (Mf)]],1),[@[Effectiveness - Quantitative]]),0)
6 | 16 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Benefit Length (yrs) | Q
6 | 17 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Effectiveness Degradation Rate | R
6 | 18 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Effectiveness Degradation Method | S
6 | 19 | 4-Eff - Conseq Programs | TableConseqPrograms | Input | Explanation of Benefit Length, Degradation Rate | T
6 | 20 | 4-Eff - Conseq Programs | TableConseqPrograms | Formula | Same benefit set across program? | U | =SUMPRODUCT((([Program]=[@Program]))/COUNTIFS([Program],[Program]&"",[Benefit Length (yrs)],[Benefit Length (yrs)]&"",[Effectiveness Degradation Rate],[Effectiveness Degradation Rate]&"",[Effectiveness Degradation Method],[Effectiveness Degradation Method]&""))=1
6 | 21 | 4-Eff - Conseq Programs | TableConseqPrograms | Formula | Risk ID | V | =IFERROR(INDEX(Table_RiskNameLookup[RISK ID],MATCH(TableFreqPrograms[@[Risk (for Cross Cutter only)]],Table_RiskNameLookup[Risk/Cross Cutting Factor Name],0)),RiskID)

## Summary of Programs
Pacific Gas and Electric Company
2022 WMP
Control and Mitigation Program Workpaper
| RISK Name: | Wildfire
| RISK ID: | WLDFR
| Total mitigations: | 7
| Total controls: | 10
* When reference is made to "PSPS_RSE Input File_v2.2_EO_WLDFR_Template.xlsx", refer to attachment 2022-02-25_PGE_2022_WMP-Update_R0_Section 7.3.a_Atch09
Program ID | Program | Mitigation or Control? | MAT or MWC | Program Description | Modifying Likelihood of Failure (LOF) or Consequence of Failure (COF) | Risk Drivers and/or Consequences being addressed by Program | Year(s) of Implementation | Justification for Effectiveness % | Benefit Length | Justification for Benefit Length | Assumptions / Comments | Mitigation Program Count | Control Program Count
7.3.3.1 | 7.3.3.1 Capacitor maintenance and replacement program | Control | KAF, KBC, 2AE, 2BD, 17P, 06A, 06D, 06H, 06K | Remediation, adjustments, or installations of new equipment to improve or replace existing capacitor equipment. | LOF | Equipment / facility failure | Ongoing | 90% - Per SME judgement. Capacitors maintained are highly unlike to fail causing an ignition within a given year. Per the WMP 2022 narrative, "all distribution capacitor banks are inspected as governed by TD-2302B-006 and TD-2302P-05" each year. To be conservative PG&E assumes an effectiveness of 90%, leaving a 10% chance of risk due to unseen/unpredictable future events. | 1 | Per the WMP 2022 narrative, "all distribution capacitor banks are inspected as governed by TD-2302B-006 and TD-2302P-05" each year |  | 0 | 1
7.3.3.2-D | 7.3.3.2-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Distribution | Control | GCB, GCM, GCS, GCV | Remediation, adjustments, or installations of new equipment to improve or replace existing fast switching circuit breaker equipment to improve the ability to protect electrical circuits from damage caused by overload of electricity or short circuit. | LOF | Equipment / facility failure | Ongoing | 90% - Per SME judgement | 1 | Since the choice is work unit within Program Exposure tab, the units that are worked on will not cause an ignition within a year with an assumed 90% effectiveness rate per SME judgement. |  | 0 | 2
7.3.3.2-T | 7.3.3.2-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Transmission | Control | AMB, AMM, AMS, AMV | Remediation, adjustments, or installations of new equipment to improve or replace existing fast switching circuit breaker equipment to improve the ability to protect electrical circuits from damage caused by overload of electricity or short circuit. | LOF | Equipment / facility failure | Ongoing | 90% - Per SME judgement | 1 | Since the choice is work unit within Program Exposure tab, the units that are worked on will not cause an ignition within a year with an assumed 90% effectiveness rate per SME judgement. |  | 0 | 3
7.3.3.3 | 7.3.3.3 Covered conductor installation | Mitigation |  | Installation of covered or insulated conductors to replace standard bare or unprotected conductors (defined in accordance with GO 95 as supply conductors, including but not limited to lead wires, not enclosed in a grounded metal pole or not covered by: a “suitable protective covering” (in accordance with Rule 22.8 ), grounded metal conduit, or grounded metal sheath or shield). In accordance with GO 95, conductor is defined as a material suitable for: (1) carrying electric current, usually in the form of a wire, cable or bus bar, or (2) transmitting light in the case of fiber optics; insulated conductors as those which are surrounded by an insulating material (in accordance with Rule 21.6), the dielectric strength of which is sufficient to withstand the maximum difference of potential at normal operating voltages of the circuit without breakdown or puncture; and suitable protective covering as a covering of wood or other non-conductive material having the electrical insulating efficiency (12kV/in. dry) and impact strength (20ft.-lbs) of 1.5 inches of redwood or other material meeting the requirements of Rule 22.8-A, 22.8-B, 22.8-C or 22.8-D. | LOF | Covered conductor installation work is part of System Hardening program under 7.3.3.17.1. No RSE will be calculated separately for this program. RSE of 7.3.3.3 can be considered embedded within 7.3.3.17.1 | [5 empty] | 1 | 2
7.3.3.4 | 7.3.3.4 Covered conductor maintenance | Control |  | Remediation and adjustments to installed covered or insulated conductors. In accordance with GO 95, conductor is defined as a material suitable for: (1) carrying electric current, usually in the form of a wire, cable or bus bar, or (2) transmitting light in the case of fiber optics; insulated conductors as those which are surrounded by an insulating material (in accordance with Rule 21.6), the dielectric strength of which is sufficient to withstand the maximum difference of potential at normal operating voltages of the circuit without breakdown or puncture; and suitable protective covering as a covering of wood or other non-conductive material having the electrical insulating efficiency (12kV/in. dry) and impact strength (20ft.-lbs) of 1.5 inches of redwood or other material meeting the requirements of Rule 22.8-A, 22.8-B, 22.8-C or 22.8-D. | LOF | Equipment / facility failure | Ongoing | 90% - Per SME judgement. The Covered Conductors maintained/repaired are highly unlikely to fail causing an ignition within a given year. To be conservative PG&E assumes an effectiveness of 90%, leaving a 10% chance of ignition due to unseen/unpredictable future events. | 1 | Since the choice is work unit within Program Exposure tab, the units that are worked on will not cause an ignition within a year with an assumed 90% effectiveness rate per SME judgement. |  | 1 | 3
7.3.3.5 | 7.3.3.5 Crossarm maintenance, repair, and replacement | Control |  | Remediation, adjustments, or installations of new equipment to improve or replace existing crossarms, defined as horizontal support attached to poles or structures generally at right angles to the conductor supported in accordance with GO 95. | LOF | Equipment / facility failure | Ongoing | 90% - Per SME judgement. The Crossarms replaced, maintained/repaired are highly unlikely to fail causing an ignition within a given year. To be conservative PG&E assumes an effectiveness of 90%, leaving a 10% chance of ignition due to unseen/unpredictable future events. | 1 | Since the choice is work unit within Program Exposure tab, the units that are worked on will not cause an ignition within a year with an assumed 90% effectiveness rate per SME judgement. |  | 1 | 4
7.3.3.6 | 7.3.3.6 Distribution pole replacement and reinforcement, including with composite poles | Control | 07D, 07C, GAD | Remediation, adjustments, or installations of new equipment to improve or replace existing distribution poles (i.e., those supporting lines under 65kV), including with equipment such as composite poles manufactured with materials reduce ignition probability by increasing pole lifespan and resilience against failure from object contact and other events. | LOF | Equipment / facility failure | Ongoing | 90% - Per SME judgement. A pole replaced or reinforced would be assumed to have 100% wood strength , but could fail through a 3rd party cause within the first year - the probability could be 0% or very low. | 1 | Since the choice is work unit within Program Exposure tab, the units that are worked on will not cause an ignition within a year with an assumed 90% effectiveness rate per SME judgement. |  | 0 | 2
7.3.3.7 | 7.3.3.7 Expulsion fuse replacement | Mitigation | 2AP | Installations of new and CAL FIRE-approved power fuses to replace existing expulsion fuse equipment. | LOF | Equipment / facility failure | 3 | 90% - Per SME judgement. Non-expulsion fuses are built to prevent sparks and hence there's no record of ignitions. To be conservative PG&E assumes an effectiveness of 90%, leaving a 10% chance of ignition due to unseen/unpredictable future events. | 30 | SMEs confirmed that 30 years is potentially the benefit length of replacing a non-exempt fuse with an exempt one, which is also industry standard. |  | 1 | 2
7.3.3.8.1 | 7.3.3.8.1 Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Sectionalizing | Mitigation | 49H | Refer to "PSPS RSE Input File_v2.2_EO_WLDFR_Template.xlsx" | COF | Refer to "PSPS RSE Input File_v2.2_EO_WLDFR_Template.xlsx" | [5 empty] | 2 | 2
7.3.3.8.2 | 7.3.3.8.2 Grid topology improvements to mitigate or reduce PSPS events, Transmission Line Sectionalizing | Mitigation | 94A | Refer to "PSPS RSE Input File_v2.2_EO_WLDFR_Template.xlsx" | COF | Refer to "PSPS RSE Input File_v2.2_EO_WLDFR_Template.xlsx" | [5 empty] | 2 | 2
7.3.3.8.3 | 7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Motorized Switch Operator (MSO) Replacements | Mitigation | 49H | Plan to support and actions taken to mitigate or reduce PSPS events in terms of geographic scope and number of customers affected, such as installation and operation of electrical equipment to sectionalize or island portions of the grid, microgrids, or local generation (Distribution Line Motorized Switch Operator (MSO) Replacements) | LOF | Equipment / facility failure | 2021-2024 | 90% - Per SME judgement This program aims at replacing the previously installed MSO switches that were reported to exhibit an arc flash during operation with various other devices including SCADA-enabled Reclosers, newly introduced SCADAMATE-SD Switches, or standard manually operated US Switches. This will completely eliminate the probability of any arc flashing and hence ignition. To be conservative PG&E assumes an effectiveness of 90%, leaving a 10% chance of ignition due to unseen/unpredictable future events. | 30 | Per the SME, the replaced switches would last for the entire lifetime of the equipment which is expected to be 30 years for distribution |  | 2 | 2
7.3.3.9.1 | 7.3.3.9.1 Installation of system automation equipment | Mitigation | 49A | Installation of electric equipment (system automation equipment) that increases the ability of the utility to automate system operation and monitoring, including equipment that can be adjusted remotely such as automatic reclosers (switching devices designed to detect and interrupt momentary faults that can reclose automatically and detect if a fault remains, remaining open if so). | LOF | Foundational | [5 empty] | 2 | 2
7.3.3.9.2 | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers | Mitigation | 49T | Installation of electric equipment (Single phase reclosers) that increases the ability of the utility to automate system operation and monitoring, including equipment that can be adjusted remotely such as automatic reclosers (switching devices designed to detect and interrupt momentary faults that can reclose automatically and detect if a fault remains, remaining open if so). | LOF | Equipment/facility failure Vegetation Contact Contact from Object Vandalism/Theft Unknown /Others | Ongoing | Refer tab "7.3.3.9.1_Effectiveness" | 30 Years | Per SME Judgement, RCU Electronic Component lasts 30 years |  | 3 | 2
7.3.3.10 | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps | Control |  | Remediation, adjustments, or installations of new equipment to improve or replace existing connector equipment, such as hotline clamps. | LOF | Equipment / facility failure | Ongoing | 90% - Per SME judgement. The replaced/repaired connectors and hotline clamps are highly unlikely to fail causing an ignition within a given year. | 1 Year | Due to the choice of work units in the Program Exposure tab for this program. |  | 3 | 3
7.3.3.11.1 | 7.3.3.11.1 Mitigation of impact on customers and other residents affected during PSPS event, Generation for PSPS Mitigation | Mitigation | IG, 21, 49M | Refer to "PSPS RSE Input File_v2.2_EO_WLDFR_Template.xlsx" | COF | Refer to "PSPS RSE Input File_v2.2_EO_WLDFR_Template.xlsx" | [5 empty] | 4 | 3
7.3.3.11.2 | 7.3.3.11.2 Mitigation of impact on customers and other residents affected during PSPS event, Substation activities to enable reduction of PSPS impacts | Mitigation | 48D, 67D, 09D, 94B, 59F | Refer to "PSPS RSE Input File_v2.2_EO_WLDFR_Template.xlsx" | COF | Refer to "PSPS RSE Input File_v2.2_EO_WLDFR_Template.xlsx" | [5 empty] | 5 | 3
7.3.3.11.3 | 7.3.3.11.3 Mitigation of impact on customers and other residents affected during PSPS event, Emergency Back-up Generation – PG&E Service Centers & Materials Distribution Centers | Mitigation |  | Actions taken to improve access to electricity for customers and other residents during PSPS events, such as installation and operation of local generation equipment (at the community, household, or other level) | COF | Foundational | [5 empty] | 5 | 3
7.3.3.11.4 | 7.3.3.11.4 Fixed Power Solutions | Mitigation |  | Actions taken to improve access to electricity for customers and other residents during PSPS events, such as installation and operation of local generation equipment (at the community, household, or other level). | COF | Risk reduction not quantified. Initiative does not currently capture data determined to be usable for RSE calculation. | [5 empty] | 6 | 3
7.3.3.12.1 | 7.3.3.12.1 Other corrective action, Distribution Substation | Control | 48X | Other maintenance, repair, or replacement of utility equipment and structures for Distribution Substation so that they function properly and safely, including remediation activities (such as insulator washing) of other electric equipment deficiencies that may increase ignition probability due to potential equipment failure or other drivers. | LOF | Risk reduction not quantified. Initiative does not currently capture data determined to be usable for RSE calculation. | [5 empty] | 3 | 4
7.3.3.12.2 | 7.3.3.12.2 Other corrective action, Transmission Substation | Control | 66X | Other maintenance, repair, or replacement of utility equipment and structures for Transmission Substation so that they function properly and safely, including remediation activities (such as insulator washing) of other electric equipment deficiencies that may increase ignition probability due to potential equipment failure or other drivers. | LOF | Risk reduction not quantified. Initiative does not currently capture data determined to be usable for RSE calculation. | [5 empty] | 3 | 5
7.3.3.12.3 | 7.3.3.12.3 Other corrective action, Maintenance, Transmission | Control |  | Other maintenance, repair, or replacement of utility equipment and structures for Transmission so that they function properly and safely, including remediation activities (such as insulator washing) of other electric equipment deficiencies that may increase ignition probability due to potential equipment failure or other drivers. | LOF | Equipment / facility failure | Ongoing | 90% - Per SME judgement The units worked on are assumed not to fail causing an ignition within a given year. | 1 Year | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year |  | 3 | 6
7.3.3.12.4 | 7.3.3.12.4 Other corrective action, Maintenance, Distribution | Control |  | Other maintenance, repair, or replacement of utility equipment and structures for Distribution so that they function properly and safely, including remediation activities (such as insulator washing) of other electric equipment deficiencies that may increase ignition probability due to potential equipment failure or other drivers. | LOF | Equipment / facility failure | Ongoing | 90% - Per SME judgement The units worked on are assumed not to fail causing an ignition within a given year. | 1 Year | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year |  | 3 | 7
7.3.3.12.5 | 7.3.3.12.5 Other corrective action, Maintenance, Generation Substation | Control | IG# | Other maintenance, repair, or replacement of utility equipment and structures for Generation Substation so that they function properly and safely, including remediation activities of other electric equipment deficiencies that may increase ignition probability due to potential equipment failure or other drivers. | LOF | Risk reduction not quantified. Initiative does not currently capture data determined to be usable for RSE calculation. | [5 empty] | 3 | 8
7.3.3.13 | 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program | Control | O7O | Actions taken to remediate, adjust, or install replacement equipment for poles that the utility has identified as failing to meet safety factor requirements in accordance with GO 95 or additional utility standards in the utility's pole loading assessment program. | LOF | Equipment / facility failure | Ongoing | This is a replacement program that addresses functional failure. Each proactive replacement is assumed to be 100% effective at mitigating a potential outage on the asset replaced. Use 90% to be conservative. | 1 Year | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year |  | 3 | 8
7.3.3.14 | 7.3.3.14 Transformers maintenance and replacement | Control |  | Remediation, adjustments, or installations of new equipment to improve or replace existing transformer equipment | LOF | Equipment / facility failure | Ongoing | 90% - Per SME judgement Transformers maintained/replaced through this program will not fail causing an ignition within a given year. To be conservative PG&E uses a 90% effectiveness. | 1 | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year |  | 3 | 9
7.3.3.15 | 7.3.3.15 Transmission tower maintenance and replacement | Control | ICQ, ICS, ICX, 70S | Remediation, adjustments, or installations of new equipment to improve or replace existing transmission towers (e.g., structures such as lattice steel towers or tubular steel poles that support lines at or above 65kV) | LOF | Equipment / facility failure | Ongoing | 90% - SME judgement The maintenance/replacement work done is considered to be 100% effective in avoiding a failure causing an ignition within a given year. To be conservative PG&E uses a 90% effectiveness. | 1 Year | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year |  | 3 | 10
7.3.3.16 | 7.3.3.16 Undergrounding of electric lines and/or equipment | Mitigation |  | Actions taken to convert overhead electric lines and/or equipment to underground electric lines and/or equipment (i.e., located underground and in accordance with GO 128) | LOF | Initiative complementary to "7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution " | [5 empty] | 4 | 10
7.3.3.17.1 (OH) | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution | Mitigation | 08W | Changes in the plan, installation, construction, removal, and/or undergrounding for Distribution to minimize the risk of ignition due to the design, location, or configuration of utility electric equipment in HFTDs. | LOF | Equipment/ facility failure Contamination Vegetation Contact Contact from Object Other/Unknown | Ongoing | Refer tab "7.3.3.17.1 (OH)_Effectiveness" | 45 years for Overhead Equipment. | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs |  | 2 | 2
7.3.3.17.1 (UG) | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution | Mitigation | 08W | Changes in the plan, installation, construction, removal, and/or undergrounding for Distribution to minimize the risk of ignition due to the design, location, or configuration of utility electric equipment in HFTDs. | LOF | Equipment/facility failure Vandalism Vegetation Contact Contamination Other/Unknown | Ongoing | PG&E assumes that undergrounding the conductor will eliminate all the exposure to wildfire risk. Assume 99% to be conservative | 49 years for Underground Equipment. | The life time of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs |  | 3 | 2
7.3.3.17.2 | 7.3.3.17.2 Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Transmission | Mitigation | 60X, 93N, 93C, 70S, 93P, 94L, 92F, 82B, 93J | Changes in the plan, installation, construction, removal, and/or undergrounding for Transmission to minimize the risk of ignition due to the design, location, or configuration of utility electric equipment in HFTDs. | LOF | Risk reduction not quantified. Initiative does not currently capture data determined to be usable for RSE calculation. | [5 empty] | 3 | 2
7.3.3.17.3 | 7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs, Surge Arrestor | Mitigation | 2AR | Changes in the plan, installation, construction, removal, and/or undergrounding for Surge Arrestors to minimize the risk of ignition due to the design, location, or configuration of utility electric equipment in HFTDs | LOF | Equipment / facility failure |  | 90% - This is a "replacement" mitigation that addresses "functional failure". PG&E subject matter experts assume that replacing non-exempt surge arresters with exempt surge arresters will eliminate 90% of ignition risk associated with surge arresters. | 30 | Asset life will be between 20 to 40 years. |  | 4 | 2
7.3.3.17.4 | 7.3.3.17.4 Updates to grid topology to minimize risk of ignition in HFTDs, Rapid Earth Current Fault Limiter | Mitigation | 49R | Changes in the plan, installation, construction, removal, and/or undergrounding for Rapid Earth Current Fault Limiter to minimize the risk of ignition due to the design, location, or configuration of utility electric equipment in HFTDs. | LOF | Risk reduction not quantified. Initiative does not currently capture data determined to be usable for RSE calculation. | [5 empty] | 5 | 2
7.3.3.17.5 | 7.3.3.17.5 Updates to grid topology to minimize risk of ignition in HFTDs, Remote Grid | Mitigation | AB | Changes in the plan, installation, construction, removal, and/or undergrounding for Remote Grid to minimize the risk of ignition due to the design, location, or configuration of utility electric equipment in HFTDs | LOF | Risk reduction not quantified. Initiative does not currently capture data determined to be usable for RSE calculation. | [5 empty] | 6 | 2
7.3.3.17.6 | 7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs, Butte County Rebuild | Mitigation | 08W, 95F, IFF | Changes in the plan, installation, construction, removal, and/or undergrounding for Butte County Rebuild to minimize the risk of ignition due to the design, location, or configuration of utility electric equipment in HFTDs | LOF | All drivers |  | Undergrounding of electric assets eliminated the risk of ignition caused by the failure of these equipment by 100%. To be conservative, program effectiveness of 99% is used. | 49 years for Underground Equipment. | Aligned benefit length with System Hardening[Underground],the lifetime of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs |  | 7 | 2

## 1-Program Exposure
Program Exposure | [7 empty] | 55300 | 68.52% | 90%
For each program, specify either the units of exposure (as defined in the Risk Model Input file), or the fraction of the total tranche exposure, to which the program applies | [7 empty] | 171.2 | 31.48% |  |  |  | 1000
If the exposure number applies all tranches, leave the 'Tranche' column blank and include only one line in the table below |  |  |  |  | 0.6738% |  |  | 6928.8
The tranche names in this table must match identically to the tranche names in the Risk Model Input File |  |  | 203564781.34
| Exposure Table |  |  |  | 7181*85%
| Program ID | Type | Program | Risk (for Cross Cutter only) | Tranche | Tranche Exposure | Tranche Exposure Unit | Program Exposure 2020 | Program Exposure 2021 | Program Exposure 2022 | Program Exposure 2023 | Program Exposure 2024 | Program Exposure 2025 | Program Exposure 2026 | Unit for Program Exposure | Work Units 2020 | Work Units 2021 | Work Units 2022 | Work Units 2023 | Work Units 2024 | Work Units 2025 | Work Units 2026 | Unit for work units | Explanation of relationship between different units | Other Note | Flag for modeler | Risk ID
| 7.3.3.1 | Control | 7.3.3.1 Capacitor maintenance and replacement program |  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles | 3.4567 | 4.4272 | 4.4286 |  |  |  |  | Work unit | 53.9492 | 69.0958 | 69.1186 | 69.1165 | 0 | 0 | 0 | Number of Capacitors maintained |  | Multiplied the units with annual Ignition to Outage rate of Capacitors to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.1 | Control | 7.3.3.1 Capacitor maintenance and replacement program |  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles | 8.9107 | 11.4125 | 11.4163 |  |  |  |  | Work unit | 139.0713 | 178.1166 | 178.1753 | 178.17 |  |  |  | Number of Capacitors maintained |  | Multiplied the units with annual Ignition to Outage rate of Capacitors to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.1 | Control | 7.3.3.1 Capacitor maintenance and replacement program |  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles | 0.0072967 | 0.0093453 | 0.0093484 |  |  |  |  | Work unit | 0.11388 | 0.14585 | 0.1459 | 0.1459 |  |  |  | Number of Capacitors maintained |  | Multiplied the units with annual Ignition to Outage rate of Capacitors to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.1 | Control | 7.3.3.1 Capacitor maintenance and replacement program |  | non-HFTD - Distribution | 55300 | Miles | 27.0295 | 34.6182 | 34.6296 |  |  |  |  | Work unit | 421.8526 | 540.2909 | 540.469 | 540.453 |  |  |  | Number of Capacitors maintained |  | Multiplied the units with annual Ignition to Outage rate of Capacitors to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.2-D | Control | 7.3.3.2-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Distribution |  | HFTD - Substation | 1 | Unit | 15.1617 | 13.91 | 18.9572 | 18.9572 |  |  |  | Work unit | 707.5461 | 649.1335 | 884.6682 | 884.6682 |  |  |  | Number of Circuit Breakers replaced + repaired |  | Multiplied the units with annual Ignition to Outage rate of Recloser/Sectionalizer to define exposure based on number of ignitions avoided each year. Since there is no choice of Circuit Breaker sub-driver due to no historical ignitions. |  | WLDFR
| 7.3.3.2-D | Control | 7.3.3.2-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Distribution |  | non-HFTD - Substation | 1 | Unit | 33.1169 | 30.3829 | 41.4071 | 41.4071 |  |  |  | Work unit | 1545.4539 | 1417.8665 | 1932.3318 | 1932.3318 |  |  |  | Number of Circuit Breakers replaced + repaired |  | Multiplied the units with annual Ignition to Outage rate of Recloser/Sectionalizer to define exposure based on number of ignitions avoided each year. Since there is no choice of Circuit Breaker sub-driver due to no historical ignitions. |  | WLDFR
| 7.3.3.2-T | Control | 7.3.3.2-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Transmission |  | HFTD - Substation | 1 | Unit | 30.2584 | 23.2988 | 22.2812 | 24.0489 |  |  |  | Work unit | 1412.0584 | 1087.2758 | 1039.7912 | 1122.2805 |  |  |  | Number of Circuit Breakers replaced + repaired |  | Multiplied the units with annual Ignition to Outage rate of Recloser/Sectionalizer to define exposure based on number of ignitions avoided each year. Since there is no choice of Circuit Breaker sub-driver due to no historical ignitions. |  | WLDFR
| 7.3.3.2-T | Control | 7.3.3.2-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Transmission |  | non-HFTD - Substation | 1 | Unit | 69.1487 | 53.2441 | 50.9188 | 54.9583 |  |  |  | Work unit | 3226.9416 | 2484.7242 | 2376.2088 | 2564.7195 |  |  |  | Number of Circuit Breakers replaced + repaired |  | Multiplied the units with annual Ignition to Outage rate of Recloser/Sectionalizer to define exposure based on number of ignitions avoided each year. Since there is no choice of Circuit Breaker sub-driver due to no historical ignitions. |  | WLDFR
| 7.3.3.4 | Control | 7.3.3.4 Covered conductor maintenance |  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles | 0 | 38.8277 | 60.5076 | 60.5076 |  |  |  | Work unit | 0 | 995.5495 | 1551.4259 | 1551.4259 |  |  |  | Number of Covered Conductors maintained |  | Multiplied the units with annual Ignition to Outage rate of Conductor to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.4 | Control | 7.3.3.4 Covered conductor maintenance |  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles | 0 | 100.0909 | 155.9778 | 155.9778 |  |  |  | Work unit | 0 | 2566.349 | 3999.2992 | 3999.2992 |  |  |  | Number of Covered Conductors maintained |  | Multiplied the units with annual Ignition to Outage rate of Conductor to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.4 | Control | 7.3.3.4 Covered conductor maintenance |  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles | 0 | 0.081961 | 0.12773 | 0.12773 |  |  |  | Work unit | 0 | 2.1015 | 3.2749 | 3.2749 |  |  |  | Number of Covered Conductors maintained |  | Multiplied the units with annual Ignition to Outage rate of Conductor to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.4 | Control | 7.3.3.4 Covered conductor maintenance |  | non-HFTD - Distribution | 55300 | Miles | 0 | 107.6045 | 88.7279 | 88.7279 |  |  |  | Work unit | 0 | 2759 | 2275 | 2275 |  |  |  | Number of Covered Conductors maintained |  | Multiplied the units with annual Ignition to Outage rate of Conductor to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement |  | HFTD - Transmission - Tier 3 - All | 1380.98 | Miles | 0.60722 | 0.87743 | 0.60203 | 0.61484 |  |  |  | Work unit | 94.8097 | 137 | 94 | 96 |  |  |  | Number of Crossarms repaired and replaced/installed. |  | Multiplied the units with annual Ignition to Outage rate of Crossarm to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement |  | HFTD - Transmission - Tier 2 - All | 4478.34 | Miles | 1.2231 | 1.4987 | 0.98631 | 1.0375 |  |  |  | Work unit | 190.9765 | 234 | 154 | 162 |  |  |  | Number of Crossarms repaired and replaced/installed. |  | Multiplied the units with annual Ignition to Outage rate of Crossarm to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement |  | HFTD - Transmission - Zone 1 - All | 6.17 | Miles | 0 | 0 | 0 | 0 |  |  |  | Work unit | 0 | 0 | 0 | 0 |  |  |  | Number of Crossarms repaired and replaced/installed. |  | Multiplied the units with annual Ignition to Outage rate of Crossarm to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement |  | non-HFTD - Transmission - All | 13220.51 | Miles | 0.78913 | 0.85181 | 0.61484 | 0.64686 |  |  |  | Work unit | 123.2138 | 133 | 96 | 101 |  |  |  | Number of Crossarms repaired and replaced/installed. |  | Multiplied the units with annual Ignition to Outage rate of Crossarm to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement |  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles | 3.6851 | 4.4779 | 5.6569 | 5.6569 |  |  |  | Work unit | 575.3826 | 699.1752 | 883.2569 | 883.2569 |  |  |  | Number of Crossarms repaired and replaced/installed. |  | Multiplied the units with annual Ignition to Outage rate of Crossarm to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement |  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles | 9.4995 | 11.5433 | 14.5825 | 14.5825 |  |  |  | Work unit | 1483.2337 | 1802.3489 | 2276.8787 | 2276.8787 |  |  |  | Number of Crossarms repaired and replaced/installed. |  | Multiplied the units with annual Ignition to Outage rate of Crossarm to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement |  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles | 0.0077788 | 0.0094524 | 0.011941 | 0.011941 |  |  |  | Work unit | 1.2146 | 1.4759 | 1.8645 | 1.8645 |  |  |  | Number of Crossarms repaired and replaced/installed. |  | Multiplied the units with annual Ignition to Outage rate of Crossarm to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement |  | non-HFTD - Distribution | 55300 | Miles | 14.918 | 25.8489 | 24.4655 | 24.4655 |  |  |  | Work unit | 2329.2606 | 4036 | 3820 | 3820 |  |  |  | Number of Crossarms repaired and replaced/installed. |  | Multiplied the units with annual Ignition to Outage rate of Crossarm to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.6 | Control | 7.3.3.6 Distribution pole replacement and reinforcement, including with composite poles |  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles | 59.0994 | 69.3399 | 80.0487 | 84.7936 |  |  |  | Work unit | 3427.768 | 4021.7119 | 4642.8251 | 4918.0298 |  |  |  | Number of poles replaced + reinforced |  | Multiplied the units with annual Ignition to Outage rate of Poles to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.6 | Control | 7.3.3.6 Distribution pole replacement and reinforcement, including with composite poles |  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles | 88.5794 | 177.959 | 205.371 | 217.5325 |  |  |  | Work unit | 5137.606 | 10321.6223 | 11911.5191 | 12616.8867 |  |  |  | Number of poles replaced + reinforced |  | Multiplied the units with annual Ignition to Outage rate of Poles to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.6 | Control | 7.3.3.6 Distribution pole replacement and reinforcement, including with composite poles |  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles | 0.68966 | 0.13606 | 0.15613 | 0.16523 |  |  |  | Work unit | 40 | 7.8917 | 9.0558 | 9.5835 |  |  |  | Number of poles replaced + reinforced |  | Multiplied the units with annual Ignition to Outage rate of Poles to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.6 | Control | 7.3.3.6 Distribution pole replacement and reinforcement, including with composite poles |  | non-HFTD - Distribution | 55300 | Miles | 93.166 | 84.7892 | 99.6828 | 59.9569 |  |  |  | Work unit | 5403.626 | 4917.7742 | 5781.6 | 3477.5 |  |  |  | Number of poles replaced + reinforced |  | Multiplied the units with annual Ignition to Outage rate of Poles to define exposure based on number of ignitions avoided each year. |  | WLDFR
| 7.3.3.7 | Mitigation | 7.3.3.7 Expulsion fuse replacement |  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles | 243.516 | 541.1887 | 1418.7322 | 1136.1553 |  |  |  | Exposure unit | [9 empty] | Refer to tab 7.3.3.7_Exposure. |  | WLDFR
| 7.3.3.7 | Mitigation | 7.3.3.7 Expulsion fuse replacement |  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles | 627.7407 | 1395.0878 | 2507.6122 | 2928.8057 |  |  |  | Exposure unit | [9 empty] | Refer to tab 7.3.3.7_Exposure. |  | WLDFR
| 7.3.3.7 | Mitigation | 7.3.3.7 Expulsion fuse replacement |  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles | 0.51404 | 1.1424 | 141.0149 | 2.3983 |  |  |  | Exposure unit | [9 empty] | Refer to tab 7.3.3.7_Exposure. |  | WLDFR
| 7.3.3.8.3 | Mitigation | 7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Motorized Switch Operator (MSO) Replacements |  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles | 0 | 2309.1988 | 2309.1988 | 4618.3976 |  |  |  | Exposure unit | [9 empty] | Refer to tab 7.3.3.8.3_Exposure |  | WLDFR
| 7.3.3.8.3 | Mitigation | 7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Motorized Switch Operator (MSO) Replacements |  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles | 0 | 5952.7025 | 5952.7025 | 11905.405 |  |  |  | Exposure unit | [9 empty] | Refer to tab 7.3.3.8.3_Exposure |  | WLDFR
| 7.3.3.8.3 | Mitigation | 7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Motorized Switch Operator (MSO) Replacements |  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles | 0 | 4.8745 | 4.8745 | 9.7489 |  |  |  | Exposure unit | [9 empty] | Refer to tab 7.3.3.8.3_Exposure |  | WLDFR
| 7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  | HFTD - Distribution - All | 25461.6694 | Miles | 0% | 0.2125% | 0.2394% | 0.2394% |  |  |  | % of tranche exposure | [9 empty] | Refer tab "7.3.3.9.2_Exposure" |  | WLDFR
| 7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  | non-HFTD - Distribution | 55300 | Miles | 0% | 0% | 0% | 0% |  |  |  | % of tranche exposure | [9 empty] | Refer tab "7.3.3.9.2_Exposure" |  | WLDFR
| 7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps |  | HFTD - Transmission - Tier 3 - All | 1380.98 | Miles | 0.20234 | 0.056604 | 0.037736 | 0.037736 |  |  |  | Work unit | 10.724 | 3 | 2 | 2 |  |  |  | Number of Connectors, Hotline clamps |  |  |  | WLDFR
| 7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps |  | HFTD - Transmission - Tier 2 - All | 4478.34 | Miles | 0.28823 | 0.26415 | 0.13208 | 0.13208 |  |  |  | Work unit | 15.276 | 14 | 7 | 7 |  |  |  | Number of Connectors, Hotline clamps |  |  |  | WLDFR
| 7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps |  | HFTD - Transmission - Zone 1 - All | 6.17 | Miles | 0 | 0 | 0 | 0 |  |  |  | Work unit | 0 | 0 | 0 | 0 |  |  |  | Number of Connectors, Hotline clamps |  |  |  | WLDFR
| 7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps |  | non-HFTD - Transmission - All | 13220.51 | Miles | 0 | 0.18868 | 0.09434 | 0.09434 |  |  |  | Work unit | 0 | 10 | 5 | 5 |  |  |  | Number of Connectors, Hotline clamps |  |  |  | WLDFR
| 7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps |  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles | 39.6212 | 39.5812 | 31.4436 | 31.4436 |  |  |  | Work unit | 2099.923 | 2097.8049 | 1666.5119 | 1666.5119 |  |  |  | Number of Connectors, Hotline clamps |  |  |  | WLDFR
| 7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps |  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles | 102.1364 | 102.0333 | 81.056 | 81.056 |  |  |  | Work unit | 5413.2268 | 5407.7668 | 4295.9703 | 4295.9703 |  |  |  | Number of Connectors, Hotline clamps |  |  |  | WLDFR
| 7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps |  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles | 0.083636 | 0.083552 | 0.066374 | 0.066374 |  |  |  | Work unit | 4.4327 | 4.4282 | 3.5178 | 3.5178 |  |  |  | Number of Connectors, Hotline clamps |  |  |  | WLDFR
| 7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps |  | non-HFTD - Distribution | 55300 | Miles | 15.5521 | 12.8113 | 9.4528 | 9.4528 |  |  |  | Work unit | 824.2628 | 679 | 501 | 501 |  |  |  | Number of Connectors, Hotline clamps |  |  |  | WLDFR
| 7.3.3.12.3 | Control | 7.3.3.12.3 Other corrective action, Maintenance, Transmission |  | HFTD - Transmission - Tier 3 - All | 1380.98 | Miles | 14.2264 | 13.4415 | 13.592 | 17.1126 |  |  |  | Work unit | 1129.5129 | 1067.193 | 1079.1448 | 1358.6595 |  |  |  | Various repair and replacement work of assets in Transmission. |  | Multiplied the planned units with the overall ignition to outage rate of Equipment failure drivers |  | WLDFR
| 7.3.3.12.3 | Control | 7.3.3.12.3 Other corrective action, Maintenance, Transmission |  | HFTD - Transmission - Tier 2 - All | 4478.34 | Miles | 46.5772 | 44.0073 | 44.5002 | 56.0264 |  |  |  | Work unit | 3698.0183 | 3493.9833 | 3533.1133 | 4448.2429 |  |  |  | Various repair and replacement work of assets in Transmission. |  | Multiplied the planned units with the overall ignition to outage rate of Equipment failure drivers |  | WLDFR
| 7.3.3.12.3 | Control | 7.3.3.12.3 Other corrective action, Maintenance, Transmission |  | HFTD - Transmission - Zone 1 - All | 6.17 | Miles | 0.066067 | 0.062422 | 0.063121 | 0.07947 |  |  |  | Work unit | 5.2454 | 4.956 | 5.0115 | 6.3096 |  |  |  | Various repair and replacement work of assets in Transmission. |  | Multiplied the planned units with the overall ignition to outage rate of Equipment failure drivers |  | WLDFR
| 7.3.3.12.3 | Control | 7.3.3.12.3 Other corrective action, Maintenance, Transmission |  | non-HFTD - Transmission - All | 13220.51 | Miles | 139.104 | 131.429 | 132.9009 | 167.3243 |  |  |  | Work unit | 11044.2234 | 10434.8677 | 10551.7305 | 13284.788 |  |  |  | Various repair and replacement work of assets in Transmission. |  | Multiplied the planned units with the overall ignition to outage rate of Equipment failure drivers |  | WLDFR
| 7.3.3.12.4 | Control | 7.3.3.12.4 Other corrective action, Maintenance, Distribution |  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles | 167.823 | 149.5778 | 111.9742 | 144.9523 |  |  |  | Work unit | 13324.3851 | 11875.7993 | 8890.2431 | 11508.5576 |  |  |  | Various repair and replacement work of assets in Distribution. |  | Multiplied the planned units with the overall ignition to outage rate of Equipment failure drivers |  | WLDFR
| 7.3.3.12.4 | Control | 7.3.3.12.4 Other corrective action, Maintenance, Distribution |  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles | 432.6178 | 385.5849 | 288.6495 | 373.6613 |  |  |  | Work unit | 34347.8872 | 30613.6914 | 22917.4603 | 29667.0078 |  |  |  | Various repair and replacement work of assets in Distribution. |  | Multiplied the planned units with the overall ignition to outage rate of Equipment failure drivers |  | WLDFR
| 7.3.3.12.4 | Control | 7.3.3.12.4 Other corrective action, Maintenance, Distribution |  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles | 0.35426 | 0.31574 | 0.23637 | 0.30598 |  |  |  | Work unit | 28.1263 | 25.0685 | 18.7663 | 24.2933 |  |  |  | Various repair and replacement work of assets in Distribution. |  | Multiplied the planned units with the overall ignition to outage rate of Equipment failure drivers |  | WLDFR
| 7.3.3.12.4 | Control | 7.3.3.12.4 Other corrective action, Maintenance, Distribution |  | non-HFTD - Distribution | 55300 | Miles | 317.1022 | 299.8573 | 236.6071 | 298.8476 |  |  |  | Work unit | 25176.4748 | 23807.3041 | 18785.5302 | 23727.1413 |  |  |  | Various repair and replacement work of assets in Distribution. |  | Multiplied the planned units with the overall ignition to outage rate of Equipment failure drivers |  | WLDFR
| 7.3.3.13 | Control | 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program |  | HFTD - Distribution - All | 25461.6694 | Miles | 2.4655 | 6.7414 | 3.8448 | 3.7414 |  |  |  | Work unit | 143 | 391 | 223 | 217 |  |  |  | Number of poles |  |  |  | WLDFR
| 7.3.3.13 | Control | 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program |  | non-HFTD - Distribution | 55300 | Miles | 2.5 | 2.8966 | 0.7931 | 0.77586 |  |  |  | Work unit | 145 | 168 | 46 | 45 |  |  |  | Number of poles |  |  |  | WLDFR
| 7.3.3.14 | Control | 7.3.3.14 Transformers maintenance and replacement |  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles | 0.031411 | 1.471 | 0.87765 | 1.0599 |  |  |  | Work unit | 9.6276 | 450.8465 | 268.9995 | 324.8665 |  |  |  | Number of Transformers repaired/replaced |  |  |  | WLDFR
| 7.3.3.14 | Control | 7.3.3.14 Transformers maintenance and replacement |  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles | 0.080973 | 3.7918 | 2.2624 | 2.7323 |  |  |  | Work unit | 24.8181 | 1162.2018 | 693.4327 | 837.4478 |  |  |  | Number of Transformers repaired/replaced |  |  |  | WLDFR
| 7.3.3.14 | Control | 7.3.3.14 Transformers maintenance and replacement |  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles | 6.6306e-05 | 0.003105 | 0.0018526 | 0.0022374 |  |  |  | Work unit | 0.020323 | 0.95169 | 0.56783 | 0.68576 |  |  |  | Number of Transformers repaired/replaced |  |  |  | WLDFR
| 7.3.3.14 | Control | 7.3.3.14 Transformers maintenance and replacement |  | non-HFTD - Distribution | 55300 | Miles | 0.066096 | 4.1892 | 1.7129 | 1.7129 |  |  |  | Work unit | 20.2584 | 1284 | 525 | 525 |  |  |  | Number of Transformers repaired/replaced |  |  |  | WLDFR
| 7.3.3.15 | Control | 7.3.3.15 Transmission tower maintenance and replacement |  | HFTD - Transmission - Tier 3 - All | 1380.98 | Miles | 40.3841 | 37.38 | 31.1417 | 32.6084 |  |  |  | Work unit | 1637.0208 | 1515.2489 | 1262.3692 | 1321.8232 |  |  |  | Number of Connector, Conductor, Other equipment |  | Multiplied the units with the ignition to outage rate of Conductor, Connector/Splice/Jumper/Kearney, Other, assuming these sub-drivers form part transmission tower asset |  | WLDFR
| 7.3.3.15 | Control | 7.3.3.15 Transmission tower maintenance and replacement |  | HFTD - Transmission - Tier 2 - All | 4478.34 | Miles | 85.959 | 79.5648 | 66.2862 | 69.4081 |  |  |  | Work unit | 3484.4591 | 3225.263 | 2686.9992 | 2813.5493 |  |  |  | Number of Connector, Conductor, Other equipment |  | Multiplied the units with the ignition to outage rate of Conductor, Connector/Splice/Jumper/Kearney, Other, assuming these sub-drivers form part transmission tower asset |  | WLDFR
| 7.3.3.15 | Control | 7.3.3.15 Transmission tower maintenance and replacement |  | HFTD - Transmission - Zone 1 - All | 6.17 | Miles | 0 | 0 | 0 | 0 |  |  |  | Work unit | 0 | 0 | 0 | 0 |  |  |  | Number of Connector, Conductor, Other equipment |  | Multiplied the units with the ignition to outage rate of Conductor, Connector/Splice/Jumper/Kearney, Other, assuming these sub-drivers form part transmission tower asset |  | WLDFR
| 7.3.3.15 | Control | 7.3.3.15 Transmission tower maintenance and replacement |  | non-HFTD - Transmission - All | 13220.51 | Miles | 72.6391 | 67.2357 | 56.0148 | 58.6529 |  |  |  | Work unit | 2944.5201 | 2725.4881 | 2270.6317 | 2377.572 |  |  |  | Number of Connector, Conductor, Other equipment |  | Multiplied the units with the ignition to outage rate of Conductor, Connector/Splice/Jumper/Kearney, Other, assuming these sub-drivers form part transmission tower asset |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | 163.6441 | Miles |  | 2.1301 | 4.4163 | 2.4615 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | 353.5334 | Miles |  | 5.0607 | 10.4924 | 5.8482 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | 1013.9529 | Miles |  | 13.7063 | 28.4176 | 15.8393 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | 1483.0022 | Miles |  | 19.4222 | 40.2685 | 22.4447 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | 1601.5759 | Miles |  | 21.8878 | 45.3803 | 25.294 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | 193.7699 | Miles |  | 1.9466 | 4.0358 | 2.2495 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | 543.1039 | Miles |  | 5.1237 | 10.6231 | 5.9211 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | 946.5765 | Miles |  | 9.4231 | 19.5372 | 10.8896 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | 1078.9824 | Miles |  | 10.9692 | 22.7428 | 12.6763 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | 1464.9153 | Miles |  | 15.5687 | 32.2789 | 17.9915 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | 489.6273 | Miles |  | 1.6863 | 3.4962 | 1.9487 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | 791.1377 | Miles |  | 2.2079 | 4.5777 | 2.5515 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | 791.1875 | Miles |  | 3.0955 | 6.4179 | 3.5772 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | 741.5879 | Miles |  | 2.0596 | 4.2702 | 2.3801 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | 715.8465 | Miles |  | 2.1629 | 4.4845 | 2.4995 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | 772.1066 | Miles |  | 1.0587 | 2.1951 | 1.2235 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | 522.2177 | Miles |  | 0.60343 | 1.2511 | 0.69734 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | 750.2287 | Miles |  | 0.8669 | 1.7974 | 1.0018 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | 696.1473 | Miles |  | 0.81396 | 1.6876 | 0.94063 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | 470.836 | Miles |  | 0.54406 | 1.128 | 0.62873 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | 752.6401 | Miles |  | 0.87064 | 1.8051 | 1.0061 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | 768.4668 | Miles |  | 0.88798 | 1.8411 | 1.0262 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | 467.0501 | Miles |  | 0.54213 | 1.124 | 0.62649 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | 347.2658 | Miles |  | 0.43213 | 0.89595 | 0.49938 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | 406.8993 | Miles |  | 0.47066 | 0.97582 | 0.5439 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | 58.7222 | Miles |  | 0.83561 | 1.7325 | 0.96565 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | 156.5661 | Miles |  | 2.2736 | 4.7139 | 2.6274 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | 56.2394 | Miles |  | 0.84059 | 1.7428 | 0.9714 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | 111.286 | Miles |  | 1.6689 | 3.4601 | 1.9286 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | 65.8407 | Miles |  | 0.9427 | 1.9545 | 1.0894 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | 184.1265 | Miles |  | 1.2997 | 2.6946 | 1.5019 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | 264.4574 | Miles |  | 1.8944 | 3.9278 | 2.1893 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | 279.2931 | Miles |  | 2.5902 | 5.3704 | 2.9933 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | 108.7427 | Miles |  | 1.0384 | 2.1529 | 1.2 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | 22.7224 | Miles |  | 0.22139 | 0.45902 | 0.25585 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | 423.2024 | Miles |  | 1.5808 | 3.2775 | 1.8268 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | 595.3479 | Miles |  | 2.0769 | 4.306 | 2.4001 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | 215.5262 | Miles |  | 0.53584 | 1.111 | 0.61923 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | 223.3454 | Miles |  | 0.59399 | 1.2315 | 0.68643 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | 134.3564 | Miles |  | 0.15525 | 0.32189 | 0.17941 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | 607.6134 | Miles |  | 0.7524 | 1.56 | 0.86949 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | 572.0063 | Miles |  | 0.66096 | 1.3704 | 0.76382 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | 384.7705 | Miles |  | 0.484 | 1.0035 | 0.55932 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | 202.884 | Miles |  | 0.23444 | 0.48606 | 0.27092 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | 117.3278 | Miles |  | 0.13557 | 0.28109 | 0.15667 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | 1430.0123 | Miles |  | 1.6548 | 3.4309 | 1.9123 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | 527.1275 | Miles |  | 0.63054 | 1.3073 | 0.72867 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | 190.7177 | Miles |  | 0.23018 | 0.47723 | 0.266 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | 95.1547 | Miles |  | 0.10995 | 0.22797 | 0.12706 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | 97.3625 | Miles |  | 0.1125 | 0.23326 | 0.13001 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Zone 1 - 1QU CoRE ¦ 5QU LoRE | 0.18783 | Miles |  | 0.00021704 | 0.00045 | 0.00025082 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | 0.13442 | Miles |  | 0.00015532 | 0.00032203 | 0.00017949 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | 10.0154 | Miles |  | 0.011573 | 0.023994 | 0.013374 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | 0.27822 | Miles |  | 0.00032149 | 0.00066654 | 0.00037152 |  |  |  | Exposure unit | [7 empty] | Overhead miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | 163.6441 | Miles |  | 0.72 | 2.0923 | 4.3734 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | 353.5334 | Miles |  | 1.7106 | 4.971 | 10.3906 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | 1013.9529 | Miles |  | 4.633 | 13.4634 | 28.1418 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | 1483.0022 | Miles |  | 6.5651 | 19.078 | 39.8777 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | 1601.5759 | Miles |  | 7.3985 | 21.4999 | 44.9399 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | 193.7699 | Miles |  | 0.65798 | 1.9121 | 3.9967 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | 543.1039 | Miles |  | 1.7319 | 5.0329 | 10.52 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | 946.5765 | Miles |  | 3.1852 | 9.2561 | 19.3476 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | 1078.9824 | Miles |  | 3.7078 | 10.7749 | 22.5221 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | 1464.9153 | Miles |  | 5.2626 | 15.2928 | 31.9656 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | 489.6273 | Miles |  | 0.57 | 1.6564 | 3.4623 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | 791.1377 | Miles |  | 0.74631 | 2.1688 | 4.5332 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | 791.1875 | Miles |  | 1.0463 | 3.0406 | 6.3556 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | 741.5879 | Miles |  | 0.69618 | 2.0231 | 4.2287 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | 715.8465 | Miles |  | 0.73112 | 2.1246 | 4.441 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | 772.1066 | Miles |  | 0.35788 | 1.04 | 2.1738 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | 522.2177 | Miles |  | 0.20397 | 0.59274 | 1.239 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | 750.2287 | Miles |  | 0.29303 | 0.85154 | 1.7799 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | 696.1473 | Miles |  | 0.27514 | 0.79953 | 1.6712 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | 470.836 | Miles |  | 0.1839 | 0.53442 | 1.1171 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | 752.6401 | Miles |  | 0.2943 | 0.85521 | 1.7876 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | 768.4668 | Miles |  | 0.30016 | 0.87224 | 1.8232 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | 467.0501 | Miles |  | 0.18325 | 0.53252 | 1.1131 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | 347.2658 | Miles |  | 0.14607 | 0.42448 | 0.88726 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | 406.8993 | Miles |  | 0.15909 | 0.46232 | 0.96635 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | 58.7222 | Miles |  | 0.28246 | 0.82081 | 1.7157 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | 156.5661 | Miles |  | 0.76853 | 2.2333 | 4.6682 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | 56.2394 | Miles |  | 0.28414 | 0.82569 | 1.7259 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | 111.286 | Miles |  | 0.56412 | 1.6393 | 3.4265 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | 65.8407 | Miles |  | 0.31865 | 0.92599 | 1.9355 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | 184.1265 | Miles |  | 0.43932 | 1.2766 | 2.6685 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | 264.4574 | Miles |  | 0.64036 | 1.8609 | 3.8897 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | 279.2931 | Miles |  | 0.87555 | 2.5443 | 5.3182 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | 108.7427 | Miles |  | 0.35099 | 1.02 | 2.132 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | 22.7224 | Miles |  | 0.074835 | 0.21747 | 0.45456 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | 423.2024 | Miles |  | 0.53434 | 1.5528 | 3.2457 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | 595.3479 | Miles |  | 0.70203 | 2.0401 | 4.2642 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | 215.5262 | Miles |  | 0.18112 | 0.52634 | 1.1002 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | 223.3454 | Miles |  | 0.20078 | 0.58346 | 1.2196 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | 134.3564 | Miles |  | 0.052478 | 0.1525 | 0.31876 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | 607.6134 | Miles |  | 0.25433 | 0.73907 | 1.5448 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | 572.0063 | Miles |  | 0.22342 | 0.64925 | 1.3571 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | 384.7705 | Miles |  | 0.1636 | 0.47542 | 0.99374 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | 202.884 | Miles |  | 0.079244 | 0.23028 | 0.48134 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | 117.3278 | Miles |  | 0.045827 | 0.13317 | 0.27836 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | 1430.0123 | Miles |  | 0.55935 | 1.6254 | 3.3976 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | 527.1275 | Miles |  | 0.21314 | 0.61937 | 1.2946 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | 190.7177 | Miles |  | 0.077805 | 0.2261 | 0.4726 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | 95.1547 | Miles |  | 0.037166 | 0.108 | 0.22576 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | 97.3625 | Miles |  | 0.038029 | 0.11051 | 0.23099 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Zone 1 - 1QU CoRE ¦ 5QU LoRE | 0.18783 | Miles |  | 7.3365e-05 | 0.0002132 | 0.00044563 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | 0.13442 | Miles |  | 5.2502e-05 | 0.00015257 | 0.00031891 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | 10.0154 | Miles |  | 0.0039119 | 0.011368 | 0.023762 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | 0.27822 | Miles |  | 0.00010867 | 0.00031579 | 0.00066007 |  |  |  | Exposure unit | [7 empty] | Underground miles |  |  |  | WLDFR
| 7.3.3.17.3 | Mitigation | 7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs, Surge Arrestor |  | HFTD - Distribution - All | 25461.6694 | Miles | 17258.64 | 26001.36 | 8400 | 0 |  |  |  | Exposure unit | [11 empty] | WLDFR
| 7.3.3.17.3 | Mitigation | 7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs, Surge Arrestor |  | non-HFTD - Distribution | 55300 | Miles | 4058.01 | 0 | 2722.5 | 4352.04 |  |  |  | Exposure unit | [11 empty] | WLDFR
| 7.3.3.17.5 | Mitigation | 7.3.3.17.5 Updates to grid topology to minimize risk of ignition in HFTDs, Remote Grid |  | HFTD - Distribution - All | 25461.6694 | Miles | [7 empty] | Exposure unit | [11 empty] | WLDFR
| 7.3.3.17.6 | Mitigation | 7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs, Butte County Rebuild |  | HFTD - Distribution - All | 25461.6694 | Miles |  | 19.1295 | 18.563 | 21.4228 |  |  |  | Exposure unit | [11 empty] | WLDFR
| 7.3.3.17.6 | Mitigation | 7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs, Butte County Rebuild |  | non-HFTD - Distribution | 55300 | Miles |  | 4.5105 | 4.377 | 5.0512 |  |  |  | Exposure unit | [11 empty] | WLDFR

## 2-Program Cost
Program Spend from Control File
Program ID | Type | Program | MAT (optional) | CapEx USD 2020 | CapEx USD 2021 | CapEx USD 2022 | CapEx USD 2023 | CapEx USD 2024 | CapEx USD 2025 | CapEx USD 2026 | OpEx USD 2020 | OpEx USD 2021 | OpEx USD 2022 | OpEx USD 2023 | OpEx USD 2024 | OpEx USD 2025 | OpEx USD 2026 | Asset Type | Generic Capital PVRR Multiplier | Custom Capital PVRR Multiplier | Generic Lifetime Incremental O&M PVRR Multiplier | Custom Lifetime Incremental O&M PVRR Multiplier (optional; specify if 0) | Lifetime Incremental O&M PVRR Multiplier | PVRR Multiplier | In Exposure tab? | In Allocation table | In Eff Table
7.3.3.1 | Control | 7.3.3.1 Capacitor maintenance and replacement program | KAF, KBC, 2AE, 2BD, 17P, 06A, 06D, 06H, 06K | 8248002.2642 | 11358483.6122 | 10549235.774 | 11964722.2018 |  |  |  | 2383379.68 | 2959176.0607 | 2369236.2738 | 2436159.7214 |  |  |  |  | #N/A |  | #N/A |  | #N/A | 0 | TRUE | TRUE | TRUE | 2022 | 2022 | 2022
7.3.3.2-D | Control | 7.3.3.2-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Distribution | GCB, GCM, GCS, GCV | [7 empty] | 2368310 | 2638202 | 2585980.3424 | 2411392 | [9 empty] | 0 | TRUE | TRUE | TRUE | Cost (Capital + Expense) | Total number on Conductors (Capital + Expense) | Cost per Unit
7.3.3.2-T | Control | 7.3.3.2-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Transmission | AMB, AMM, AMS, AMV | [7 empty] | 2414211 | 2088398 | 2444531.6006 | 2444531.6006 | [9 empty] | 0 | TRUE | TRUE | TRUE | 2444531.6006 | 7829 | 312.2406
7.3.3.4 | Control | 7.3.3.4 Covered conductor maintenance | 0 | 18576556 | 29052111 | 44386310 | 44386310 |  |  |  | 17027136 | 15281398 | 9013305 | 9013305 |  |  |  |  | #N/A |  | #N/A |  | #N/A | 0 | TRUE | TRUE | TRUE
7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement | 0 | 52085714.4211 | 80299618.481 | 71788164.6441 | 68996612.7609 |  |  |  | 966638.9894 | 2820125.7166 | 2567165.8314 | 2760698.0871 |  |  |  |  | #N/A |  | #N/A |  | #N/A | 0 | TRUE | TRUE | TRUE
7.3.3.6 | Control | 7.3.3.6 Distribution pole replacement and reinforcement, including with composite poles | 07D, 07C, GAD | 238929563 | 390886885.74 | 419170185 | 434217542.672 |  |  |  | 4783468.28 | 2800146.93 | 3460022.1071 | 3911424.0567 |  |  |  |  | #N/A |  | #N/A |  | #N/A | 0 | TRUE | TRUE | TRUE
7.3.3.7 | Mitigation | 7.3.3.7 Expulsion fuse replacement | 2AP | 7846551 | 11295164.53 | 35000000 | 35000000 | [10 empty] | Electric distribution (<69kV) - Overhead | 1.3891 |  | 0 |  | 0 | 1.3891 | TRUE | TRUE | TRUE
7.3.3.8.3 | Mitigation | 7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Motorized Switch Operator (MSO) Replacements | 49H | 34977990.95 | 14912755.555 | 10452198.8726 | 5948759.85 | [10 empty] | Electric distribution (<69kV) - Overhead | 1.3891 |  | 0 |  | 0 | 1.3891 | TRUE | TRUE | TRUE
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers | 49T | 0 | 6730335.85 | 4400000 | 4400000 | [10 empty] | Electric distribution (<69kV) - Overhead | 1.3891 |  | 0 |  | 0 | 1.3891 | TRUE | TRUE | TRUE
7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps |  | 0 | 1583868.2267 | 3134723.1192 | 3134723.1192 |  |  |  | 24792900.6661 | 23651413.6307 | 14596800.5293 | 14597698.8379 |  |  |  |  | #N/A |  | #N/A |  | #N/A | 0 | TRUE | TRUE | TRUE
7.3.3.12.3 | Control | 7.3.3.12.3 Other corrective action, Maintenance, Transmission | 0 | 449179013.8168 | 360362223.99 | 412054650.1115 | 381315733.3912 |  |  |  | 99945964.18 | 89135581.21 | 127975538.0805 | 139107312 |  |  |  |  | #N/A |  | #N/A |  | #N/A | 0 | TRUE | TRUE | TRUE
7.3.3.12.4 | Control | 7.3.3.12.4 Other corrective action, Maintenance, Distribution | 0 | 331098926.4 | 295107958.9417 | 196540836.8751 | 329592612.5273 |  |  |  | 75248474.0009 | 74702949.0218 | 93704432.5808 | 73465810.1603 |  |  |  |  | #N/A |  | #N/A |  | #N/A | 0 | TRUE | TRUE | TRUE
7.3.3.13 | Control | 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program | O7O | 13793345.9 | 19998089.91 | 9236196 | 9220919 |  |  |  | 61071.45 | 410.75 | 154455 | 158910 |  |  |  | Electric distribution (<69kV) - Overhead | 1.3891 |  | 0 |  | 0 | 1.3891 | TRUE | TRUE | TRUE
7.3.3.14 | Control | 7.3.3.14 Transformers maintenance and replacement | 0 | 858930.12 | 48102836.8179 | 22485216.4745 | 17358716.4745 |  |  |  | 129234.1601 | 108453.55 | 1335043.5552 | 1372543.5552 |  |  |  |  | #N/A |  | #N/A |  | #N/A | 0 | TRUE | TRUE | TRUE
7.3.3.15 | Control | 7.3.3.15 Transmission tower maintenance and replacement | ICQ, ICS, ICX, 70S | 40848309.96 | 60006797.64 | 154981000 | 175000000 |  |  |  | 51008442.53 | 57675555.1978 | 50261232.5 | 53422010 |  |  |  | Electric transmission (69kV+) | 1.3758 |  | 0 |  | 0 | 1.3758 | TRUE | TRUE | TRUE
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution | 08W |  | 286120000 | 366000000 | 265376800 | [10 empty] | Electric distribution (<69kV) - Overhead | 1.3891 |  | 0 |  | 0 | 1.3891 | TRUE | TRUE | TRUE
7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution | 08W |  | 129534000 | 664125000 | 1246649625 |  |  |  |  | -6461778.7103 | -15971792.8846 | -33681808.0124 |  |  |  | Electric distribution (<69kV) - Underground | 1.3891 |  | 0 |  | 0 | 1.3891 | TRUE | TRUE | TRUE
7.3.3.17.3 | Mitigation | 7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs, Surge Arrestor | 2AR | 63497995.35 | 74190939.07 | 33172115.7824 | 17706361.1148 | [10 empty] | Electric distribution (<69kV) - Overhead | 1.3891 |  | 0 |  | 0 | 1.3891 | TRUE | TRUE | TRUE
7.3.3.17.6 | Mitigation | 7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs, Butte County Rebuild | 08W, 95F, IFF | 38716806 | 58736957.58 | 94912351 | 114341000 | [10 empty] | Electric distribution (<69kV) - Overhead | 1.3891 |  | 1.1158 |  | 1.1158 | 2.5049 | TRUE | TRUE | TRUE
Program Spend Allocation to Tranches
Program ID | Type | Program | MAT (optional) | Allocation method | Tranche | Spend USD 2020 | Spend USD 2021 | Spend USD 2022 | Spend USD 2023 | Spend USD 2024 | Spend USD 2025 | Spend USD 2026
7.3.3.1 | Control | 7.3.3.1 Capacitor maintenance and replacement program | KAF, KBC, 2AE, 2BD, 17P, 06A, 06D, 06H, 06K | prorate by Program Exposure
7.3.3.2-D | Control | 7.3.3.2-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Distribution | GCB, GCM, GCS, GCV | prorate by Program Exposure
7.3.3.2-T | Control | 7.3.3.2-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Transmission | AMB, AMM, AMS, AMV | prorate by Program Exposure
7.3.3.4 | Control | 7.3.3.4 Covered conductor maintenance | 0 | prorate by Program Exposure
7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement | 0 | prorate by Program Exposure
7.3.3.6 | Control | 7.3.3.6 Distribution pole replacement and reinforcement, including with composite poles | 07D, 07C, GAD | prorate by Program Exposure
7.3.3.7 | Mitigation | 7.3.3.7 Expulsion fuse replacement | 2AP | prorate by Program Exposure
7.3.3.8.3 | Mitigation | 7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Motorized Switch Operator (MSO) Replacements | 49H | prorate by Program Exposure
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers | 49T | prorate by Program Exposure
7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps | 0 | prorate by Program Exposure
7.3.3.12.3 | Control | 7.3.3.12.3 Other corrective action, Maintenance, Transmission | 0 | prorate by Program Exposure
7.3.3.12.4 | Control | 7.3.3.12.4 Other corrective action, Maintenance, Distribution | 0 | prorate by Program Exposure
7.3.3.13 | Control | 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program | O7O | prorate by Program Exposure
7.3.3.14 | Control | 7.3.3.14 Transformers maintenance and replacement | 0 | prorate by Program Exposure
7.3.3.15 | Control | 7.3.3.15 Transmission tower maintenance and replacement | ICQ, ICS, ICX, 70S | prorate by Program Exposure
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution | 08W | prorate by Program Exposure
7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution | 08W | prorate by Program Exposure
7.3.3.17.3 | Mitigation | 7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs, Surge Arrestor | 2AR | prorate by Program Exposure
7.3.3.17.6 | Mitigation | 7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs, Butte County Rebuild | 08W, 95F, IFF | prorate by Program Exposure
Update Cost Data

## 3-Eff - Freq Programs
Effectiveness for Programs that Modify Frequency | [21 empty] | Qualitative Program Effectiveness Cap for different types of programs affecting event frequency
Dimensions over which effectiveness differs
Please see Instructions for detailed guidance on each column. See 'Control Effectiveness Guidance' documentation for more details on qualitative methodology.
Effectiveness by Model Element | [22 empty] | Risk Driver is Primarily Due to… |  |  |  | Effectiveness Mapping Table
ID | Type | Program | Risk (for Cross Cutter only) | Tranche | Driver | Subdriver | Outcome | Does this use qualitative measure? | Effectiveness - Quantitative | Category | Risk driver primarily due to… | Explanation of Program Category and Risk Driver type | Effectiveness Cap (Ec) | Maturity Factor (Mf) | Effectiveness (Ec * Mf) | Benefit Length (yrs) | Effectiveness Degradation Rate | Effectiveness Degradation Method | Explanation of Benefit Length | Same benefit set across program? | Risk ID | Program Category | Human Error | Functional Failure | Malicious Action | Natural/Outside Force | Program | Tranche | Driver | Subdriver | Outcome
7.3.3.1 | Control | 7.3.3.1 Capacitor maintenance and replacement program |  |  | Equipment / facility failure | Capacitor bank damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | Per the WMP 2022 narrative, "all distribution capacitor banks are inspected as governed by TD-2302B-006 and TD-2302P-05" each year | TRUE | WLDFR | Elimination | 90% | 90% | 90% | 90%
7.3.3.2-D | Control | 7.3.3.2-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Distribution |  |  | Equipment / facility failure | Recloser damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | Since the choice is work unit within Program Exposure tab, the units that are worked on will not cause an ignition within a year with an assumed 90% effectiveness rate per SME judgement. | TRUE | WLDFR | Engineered barrier | 90% | 75% | 50% | 50%
7.3.3.2-T | Control | 7.3.3.2-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Maintenance Substation Transmission |  |  | Equipment / facility failure | Recloser damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | Since the choice is work unit within Program Exposure tab, the units that are worked on will not cause an ignition within a year with an assumed 90% effectiveness rate per SME judgement. | TRUE | WLDFR | Substitution | 75% | 50% | 50% | 0%
7.3.3.4 | Control | 7.3.3.4 Covered conductor maintenance |  |  | Equipment / facility failure | Conductor damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | Since the choice is work unit within Program Exposure tab, the units that are worked on will not cause an ignition within a year with an assumed 90% effectiveness rate per SME judgement. | TRUE | WLDFR | Administrative barrier | 30% | 0% | 0% | 0%
7.3.3.5 | Control | 7.3.3.5 Crossarm maintenance, repair, and replacement |  |  | Equipment / facility failure | Crossarm damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | Since the choice is work unit within Program Exposure tab, the units that are worked on will not cause an ignition within a year with an assumed 90% effectiveness rate per SME judgement. | TRUE | WLDFR | Distance gap | 20% | 0% | 0% | 15%
7.3.3.6 | Control | 7.3.3.6 Distribution pole replacement and reinforcement, including with composite poles |  |  | Equipment / facility failure | Pole damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | Since the choice is work unit within Program Exposure tab, the units that are worked on will not cause an ignition within a year with an assumed 90% effectiveness rate per SME judgement. | TRUE | WLDFR | Detect/Notify/Respond | 10% | 10% | 25% | 10%
7.3.3.7 | Mitigation | 7.3.3.7 Expulsion fuse replacement |  |  | Equipment / facility failure | Fuse damage or failure |  | FALSE | 90% | [5 empty] | 90% | 30 |  |  | SMEs confirmed that 30 years is potentially the benefit length of replacing a non-exempt fuse with an exempt one, which is also industry standard. | TRUE | WLDFR | Minor or preventative main. | 0% | 25% | 5% | 5%
7.3.3.8.3 | Mitigation | 7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Motorized Switch Operator (MSO) Replacements |  |  | Equipment / facility failure | Switch damage or failure |  | FALSE | 90% | [5 empty] | 90% | 30 |  |  | Per the SME, the replaced switches would last for the entire lifetime of the equipment which is expected to be 30 years for distribution | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Contact from object | Animal contact |  | FALSE | 2.18% | [5 empty] | 2.18% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Contact from object | Balloon contact |  | FALSE | 30.73% | [5 empty] | 30.73% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Branch (Not overhanging, > 12ft) |  | FALSE | 22.8% | [5 empty] | 22.8% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Branch (Not overhanging, 4-12ft) |  | FALSE | 21.63% | [5 empty] | 21.63% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Branch (Not overhanging, Distance Unknown) |  | FALSE | 28.21% | [5 empty] | 28.21% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Branch (Not overhanging, within 4ft) |  | FALSE | 0% | [5 empty] | 0% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Branch (OverHanging) |  | FALSE | 24.58% | [5 empty] | 24.58% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Equipment / facility failure | Conductor damage or failure |  | FALSE | 51.23% | [5 empty] | 51.23% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Equipment / facility failure | Connection device damage or failure |  | FALSE | 14.9% | [5 empty] | 14.9% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Equipment / facility failure | Crossarm damage or failure |  | FALSE | 5.612% | [5 empty] | 5.612% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Dead |  | FALSE | 26.33% | [5 empty] | 26.33% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Fell into (Moderate-Severe defect) |  | FALSE | 41.96% | [5 empty] | 41.96% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Fell into (No defect) |  | FALSE | 45.25% | [5 empty] | 45.25% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Fell into (slight defect) |  | FALSE | 45.36% | [5 empty] | 45.36% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Equipment / facility failure | Fuse damage or failure |  | FALSE | 0.218% | [5 empty] | 0.218% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Grow Into |  | FALSE | 9.286% | [5 empty] | 9.286% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Equipment / facility failure | Insulator and brushing damage or failure |  | FALSE | 7.576% | [5 empty] | 7.576% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Equipment / facility failure | Lightning arrestor damage or failure |  | FALSE | 0.2767% | [5 empty] | 0.2767% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Contact from object | Other contact from object |  | FALSE | 20.62% | [5 empty] | 20.62% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Equipment / facility failure | Other equipment / facility failure |  | FALSE | 0.7364% | [5 empty] | 0.7364% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vegetation Contact | Other/Unknown |  | FALSE | 21.32% | [5 empty] | 21.32% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Equipment / facility failure | Pole damage or failure |  | FALSE | 13.59% | [5 empty] | 13.59% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Equipment / facility failure | Switch damage or failure |  | FALSE | 0.7865% | [5 empty] | 0.7865% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Equipment / facility failure | Transformer damage or failure |  | FALSE | 0.7308% | [5 empty] | 0.7308% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Vandalism / Theft | Vandalism / Theft |  | FALSE | 11.88% | [5 empty] | 11.88% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.9.2 | Mitigation | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers |  |  | Contact from object | Vehicle contact |  | FALSE | 26.3% | [5 empty] | 26.3% | 30 |  |  | Per SME Judgement, RCU Electronic Component lasts 30 years | TRUE | WLDFR
7.3.3.10 | Control | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps |  |  | Equipment / facility failure | Connection device damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | Due to the choice of work units in the Program Exposure tab for this program. | TRUE | WLDFR
7.3.3.12.3 | Control | 7.3.3.12.3 Other corrective action, Maintenance, Transmission |  |  | Equipment / facility failure |  |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year | TRUE | WLDFR
7.3.3.12.4 | Control | 7.3.3.12.4 Other corrective action, Maintenance, Distribution |  |  | Equipment / facility failure |  |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year | TRUE | WLDFR
7.3.3.13 | Control | 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program |  |  | Equipment / facility failure | Pole damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year | TRUE | WLDFR
7.3.3.14 | Control | 7.3.3.14 Transformers maintenance and replacement |  |  | Equipment / facility failure | Transformer damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year | TRUE | WLDFR
7.3.3.15 | Control | 7.3.3.15 Transmission tower maintenance and replacement |  |  | Equipment / facility failure | Conductor damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year | TRUE | WLDFR
7.3.3.15 | Control | 7.3.3.15 Transmission tower maintenance and replacement |  |  | Equipment / facility failure | Connection device damage or failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year | TRUE | WLDFR
7.3.3.15 | Control | 7.3.3.15 Transmission tower maintenance and replacement |  |  | Equipment / facility failure | Other equipment / facility failure |  | FALSE | 90% | [5 empty] | 90% | 1 |  |  | For Proactive Asset Maintenance/Replacement Control Programs, the units that are planned for maintenance/replacement are assumed to likely fail if not replaced/maintained. These replacements address a portion of the inherent risk for that particular year. Hence the units replaced in one given year under this program would address the risk for that year alone, so the benefit length assumed is 1 year | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Contact from object | Animal contact |  | FALSE | 58.48% | [5 empty] | 58.48% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Contact from object | Balloon contact |  | FALSE | 75.6% | [5 empty] | 75.6% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Contact from object | Other contact from object |  | FALSE | 52.87% | [5 empty] | 52.87% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Contact from object | Vehicle contact |  | FALSE | 46.48% | [5 empty] | 46.48% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Branch (Not overhanging, > 12ft) |  | FALSE | 52.5% | [5 empty] | 52.5% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Branch (Not overhanging, 4-12ft) |  | FALSE | 65% | [5 empty] | 65% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Branch (Not overhanging, Distance Unknown) |  | FALSE | 47.97% | [5 empty] | 47.97% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Branch (Not overhanging, within 4ft) |  | FALSE | 58.09% | [5 empty] | 58.09% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Branch (Overhanging) |  | FALSE | 46.49% | [5 empty] | 46.49% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Dead |  | FALSE | 53.18% | [5 empty] | 53.18% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Fell into (Moderate-Severe defect) |  | FALSE | 46.25% | [5 empty] | 46.25% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Fell into (No defect) |  | FALSE | 50.75% | [5 empty] | 50.75% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Fell into (slight defect) |  | FALSE | 45.49% | [5 empty] | 45.49% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Grow Into |  | FALSE | 50% | [5 empty] | 50% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact | Other/Unknown |  | FALSE | 48.13% | [5 empty] | 48.13% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Contamination | Contamination |  | FALSE | 30% | [5 empty] | 30% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Anchor / guy damage or failure |  | FALSE | 56.67% | [5 empty] | 56.67% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Capacitor bank damage or failure |  | FALSE | 25% | [5 empty] | 25% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Conductor damage or failure |  | FALSE | 45.36% | [5 empty] | 45.36% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Connection device damage or failure |  | FALSE | 66.28% | [5 empty] | 66.28% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Crossarm damage or failure |  | FALSE | 68.33% | [5 empty] | 68.33% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Fuse damage or failure |  | FALSE | 62.11% | [5 empty] | 62.11% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Insulator and brushing damage or failure |  | FALSE | 57.2% | [5 empty] | 57.2% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Lightning arrestor damage or failure |  | FALSE | 90% | [5 empty] | 90% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Other equipment / facility failure |  | FALSE | 46.4% | [5 empty] | 46.4% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Pole damage or failure |  | FALSE | 44.15% | [5 empty] | 44.15% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Recloser damage or failure |  | FALSE | 45% | [5 empty] | 45% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Sectionalizer damage or failure |  | FALSE | 40% | [5 empty] | 40% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Switch damage or failure |  | FALSE | 83.33% | [5 empty] | 83.33% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Transformer damage or failure |  | FALSE | 63.91% | [5 empty] | 63.91% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure | Voltage regulator / booster damage or failure |  | FALSE | 14.44% | [5 empty] | 14.44% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Other | All Other |  | FALSE | 52% | [5 empty] | 52% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Unknown | Unknown |  | FALSE | 30.71% | [5 empty] | 30.71% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vandalism / Theft | Vandalism / Theft |  | FALSE | 44.17% | [5 empty] | 44.17% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Utility work / Operation | Utility work / Operation |  | FALSE | 0% | [5 empty] | 0% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (OH) | Mitigation | 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | CC - Seismic Scenario | Seismic Scenario |  | FALSE | 50.65% | [5 empty] | 50.65% | 45 |  |  | The life time of overhead hardening project is approximately 45 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Contact from object |  |  | FALSE | 99% | [5 empty] | 99% | 49 |  |  | The life time of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Contamination |  |  | FALSE | 99% | [5 empty] | 99% | 49 |  |  | The life time of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Equipment / facility failure |  |  | FALSE | 99% | [5 empty] | 99% | 49 |  |  | The life time of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Other |  |  | FALSE | 99% | [5 empty] | 99% | 49 |  |  | The life time of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Unknown |  |  | FALSE | 99% | [5 empty] | 99% | 49 |  |  | The life time of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vandalism / Theft |  |  | FALSE | 99% | [5 empty] | 99% | 49 |  |  | The life time of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Vegetation Contact |  |  | FALSE | 99% | [5 empty] | 99% | 49 |  |  | The life time of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.1 (UG) | Mitigation | 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  |  | Wire-to-wire contact |  |  | FALSE | 99% | [5 empty] | 99% | 49 |  |  | The life time of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR
7.3.3.17.3 | Mitigation | 7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs, Surge Arrestor |  |  | Equipment / facility failure | Lightning arrestor damage or failure |  | FALSE | 90% | [5 empty] | 90% | 30 |  |  | Asset life will be between 20 to 40 years. | TRUE | WLDFR
7.3.3.17.5 | Mitigation | 7.3.3.17.5 Updates to grid topology to minimize risk of ignition in HFTDs, Remote Grid |  |  | Equipment / facility failure |  |  | FALSE | 90% | [5 empty] | 90% | 30 |  |  | 0 | TRUE | WLDFR
7.3.3.17.6 | Mitigation | 7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs, Butte County Rebuild | [5 empty] | FALSE | 99% | [5 empty] | 99% | 49 |  |  | Aligned benefit length with System Hardening[Underground],the lifetime of underground hardening project is approximately 49 years, based on an updated economic analysis from System Hardening SMEs | TRUE | WLDFR

## 4-Eff - Conseq Programs
Effectiveness Mapping - Programs that Modify Consequence | [20 empty] | Qualitative Program Effectiveness Cap for different types of programs affecting event frequency
Dimensions over which effectiveness differs
Please see Instructions for detailed guidance on each column. See 'Control Effectiveness Guidance' documentation for more details on qualitative methodology.
Effectiveness by Model Element | [21 empty] | Consequence development happens… |  | Effectiveness Mapping Table
ID | Type | Program | Risk (for Cross Cutter only) | Tranche | Outcome | Attribute | Does this use qualitative measure? | Effectiveness - Quantitative | Category | Consequence develops… | Explanation of Program Category and Consequence type | Effectiveness Cap (Ec) | Maturity Factor (Mf) | Effectiveness (Ec * Mf) | Benefit Length (yrs) | Effectiveness Degradation Rate | Effectiveness Degradation Method | Explanation of Benefit Length, Degradation Rate | Same benefit set across program? | Risk ID | Control Program Category | Rapidly | Gradually | Program | Tranche | Attribute | Outcome
No match in Program Cost tab | No match in Summary of Programs tab | Safety Infrastructure Protection Teams (B) |  |  | Non-Red Flag Warning - Catastrophic Fires | Financial | FALSE | #REF! | [5 empty] | 0% | 1 |  |  | SIPT crews treat poles before a wildfire to prevent them from being damaged during the wildfire. The benefit length is when the wildfire occurs. | TRUE | WLDFR | Replacement | 90% | 100%
[21 empty] | Engineered barrier | 50% | 75%
[21 empty] | Automated response | 25% | 50%
[21 empty] | Manual response | 10% | 25%

## RSE Results
Results for different programs and scenarios
Batch Run Complete 02/24 09:21 with v2.5 and risk data file EO_WLDFR_20220209_SplitByTier_192656_194748_Baseline_rselite_(add 2020).xlsx. WARNING - PVRR multiplier for Capital Cost not specified. Defaulting to 1 WARNING - PVRR multiplier for Capital Cost not specified. Defaulting to 1 WARNING - PVRR multiplier for Capital Cost not specified. Defaulting to 1 WARNING - PVRR multiplier for Capital Cost not specified. Defaulting to 1 WARNING - PVRR multiplier for Capital Cost not specified. Defaulting to 1 WARNING - PVRR multiplier for Capital Cost not specified. Defaulting to 1 WARNING - PVRR multiplier for Capital Cost not specified. Defaulting to 1 WARNING - PVRR multiplier for Capital Cost not specified. Defaulting to 1 WARNING - Program Subdriver Branch (Overhanging) for 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs System Hardening Distribution is not in bowtie Subdriver list for WLDFR WARNING - Batch output table does not exist in RSE Results tab. Writing detailed run table to TableRSE in RSE Lite tab WARNING - Batch output table does not exist in RSE Results tab. Writing detailed run table to TableProgramRR in RSE Lite tab
| Program | 2020 Program Risk Reduction NPV | 2021 Program Risk Reduction NPV | 2022 Program Risk Reduction NPV | 2023 Program Risk Reduction NPV | 2024 Program Risk Reduction NPV | 2025 Program Risk Reduction NPV | 2026 Program Risk Reduction NPV | 2022-2022 Program Risk Reduction NPV | 2020 Program RSE | 2021 Program RSE | 2022 Program RSE | 2023 Program RSE | 2024 Program RSE | 2025 Program RSE | 2026 Program RSE | 2022-2022 Program RSE | 2022-2022 Capital Cost NPV with PVRR ($M) | 2022-2022 Expense Cost NPV ($M) | 2022-2022 Total Cost NPV ($M) | 2022-2022 Program Freq Reduction NPV
| 7.3.3.1 Capacitor maintenance and replacement program | 2320.6936 | 2972.2455 | 2875.0694 |  |  |  |  | 2875.0694 | 218.2871 | 207.593 | 238.1338 |  |  |  |  | 238.1338 | 9.8591 | 2.2142 | 12.0733 | 41.0419
| 7.3.3.2-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault Maintenance Substation Distribution | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 2.4168 | 2.4168 | 0
| 7.3.3.2-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault Maintenance Substation Transmission | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 2.2846 | 2.2846 | 0
| 7.3.3.4 Covered conductor maintenance |  | 57266.3144 | 83346.7426 | 80748.4177 |  |  |  | 83346.7426 |  | 1291.7163 | 1670.0685 | 1731.2646 |  |  |  | 1670.0685 | 41.4825 | 8.4236 | 49.9062 | 256.8242
| 7.3.3.5 Crossarm maintenance repair and replacement | 5007.2401 | 6092.7565 | 7135.6118 | 6913.1716 |  |  |  | 7135.6118 | 94.383 | 73.301 | 102.684 | 110.3008 |  |  |  | 102.684 | 67.0917 | 2.3992 | 69.491 | 37.7559
| 7.3.3.6 Distribution pole replacement and reinforcement including with composite poles | 27698.1532 | 51879.1421 | 55606.446 | 57026.2263 |  |  |  | 55606.446 | 113.6507 | 131.7776 | 140.7824 | 149.0185 |  |  |  | 140.7824 | 391.7478 | 3.2337 | 394.9815 | 324.0435
| 7.3.3.7 Expulsion fuse replacement | 302.1377 | 633.628 | 1123.3279 | 1169.38 |  |  |  | 1123.3279 | 27.7203 | 40.3844 | 24.7226 | 27.5377 |  |  |  | 24.7226 | 45.4372 | 0 | 45.4372 | 2.4384
| 7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events Distribution Line Motorized Switch Operator (MSO) Replacements |  | 0 | 0 | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  |  | 0 | 13.5691 | 0 | 13.5691 | 0
| 7.3.3.9.2 Installation of system automation equipment Single phase reclosers |  | 187.5832 | 197.5349 | 186.4044 |  |  |  | 197.5349 |  | 20.0646 | 34.5818 | 34.9175 |  |  |  | 34.5818 | 5.7121 | 0 | 5.7121 | 0.96291
| 7.3.3.10 Maintenance repair and replacement of connectors including hotline clamps | 47220.7628 | 47167.6669 | 34974.3126 | 33883.9659 |  |  |  | 34974.3126 | 1904.6082 | 1869.1159 | 2110.5075 | 2187.7301 |  |  |  | 2110.5075 | 2.9296 | 13.6419 | 16.5715 | 102.6741
| 7.3.3.12.3 Other corrective action Maintenance Transmission | 4917.1591 | 4645.859 | 4390.5506 | 5355.4044 |  |  |  | 4390.5506 | 8.9545 | 10.3357 | 8.6993 | 11.7816 |  |  |  | 8.6993 | 385.0978 | 119.6033 | 504.7011 | 160.7015
| 7.3.3.12.4 Other corrective action Maintenance Distribution | 173089.2659 | 154284.0933 | 107303.6317 | 134570.9138 |  |  |  | 107303.6317 | 425.9638 | 417.1972 | 395.5788 | 382.2529 |  |  |  | 395.5788 | 183.683 | 87.5742 | 271.2573 | 536.1839
| 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program | 518.7056 | 1414.7331 | 748.638 | 705.7876 |  |  |  | 748.638 | 26.9862 | 50.9274 | 61.6932 | 62.3139 |  |  |  | 61.6932 | 11.9905 | 0.14435 | 12.1348 | 3.901
| 7.3.3.14 Transformers maintenance and replacement | 12.776 | 599.0244 | 332.1382 | 388.3947 |  |  |  | 332.1382 | 12.929 | 12.425 | 14.9196 | 23.7396 |  |  |  | 14.9196 | 21.0142 | 1.2477 | 22.2619 | 4.0819
| 7.3.3.15 Transmission tower maintenance and replacement | 10345.0148 | 9575.4873 | 7455.5469 | 7563.2792 |  |  |  | 7455.5469 | 96.4955 | 68.283 | 30.2769 | 29.4345 |  |  |  | 30.2769 | 199.2726 | 46.9731 | 246.2457 | 110.8652
| 7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs System Hardening Distribution |  | 1837.2929 | 3590.4157 | 1888.6164 |  |  |  | 3590.4157 |  | 4.6228 | 7.5565 | 5.8657 |  |  |  | 7.5565 | 475.1438 | 0 | 475.1438 | 8.3579
| 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs System Hardening Distribution |  | 1363.0844 | 3729.1539 | 7356.4753 |  |  |  | 3729.1539 |  | 7.8577 | 4.4015 | 4.9602 |  |  |  | 4.4015 | 862.1717 | -14.9269 | 847.2448 | 9.1227
| 7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs Surge Arrestor | 469.87 | 646.8703 | 192.0531 | 2.2977 |  |  |  | 192.0531 | 5.3271 | 6.2768 | 4.4597 | 0.10696 |  |  |  | 4.4597 | 43.0643 | 0 | 43.0643 | 2.1632
| 7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs Butte County Rebuild |  | 284.8387 | 258.4742 | 281.518 |  |  |  | 258.4742 |  | 1.936 | 1.1633 | 1.1253 |  |  |  | 1.1633 | 222.1934 | 0 | 222.1934 | 1.7631
Difference from previous WMP or GRC submission:
| Program | NPV Risk Reduction -2020 | NPV Risk Reduction -2021 | NPV Risk Reduction -2022 | NPV Risk Reduction -2023 | NPV Risk Reduction -2024 | NPV Risk Reduction -2025 | NPV Risk Reduction -2026 | NPV Risk Reduction - 2020-2022 Total | Risk Spend Eff - 2020 | Risk Spend Eff - 2021 | Risk Spend Eff - 2022 | Risk Spend Eff - 2023 | Risk Spend Eff - 2024 | Risk Spend Eff - 2025 | Risk Spend Eff - 2026 | Risk Spend Eff - 2020-2022 Total | NPV Capital Cost ($M) - 2020-2022 | NPV Expense Cost ($M) - 2020-2022 | NPV Cost ($M) - 2020-2022 | NPV Freq Reduction - 2020-2022
| 7.3.3.1 Capacitor maintenance and replacement program | 1171.4624 | 1407.4028 | 1998.4025 | 0 | 0 | 0 | 0 | -715.6714 | 84.058 | 63.9821 | 110.4158 | 0 | 0 | 0 | 0 | 101.7189 | -15.5869 | 1.338 | -14.2489 | 6.1618
7.3.3.2-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault Maintenance Substation Distribution
7.3.3.2-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault Maintenance Substation Transmission
| 7.3.3.4 Covered conductor maintenance | -20709.5269 | 38794.0539 | 73114.2148 | 80748.4177 | 0 | 0 | 0 | 33932.4273 | -1074.8133 | 448.3411 | 961.0577 | 1731.2646 | 0 | 0 | 0 | 781.3685 | 6.4537 | -12.1504 | -5.6967 | -164.032
| 7.3.3.5 Crossarm maintenance repair and replacement | -6676.1873 | -2948.0534 | -73.0259 | 6913.1716 | 0 | 0 | 0 | -20797.2632 | -77.6338 | -83.3682 | -69.1432 | 110.3008 | 0 | 0 | 0 | -64.0003 | -98.6207 | 0.53222 | -98.0885 | -280.7907
| 7.3.3.6 Distribution pole replacement and reinforcement including with composite poles | 9316.7462 | 22324.1732 | 25226.2565 | 57026.2263 | 0 | 0 | 0 | -22710.1195 | 38.1839 | 27.8136 | 43.9292 | 149.0185 | 0 | 0 | 0 | 47.7171 | -438.7481 | -7.7933 | -446.5413 | -409.2832
| 7.3.3.7 Expulsion fuse replacement | 302.1377 | 553.9413 | 1049.043 | 1099.3567 | -66.4804 | -63.1544 | -60.0324 | 863.6374 | 27.7203 | 36.5916 | 21.0042 | 23.8737 | -3.6064 | -3.5521 | -3.5008 | 21.1393 | -27.0354 | 0 | -27.0354 | 1.8518
7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events Distribution Line Motorized Switch Operator (MSO) Replacements
| 7.3.3.9.2 Installation of system automation equipment Single phase reclosers | 0 | 17.8077 | 10.9814 | 3.3657 | -177.0936 | -169.3037 | -163.8598 | -495.7609 | 0 | 0.21728 | 12.2754 | 15.609 | -19.4626 | -19.3859 | -19.5483 | 15.1587 | -29.9824 | 0 | -29.9824 | -3.1409
| 7.3.3.10 Maintenance repair and replacement of connectors including hotline clamps | 30427.7299 | 46584.0605 | 34687.4523 | 33883.9659 | 0 | 0 | 0 | 17310.8129 | 72.355 | 1284.4048 | 1578.7378 | 2187.7301 | 0 | 0 | 0 | 460.1437 | 1.3592 | 4.5095 | 5.8687 | -10.0551
7.3.3.12.3 Other corrective action Maintenance Transmission
| 7.3.3.12.4 Other corrective action Maintenance Distribution | 134481.8692 | 125445.603 | 80376.9367 | 134570.9138 | 0 | 0 | 0 | 12931.0497 | 356.0347 | 360.3762 | 316.4741 | 382.2529 | 0 | 0 | 0 | 328.1708 | -924.3112 | -204.4508 | -1128.762 | -204.6186
| 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program | -30467.3891 | -23033.4498 | -14737.3478 | 705.7876 | 0 | 0 | 0 | -70171.6254 | -64.4081 | -30.5707 | 1.4948 | 62.3139 | 0 | 0 | 0 | -17.4349 | -695.5001 | -188.6359 | -884.136 | -575.9564
| 7.3.3.14 Transformers maintenance and replacement | 12.776 | -406.8294 | -510.0046 | -402.6954 | -790.4414 | -786.4918 | -776.7024 | -2812.5875 | 12.929 | -54.1455 | -67.6955 | -59.4615 | -81.0553 | -79.0281 | -76.8086 | -65.0495 | -18.3101 | 1.2477 | -17.0623 | -10.0285
| 7.3.3.15 Transmission tower maintenance and replacement | 10053.9275 | 9045.1739 | 7029.3421 | 7563.2792 | 0 | 0 | 0 | 6207.9415 | 81.5283 | 45.3209 | 7.45 | 29.4345 | 0 | 0 | 0 | 9.896 | 138.1763 | 46.8547 | 185.031 | 95.7514
7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs System Hardening Distribution
| 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs System Hardening Distribution | 0 | -903.2391 | -1279.4624 | 2622.55 | -4277.3523 | -4038.9137 | -3816.1282 | -13137.1656 | 0 | 2.1554 | -1.4153 | -1.1245 | -6.0767 | -6.1201 | -6.1645 | -1.7075 | -1898.7317 | -14.9269 | -1913.6586 | -30.1246
| 7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs Surge Arrestor | 469.87 | -115.654 | -1283.2625 | -1439.8443 | -1268.043 | -1099.623 | -864.0654 | -4481.8203 | 5.3271 | 1.9461 | 0.071415 | -4.4334 | -4.4082 | -4.385 | -4.6421 | -0.024966 | -1022.0832 | 22.954 | -999.1291 | -9.5653
| 7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs Butte County Rebuild | 0 | 216.9109 | 253.366 | 279.5796 | -3.5521 | -3.3486 | -3.1583 | 246.4768 | 0 | 1.3856 | 0.92913 | 1.0354 | -0.088313 | -0.086739 | -0.085237 | 1.076 | 84.7667 | 0 | 84.7667 | -12.8743
| 0 | 0 | -179.4705 | -244.9513 | -267.138 | -215.4328 | -133.1763 | 0 | -615.7471 | 0 | -1.7464 | -1.1024 | -1.0678 | -1.0036 | -0.90315 | 0 | -1.0056 | -612.2906 | 0 | -612.2906 | -4.4203
Percentage difference:
Justification for the difference | Program | NPV Risk Reduction -2020 | NPV Risk Reduction -2021 | NPV Risk Reduction -2022 | NPV Risk Reduction -2023 | NPV Risk Reduction -2024 | NPV Risk Reduction -2025 | NPV Risk Reduction -2026 | NPV Risk Reduction - 2020-2022 Total | Risk Spend Eff - 2020 | Risk Spend Eff - 2021 | Risk Spend Eff - 2022 | Risk Spend Eff - 2023 | Risk Spend Eff - 2024 | Risk Spend Eff - 2025 | Risk Spend Eff - 2026 | Risk Spend Eff - 2020-2022 Total | NPV Capital Cost ($M) - 2020-2022 | NPV Expense Cost ($M) - 2020-2022 | NPV Cost ($M) - 2020-2022 | NPV Freq Reduction - 2020-2022
Number of expense units increased significantly between last WMP and this WMP. Methodology to define programs exposure changed - used 'Work Unit' choice this time compared to '% of Tranche Expousre" last time, multiplying directly the number of Capacitors worked on by the Ignition to Outage rate of Capacitors. | 7.3.3.1 Capacitor maintenance and replacement program | 101.9% | 89.94% | 228% |  |  |  |  | -19.93% | 62.62% | 44.55% | 86.45% |  |  |  |  | 74.57% | -61.25% | 152.7% | -54.13% | 17.67%
7.3.3.2-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault Maintenance Substation Distribution
7.3.3.2-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault Maintenance Substation Transmission
Due to the choice of Work Units in exposure calculations. | 7.3.3.4 Covered conductor maintenance | -100% | 210% | 714.5% |  |  |  |  | 68.67% | -100% | 53.16% | 135.5% |  |  |  |  | 87.92% | 18.42% | -59.06% | -10.25% | -38.98%
Due to the choice of Work Units in exposure calculations. | 7.3.3.5 Crossarm maintenance repair and replacement | -57.14% | -32.61% | -1.013% |  |  |  |  | -74.45% | -45.13% | -53.21% | -40.24% |  |  |  |  | -38.4% | -59.51% | 28.51% | -58.53% | -88.15%
Due to the choice of Work Units in exposure calculations. GRC has the programs/MAT codes split. Not exactly adding up and hence difficult to compare. | 7.3.3.6 Distribution pole replacement and reinforcement including with composite poles | 50.69% | 75.53% | 83.04% |  |  |  |  | -29% | 50.6% | 26.75% | 45.36% |  |  |  |  | 51.27% | -52.83% | -70.67% | -53.06% | -55.81%
The miles covered per expulsion fuse replacement assumption changed from 4.33 to 1.37 per SME input, which caused a decrease in exposure values. However the effectiveness % increased from 38% to 90% as the SME did not agree with the earlier assumption that fuse is only 42% of the cutout assembly. | 7.3.3.7 Expulsion fuse replacement |  | 695.1% | 1412% | 1570% | -100% | -100% | -100% | 332.6% |  | 964.8% | 564.9% | 651.6% | -100% | -100% | -100% | 589.9% | -37.3% |  | -37.3% | 315.7%
7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events Distribution Line Motorized Switch Operator (MSO) Replacements
Same methodology as GRC. The forecast between GRC and WMP are very similar under same MAT 49T. However the unit forecast are way off. Used the units provided in the financial, which has no work in non-HFTD and no work in the year 2020. | 7.3.3.9.2 Installation of system automation equipment Single phase reclosers |  | 10.49% | 5.886% | 1.839% | -100% | -100% | -100% | -71.51% |  | 1.095% | 55.03% | 80.84% | -100% | -100% | -100% | 78.05% | -84% |  | -84% | -76.54%
Choice of work units in program exposure tab. | 7.3.3.10 Maintenance repair and replacement of connectors including hotline clamps | 181.2% | 7982% | 12092% |  |  |  |  | 98% | 3.949% | 219.7% | 296.9% |  |  |  |  | 27.88% | 86.55% | 49.38% | 54.83% | -8.92%
(compare to previous WMP) Program expousre methodology change from % of tranche exposure to expousre units. Effectiveness also changed to 90% based on SME judgement, from a qualitative measure used last time around. | 7.3.3.12.3 Other corrective action Maintenance Transmission
Change in sub-driver choices - Applied effectiveness to all equipment failure sub-drivers. Change in methodology of using Work unit choice. Updated ignition to outage rate for all equipment failure drivers. | 7.3.3.12.4 Other corrective action Maintenance Distribution | 348.3% | 435% | 298.5% |  |  |  |  | 13.7% | 509.1% | 634.2% | 400.1% |  |  |  |  | 486.8% | -83.42% | -70.01% | -80.62% | -27.62%
Change in sub-driver choices - Applied effectiveness to all equipment failure sub-drivers. Change in methodology of using Work unit choice. Updated ignition to outage rate for all equipment failure drivers. | 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program | -98.33% | -94.21% | -95.17% |  |  |  |  | -98.94% | -70.47% | -37.51% | 2.483% |  |  |  |  | -22.03% | -98.31% | -99.92% | -98.65% | -99.33%
Compared to GRC. Instead of multiplying effectiveness with ignition to outage rate like in GRC, multiplied exposure with ignition to outage rate. Costs are different between GRC and current WMP, with current WMP having OPEX costs uder the same MAT code 07O. | 7.3.3.14 Transformers maintenance and replacement |  | -40.45% | -60.56% | -50.9% | -100% | -100% | -100% | -89.44% |  | -81.34% | -81.94% | -71.47% | -100% | -100% | -100% | -81.34% | -46.56% |  | -43.39% | -71.07%
Methodology change - used the choice of work unit in Program Exposure tab | 7.3.3.15 Transmission tower maintenance and replacement | 3454% | 1706% | 1649% |  |  |  |  | 497.6% | 544.7% | 197.4% | 32.64% |  |  |  |  | 48.56% | 226.2% | 39583% | 302.3% | 633.5%
7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs System Hardening Distribution
| 7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs System Hardening Distribution |  | -39.85% | -25.55% | 55.4% | -100% | -100% | -100% | -77.89% |  | 37.8% | -24.33% | -18.48% | -100% | -100% | -100% | -27.95% | -68.77% |  | -69.31% | -76.76%
| 7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs Surge Arrestor |  | -15.17% | -86.98% | -99.84% | -100% | -100% | -100% | -95.89% |  | 44.94% | 1.627% | -97.64% | -100% | -100% | -100% | -0.5567% | -95.96% | -100% | -95.87% | -81.56%
The miles were input directly (exposure unit choice) rather than the % of tranche exposure as in GRC filing. Units and financials have changed between GRC and current WMP. | 7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs Butte County Rebuild |  | 319.3% | 4960% | 14423% | -100% | -100% | -100% | 2054% |  | 251.8% | 396.8% | 1151% | -100% | -100% | -100% | 1233% | 61.68% |  | 61.68% | -87.95%
Program exposure is input as miles with exposure unit choice, unlike last WMP that used % of tranche exposure. Units and financials have changed since last WMP. For effectiveness, last submission had all drivers chosen, but the new run no choice was made (assuming no choice would apply effectiveness value across all drivers) | 0 |  | -100% | -100% | -100% | -100% | -100% |  | -100% |  | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% |  | -100% | -100%
Previous WMP submission:
| Program | NPV Risk Reduction -2020 | NPV Risk Reduction -2021 | NPV Risk Reduction -2022 | NPV Risk Reduction -2023 | NPV Risk Reduction -2024 | NPV Risk Reduction -2025 | NPV Risk Reduction -2026 | NPV Risk Reduction - 2020-2022 Total | Risk Spend Eff - 2020 | Risk Spend Eff - 2021 | Risk Spend Eff - 2022 | Risk Spend Eff - 2023 | Risk Spend Eff - 2024 | Risk Spend Eff - 2025 | Risk Spend Eff - 2026 | Risk Spend Eff - 2020-2022 Total | NPV Capital Cost ($M) - 2020-2022 | NPV Expense Cost ($M) - 2020-2022 | NPV Cost ($M) - 2020-2022 | NPV Freq Reduction - 2020-2022
| 7.3.3.1_Capacitor maintenance and replacement program | 1149.2313 | 1564.8426 | 876.6669 |  |  |  |  | 3590.7407 | 134.2291 | 143.6109 | 127.7179 |  |  |  |  | 136.4149 | 25.446 | 0.87625 | 26.3222 | 34.8801
| 7.3.3.4_Covered conductor maintenance | 20709.5269 | 18472.2605 | 10232.5278 |  |  |  |  | 49414.3153 | 1074.8133 | 843.3752 | 709.0108 |  |  |  |  | 888.7 | 35.0289 | 20.574 | 55.6029 | 420.8561
| 7.3.3.5_Crossarm maintenance, repair, and replacement | 11683.4273 | 9040.81 | 7208.6376 |  |  |  |  | 27932.8749 | 172.0168 | 156.6691 | 171.8273 |  |  |  |  | 166.6844 | 165.7125 | 1.867 | 167.5795 | 318.5466
| 7.3.3.6_Distribution pole replacement and reinforcement, including with composite poles | 18381.407 | 29554.9689 | 30380.1895 |  |  |  |  | 78316.5654 | 75.4668 | 103.964 | 96.8532 |  |  |  |  | 93.0653 | 830.4959 | 11.027 | 841.5228 | 733.3268
| 7.3.3.7_Expulsion fuse replacement | 204.1007 | 354.0305 | 332.7692 |  |  |  |  | 890.9004 | 26.0115 | 25.069 | 24.732 |  |  |  |  | 25.1497 | 35.4238 | 0 | 35.4238 | 4.6623
| 7.3.3.10_Maintenance, repair, and replacement of connectors, including hotline clamps | 16793.033 | 583.6064 | 286.8603 |  |  |  |  | 17663.4997 | 1832.2532 | 584.7112 | 531.7697 |  |  |  |  | 1650.3639 | 1.5704 | 9.1323 | 10.7028 | 112.7292
| 7.3.3.12.3_Other corrective action | 38607.3967 | 28838.4903 | 26926.695 |  |  |  |  | 94372.582 | 69.929 | 56.821 | 79.1047 |  |  |  |  | 67.4081 | 1107.9942 | 292.025 | 1400.0192 | 740.8025
| 7.3.3.12.4_Other corrective action | 30986.0947 | 24448.1829 | 15485.9858 |  |  |  |  | 70920.2634 | 91.3943 | 81.4982 | 60.1985 |  |  |  |  | 79.1282 | 707.4906 | 188.7802 | 896.2709 | 579.8574
| 7.3.3.13_Pole loading infrastructure hardening and replacement program based on pole loading assessment program | 354.0333 | 558.4214 | 1.6207 |  |  |  |  | 914.0754 | 25.7061 | 48.0747 | 0.22698 |  |  |  |  | 28.1011 | 32.5281 | 0 | 32.5281 | 13.678
| 7.3.3.14_Transformers maintenance and replacement | 291.0872 | 530.3134 | 426.2048 |  |  |  |  | 1247.6054 | 14.9672 | 22.9621 | 22.8269 |  |  |  |  | 20.3808 | 61.0963 | 0.11837 | 61.2147 | 15.1138
| 7.3.3.17.1_Updates to grid topology to minimize risk of ignition in HFTDs | 2386.268 | 1133.6339 | 2746.7792 |  |  |  |  | 6266.6811 | 5.1859 | 3.5878 | 3.6118 |  |  |  |  | 4.0783 | 1536.6044 | 0 | 1536.6044 | 33.0002
| 7.3.3.17.3_Updates to grid topology to minimize risk of ignition in HFTDs | 102.0567 | 221.8796 | 0.95428 |  |  |  |  | 324.8906 | 1.6072 | 2.6743 | 0.064947 |  |  |  |  | 2.016 | 161.1596 | 0 | 161.1596 | 6.607
| 7.3.3.17.4_Updates to grid topology to minimize risk of ignition in HFTDs | 608.7329 |  | 895.278 |  |  |  |  | 1504.0109 | 31.3013 |  | 40.8335 |  |  |  |  | 36.3528 | 34.9473 | 6.4253 | 41.3727 | 7.9958
| 7.3.3.17.6_Grid topology improvements to mitigate or reduce PSPS events | 253.3194 | 170.7675 | 160.5291 |  |  |  |  | 584.6159 | 8.5018 | 3.415 | 3.3219 |  |  |  |  | 4.5629 | 128.1247 | 0 | 128.1247 | 4.4271
GRC 2023 Results:
| Program | NPV Risk Reduction -2020 | NPV Risk Reduction -2021 | NPV Risk Reduction -2022 | NPV Risk Reduction -2023 | NPV Risk Reduction -2024 | NPV Risk Reduction -2025 | NPV Risk Reduction -2026 | NPV Risk Reduction - 2023-2026 Total | Risk Spend Eff - 2020 | Risk Spend Eff - 2021 | Risk Spend Eff - 2022 | Risk Spend Eff - 2023 | Risk Spend Eff - 2024 | Risk Spend Eff - 2025 | Risk Spend Eff - 2026 | Risk Spend Eff - 2023-2026 Total | NPV Capital Cost with PVRR ($M) - 2023-2026 | NPV Expense Cost ($M) - 2023-2026 | NPV Cost ($M) - 2023-2026 | NPV Freq Reduction - 2023-2026
| Enhanced Vegetation Management |  | 2107.8071 | 1989.9163 | 1890.9247 | 1788.0854 | 1691.974 | 1602.1502 | 6973.1343 |  | 3.9328 | 3.8439 | 3.9313 | 3.8833 | 3.8383 | 3.8146 | 3.8691 | 0 | 1802.2639 | 1802.2639 | 26.1535
| System Hardening [Overhead] |  | 2266.3235 | 5008.6163 | 4733.9253 | 4277.3523 | 4038.9137 | 3816.1282 | 16866.3195 |  | 5.7022 | 5.8168 | 6.0847 | 6.0767 | 6.1201 | 6.1645 | 6.109 | 2760.9034 | 0 | 2760.9034 | 39.2473
| System Hardening [Underground] |  | 762.5243 | 1475.3156 | 1442.142 | 1268.043 | 1099.623 | 864.0654 | 4673.8734 |  | 4.3307 | 4.3883 | 4.5404 | 4.4082 | 4.385 | 4.6421 | 4.4847 | 1065.1475 | -22.954 | 1042.1934 | 11.7285
| Non-Exempt Surge Arrester Replacement Program |  | 67.9278 | 5.1082 | 1.9384 | 3.5521 | 3.3486 | 3.1583 | 11.9974 |  | 0.55032 | 0.23415 | 0.089965 | 0.088313 | 0.086739 | 0.085237 | 0.087301 | 137.4267 | 0 | 137.4267 | 14.6374
| Expulsion Fuse Replacement |  | 79.6868 | 74.2848 | 70.0233 | 66.4804 | 63.1544 | 60.0324 | 259.6905 |  | 3.7928 | 3.7184 | 3.664 | 3.6064 | 3.5521 | 3.5008 | 3.5833 | 72.4727 | 0 | 72.4727 | 0.58653
| Situational Awareness and Forecasting Initiatives - Line Sensors |  | 1725.5369 | 1215.2348 | 863.5344 | 611.2656 | 433.0995 | 307.7106 | 2215.61 |  | 62.9056 | 28.2301 | 22.9217 | 19.316 | 14.9008 | 11.0306 | 17.5452 | 126.2804 | 0 | 126.2804 | 10.8536
| Situational Awareness and Forecasting Initiatives - EFD |  | 184.3485 | 519.2483 | 818.9087 | 928.5497 | 1024.276 | 1107.5496 | 3879.2839 |  | 51.9012 | 47.7261 | 68.8736 | 72.8438 | 71.5999 | 70.5843 | 71.0051 | 54.6339 | 0 | 54.6339 | 15.0973
| Situational Awareness and Forecasting Initiatives - Cameras |  | 1314.5404 | 1202.5304 |  |  |  |  | 0 |  | 140.0641 | 111.5785 |  |  |  |  | 0 | 0 | 0 | 0 | 0
| Situational Awareness and Forecasting Initiatives - Satellite Fire Detection |  | 59.8118 | 52.4652 | 50.8544 | 47.5275 | 44.4182 | 41.5123 | 184.3123 |  | 175.5762 | 159.8956 | 160.8024 | 156.5459 | 152.4019 | 148.3676 | 154.741 | 0 | 1.1911 | 1.1911 | 0.043383
| Situational Awareness and Forecasting Initiatives - Cameras [Control] |  |  |  | 152.3203 | 143.8529 | 136.0092 | 128.7275 | 560.9099 |  |  |  | 21.1801 | 19.9663 | 18.8462 | 17.8113 | 19.4487 | 0 | 28.8405 | 28.8405 | 0.09083
| Situational Awareness and Forecasting Initiatives - Partial Voltage Technologies [Control] |  |  | 62.2259 | 58.8764 | 55.5047 | 52.5407 | 49.8016 | 216.7233 |  |  | 79.2904 | 289.6024 | 284.3957 | 280.4283 | 276.8865 | 283.0434 | 0 | 0.76569 | 0.76569 | 0.045856
| Situational Awareness and Forecasting Initiatives - Partial Voltage Technologies |  | 303.2342 | [5 empty] | 0 |  | 365.7124 | [5 empty] | 0 | 0 | 0 | 0 | 0
| Safety Infrastructure Protection Teams (B) |  | 27.9036 | 24.4445 | 23.7116 | 22.1603 | 20.7106 | 19.3557 | 85.9382 |  | 0.90941 | 0.93845 | 1.0249 | 0.9895 | 0.96969 | 0.94387 | 0.98333 | 2.1659 | 85.2294 | 87.3953 | 0
| Additional System Automation and Protection - FuseSaver |  | 169.7755 | 186.5535 | 183.0388 | 177.0936 | 169.3037 | 163.8598 | 693.2958 |  | 19.8473 | 22.3064 | 19.3085 | 19.4626 | 19.3859 | 19.5483 | 19.423 | 35.6945 | 0 | 35.6945 | 4.1038
| Additional System Automation and Protection - REFCL |  |  | 945.7472 | 894.4917 | 844.8749 | 798.504 | 755.1667 | 3293.0373 |  |  | 23.939 | 23.5897 | 23.213 | 22.8579 | 22.5226 | 23.064 | 142.7781 | 0 | 142.7781 | 20.2903
| Butte County Rebuild |  | 179.4705 | 244.9513 | 267.138 | 215.4328 | 133.1763 |  | 615.7471 |  | 1.7464 | 1.1024 | 1.0678 | 1.0036 | 0.90315 |  | 1.0056 | 612.2906 | 0 | 612.2906 | 4.4203
| Pole Programs - Replace Tree Attachments |  |  | 2.796 | 2.5755 | 2.5189 | 2.4535 | 2.3894 | 9.9374 |  |  | 0.36161 | 0.3571 | 0.35198 | 0.34616 | 0.34096 | 0.34911 | 28.4646 | 0 | 28.4646 | 0.055785
| System Hardening [Remote Grid] |  | 382.3314 | 584.2862 | 552.2366 | 1142.4965 | 1495.152 | 1609.3381 | 4799.2232 |  | 29.3585 | 30.0945 | 29.8919 | 32.2052 | 32.3811 | 32.5308 | 32.0815 | 137.0719 | 12.523 | 149.5949 | 11.3253
| Patrols - Distribution Overhead |  | 502.6937 | 459.5152 | 668.2587 | 624.5409 | 583.6831 | 545.4982 | 2421.9809 |  | 129.1893 | 126.1753 | 165.2432 | 170.669 | 169.172 | 163.8943 | 167.2402 | 0 | 14.4821 | 14.4821 | 16.3423
| Inspections - Distribution Overhead |  | 9208.4954 | 8417.3291 | 4267.2396 | 3988.0744 | 3727.1724 | 3483.3387 | 15465.8251 |  | 98.644 | 148.7827 | 83.0774 | 85.8053 | 85.0526 | 82.3992 | 84.0814 | 0 | 183.9387 | 183.9387 | 118.2735
| Infrared Inspections - Distribution Overhead |  | 128.7352 | 117.6737 | 113.2546 | 105.8454 | 98.921 | 92.4495 | 410.4706 |  | 55.4893 | 54.193 | 49.976 | 51.6169 | 51.1642 | 49.568 | 50.5799 | 0 | 8.1153 | 8.1153 | 1.6675
| Patrols and Inspections - Substation |  | 433.3948 | 395.7909 | 381.0105 | 356.0846 | 332.7893 | 311.0181 | 1380.9025 |  | 147.1818 | 143.6109 | 139.3836 | 135.6939 | 132.1019 | 128.605 | 134.1294 | 0 | 10.2953 | 10.2953 | 28.8023
| Vegetation Management - Distribution Overhead |  | 2637726.0689 | 2217013.9704 | 2132985.2751 | 1993444.1823 | 1863031.9461 | 1741151.3515 | 7730612.7551 |  | 3947.965 | 4053.4963 | 4245.3883 | 4135.1138 | 4017.3187 | 3910.7865 | 4082.7774 | 0 | 1893.4691 | 1893.4691 | 56067.1423
| Vegetation Management - CEMA/Tree Mortality |  | 220644.4545 | 201218.7923 | 193730.882 | 182747.1355 | 172294.6681 | 162439.0043 | 711211.6899 |  | 3245.8371 | 3122.5894 | 3134.0911 | 3059.1421 | 2985.9855 | 2914.5783 | 3026.6069 | 0 | 234.9865 | 234.9865 | 2643.0464
| Pole Replacement |  | 46515.2023 | 48685.5689 | 41640.0187 | 39921.697 | 36309.4577 | 33079.3969 | 150950.5703 |  | 111.2477 | 105.5512 | 93.1651 | 90.7136 | 88.3323 | 86.0043 | 89.7066 | 1682.7139 | 0 | 1682.7139 | 784.342
| Intrusive Wood Pole Inspection Program |  | 8640.1574 | 8468.1789 | 7200.1098 | 6235.7279 | 5674.503 | 5311.1151 | 24421.4557 |  | 407.0349 | 426.2371 | 426.9012 | 413.9447 | 401.3815 | 389.1996 | 408.9749 | 0 | 59.7138 | 59.7138 | 318.5238
| Overloaded Pole Replacements |  | 1005.8539 | 842.1428 | 791.0901 | 790.4414 | 786.4918 | 776.7024 | 3144.7256 |  | 66.5704 | 82.6151 | 83.2011 | 81.0553 | 79.0281 | 76.8086 | 79.9691 | 39.3243 | 0 | 39.3243 | 14.1104
| Equipment Maintenance and Replacement – Distribution Overhead |  | 62495.6621 | 49777.85 | 52141.7886 | 44290.9916 | 41062.81 | 38542.02 | 176037.6102 |  | 167.434 | 162.2527 | 173.6937 | 157.4931 | 152.0685 | 145.8488 | 157.7812 | 949.8795 | 165.8278 | 1115.7073 | 1409.1392
| Animal Abatement |  | 5.3601 | 6.5305 | 6.1762 | 5.9118 | 5.5262 | 5.5758 | 23.19 |  | 0.29064 | 0.35162 | 0.34998 | 0.34374 | 0.34196 | 0.36717 | 0.35034 | 58.1384 | 8.0537 | 66.192 | 4.6266
| Pole Restoration Program |  | 4948.4538 | 4521.1464 | 4676.1576 | 4370.2407 | 4084.3371 | 3817.1375 | 16947.8729 |  | 1431.0136 | 1396.9282 | 1364.2896 | 1324.7915 | 1285.9639 | 1249.2012 | 1307.8973 | 0 | 12.9581 | 12.9581 | 221.0475
| Proactive Asset Replacement - Ground Grid |  | 0.039189 | 0.091707 | 0.031412 | 0.019432 | 0.017471 | 0.016264 | 0.084579 |  | 0.0064159 | 0.0061375 | 0.0061353 | 0.0059508 | 0.0057719 | 0.0055984 | 0.0059075 | 14.3174 | 0 | 14.3174 | 0.11254
| Substation Proactive Asset Replacement - Breakers |  | 3.7147 | 7.1975 | 6.1419 | 6.2346 | 6.0887 | 4.6981 | 23.1634 |  | 0.18713 | 0.17739 | 0.17722 | 0.17189 | 0.16672 | 0.16171 | 0.1697 | 136.4992 | 0 | 136.4992 | 0.9004
| Substation Proactive Asset Replacement - Switches |  | 0.1178 | 0.38171 | 0.22334 | 0.41586 | 0.38714 | 0.27031 | 1.2967 |  | 0.089714 | 0.085049 | 0.084971 | 0.082416 | 0.079938 | 0.077535 | 0.081022 | 16.0036 | 0 | 16.0036 | 0.07038
| Substation Proactive Asset Replacement - Switchgear |  | 1.2697 | 1.312 | 1.2707 | 0.59273 | 0.53401 | 0.45676 | 2.8542 |  | 0.034098 | 0.032321 | 0.032291 | 0.03132 | 0.030379 | 0.029465 | 0.031243 | 91.3551 | 0 | 91.3551 | 0.11095
| Substation Proactive Asset Replacement - Insulators |  |  | 0.67829 | 6.5043 | 6.0555 | 5.6372 | 5.248 | 23.445 |  |  | 0.99074 | 0.98982 | 0.96006 | 0.9312 | 0.9032 | 0.94755 | 24.7427 | 0 | 24.7427 | 0.80566
| Substation Proactive Asset Replacement - Batteries |  | 0.0040408 | 0.060251 | 0.060474 | 0.056301 | 0.052413 | 0.048793 | 0.21798 |  | 0.01604 | 0.015344 | 0.015338 | 0.014877 | 0.01443 | 0.013996 | 0.014683 | 14.8456 | 0 | 14.8456 | 0.29004
| Substation Proactive Asset Replacement - Transformer |  | 0.70946 | 0.40066 | 0.27136 | 0.36851 | 0.39644 | 0.39542 | 1.4317 |  | 0.014747 | 0.013979 | 0.013967 | 0.013547 | 0.013139 | 0.012744 | 0.013277 | 107.8323 | 0 | 107.8323 | 0.06504
| Substation Security Enhancements |  | 0.00010055 | 9.4073e-05 | 8.8507e-05 | 8.3201e-05 | 7.8241e-05 | 7.3607e-05 | 0.00032356 |  | 5.9243e-05 | 2.3812e-05 | 8.1187e-06 | 7.315e-06 | 8.9589e-06 | inf | 1.0434e-05 | 31.009 | 0 | 31.009 | 1.0539e-05
| Fire Protection / Fire Suppression Systems Substation |  | 198.7564 | 185.9523 | 174.9505 | 164.4612 | 154.658 | 145.4962 | 639.5659 |  | 47.1999 | 20487.9019 | 24.607 | 24.0991 | 70.8357 | 69.4301 | 35.1158 | 18.2131 | 0 | 18.2131 | 20.8324
| Vegetation Management - Substation |  | 4.5579 | 4.1615 | 3.9938 | 3.7325 | 3.4883 | 3.2601 | 14.4748 |  | 0.58409 | 0.56712 | 0.46168 | 0.41948 | 0.59226 | 0.50868 | 0.48496 | 0 | 29.8475 | 29.8475 | 0.2305
Start Batch Run

## Table_12_RSE
index | (Multiple Items)
Row Labels | Sum of 2022 Program Risk Reduction NPV | Sum of 2022-2022 Capital Cost NPV with PVRR | Sum of 2022-2022 Expense Cost NPV | Sum of 2022 RSE
7.3.3.1 Capacitor maintenance and replacement program | 2687.6383 | 2122724.979 | 476739.465 | 1033.92
7.3.3.10 Maintenance repair and replacement of connectors including hotline clamps | 30431.1876 | 1942937.8335 | 9047266.6703 | 2768.9373
7.3.3.12.3 Other corrective action Maintenance Transmission | 3159.4535 | 89695705.6469 | 27857606.2437 | 26.8768
7.3.3.12.4 Other corrective action Maintenance Distribution | 95764.5132 | 83172932.1505 | 39654214.041 | 779.669
7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program | 674.4743 | 7154472.9235 | 86130.8511 | 93.1517
7.3.3.14 Transformers maintenance and replacement | 297.4832 | 9792975.56 | 581450.8801 | 28.6747
7.3.3.15 Transmission tower maintenance and replacement | 4706.2321 | 86084450.4064 | 20292077.1848 | 44.2413
7.3.3.17.1 (OH) Updates to grid topology to minimize risk of ignition in HFTDs System Hardening Distribution | 3164.9599 | 399028057.4024 | 0 | 7.9317
7.3.3.17.1 (UG) Updates to grid topology to minimize risk of ignition in HFTDs System Hardening Distribution | 3276.7175 | 724056034.4873 | -12535691.089 | 4.6052
7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs Surge Arrestor | 173.8589 | 23408951.6765 | 0 | 7.427
7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs Butte County Rebuild | 215.9398 | 132538971.6012 | 0 | 1.6293
7.3.3.4 Covered conductor maintenance | 74032.0385 | 21190581.0849 | 4303064.8514 | 2903.9408
7.3.3.5 Crossarm maintenance repair and replacement | 6288.7319 | 20851727.6152 | 745663.8977 | 291.1802
7.3.3.6 Distribution pole replacement and reinforcement including with composite poles | 50054.1073 | 208830246.2239 | 1723780.2077 | 237.7257
7.3.3.7 Expulsion fuse replacement | 925.0296 | 28013014.3874 | 0 | 33.0214
7.3.3.9.2 Installation of system automation equipment Single phase reclosers | 163.4176 | 4111351.3961 | 0 | 39.7479
Grand Total | 276015.7829 | 1841995135.3746 | 92232303.2039

## Ignition Frequency
Source file: | RiskInputs_v1.2.1_EO_WLDFR_20211123_ClimateConseqMult.xlsx
Source file location: | RMC -> Model > Risk Scores -> 0_Working Folder
tranche | outcome | driver | subdriver | frequency
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.9222e-07 |  | 337.347 | 2015-2020 frequency
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00067736 | animal contact | 56.2245 | Annual frequency (2015-2020)
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 3.1214e-05 | capacitor bank damage or failure | 9.5035
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00020851 | sectionalizer damage or failure | 0.16667
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00084758 |  | 146.2082
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 3.3e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 4.2946e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 2.6964e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 4.097e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.0036e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.2162e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.9714e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3526e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.2542e-08
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.8113e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.6951e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 7.8326e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.013e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00050904
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00074857
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0.00012101
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.5974e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8377e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.5062e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.5382e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.6303e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.3955e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.6366e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.8719e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00011026
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.3141e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.003e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 9.4978e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0015655
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00056586
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.8845e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00018654
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00054943
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.0252e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.5205e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 9.2455e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00020715
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00011248
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.2667e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 7.0538e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.6312e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.8058e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.9881e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.0666e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.7605e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.9841e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00047
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00070779
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0.00010592
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.7165e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.5799e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.1231e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.8339e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.9013e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 8.461e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.079e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.6654e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00027481
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 5.7676e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.9922e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00023672
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0014936
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0019822
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 4.2088e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00066307
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0023601
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 8.6874e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 7.1744e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00049662
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0012834
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00046563
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00010361
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 4.7685e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.0506e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.313e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00034472
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0001252
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0001509
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.0434e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0011892
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0020164
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00036286
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00012736
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.6369e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.3879e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00021806
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1078e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00049298
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.000232
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00026535
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.001563
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00032803
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.8393e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0013464
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0037462
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.10901
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0029354
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.046415
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.10079
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0046187
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0010079
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.085843
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.21248
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.12889
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.012699
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0064323
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0036766
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00030094
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.057642
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.021393
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.018174
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00045496
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.081663
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.13445
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.020575
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0061901
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0021573
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0052096
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.017784
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00090905
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.040453
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.01892
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.021641
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.12747
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.026753
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0023156
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.1098
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.27556
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 8.29e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00030954
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.0031011
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.018667
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0063809
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.0013241
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0012704
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0010793
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.6506e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0025833
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.0013566
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00070847
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.3678e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00029407
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00046723
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0022583
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.9817e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0041192
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0017132
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0014072
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0057625
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0015167
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00015965
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0077872
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 5.5153e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0.00053514
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0047501
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.0018028
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00026245
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00022878
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00018598
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.5845e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00057338
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00027207
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00012566
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.2865e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.6882e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.8607e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00028327
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.7554e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00051657
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00021489
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00017651
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00072282
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00019025
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.0026e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00097679
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00014249
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.0015739
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.016113
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0040862
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0011754
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0008468
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00067077
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.8252e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0013548
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00060816
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00037612
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.095e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00011627
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00018251
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00088213
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.7931e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.001648
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0006692
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00054967
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.002251
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00059246
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 6.2364e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0030418
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0020816
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 9.7924e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0015994
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0041114
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 5.0224e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00031321
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0042568
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.041742
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.017698
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0022541
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0017873
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0012649
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 6.5457e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0035447
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0016261
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00070876
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.1796e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0024358
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0057073
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00055109
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00010397
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00085778
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0013422
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0064875
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00020669
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.012195
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0049216
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0040425
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.016554
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0043572
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00045865
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.022371
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0091924
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.6808e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00052363
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 3.402e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00055068
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.0011187
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 3.413e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.4743e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.3836e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.3022e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.1368e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 5.4094e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 4.9853e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.5753e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.9668e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.3354e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.1149e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.2386e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.559e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00061064
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00055966
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 5.8294e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.1743e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.0201e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.2449e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.4731e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2807e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.699e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.6312e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.0095e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00017727
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 3.7205e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.2203e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0001527
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00096134
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00039928
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.9978e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00042857
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00067256
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.0112e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 7.8737e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 4.3578e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00014061
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.8656e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.0756e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.6263e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.1274e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.972e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 8.2378e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.2137e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.143e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.7808e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00054232
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00046572
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 4.5598e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 8.6708e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.1929e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.7243e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.886e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.0522e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00013582
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 6.2622e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 7.1625e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0004219
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 8.8546e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 7.6642e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00036343
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00082824
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0017036
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 7.0522e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0014643
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0032017
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 9.746e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.8276e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00026537
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00095337
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00035366
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00012182
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00012112
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.7609e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.102e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00050992
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0002835
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00025464
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.3103e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0018706
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0017866
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00017841
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 5.1679e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.3513e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00010489
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00035804
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.8368e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00081736
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00038093
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0004357
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0025664
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00053862
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 4.6621e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0022107
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0033022
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.082322
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0034413
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.074422
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.15598
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0048164
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0013838
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.029667
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.12271
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.038965
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.017899
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.020508
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.007136
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0015054
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.078402
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.033611
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.035936
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0042488
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.081736
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.079248
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.010313
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.002262
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.003216
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0077838
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.026571
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0013523
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.060177
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.028269
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.032334
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.19046
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.039972
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0034598
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.16406
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.16268
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 7.2493e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00017834
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.0015912
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.015046
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0036202
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.002227
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0032128
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.001257
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0.000301
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0033309
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.0019654
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.0011203
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.1326e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00048326
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0007512
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0036308
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00011718
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0069137
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0027544
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0022624
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0092648
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0024385
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00025669
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.01252
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.8561e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0.00025224
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0032243
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00077985
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00043005
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00052747
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00020591
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 5.0064e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00059131
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00037384
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00018859
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.1222e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.7925e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.9976e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00043488
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4055e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00082925
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00032991
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00027098
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0011097
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00029208
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.0745e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0014996
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 5.616e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00084099
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.01197
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0031036
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.001382
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0021509
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00082694
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00015319
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0020041
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0013772
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00063467
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.3215e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00019186
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00029967
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0014484
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.6311e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0027323
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0010988
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00090254
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.003696
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0009728
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.0001024
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0049946
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0015721
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0001148
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0025644
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0063628
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 5.2374e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00043005
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0014711
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.024106
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0053505
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0031771
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0056985
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0024551
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00032743
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0048213
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0025547
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0014015
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.705e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.002438
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0033641
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00027622
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.7993e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0012788
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0020055
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0096932
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00030746
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.01814
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0073534
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00604
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.024734
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0065102
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00068528
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.033425
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0054268
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.1331e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0019483
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 7.8597e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00086298
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.0026443
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 8.7512e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.2105e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.3451e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 4.8927e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.7676e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 8.2218e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 7.84e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.0943e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 8.833e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.5252e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.6074e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.4875e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.9416e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00084674
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.0013892
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0.00016862
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.8175e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.9182e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.4337e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.3078e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.1151e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00018312
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 8.8388e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0001011
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00059549
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00012498
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.0818e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00051296
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0029265
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0012992
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.8998e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00055823
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.0015463
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 5.1297e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.9189e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 4.3376e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00019847
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 7.3236e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.7243e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.5525e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.5302e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.9225e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00021966
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 8.7473e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00011319
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.5998e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00061347
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.0010008
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0.00011613
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.0497e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.3075e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.6607e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00019324
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.5766e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00042616
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00020559
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00023515
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0013851
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00029069
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.5161e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0011931
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0021592
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0065629
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00024917
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0027145
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0086496
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00032445
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 4.3094e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00039298
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0011538
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00046803
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00023285
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00021239
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00028682
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 2.9545e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0016767
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00060027
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00092191
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.897e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0031409
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0043863
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00069587
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00014834
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00018196
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00043765
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.001494
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.6967e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.003425
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0015895
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.001818
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.010708
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0022474
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00019453
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0092244
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0099024
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.316
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.01362
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.12251
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.37411
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.013561
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0046578
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.03727
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.16078
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.063288
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.033624
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.028938
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.035264
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0030978
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.21584
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.077134
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.11572
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0068795
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.12519
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.1957
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.028401
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0033254
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.012477
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.030108
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.10278
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0052615
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.23414
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.10935
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.12507
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.73668
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.15461
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.013383
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.63459
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.41655
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 9.1999e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00087252
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.001547
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.022293
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0056294
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.0033848
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0050525
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0087316
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00044559
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0093066
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.0045965
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.0031545
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00010766
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0015871
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0025234
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.012197
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00037653
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.022215
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0092526
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0075999
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.031122
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0081915
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00086226
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.042057
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0.00014215
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0.00025106
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0045511
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.0011738
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00056444
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00082787
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0014177
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 7.4195e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.0015767
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00077607
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00051528
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.7683e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00018583
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00029539
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0014277
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.4099e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.0026018
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.0010831
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00088963
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0036431
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00095889
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0.00010094
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0049232
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00085589
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.0012454
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.014486
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0041073
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0026415
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0037717
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0063065
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00041069
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0065896
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0029159
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0022978
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.9644e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00080231
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0012504
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0060437
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00019406
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.011449
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0045849
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0037659
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.015422
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0040591
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00042727
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.02084
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0060346
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00045436
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0042213
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.015261
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00014747
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0014475
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0018482
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.031585
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0086903
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0059685
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0080409
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.012132
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00067378
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.013273
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0058629
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0045131
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00010856
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0037342
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0083074
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00076072
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 5.5854e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0049611
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0077572
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.037493
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0011963
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.07058
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.028443
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.023363
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.095672
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.025181
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0026507
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.12929
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.013896
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.2631e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0023178
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 6.3762e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00080899
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.0027431
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0.0001271
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 6.2954e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 6.3163e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.4456e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.5576e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.8053e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.2975e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8215e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.5371e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 8.5725e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.5677e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.6329e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.07e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00090212
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.0013065
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0.00016471
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.4884e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1747e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.9615e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00010109
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.7423e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00021103
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00010755
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00012302
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00072462
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00015208
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.3163e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00062419
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0024314
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0014669
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 3.8118e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00049038
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.0015952
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 7.3811e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.0696e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.996e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00019811
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 9.9682e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.8699e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 4.2599e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.8319e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.9447e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00028074
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.0001171
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00021194
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.4437e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00058436
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00089362
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0.00010634
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 5.0233e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.7041e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.8203e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00023282
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0911e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00048553
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.0002477
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00028331
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0016688
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00035024
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.0315e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0014375
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0016271
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0082729
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00028233
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0031568
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.010666
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00047214
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.3435e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00014725
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0014231
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00058578
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00055695
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00033293
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00046191
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 4.0186e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0021691
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00086933
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0016885
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00032412
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0033759
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0046463
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00075429
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00033436
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00020284
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00051191
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0017475
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.1795e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0036399
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0018591
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0021264
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.012525
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0026288
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00022754
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.01079
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.008187
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.31661
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.013321
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.10951
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.39294
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.017726
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0036862
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0077801
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.16052
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.070806
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.059349
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.043016
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.041817
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0042473
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.25864
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.10185
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.17472
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.033289
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.1319
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.18447
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.028617
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.016387
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.011955
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.030461
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.10398
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0047729
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.21239
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.11063
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.12653
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.74532
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.15642
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.013539
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.64203
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.31677
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.4073e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00045375
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00072643
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.024812
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0081453
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.0074322
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0083616
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.014534
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00077541
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.012227
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.0062894
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.0059995
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00039162
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0018797
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0030706
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.014841
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00043392
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.025601
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.011259
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0092479
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.037871
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0099678
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.0010492
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.051177
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 7.5074e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0.00011553
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0045427
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.0015977
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.0012162
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.0013816
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.002342
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00012554
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.0020151
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.0010389
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00096476
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.3432e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00021776
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0003559
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0017202
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.0242e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.0029643
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.001305
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.0010719
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0043894
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.0011553
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0.00012161
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0059316
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00046544
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00046666
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.017867
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0051406
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0063183
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0059123
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.010156
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00055861
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0085246
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0042229
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0042083
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00032689
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00089439
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0014626
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0070691
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00020623
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.012168
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0053628
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0044049
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.018038
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0047478
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00049977
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.024376
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0060461
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00044439
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0037736
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.016029
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00019275
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0011456
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0003858
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.031534
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0097226
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.010535
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.011953
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.014387
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00092381
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.015905
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0077413
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.006814
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00052532
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0039344
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0078309
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0007665
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00027524
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0047538
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0078481
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.037933
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0010852
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.064026
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.028777
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.023636
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.096794
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.025476
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0026817
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.1308
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.010567
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.1214e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0019653
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0.00012544
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00082828
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.0019868
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0.00013904
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 3.2171e-07
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 4.6509e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.4395e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.4828e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.9633e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.2944e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.2367e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.5242e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 5.7608e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 4.1474e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.7632e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.062e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00054344
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.0011086
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 8.762e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.9559e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.2339e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.0945e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.1497e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.2928e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00014653
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.6067e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 8.7003e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00051247
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00010756
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 9.3096e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00044145
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0015391
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0011372
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.1739e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00048197
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.0011395
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 7.9578e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.0447e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0.0001461
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00011313
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 5.0837e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 6.2956e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 4.1269e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.9242e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 8.0177e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00018529
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00013649
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00011971
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.6042e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00033798
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00067231
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 5.223e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.1444e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8736e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.7673e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00016274
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.4902e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00033332
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00017314
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00019803
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0011665
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00024481
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.119e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0010048
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00096004
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0065207
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00036251
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.002746
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0066644
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00042136
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 8.1872e-06
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.0010542
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00080524
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0003646
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0004608
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00031997
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00026479
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.664e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0014569
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00089101
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00091456
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00011428
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0019208
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0036768
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00028812
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 5.1269e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00012582
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00032847
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0011213
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.8915e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0021767
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0011929
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0013645
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0080371
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0016868
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0.000146
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0069232
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0052124
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.24209
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.017233
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.10597
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.28493
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.018046
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0017139
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.078392
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.12135
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.052731
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.065807
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.043741
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.033664
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0078097
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.19238
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.12901
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.12079
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.010749
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.088092
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.16006
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.017575
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0050436
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0077247
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0202
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.068956
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0029974
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.13338
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.073364
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.083911
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.49426
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.10373
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0089788
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.42577
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.24987
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.7775e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00023188
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.005349
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.015671
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0047224
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.0080827
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.008342
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0098681
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0012734
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0082163
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.0073114
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.0034038
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00018527
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0013176
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0021717
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.010496
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00030129
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.017776
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0079628
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0065405
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.026784
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0070496
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00074206
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.036194
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.7895e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0.00084561
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.002594
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.0008148
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.0013044
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.0013385
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015759
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00020355
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00133
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.0012109
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00054492
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.955e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00015088
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00024877
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0012024
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.4492e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.002035
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00091214
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00074922
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0030681
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00080754
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 8.5004e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0041461
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00016261
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.0033409
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.01011
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0031996
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0052275
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.005682
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0058221
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00078734
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0057258
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0043283
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0022795
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00011525
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00055479
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00093848
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.004536
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00012333
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0072764
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0034411
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0028265
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.011575
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0030465
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00032068
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.015641
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.004623
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00057489
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0036515
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.011623
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00019623
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00053262
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0038873
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.02384
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0072407
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.011681
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.012154
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.011582
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0016987
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.01183
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0098061
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0047109
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00016962
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0026276
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0067945
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00047073
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 8.4714e-05
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0030715
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0052046
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.025155
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00068149
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.040208
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.019083
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.015675
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.06419
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.016895
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0017784
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.086743
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0083354
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.9795e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00034953
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.0737e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 7.0901e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00026666
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.5295e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.8573e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.5439e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.418e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 3.4962e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.2363e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 7.4988e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 5.2354e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0419e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 7.698e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.2133e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.35e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.447e-08
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00035235
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00033645
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.2736e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.6085e-08
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.9906e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.3143e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.9003e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.3738e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.9463e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 8.4053e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 9.6137e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 5.6628e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.1885e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.0287e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.878e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00085531
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0002985
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.452e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 5.9733e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00018574
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 9.7862e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 9.6617e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 5.3066e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.1349e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.8327e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.1174e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.9914e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8463e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.6858e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.4229e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.1768e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 8.734e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.1759e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00032502
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00029513
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.809e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 3.0083e-08
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.6423e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.1591e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.1025e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1504e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.1192e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.2369e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.5585e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0001507
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.1629e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.7376e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00012982
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00079771
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0016429
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.9374e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0002684
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0011308
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 6.0817e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.1968e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00037455
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00054781
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00012801
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.8165e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.2362e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3063e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 2.3747e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00039645
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 9.4298e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00012296
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.9431e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0017523
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0017946
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00019722
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.0614e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8096e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.2779e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00014603
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.7788e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00034616
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00015537
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0001777
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0010467
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00021968
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.9015e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00090167
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0041841
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.12644
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0050933
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.030769
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.098885
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0062871
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.002356
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.13488
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.15282
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.034675
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.012332
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0072714
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0052768
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0012034
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.082292
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.028561
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.021124
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00059359
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.10659
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.14098
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.020166
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.8256e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0032169
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0074293
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.025361
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0014121
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.062838
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.026982
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.030861
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.18178
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.038151
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0033022
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.15659
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.31231
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 8.5375e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00020594
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.0017757
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0064608
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0011134
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00050896
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00048326
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00041776
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.2559e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0010979
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00056647
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00021256
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.3596e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00015987
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00023997
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0011598
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.002e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0023612
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00087987
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00072271
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0029596
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00077897
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 8.1997e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0039994
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.5047e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0.00030715
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0016361
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00029373
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00010603
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 9.7021e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 7.4143e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 9.3576e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.0002457
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.0001044
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.9758e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.008e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.1279e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.2139e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00015534
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.2974e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00031255
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00011784
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 9.6795e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00039639
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00010433
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.0982e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00053566
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00043631
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.001187
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0068778
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0011234
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0010002
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00039712
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00028724
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.301e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0015581
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00045807
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00030647
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.9597e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.9791e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00012223
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00059076
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.9613e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0011572
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00044816
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00036811
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0015075
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00039677
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 4.1765e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0020371
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0024146
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00016991
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0010602
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0040338
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 6.8366e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00073216
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0066886
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.030023
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0047613
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.002189
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0020205
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0018155
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00026174
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0050605
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0021709
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00082381
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.3673e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0031793
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0059849
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00054014
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.0664e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0012791
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0019142
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0092517
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00032106
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.018943
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0070186
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0057649
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.023608
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0062137
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00065407
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.031903
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.010419
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.08e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00034227
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.8709e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00012756
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00056598
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.6265e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 3.0818e-08
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 3.4735e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.0198e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.504e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.6141e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.3451e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.5323e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.3949e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.011e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.8718e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 4.3464e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.1714e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00020803
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.0003623
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 5.6992e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.708e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.1629e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.1158e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.7464e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.2934e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 4.1355e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.858e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.1251e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00012517
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.6271e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.2739e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00010783
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00062095
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00024145
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.1877e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 8.5041e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00034721
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.62e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.1091e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.1857e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.1557e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.9467e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 9.1804e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 8.0274e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.2029e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 5.1822e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.5753e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.3979e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.5005e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.041e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00016196
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00027372
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 4.2806e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.8344e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.3138e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2567e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.2899e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.2834e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00010161
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.5641e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 5.2203e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00030749
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 6.4535e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 5.5859e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00026488
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00050098
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0014829
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 5.3671e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00051993
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0026215
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00011178
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.2859e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 7.7301e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00041546
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0001689
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 9.4971e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 9.4197e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 5.3213e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.8782e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00031155
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00012229
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00013602
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.1513e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00095445
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0017953
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00026157
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00018245
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.4649e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00010376
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00035421
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.9491e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00086737
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00037685
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00043103
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0025389
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00053286
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 4.6122e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0021871
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0031025
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.15039
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0082461
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.064075
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.22386
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.012855
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00073772
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.036429
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.12155
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.052398
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.028462
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.030756
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.018205
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0016952
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.11294
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.037873
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.047691
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.013
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.078259
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.15936
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.018345
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.019284
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0078986
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.018589
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.063457
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0034093
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.15171
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.067512
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.077219
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.45484
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.09546
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0082627
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.39181
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.25549
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.6581e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.2213e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00039948
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0046463
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0014344
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.0010762
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0015113
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0012227
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 7.0367e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.001442
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00068254
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00039313
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.2873e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0003461
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00053044
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0025638
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.5033e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.005017
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.001945
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0015975
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0065421
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0017219
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00018125
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0088407
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 4.023e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 6.8627e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00095293
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00031201
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00019021
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00026036
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00020894
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.3157e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00025663
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00012402
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 6.8306e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.4434e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.2792e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.5577e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00031696
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0515e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00062036
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00024045
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.0001975
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00080879
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00021287
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.2408e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.001093
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.554e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00024498
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0052162
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0014822
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0010774
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0016728
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00117
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.3909e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0012244
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00059406
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00033901
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.1696e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00019687
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00029647
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0014329
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.9144e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0028995
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.001087
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00089288
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0036564
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00096238
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.0001013
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0049411
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0028719
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00027508
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0022079
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0091319
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00013979
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00022926
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0018064
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.023879
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0071949
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0050522
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0085459
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0062635
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00036871
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0069454
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0028787
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0018599
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00020515
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0023343
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.006765
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00049136
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0003239
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0031407
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0047895
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.023149
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00077515
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.045734
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.017561
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.014425
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.05907
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.015547
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0016366
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.079825
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0085229
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.1308e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00065764
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.36e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00026953
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.0010804
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 3.056e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.3828e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.4317e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.1769e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 5.89e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 4.6217e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.7468e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.4165e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 3.7304e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.1212e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.4667e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.065e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.1759e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00028487
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00051834
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.9322e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.1107e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.1998e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.1947e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.7974e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2704e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.6535e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.9762e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.4041e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00020051
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.2082e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.6425e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00017272
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00078797
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00041991
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.5377e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.0001662
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00065559
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.8449e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 7.7078e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 4.8444e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.6983e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.2948e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.6114e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 9.1296e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 8.0226e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.2353e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.3287e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.8637e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.5742e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.2599e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00019596
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00035966
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.4924e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.2759e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.6646e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9617e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.6966e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.0451e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.0001355
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.1246e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 8.1489e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00048
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00010074
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 8.7197e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00041348
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00057303
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0034663
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00010476
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0013382
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0053066
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00015172
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 7.3121e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 4.1585e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00053454
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00025611
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00019162
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00010289
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 8.3009e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.2605e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00084772
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00021864
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00043364
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.7331e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0017118
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00298
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00023449
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00010833
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.614e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00019598
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00066899
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.0066e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0013379
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00071175
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00081408
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0047952
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0010064
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 8.711e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0041307
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0044231
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.24831
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0095586
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.10887
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.42317
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.013533
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0026805
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.017557
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.12199
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.055906
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.045501
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.029755
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.024803
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0039859
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.20273
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.055485
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.11023
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.023168
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.11594
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.20005
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.019315
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.010886
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.011076
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.028034
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.095697
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0044529
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.19815
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.10181
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.11645
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.68593
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.14396
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.012461
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.59087
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.30869
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 9.1899e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00017174
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00016466
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0053625
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0018758
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.0019027
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0017702
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0019282
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00018818
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0030254
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00096371
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00096333
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.9638e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00051203
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00084968
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0041068
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00011624
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0068584
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0031155
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.002559
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.010479
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0027582
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00029034
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.014161
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.7959e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.804e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0010773
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00036781
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00033387
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.0002961
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00032218
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.1361e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00052604
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00016535
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.0001627
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.3373e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.1724e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00010237
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00049477
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4022e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.0008273
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00037535
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.0003083
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0012625
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.0003323
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.4979e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0017061
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00014523
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00013179
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0067112
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0022475
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0021738
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0018271
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0018252
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00017522
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0033316
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0010621
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0010808
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.7991e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00033573
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00055993
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0027063
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.5805e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0044725
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0020531
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0016864
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0069058
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0018176
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00019133
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0093322
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0047418
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00031887
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0037512
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.017262
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00014716
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00083303
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00087061
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.023966
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0076766
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0080767
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0082677
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0085333
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00086695
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.012467
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0042174
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.004299
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00036561
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0034583
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.008492
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00051735
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00018284
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0044041
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0072229
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.034911
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0010124
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.059734
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.026484
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.021753
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.089082
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.023447
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0024681
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.12038
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.010298
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.9443e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00059244
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 3.7672e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00017261
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00076473
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 3.0741e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.8804e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 3.3961e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.3516e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.4026e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 4.479e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.7208e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.421e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 4.1151e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.9069e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 9.3546e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.2801e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.5672e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.0002538
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00045762
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.133e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.5545e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.0299e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.718e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6346e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2099e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.3841e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.803e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.206e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00018884
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 3.9634e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.4306e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00016267
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00068659
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0003762
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.2899e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00010949
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00046645
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.8629e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 6.4655e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.1714e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 5.2349e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.7643e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.5453e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 9.1545e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 8.1012e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.3887e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 6.5686e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.1709e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.3112e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.4968e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00018035
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00032025
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 2.9022e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 9.0327e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.287e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.8571e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.3396e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.9083e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00012942
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 6.7448e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 7.7145e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00045441
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 9.5369e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 8.2548e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00039143
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00048079
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0032639
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00016704
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00096656
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0041679
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00016477
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.2205e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00023349
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00065064
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00019301
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00019755
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00011567
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 9.7806e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.4202e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00074947
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00035724
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00049743
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.8334e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0014332
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0024175
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00023142
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 2.6157e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.7589e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00020168
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00068847
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.0309e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0013487
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00073247
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00083778
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0049348
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0010357
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 8.9646e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0042509
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0043542
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.25155
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.016047
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.077091
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.31489
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.013857
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0030988
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.039012
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.13185
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.041664
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.04736
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.031787
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.025879
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.004161
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.19053
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.093187
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.13545
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.024289
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.10363
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.18901
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.015563
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0064833
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.010456
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.026502
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.090467
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0041974
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.18678
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.096249
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.11009
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.64845
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.13609
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.01178
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.55858
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.2855
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 8.3856e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00013554
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00039058
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0061584
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0014021
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.001844
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0017534
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0019319
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00020759
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0027198
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.0016491
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.0011579
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.3958e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00048484
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00080025
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0038679
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00011071
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0065316
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0029342
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0024101
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0098697
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0025977
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00027345
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.013337
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.3453e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 6.7805e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0012004
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00028278
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00032017
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00029691
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00032533
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.5257e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00047148
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00028132
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00019625
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.5651e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.8683e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.691e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0004684
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3392e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00079014
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00035533
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00029187
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0011952
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00031458
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.3114e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0016152
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.0002424
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00073998
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0081689
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0016938
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0022411
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0020541
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0021505
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00019741
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0029455
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0017354
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0012398
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.9002e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00034212
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00057623
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0027851
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.6417e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0045086
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0021129
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0017355
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0071069
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0018706
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.0001969
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0096039
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0048038
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00053532
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0026564
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.012845
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00015068
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00096301
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0019345
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.025902
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0057211
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0084068
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0088325
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0089037
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00090505
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.011717
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0070831
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0052825
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00038329
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.003091
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0080237
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00041685
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0001089
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0041576
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0068281
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.033002
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00095434
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.056306
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.025036
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.020564
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.084213
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.022165
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0023332
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.1138
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0095242
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.9478e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00060127
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 5.8002e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00019649
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00067933
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 4.1677e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 4.7276e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.3444e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 9.1817e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.4733e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.3805e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.8104e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 8.4272e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.2332e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.1264e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.5824e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.0017e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.0002931
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00054896
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.5826e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.1295e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5205e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.5206e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.2259e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.8977e-07
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 4.4045e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.3682e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.7087e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00015955
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 3.3485e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.8984e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00013744
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00072996
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00037553
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 3.4256e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00012184
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00040558
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.4904e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.5659e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 5.0021e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.5463e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.1818e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.1102e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 9.3937e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.7781e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.5782e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.7338e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 5.2473e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.6481e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00018835
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00035094
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 2.9152e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.8684e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.9871e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.5485e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.2861e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.3516e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00010465
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 5.624e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.4326e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0003789
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 7.9522e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 6.8831e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00032639
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00048033
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0036307
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00032993
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00087747
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0030918
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00021123
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.3059e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00060041
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00046097
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00029676
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00010663
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00011676
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 2.4163e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00086048
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00039011
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00062136
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00015322
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0013433
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0032696
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.0002588
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00011485
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.01e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0001551
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00052944
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.3665e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0010531
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00056328
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00064427
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0037949
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00079646
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 6.8939e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.003269
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0043106
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.23852
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.019601
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.077576
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.25892
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.016929
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.005273
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.12828
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.08092
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.058541
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.029926
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.026709
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0083827
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.20474
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.097507
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.13607
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.04103
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.10894
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.20976
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.017674
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.017548
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0076916
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.019948
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.068096
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0030121
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.13404
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.072448
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.082865
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.4881
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.10244
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0088668
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.42046
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.28238
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 8.4005e-06
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00034075
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0061254
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0029241
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.002665
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0021786
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0022425
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00042512
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0031852
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.0019857
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.0014313
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00018306
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00040332
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0006761
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0032678
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.0563e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0053432
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.002479
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0020362
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0083386
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0021947
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00023103
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.011268
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 5.6801e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.001147
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00056839
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00045204
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00036009
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00037723
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 7.0532e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00054396
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00033126
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00023886
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.0357e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.8215e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.0806e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00039056
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0829e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00063891
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00029629
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00024337
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00099661
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00026231
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.7612e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0013468
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00025936
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0075382
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0040453
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0033665
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0018935
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0025672
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00033588
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0033818
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0018951
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0015487
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00015453
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.000265
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00044313
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0021418
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.9666e-05
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0035203
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0016248
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0013346
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0054653
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0014385
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00015142
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0073855
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.004555
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00065386
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0026731
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.010562
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00018409
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0016387
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0252
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.011111
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.010391
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0083152
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0091892
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0018233
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.01259
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0074114
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0053067
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00064749
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0032494
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0089042
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00047339
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00029475
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0030583
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0051397
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.024842
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00068484
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.040405
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.018845
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.015479
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.063389
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.016684
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0017562
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.085661
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00942
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.8354e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0003873
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 9.2163e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 9.3592e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00032957
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.1611e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 4.0468e-08
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.993e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 8.3841e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 6.9454e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.4081e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 5.8083e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.8358e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 9.4881e-08
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.3224e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.9131e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.3929e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.4275e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.0001253
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.0003109
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 5.7091e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.3215e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4355e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.2288e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.1022e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.4458e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.8684e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.1726e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.3412e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 7.9002e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.6581e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.4352e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 6.8054e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00060427
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00034719
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.3401e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.9317e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00022335
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 7.6566e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.504e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 7.3473e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.1978e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.5875e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.6605e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.1393e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.6248e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.6095e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.6253e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.7981e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.2569e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.4194e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00012112
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00029047
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 5.0648e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 8.3888e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.867e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.7126e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9742e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7339e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.7157e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.1642e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.6192e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00021318
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.4741e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.8726e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00018364
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00058532
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0022948
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 4.3459e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00063453
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0020336
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 7.971e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.9299e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 7.7319e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00048713
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00039948
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 7.5341e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.7338e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.6072e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 4.4929e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00030307
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 7.3975e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00015894
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.3562e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00086124
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0019579
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00047462
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.0001097
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.2971e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.7409e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00033252
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.9168e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00085297
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00035377
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00040463
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0023834
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00050022
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 4.3297e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0020531
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0037802
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.31997
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0077348
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.1107
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.32409
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0123
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0012952
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.034627
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.26252
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.20139
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.038988
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.018077
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.023697
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0023342
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.15821
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.043775
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.076917
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0042783
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.13678
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.3339
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.07264
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.017968
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.013817
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.031128
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.10626
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0061958
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.27571
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.11305
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.1293
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.76164
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.15985
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.013836
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.65609
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.64425
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.2229e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.9168e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00022922
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00382
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0022119
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00057969
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00037431
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00054546
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 4.7864e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00090174
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00033725
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00030689
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.2248e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00022971
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00033478
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0016181
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.8979e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0034797
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0012275
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0010083
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0041289
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0010868
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00011439
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0055797
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 5.4555e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 4.2527e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00096258
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.000575
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00011728
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 6.9385e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00010541
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 9.1638e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00018844
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 6.9185e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 5.7216e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.9824e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.1142e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.5464e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00021974
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.9842e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00047107
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.0001667
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00013693
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00056072
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00014758
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.5535e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00075773
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 5.819e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00024504
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.006116
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0035057
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0008547
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00048547
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00079314
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 6.2454e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0011911
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00035935
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00039616
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.419e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00018947
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00027831
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0013452
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.8328e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0028514
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0010205
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0008382
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0034325
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00090344
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 9.5099e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0046385
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0061104
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00025803
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0038145
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.013221
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00013375
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0004025
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0017171
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.051572
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.027654
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0069206
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0050228
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.008153
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0005077
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0097293
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0033273
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0029997
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.7514e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0040798
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.014174
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0019456
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0003018
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.005494
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00802
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.038764
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0014087
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.083114
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.029407
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.024154
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.098914
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.026034
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0027405
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.13367
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.021492
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.5662e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00026691
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.0457e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00010124
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00028
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.4492e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 7.3696e-08
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 2.0018e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.3083e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.5e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.2569e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 9.5322e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.1389e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.405e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 7.7907e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.4325e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.2685e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.4504e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 7.6459e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00021935
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.4258e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 4.9324e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4758e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.4529e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.1787e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.4036e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.8496e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.254e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.4343e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 8.4487e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.7732e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.5348e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 7.2778e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00028604
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00018
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.3203e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.5232e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00018117
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 9.1641e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.6132e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 7.2081e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.2021e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.076e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 4.6849e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.4105e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.0762e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 5.0157e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.7989e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 8.6359e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.1663e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.8859e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 5.2621e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00015452
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.6554e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 3.139e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7647e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.805e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.0057e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6341e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.2719e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.1978e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.6576e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00021544
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.5216e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.9137e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00018559
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00021776
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0017973
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00014745
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00061891
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0017848
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 9.487e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 3.9597e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 9.7549e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0003103
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00013455
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 7.4757e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 6.665e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 6.8297e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 6.6848e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00037624
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00012045
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0001562
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.7364e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00050532
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0012713
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00020033
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.0222e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.7236e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00011065
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00037773
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.0474e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00091109
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00040188
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00045965
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0027075
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00056824
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 4.9185e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0023323
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0019829
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.25292
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.019134
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.098279
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.28039
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.015185
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0019099
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.061162
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.13361
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.064814
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.033638
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.025326
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.030875
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.003292
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.17926
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.056634
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.074906
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.015118
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.078015
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.19879
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.027234
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0059102
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.012076
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.02815
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.096094
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0052571
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.23394
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.10224
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.11693
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.68878
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.14456
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.012512
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.59333
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.28663
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 6.7546e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 5.3118e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00023023
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0024186
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00079619
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00051747
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0006143
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00090878
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 7.0879e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0011111
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00042882
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00029564
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.9949e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00023615
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00035802
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0017304
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.8592e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.003457
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0013127
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0010783
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0044156
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0011622
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00012234
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.005967
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 9.4791e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 4.1721e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00050494
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00017246
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 9.7068e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00011061
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0001637
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.2734e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.0002009
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.6618e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 5.3093e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.4738e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.0318e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.5947e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00022208
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.525e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00044397
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00016847
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00013838
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00056667
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00014915
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.57e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00076578
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 7.8644e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00030915
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0038959
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0011808
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00084808
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0011836
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015017
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 9.2924e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0014787
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00058509
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00038931
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.7598e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00020828
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00031615
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0015281
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.1621e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0030456
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0011592
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00095217
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0038992
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0010263
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00010803
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0052692
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0048299
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00063828
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0033865
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.011438
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00016512
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00059354
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0030329
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.026248
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0088999
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0059709
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0070371
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.010622
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00071603
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.011024
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0043047
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0029213
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00023857
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.002327
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0084388
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00072944
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 9.9269e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0048015
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0072528
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.035055
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0011953
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.070522
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.026594
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.021844
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.089452
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.023544
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0024783
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.12088
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0095619
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.1923e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00019061
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 6.4189e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00011673
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00029204
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.1287e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 6.3064e-08
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 8.6918e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.1225e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.8195e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.5894e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.1192e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 8.2187e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1448e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.276e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.7893e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 4.828e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.1457e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00011751
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00020412
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.8614e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.1244e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.2372e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.0174e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.03e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.1642e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.2981e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.0959e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.2534e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 7.383e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.5495e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.3412e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 6.3599e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00027314
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00012523
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.0262e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.728e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00018494
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 7.1764e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.1488e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 3.0301e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.0208e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 7.2151e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.7262e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.9416e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.8815e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.0525e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.2357e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 9.8714e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.7068e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.4966e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 8.8046e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00014265
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.3314e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 7.2348e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.135e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.6625e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6157e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3058e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.8108e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.7829e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.183e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00018749
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.9349e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.4059e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0001615
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00019848
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0015944
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 5.5055e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00092601
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0023773
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 9.3491e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 3.8251e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 6.1235e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00033366
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00011886
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 9.4786e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 7.5632e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 4.7756e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 6.661e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00035105
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00015898
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00029106
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.8686e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00076127
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0018671
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00013107
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00011313
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.6487e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00011679
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00039868
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.8834e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00083812
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00042416
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00048515
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0028577
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00059975
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 5.1912e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0024616
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0025407
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.19553
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0060252
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.12546
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.299
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.012737
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.002005
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.019941
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.12613
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.043265
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.038908
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.031289
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.020271
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0030091
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.15056
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.059875
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.13056
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.017212
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.080539
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.17309
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.013922
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.016022
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.010445
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.025539
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.08718
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0043489
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.19353
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.092752
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.10609
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.62488
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.13115
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.011352
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.53829
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.25247
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 9.455e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 4.5454e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 9.9965e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.002334
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00057946
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00065434
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00072129
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00065581
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.775e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00089512
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00049172
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00043669
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.6153e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00019798
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00031286
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0015122
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.7252e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0027879
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0011472
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00094226
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0038586
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0010156
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00010691
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0052144
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 7.7945e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.7538e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00046339
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00011564
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00011864
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00012784
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00011571
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0288e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00016048
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 8.7579e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 7.7695e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.5986e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5247e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.9984e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00019326
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.013e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00035477
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00014661
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00012042
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00049314
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.0001298
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.3663e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00066641
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 7.597e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00019406
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0041892
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.001043
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0010753
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0013431
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0010501
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 9.2592e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0013797
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00077228
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00072545
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.9016e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00020498
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00033369
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0016128
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.7487e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0028017
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0012235
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.001005
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0041155
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0010832
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00011402
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0055614
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0037339
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.000201
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0043229
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.012197
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.0001385
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00062311
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00098884
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.024778
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0059409
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0069064
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0086942
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0069743
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0006545
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0092586
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.004551
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0050917
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00027161
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0024023
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0073476
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0003729
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00026912
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0041532
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00658
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.031803
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00098878
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.058338
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.024127
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.019817
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.081153
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.02136
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0022484
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.10967
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0084221
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.5062e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00021295
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.1677e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 5.5552e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00020221
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.0097e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 9.3769e-08
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.1249e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.355e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.4547e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.9171e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.0528e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.7668e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0048e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.7309e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.4258e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.5646e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.0668e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 8.1146e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00011282
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.0144e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.7305e-08
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.747e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9077e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.5121e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.2031e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.4254e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 6.9283e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 7.9244e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 4.6677e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 9.7964e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 8.4794e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.0209e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00025105
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00014456
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.5136e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.7187e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.0001296
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 6.4933e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.339e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 4.0167e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.1569e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 5.9356e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 6.8816e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.7653e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6898e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.6086e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.4699e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 5.1254e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.9987e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.7935e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 5.7716e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 7.8718e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.3818e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.1166e-08
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.9739e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.866e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.6611e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.152e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.6276e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.7672e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.0213e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00011906
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.4988e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.1629e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00010256
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00017806
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0023844
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0001179
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00050092
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0022097
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00010445
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 7.5795e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 8.4887e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0003912
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 9.6504e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00016745
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 8.7261e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.1535e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 6.2049e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00047782
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.000118
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00044495
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.9458e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00079697
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0010884
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00017627
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 1.1097e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.533e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.8156e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00030093
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4415e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00064146
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00032017
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0003662
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.002157
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00045271
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.9184e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0018581
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0025977
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.21163
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.013334
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.051372
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.19523
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.010296
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0019996
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.024359
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.12097
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.029317
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.042764
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.02672
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.012661
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0029352
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.15627
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.035024
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.12755
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.021673
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.071046
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.10257
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.019073
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.315e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0060635
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.014999
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0512
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0024958
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.11106
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.054473
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.062304
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.36699
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.077023
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0066668
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.31613
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.23412
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 6.4962e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 6.7585e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00012938
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0024399
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00046328
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00078927
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00067847
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00038036
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.0689e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00096
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00025136
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00050333
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.9045e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00012397
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0001978
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00095603
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.9308e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0017292
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00072527
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00059572
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0024395
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00064209
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.7589e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0032967
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.2112e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.3249e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00049458
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 9.5135e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00014258
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00012212
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 6.7861e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 9.1614e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00017729
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.5472e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 9.0982e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.9876e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5896e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.5392e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00012273
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.7539e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00022148
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 9.3103e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 7.6473e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00031316
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 8.2426e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 8.6764e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00042319
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00015054
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00026902
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0049115
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00084688
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0018996
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0015496
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00069338
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 8.6252e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0018779
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00057321
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.001109
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.0136e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00015578
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00025187
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0012174
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.6344e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0021443
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00092354
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00075857
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0031064
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00081762
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 8.6066e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0041979
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0040415
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00044481
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0017702
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0079641
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00011196
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00062143
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0012079
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.023765
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0040257
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0075909
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0074244
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0043559
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00063842
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0096097
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0026621
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0049744
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00034202
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0021191
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0043543
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00051087
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.8883e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.002411
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0038644
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.018678
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00056745
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.033479
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.01417
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.011639
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.047661
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.012545
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0013205
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.064407
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0078102
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.1616e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00012096
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 5.6938e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00010589
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00016416
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 6.8098e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 8.2869e-08
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.7488e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.6767e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.9959e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.049e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 4.4396e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 7.422e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.6222e-08
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.9103e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.153e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.7237e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.3981e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 3.7312e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00017315
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 8.8965e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 9.205e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.9541e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2198e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.164e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.0485e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 9.1158e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 4.4301e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 5.0671e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.9847e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 6.2641e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.4219e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 2.571e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00020359
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.9122e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 3.6276e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 6.876e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00010374
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 4.3204e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.8352e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 6.3838e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.51e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 8.9186e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.8263e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.5661e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.6256e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.9506e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.7971e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.2044e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 9.6967e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.4021e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 2.667e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00012574
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 6.2749e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 5.6289e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.2696e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.1172e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0641e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.2643e-07
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.3426e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.1321e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.2949e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 7.6271e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.6007e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.3855e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.5701e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00015123
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0011767
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 3.9131e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00080087
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0018022
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 6.4551e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 4.4279e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 2.3887e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00025406
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00012259
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 9.2199e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.9145e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 5.9826e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 2.5197e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00031617
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.1795e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00020169
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.9466e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00035188
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.001535
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 7.3349e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 6.1312e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.4259e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.9496e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0002031
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.007e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00044812
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00021608
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00024715
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0014558
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00030553
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.6445e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.001254
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0018512
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.10823
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0070071
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.074477
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.13257
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0072875
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0016895
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0035484
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.089978
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.036717
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.028477
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.011315
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.017997
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0014417
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.10791
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.030133
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.062731
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0083636
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.035928
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.12331
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0076756
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0091795
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0039547
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.009507
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.032453
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0016737
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.074478
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.034528
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.039492
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.23262
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.048821
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0042258
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.20038
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.15024
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 9.3227e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 5.9729e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 2.0113e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0016752
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00063565
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00043185
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00028611
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00059224
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.8362e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00070033
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00020325
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00024636
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.7769e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.9274e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00012648
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00061131
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.8744e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0011059
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00046375
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00038092
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0015599
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00041057
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 4.3218e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.002108
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.0284e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 3.695e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00034625
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00014294
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.9277e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.0795e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00010544
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.9523e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00012899
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.7302e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.414e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.5476e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.0224e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.6266e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.8619e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4241e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00014302
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 5.9642e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.8989e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00020061
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 5.2802e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 5.5581e-06
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0002711
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 8.7944e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 7.5701e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0031898
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0010758
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0010459
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00051757
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0013154
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.5026e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0012426
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00039733
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0005027
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.9632e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00010697
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00016999
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00082161
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.539e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.001498
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00062329
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00051196
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0020965
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00055181
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 5.8085e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0028331
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0020668
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00023375
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0025663
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0054079
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 7.9244e-05
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00052505
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00017596
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.017676
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0050418
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0050549
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.003144
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0061918
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00031359
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.006636
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0022904
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0024464
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00013198
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0010716
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0052345
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00020559
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00015418
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0015725
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0024495
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.011839
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00038053
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.022451
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0089814
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0073771
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.03021
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0079514
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00083699
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.040824
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.005012
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.6539e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00016375
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 4.6433e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.5512e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.0001696
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 6.9227e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 4.3541e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 4.0109e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.4119e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.9908e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 7.2876e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 4.1125e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.3307e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 6.5336e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.9215e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 8.9067e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.5165e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.5506e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 3.4977e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00011927
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.8888e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.9646e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.5219e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.1081e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.1964e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.3313e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.9274e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.6564e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 8.7572e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 5.1582e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.0826e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 9.3705e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.4434e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0001888
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00013687
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 3.5077e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 5.4584e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00012173
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 4.9248e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.7839e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.775e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.6037e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 9.9793e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.9986e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.7003e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.325e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.5995e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.2376e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.7122e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 5.9187e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.2224e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 2.9897e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00010908
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.6396e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.709e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.7667e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.136e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.0946e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2568e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.5927e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.2285e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.5489e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00015014
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.151e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.7274e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00012933
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00017412
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0023008
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 5.8087e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00088537
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0022825
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 9.4151e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 5.3151e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 4.1424e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00049964
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00030313
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 7.6836e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 4.8475e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.1708e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.0997e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00029874
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 7.9931e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00014009
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.2297e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0005304
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0016852
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00025468
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 8.2459e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.191e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00013675
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00046683
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.8214e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0012555
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00049667
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00056807
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0033461
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00070227
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 6.0786e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0028824
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0027556
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.41796
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.014671
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.21163
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.4932
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.021001
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0041692
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.030345
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.35202
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.19757
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.053708
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.035959
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.025829
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0040251
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.21504
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.057711
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.10049
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.016628
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.11461
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.37135
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.060665
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.020981
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.024658
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.054424
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.18578
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.011245
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.5004
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.19766
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.22607
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.3316
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.27948
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.024191
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.1471
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.59572
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.0072e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 3.1383e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 4.613e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0015546
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00063401
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00030002
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00026503
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00026577
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 3.2959e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00041668
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00015701
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00013717
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.6752e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00015237
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00021859
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0010565
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.9631e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0023383
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00080148
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00065832
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0026959
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00070957
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 7.4691e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0036431
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 6.4708e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.0274e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00036774
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00015994
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 6.2128e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.5147e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.3208e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 6.5995e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 8.8837e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.2934e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.6943e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.1462e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2281e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.2019e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00015476
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.7873e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00034145
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.0001174
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 9.6432e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0003949
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00010394
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.0941e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00053365
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00010556
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00013128
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0062731
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0026602
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00087166
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00086084
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00069719
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 7.0889e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0011741
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00038828
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00034915
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.2487e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00027298
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00039072
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0018885
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.1136e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.004197
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0014327
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0011768
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0048189
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0012684
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00013351
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0065121
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0079816
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0004894
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0072924
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.020119
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00022837
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0012957
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0015047
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.069155
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.027129
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0095335
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0099918
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0088865
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00087548
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.013224
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0043865
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.003919
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00026241
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0034186
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.015764
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0016249
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0003524
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0098047
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.014022
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.067774
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0025567
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.15085
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.051415
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.042231
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.17294
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.045518
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0047914
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.2337
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.019873
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.2364e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 9.6495e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.7941e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 3.335e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00010276
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 4.7372e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 7.0526e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 7.6605e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.5407e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.3221e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.4432e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.8302e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.7054e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 6.3032e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.1506e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 8.6824e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.4596e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.772e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.4159e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 5.2056e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 7.6456e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 6.9259e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.0412e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.4254e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.2175e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7585e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 7.8254e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.4232e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.9153e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.3062e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.8402e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 4.1895e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.9866e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.7328e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 6.4631e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.7319e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.3885e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 6.8876e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 3.3031e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.2029e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.8696e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 6.2853e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.2211e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.4887e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.4745e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.0192e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.3036e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 8.1951e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.2803e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 5.4617e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.0206e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.7602e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 3.7552e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 5.425e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 4.4361e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1066e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.5691e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.7698e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.8351e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.1516e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 9.3303e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.0672e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 6.286e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.3193e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.1419e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 5.4149e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.6947e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0010433
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.6456e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00039269
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0012577
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 5.8781e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 8.1356e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 1.0813e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00014854
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 5.7568e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 6.5888e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 4.2795e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 2.394e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.9476e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00023239
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 7.8872e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00014841
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.4704e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00031211
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00055263
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 9.1685e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 6.8547e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.6194e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.988e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00020441
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1601e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00051623
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00021747
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00024874
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0014652
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0003075
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.6616e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0012621
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00084371
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.24276
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0071132
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.095497
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.30634
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.013704
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0068491
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0094911
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.10535
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.040216
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.043677
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.030759
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.018629
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0040522
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.15465
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.055954
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.099392
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.018993
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.060525
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.12194
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.021344
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.015556
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0098894
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.022653
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.077331
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0043721
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.19456
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.082273
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.094102
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.55429
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.11633
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.010069
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.47747
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.19317
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.3325e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 5.0833e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 8.8104e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00070201
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00023319
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00026526
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00024684
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00021587
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 3.1797e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00030673
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00015306
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00013203
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.0146e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.4665e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.7729e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00047236
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.609e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00094933
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00035834
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00029433
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0012053
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00031725
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.3394e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0016288
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.1618e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.661e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00014413
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 5.1627e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.1565e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 4.7824e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.093e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 5.8483e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 5.8823e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.9103e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.4862e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.88e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.9114e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.3406e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.4795e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.2265e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00013136
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.9155e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.0375e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00016534
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.3518e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.5808e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00022343
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00016158
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 3.4268e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.001865
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0005052
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00074746
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00075996
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0005264
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 8.2675e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00091333
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00038314
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00036989
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.5e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0001155
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00017109
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00082691
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.9249e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0017257
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00062731
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00051526
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0021101
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00055537
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 5.846e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0028514
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0046359
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00023729
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0032906
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.012497
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00014902
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0021285
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00047065
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.020697
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0055222
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.007753
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0085468
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0064094
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00088137
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00951
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.004253
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0038762
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00029973
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0018053
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0051763
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00057168
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00026129
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0039322
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0058367
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.02821
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00099405
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.058649
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.021401
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.017578
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.071985
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.018947
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0019944
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.097278
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0064442
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.8564e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 7.9653e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 6.752e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.4449e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 7.906e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 4.0695e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.655e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.1271e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.3658e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.0471e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 7.9489e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.962e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.1054e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 4.292e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.0362e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.7317e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.603e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.2167e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.8302e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 4.0676e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 3.8871e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.0811e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.1404e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.5175e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.2489e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.8249e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 8.121e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.4566e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.9536e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.3288e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.8875e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 4.2304e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 2.006e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 8.0328e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 5.4505e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.4728e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.6861e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 5.4056e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.8175e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.0834e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 4.5032e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 5.7958e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.9631e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.039e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.1494e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.1706e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.5523e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.876e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.9909e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 6.0809e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.358e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.3581e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.896e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 2.7644e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 7.3734e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1285e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.5944e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.8564e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.9732e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.2131e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 9.4224e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.0777e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 6.3481e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.3323e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.1532e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 5.4683e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.8661e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00099425
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0002155
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00033839
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0011282
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 6.5825e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 4.3397e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00012595
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00018158
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 8.259e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.8017e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 3.716e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.2227e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.5875e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00023815
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.923e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00018703
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.4804e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00030755
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00056245
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 5.7419e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 2.8302e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.0442e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.0126e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00023939
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3392e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00059596
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00025469
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0002913
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0017159
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00036012
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.117e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0014781
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0011757
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.21159
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.018429
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.075632
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.26237
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.013398
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0026851
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.054273
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.10812
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.047527
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.059394
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.026406
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.023273
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0027161
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.14951
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.056246
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.12831
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.016649
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.050886
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.10705
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.012107
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0062156
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.010839
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.024686
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.084269
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0048157
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.2143
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.089656
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.10255
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.60402
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.12677
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.010973
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.52032
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.19333
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 8.0066e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.9137e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00012963
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0006223
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00022443
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00032725
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00019089
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00024779
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.1651e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00029041
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.0001363
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00014499
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.1133e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.6253e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.8684e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00047697
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6698e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00098518
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00036184
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00029721
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0012171
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00032035
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.3721e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0016447
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.9298e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.6065e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0001329
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.7492e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 6.2966e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.7279e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.7009e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.9409e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 5.6533e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.6536e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.7681e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.5395e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.0878e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.3538e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.5435e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.2901e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00013512
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.964e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.0773e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00016697
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.3947e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.626e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00022564
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 8.6192e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00039917
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0022798
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00072478
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0009985
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00065989
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00070859
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 4.9868e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00093595
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00043345
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00046616
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.5016e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00013423
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00020036
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00096841
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.3766e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0019922
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00073465
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00060343
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0024711
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0006504
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 6.8463e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0033393
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0040407
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00061478
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0026061
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.010703
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00014569
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00083444
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0026913
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.02124
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0065261
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.010543
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0073372
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.008007
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00059077
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0091939
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0042752
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0050041
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00026273
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0015178
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0045443
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00032428
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0001044
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0043098
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0063604
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.030742
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0010949
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0646
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.023321
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.019156
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.078444
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.020647
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0021733
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.10601
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0064493
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.1258e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 5.0496e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.7003e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.7801e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 3.3363e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 3.1523e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.1468e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.4782e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.1666e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.0077e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.0875e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.6083e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8424e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 4.6772e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.524e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.9557e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.1362e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.7837e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.7287e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 3.6388e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.1496e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.7204e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.0613e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.9999e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.7068e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.6495e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.849e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.8159e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.0769e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.2234e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.5676e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.2224e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.0538e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.9518e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 3.7263e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.8461e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.284e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 2.3293e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.2096e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 4.4712e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 5.6917e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 9.1777e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.0373e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.3963e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.0162e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 7.0727e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.7524e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 6.1784e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.1489e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.4186e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.8925e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 2.0895e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.804e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.0098e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.4804e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.7418e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.3946e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.7607e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4062e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.0707e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 5.0649e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 5.7931e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 3.4123e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 7.1617e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 6.1989e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 2.9394e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 6.3837e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00098519
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 4.6658e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00033721
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00069778
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 6.281e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.5114e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 2.5928e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00032637
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00010198
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 9.4382e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 4.1131e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 2.732e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 4.8781e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00025524
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00012262
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00017514
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.7893e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00052275
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00075641
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 8.4803e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 5.106e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.1036e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.0231e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00017147
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.9591e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00039868
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00018243
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00020866
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0012291
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00025795
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.2327e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0010587
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0015138
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.14818
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0085596
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.059078
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.11847
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.01201
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0093036
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.008852
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.1557
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.046744
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.056738
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.024714
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.019143
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0035562
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.1365
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.069743
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.096799
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.016278
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.068984
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.1134
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.01356
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0013444
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0059058
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.013977
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.047714
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0025361
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.11286
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.050764
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.058062
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.342
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.071778
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0062129
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.29461
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.20406
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.3481e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 8.2657e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.7001e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00098716
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00022317
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00025062
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00016809
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00014701
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.3595e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00021737
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00014025
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00010277
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.5283e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.2985e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.1842e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00025057
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.9142e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00046694
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00019009
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00015613
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00063939
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00016829
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.7715e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00086404
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.6219e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 3.2944e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00021045
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.8681e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 4.9649e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.2958e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.8403e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.4489e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.4348e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.7937e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.0114e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.2696e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.624e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.2773e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.5174e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.108e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 6.5372e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.6684e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.1917e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 8.9754e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.3623e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.4867e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00012129
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00030019
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 8.2169e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0040976
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00089493
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0010707
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00073041
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0006007
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 6.7809e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0010031
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00059566
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00043653
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.8131e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.2755e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00014352
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00069366
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.2589e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0013327
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00052623
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00043223
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00177
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00046588
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 4.904e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0023919
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0028297
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00028554
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0020357
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0048328
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.0001306
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0028913
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00043895
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.030588
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0064186
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.010071
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0068672
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0065859
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00077349
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0083938
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0053011
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0037751
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00025687
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0020576
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0048137
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00036319
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.2581e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0023483
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0036013
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.017406
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00057661
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.03402
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.013205
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.010846
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.044416
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.01169
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0012306
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.060021
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0068073
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.0101e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.3617e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.385e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.1582e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.2383e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.6258e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.825e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 8.2539e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.3701e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.0061e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.1531e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3685e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.2089e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.0507e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.4743e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.2357e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.545e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 8.2402e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.3342e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.8977e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.1525e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1952e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.7391e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.3504e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.2814e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.3502e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 9.9481e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.1378e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 6.7022e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.4066e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.2175e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 5.7734e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 4.6397e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.6643e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.6637e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 8.3412e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.5263e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.1095e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 7.5115e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.5337e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.8654e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.1823e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 8.2618e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.2515e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 7.8853e-08
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.2238e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.3477e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.0073e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.5887e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 6.5839e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.7771e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 2.0824e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.3586e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.3438e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.655e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6131e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4791e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 6.5819e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.7801e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.1798e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.873e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.931e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.4025e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.6135e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.5992e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00041185
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 5.4385e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00022365
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00029606
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 2.646e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.3778e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00014246
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 6.8545e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 4.6411e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.3044e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6224e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.6888e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00017523
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 4.9602e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 7.6291e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.842e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00019988
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00060336
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 4.8669e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 2.2119e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.2093e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.7722e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.4631e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.3428e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00023775
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00010068
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00011515
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0006783
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00014236
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.2322e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0005843
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.001041
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.061048
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0061521
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.039313
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.063512
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0045087
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0013191
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.056464
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.022219
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.019269
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.014288
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0094343
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0013238
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.078633
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.021596
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.031246
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0050971
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.022853
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.069753
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0070469
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0053549
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0028106
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0063725
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.021754
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0012535
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.055781
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.023144
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.026471
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.15592
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.032725
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0028325
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.13432
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.11928
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 8.6694e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.3154e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00037607
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00013917
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00012376
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00013875
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0001092
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1143e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00014985
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 6.1248e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 4.7358e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.4935e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.9124e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.8401e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00013727
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.8324e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00028511
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00010414
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 8.5537e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00035028
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 9.2195e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 9.7047e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00047335
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.7247e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 8.1028e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.9899e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.4497e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.6796e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.1089e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.0019e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.0318e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.1956e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 9.1373e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.6103e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.6928e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.9945e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.9307e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.8109e-07
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 4.0185e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.4647e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.203e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 4.9266e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.2967e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.3649e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.6575e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.7364e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0017885
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00060153
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00052651
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00040923
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00035673
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 2.3476e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00068869
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00024095
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00019015
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.9174e-06
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.3321e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.9204e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00038282
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3471e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00079477
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00029042
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00023854
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00097685
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00025711
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 2.7064e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0013201
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0011658
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00020523
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0013546
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0025908
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 4.9027e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00040994
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.011092
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.003051
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0034203
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0039702
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0032459
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00028794
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0048356
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0016415
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0012186
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.0435e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00068165
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.002961
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00018875
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 8.9942e-05
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0011176
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0016419
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0079358
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00028501
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.016815
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0060202
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0049449
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.02025
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0053298
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00056103
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.027365
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0039789
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.1624e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.6917e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.1697e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.1131e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.8681e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.2813e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.185e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 3.6559e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.8472e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.9671e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.1282e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.1709e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.578e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.6758e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 7.7222e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.1832e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.3833e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.8762e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 9.1915e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.0162e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.0391e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.6119e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1125e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.4688e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.4277e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.0506e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.2475e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 8.9664e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.0256e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 6.0408e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.2678e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.0974e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 5.2037e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.0534e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 2.2933e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 9.6409e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 9.3054e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 2.2338e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.0364e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 5.7279e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.6159e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.9966e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.5769e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.2147e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.2605e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.066e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.5045e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.7318e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 5.3805e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.0463e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.5824e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 8.5734e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.9163e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.2302e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.3242e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.5145e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.8061e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6647e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5945e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.0956e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.835e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.2426e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.91e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.0087e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.4697e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.6453e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.8e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0026857
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00021974
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0010412
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0027259
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00011258
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.5313e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.0002406
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00061834
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00035719
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.1135e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 9.269e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.1427e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.1464e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00050402
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.033e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00019248
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.9789e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00066508
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0019832
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00032743
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 9.8529e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4247e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.5718e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00025847
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5596e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.000694
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00027499
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00031453
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0018527
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00038883
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.3656e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0015959
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0024029
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.72272
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.060269
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.28801
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.75636
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.031095
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.013208
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.20438
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.50571
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.28741
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.068449
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.076973
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.027233
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0044099
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.38649
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.067273
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.16114
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.039133
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.17428
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.52192
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.088461
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.029634
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.015115
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.033406
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.11404
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0068853
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.30639
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.12133
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.13877
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.81739
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.17155
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.014849
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.70411
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.63692
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.0132e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 8.5413e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 4.2047e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00026641
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 9.4494e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 4.6448e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 7.5457e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.653e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.8632e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00011014
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.0858e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.1557e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.1507e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.7801e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.5599e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00012373
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.6213e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00027265
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 9.3862e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 7.7096e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00031572
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 8.3097e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 8.7471e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00042664
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.0777e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 9.3531e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 6.8714e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.5274e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.0804e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.7062e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 8.2968e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 6.3585e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.6787e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.7736e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.7628e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.7568e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.8303e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.0734e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.9688e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.3425e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 4.3321e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.4936e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.2268e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 5.0239e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.3223e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.3919e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.789e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00030413
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00076249
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0077633
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0031346
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00092043
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.001646
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.000691
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 7.1539e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0019809
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00039022
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00047975
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.0214e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00015101
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00021634
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0010456
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.9321e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00232
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00079323
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00065155
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0026682
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00070227
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 7.3923e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0036056
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.013801
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0020105
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0099243
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.030854
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00033813
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0041046
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.010135
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.099347
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.039466
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.01215
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.021388
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0093693
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00095918
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.023768
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0051134
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0062843
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00061755
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0051983
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.022156
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0023694
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00049774
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0060101
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0086071
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.041601
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0015655
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.092363
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.031559
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.025922
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.10615
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.02794
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0029411
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.14345
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.021247
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 7.5046e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.6869e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.0015e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.8621e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.1905e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 8.0253e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 9.9002e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.757e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 4.3561e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.3461e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.1501e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 9.1694e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.5129e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 6.7392e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.7551e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 9.6209e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.0247e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.1698e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 5.4227e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 8.5198e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.779e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.0532e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.3293e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.8413e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.2855e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.7935e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.6881e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 6.6873e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 7.6487e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 4.5053e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 9.4556e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 8.1844e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 3.881e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.8934e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.3138e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 8.1131e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 5.3437e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.6708e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 6.0223e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 4.4764e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 6.8059e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.0998e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 6.4035e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 4.7916e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 4.0038e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.0559e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.7406e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.0927e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.044e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.2662e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.7306e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 4.5644e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 7.0707e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.5576e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 7.3582e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.4807e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.4849e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.8724e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1297e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.0271e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.992e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.2784e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.3421e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.8167e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.438e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.1561e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.62e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0011605
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 6.2231e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00060161
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0020213
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 7.6621e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.3253e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 4.7052e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00025286
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 5.7825e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 7.468e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 7.2942e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8078e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.8247e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00035175
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 6.3566e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00021508
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.9503e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00022015
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00058021
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00010446
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.0001178
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.8349e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2697e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00021403
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2907e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00057436
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0002277
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00026044
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0015341
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00032197
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.7868e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0013215
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00098306
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.30946
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.017473
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.16649
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.53455
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.021139
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.011105
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.03671
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.20718
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.045945
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.062485
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.062042
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.015244
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0032025
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.28717
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.053339
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.17763
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.016763
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.056976
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.15402
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.028745
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.035399
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.012247
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.027079
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.092437
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0055771
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.24818
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.098345
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.11248
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.66257
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.13906
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.012036
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.57075
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.24272
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.2366e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 7.1357e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 2.0207e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00019848
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.2871e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 4.7348e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 5.9092e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.0051e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 3.3997e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.782e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.696e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.7359e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.5261e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.3328e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9092e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.2277e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.4711e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00020479
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.0003e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 5.7499e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00023547
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 6.1975e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.5237e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0003182
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.6238e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 3.9393e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.815e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.0263e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 9.9277e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.2986e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.2402e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 6.9578e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.5021e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.5878e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 5.7637e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.1878e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.9978e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.8622e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3834e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.2021e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.0692e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.0495e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 8.6201e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 3.53e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 9.2911e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 9.7801e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 4.7703e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00026323
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00014912
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0031747
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00050745
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0008472
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0012953
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00039751
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.3165e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0013824
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00030878
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00053606
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.967e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.000125
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00017913
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00086581
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.2542e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00192
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00065682
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0005395
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0022093
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0005815
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 6.121e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0029856
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0059097
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00058288
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0057368
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.021806
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00022987
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.003451
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0018204
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.040702
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0063089
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.011092
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.017239
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0052445
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00069657
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.01766
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0040542
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0069275
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00026453
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0016994
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0065381
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00076993
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00059458
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0048698
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0069768
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.033721
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.001268
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.074815
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.025582
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.021012
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.086048
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.022648
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.002384
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.11628
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.008097
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.3918e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 5.5102e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 3.1812e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 3.7523e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 8.7743e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 4.7626e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 6.1324e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 4.8064e-10
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.5571e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.5199e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.9376e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 5.5434e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.4368e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.6396e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.9177e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.0089e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.6415e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.1226e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.0295e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 3.3476e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.9102e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 9.9266e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7918e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.618e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9419e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6876e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 7.51e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.1299e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.5799e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.1087e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.4256e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.8306e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.8164e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.6958e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 4.2046e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.1604e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.1996e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 6.5995e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 3.573e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.8538e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.0404e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.3197e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.9462e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.89e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.5734e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 6.1661e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0408e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.3082e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.3142e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 6.8322e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.4479e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 9.0116e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.6389e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.8844e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 6.8586e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1631e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.6365e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.0001e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.188e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.3087e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 9.5753e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.0952e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 6.4511e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.3539e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.1719e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 5.557e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 4.8873e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0005731
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 3.1035e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00025807
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00087544
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 4.8693e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 8.4825e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 3.2043e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00012425
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.7449e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 5.5214e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 4.7866e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 8.8013e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.4174e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00024033
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 6.909e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00014106
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.7084e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 7.1581e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0003677
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 3.9766e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 5.6472e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.3959e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.1774e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00010846
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.2049e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00027612
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0001154
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00013199
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00077745
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00016317
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.4123e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00066971
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00035854
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.1459
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0085048
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.070506
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.2235
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.013022
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0072511
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00026306
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.094072
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.022191
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.045244
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.039795
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0073807
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0011773
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.19625
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.053499
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.11625
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0046511
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.018303
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.092003
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.010471
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.015548
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0059481
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.013524
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.046166
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0026465
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.11777
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.049117
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.056178
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.33091
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.06945
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0060113
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.28505
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.091519
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.3254e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 4.42e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 5.5278e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 7.0947e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.4395e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.8561e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.5724e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.1465e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.3316e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.1614e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.7786e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.4848e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.1088e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.0675e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.9357e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.3189e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5442e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 9.1106e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.2764e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.6912e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00011021
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.9007e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.0533e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00014893
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.0352e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.181e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.6784e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.1193e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.9879e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 8.3463e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.4762e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.6424e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 9.3898e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.8276e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.1101e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.1929e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.3663e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.3758e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.6496e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.389e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.4095e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 5.0446e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.1435e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.6968e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.466e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.7011e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 2.293e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00016847
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 1.0155e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0015599
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00024088
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00062637
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00085002
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00019352
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.9703e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00094454
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00033562
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00035158
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.7572e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.155e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.0782e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00043878
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5644e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00092302
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00033287
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00027341
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0011197
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0002947
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 3.1021e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.001513
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0027862
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00028371
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0024295
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0091174
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00014161
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0022534
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 1.3044e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.01848
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0030471
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0080311
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.011058
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0025393
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00025607
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.012069
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0040664
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0045338
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.3397e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00054594
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0039056
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00028046
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00026116
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0023651
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0034845
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.016842
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00060172
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.035501
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.012776
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.010494
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.042975
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.011311
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0011906
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.058074
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.003053
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.3643e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 6.593e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.205e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.7754e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 7.7855e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 3.1035e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 4.3143e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 6.301e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.0143e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.3033e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.5136e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.0162e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6159e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0517e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.5477e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 8.5258e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.5335e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.3522e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.8414e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 3.1014e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.5395e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.0672e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.3083e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.729e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.9557e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.4688e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 4.2136e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.0807e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.3798e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.4018e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.942e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.5465e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.2075e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 6.4803e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 5.0496e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.6362e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.386e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 5.7984e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.3222e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.7116e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.6581e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.2467e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.8654e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.7593e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.2195e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 6.6505e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.461e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.0958e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.4616e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 6.4375e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.5072e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.372e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.4131e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.5529e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 5.7559e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.7631e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.683e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.7453e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.7668e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.2312e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 6.1125e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.9913e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 4.1181e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 8.6428e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 7.4809e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 3.5474e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.0395e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00048365
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 3.8713e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00010742
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00059124
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 2.9133e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 3.6943e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 2.0691e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 8.4371e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.565e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 3.1427e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.6237e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 7.7185e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.0934e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0001657
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 4.1611e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 9.1156e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.8487e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00010476
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00028074
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 4.432e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 4.117e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.9899e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9933e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.8045e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.2604e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00014509
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 7.2394e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 8.2802e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00048773
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00010236
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 8.8601e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00042014
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00043062
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.10415
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0099843
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.02497
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.13242
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0070552
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0030608
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00097576
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.063638
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.017624
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.021855
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.020504
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0051774
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00042296
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.11424
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.029578
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.067349
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0048941
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.023558
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.064024
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0098759
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00075947
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0030429
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0074744
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.025515
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0012612
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.056124
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.027146
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.031049
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.18289
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.038383
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0033223
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.15754
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.088168
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.8823e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 3.1096e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 7.2468e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 4.6216e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.3705e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.6816e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.9438e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.2894e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.3056e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 3.6337e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.503e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.3871e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.6092e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.6936e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.9402e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.8711e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.6639e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.1117e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.1781e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.789e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 7.3262e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.9283e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.0298e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 9.9003e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 6.2086e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.5385e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 9.7378e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.9898e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.717e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.9552e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.6707e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1326e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.8653e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.0712e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.9304e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.7512e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.4464e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.7824e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.2448e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2741e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.5171e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.2202e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.645e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.0832e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.8509e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.001e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.4637e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 7.3373e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 6.5574e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0010593
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00022509
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00035652
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00046592
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00016971
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 7.0802e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00065121
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00020213
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0002272
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.9072e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.523e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.6952e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00027527
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.2206e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00048501
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00020882
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00017152
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0007024
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00018487
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.9461e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00094919
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0019889
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00033307
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00086042
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.005402
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 7.6719e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00095121
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 4.8386e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.012502
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00242
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0038794
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0056973
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0017813
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 9.1996e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0070254
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0022482
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0026266
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.7233e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00070268
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0027178
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00026452
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.2756e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0012099
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0019258
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0093079
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00028675
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.016919
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0070612
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0057999
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.023751
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0062514
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00065804
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.032096
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0029412
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 7.0817e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.7976e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.3949e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.9511e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 5.6653e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.577e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 8.6521e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 8.645e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.5631e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.5969e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.9771e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.1929e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.622e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.3617e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.9986e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 8.2607e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.5232e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.5062e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.5278e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 3.7903e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.7759e-10
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.7772e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.2055e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.5289e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.5553e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.5821e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 8.0101e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 9.1617e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 5.3965e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.1326e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 9.8034e-09
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.6487e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 4.3001e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 2.8591e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.014e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.5227e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 4.2047e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.9915e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.6279e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.6901e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.1017e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.1546e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 8.1215e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 9.0785e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.4714e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 5.9766e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.2647e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.3978e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.2898e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.196e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.9845e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.0525e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.1491e-10
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.6411e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.6374e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.2658e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0697e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 4.76e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.4106e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.7572e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.6241e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.4085e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.9503e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.399e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.3532e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00026068
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.3788e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00015947
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00034366
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 2.5201e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 5.3722e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 5.1824e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.0821e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.5836e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 1.1981e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6975e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.6937e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00011695
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 2.2076e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 7.1398e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.8854e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00010184
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00022777
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 3.5379e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 6.538e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.0437e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.7859e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.3405e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7005e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 7.5671e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 3.554e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 4.065e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00023944
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 5.0253e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 4.3497e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00020626
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00029406
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.06385
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0038734
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.037457
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.083204
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0064844
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0031732
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.039832
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.015704
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.020437
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0092715
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.014204
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0031202
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.087841
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.017065
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.054934
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0073115
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.023326
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.055503
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0084457
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.8235e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.001622
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0038945
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.013294
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00068723
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.030582
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.014144
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.016178
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.095291
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.019999
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0017311
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.082085
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.068759
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.0543e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 6.2361e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.9389e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 8.1627e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.0691e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.2742e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.7498e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.8361e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.9421e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.2862e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 7.4719e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.5751e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4045e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.2868e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.1053e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.2531e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.9193e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 8.3851e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 6.8873e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.8204e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 7.4235e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 7.8142e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 3.8114e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.316e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 8.4615e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.7658e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.3922e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.6341e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.6458e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 6.2744e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.29e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.122e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.5467e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.1586e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.1269e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.4635e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.674e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.9257e-08
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.9062e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.27e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.0431e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 4.2717e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.1243e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.1835e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 5.7726e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.0001067
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00065065
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00018272
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00029309
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00021276
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00037325
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.1345e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00045962
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00010724
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00017795
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.9613e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.783e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.7959e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00013514
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.2874e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00025296
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00010252
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 8.4206e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00034483
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 9.0761e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 9.5538e-06
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00046599
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0012193
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00012921
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0012907
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0033941
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 7.0512e-05
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00098615
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0078251
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0021563
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0036276
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0025762
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0048867
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00067865
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0054018
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0012971
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0021424
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00011538
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00069576
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0023561
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00022622
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.0628e-07
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00064494
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0010034
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0048498
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00015625
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0092189
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0036792
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.003022
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.012375
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0032572
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00034287
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.016723
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0022938
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.8126e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00013846
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.7803e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00027501
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00013838
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 9.006e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.2781e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 3.1701e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 4.741e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 5.8081e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.0935e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.9821e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 8.7004e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 9.8416e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 5.9448e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.3209e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.7423e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.8572e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00048398
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.0001693
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.3576e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.4181e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.0601e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.709e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.2475e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.2185e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.8772e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 9.8386e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.1253e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 6.6284e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.3911e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.2041e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 5.7098e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00015101
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 9.5789e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.633e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00020486
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 8.204e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 5.2038e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 7.403e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 9.9249e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.9868e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.375e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.6145e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 9.7391e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.8772e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.1631e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.095e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.2947e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 8.8884e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.1726e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.0003404
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00012697
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.756e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.2681e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.4538e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2635e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.1381e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.7766e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 4.3506e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.2748e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.6018e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00015326
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.2165e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.784e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00013202
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00011073
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00042231
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.8231e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00059442
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00049479
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 3.0909e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.4311e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 9.3258e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 9.2699e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 1.0407e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 4.2688e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 1.0579e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.7546e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 7.4011e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00013308
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 4.0399e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 6.5319e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.1574e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0011835
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00041717
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 6.2634e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 7.7027e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.7239e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.5855e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00015653
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.5595e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0002919
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00016654
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00019048
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.001122
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00023548
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.0382e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00096651
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00039896
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.021927
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00074202
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.033418
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.028121
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.001663
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 1.2817e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0064045
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.024334
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0028531
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0072664
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0018106
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0040237
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00071498
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.023364
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0043227
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.010569
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0024428
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.044486
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.025854
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.003393
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.8941e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0015272
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0038832
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.013256
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00061099
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.027189
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.014103
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.016131
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.095016
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.019941
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0017261
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.081848
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.023033
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.213e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.642e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.0003646
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0021602
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00018497
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00086188
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00019218
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00069424
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 4.9647e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00084789
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00023286
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00024804
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.5097e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00016963
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00028089
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0013576
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.8599e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0022773
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0010299
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00084595
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0034643
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0009118
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 9.5979e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0046814
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.6854e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 5.7446e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00045558
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 5.4094e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00015777
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.1587e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00011554
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 8.0304e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00015038
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.8103e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.0461e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.0018e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.9761e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.2684e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00015797
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.502e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00026562
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00011984
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 9.8436e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0004031
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.0001061
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.1168e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00054474
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.8423e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00029555
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0011638
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 9.1325e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00048427
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00018787
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0003858
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0288e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00052302
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00019625
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0001628
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.1759e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.6011e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00013102
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00063324
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6539e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00097578
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00048039
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00039458
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0016159
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0004253
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 4.4768e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0021836
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00041873
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 2.4753e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0011515
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0011471
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 1.8083e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 3.9832e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00031759
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0047804
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00039177
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0012898
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00050311
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0013843
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00015551
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0014368
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00032856
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0004122
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.8549e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0013269
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0010975
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 9.0882e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 4.8609e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00060725
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0010005
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0048358
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00013892
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0081961
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0036685
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0030133
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.01234
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0032478
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00034188
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.016675
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00076837
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.9742e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00014481
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 8.1958e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.8559e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00020626
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.8019e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 3.2228e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 3.0068e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.6588e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.258e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.177e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.76e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 7.5274e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.4812e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 5.2222e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.5081e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.7156e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.4987e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00019531
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 8.2151e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.5876e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.527e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.9389e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3446e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.0158e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.677e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.4305e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.6362e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 9.6378e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.0227e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.7508e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 8.3022e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.4402e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 8.425e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.7446e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.3016e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00011872
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.0337e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.0576e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 9.4374e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 8.5322e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.2117e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.769e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.6595e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.4242e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.8664e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.7391e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 8.0574e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 8.7785e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.7721e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00015319
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 5.008e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.2076e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.5108e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.0651e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.0945e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3816e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 6.148e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.2923e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.7656e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00022181
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.6552e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.0294e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00019107
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.3031e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00055147
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.6671e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00028843
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00070821
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 6.6033e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 7.7031e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 6.8127e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 8.4658e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 3.0088e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.986e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 4.6181e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.911e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 4.4943e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00014713
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.359e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 7.3092e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.7647e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00077475
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0003672
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 8.7997e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.3963e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.4046e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00021863
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.0675e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0004035
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0002326
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00026604
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0015671
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00032889
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.8468e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0013499
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00040857
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.040201
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0024685
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.01536
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.049042
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.003489
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0023222
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0095559
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.015114
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0032275
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.006533
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0091309
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0043806
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0852e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.028217
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.014478
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.014503
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0075401
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.046387
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.019377
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0031081
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0027858
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0069777
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.023819
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0011322
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.050381
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.025342
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.028985
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.17073
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.035833
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0031015
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.14707
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.021815
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.2827e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00023229
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00034581
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0012114
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00023115
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00048456
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0011342
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00060065
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 7.4719e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00074482
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00044215
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00024563
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.4852e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00024435
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00040841
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.001974
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.5044e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0032476
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0014975
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00123
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0050371
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0013258
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00013956
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0068069
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.8364e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 5.4625e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00019565
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 5.1476e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.809e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00018356
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 9.735e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.2355e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00012483
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.1486e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.9961e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.7901e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.8273e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.7304e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00022864
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.362e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00037536
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00017345
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00014247
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00058341
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00015356
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.6164e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0007884
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00015299
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00021591
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0010629
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00026404
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00033874
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00082009
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00042018
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 6.2474e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00057823
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00040606
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00018218
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.7968e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00010566
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00018299
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00088444
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.2862e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0013489
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00067095
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00055111
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0022568
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00059401
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 6.2527e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0030498
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00076769
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 8.2348e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00052926
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0020006
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 3.794e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00072168
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00047386
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0029691
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00044318
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0011596
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0025371
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015071
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 2.3605e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0017352
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0011005
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00056561
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00011899
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0013836
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00082256
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 8.3251e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0011077
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0017978
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0086894
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00025741
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.015187
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.006592
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0054145
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.022173
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.005836
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00061432
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.029964
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00072772
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.1873e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.312e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.987e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.6538e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 5.256e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 4.4612e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.277e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.9516e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 5.4817e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.6351e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.6143e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.1467e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.744e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.5684e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.7888e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 9.2621e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.5947e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 8.4061e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.0371e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.1094e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 6.0218e-10
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.0586e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2196e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.1631e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3111e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.8342e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 4.4292e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 5.066e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.984e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 6.2627e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.4208e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 2.5705e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.3023e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.7074e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.728e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.5428e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 3.0592e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.6276e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 7.4353e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.9102e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.6946e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 8.6102e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 8.4552e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 6.9977e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 5.738e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 5.0781e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.8804e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.011e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.247e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 4.7471e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 6.0222e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.1961e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 3.4836e-10
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.4082e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.827e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.6505e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.039e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.3524e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.0267e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.1743e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 6.9173e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.4518e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.2566e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 5.9586e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.4238e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 5.9046e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.2219e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 9.9554e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.000218
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 1.8374e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.2279e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.5388e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 7.871e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 9.2812e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 6.4384e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3218e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.5598e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 4.1823e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.8552e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 2.576e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.2552e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 1.9852e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 5.0462e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 5.2157e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 4.4792e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.0331e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.093e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00010558
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.3558e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00014933
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00011233
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00012848
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0007568
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00015883
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.3748e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00065192
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.6972e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0041451
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 1.0733e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0072251
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.014986
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0013999
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.001695
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0032332
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00010173
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0018137
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0016772
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0016038
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00012776
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.010052
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0039065
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0062463
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0011683
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0012349
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.0032873
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00040006
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.1637e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00083333
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0025547
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0087207
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00026074
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.011603
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0092781
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.010612
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.062508
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.013119
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0011355
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.053846
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0025274
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.1206e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00016412
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00027117
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.7458e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00010848
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00016848
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0001713
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 8.7976e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00022369
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00010205
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 8.3777e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.8367e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.4945e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00012645
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00061118
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1996e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00070777
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00046365
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00038084
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0015596
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00041048
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 4.3209e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0021075
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.6971e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.3802e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.7161e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.784e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.7423e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.8101e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.4568e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.645e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.6683e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.3706e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.6648e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.5765e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.4752e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.1302e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3994e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 8.2567e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 5.4091e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.4429e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00018194
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.7888e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 5.0408e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00024587
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00024388
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0001932
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 6.9073e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00010529
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00011434
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00029062
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 4.9484e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00016437
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 9.012e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 6.4204e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.283e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.5551e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.8371e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00042713
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.4609e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0004992
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00032403
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00026615
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0010899
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00028687
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 3.0197e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0014729
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 7.9157e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 3.5804e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00024896
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00061131
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 1.5223e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00052676
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00063516
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 1.3969e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00032194
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00046604
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00055178
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 2.7789e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00061814
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00029693
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0002436
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.8436e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 3.6835e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00013955
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 1.0715e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.6342e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00033135
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00065821
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0031813
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.9283e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0034977
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0024134
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0019824
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0081179
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0021367
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00022491
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.01097
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 8.4312e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.5716e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 5.8461e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.2124e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 5.1947e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.6634e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.3604e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.2689e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.378e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.9805e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 3.7311e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.9855e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.0979e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.7172e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 5.0964e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.625e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.9467e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.3403e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.5753e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.8415e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 8.1949e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 4.8678e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 5.5676e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 3.2795e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 6.8828e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.9575e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 2.825e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.7404e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 3.484e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.4276e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 3.0209e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.5919e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.6998e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 7.3825e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.093e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 9.6141e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.2639e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.5972e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.7399e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.675e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 3.1942e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.7995e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1651e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.1702e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0822e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.3155e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.9204e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.1514e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.3169e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 7.7569e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.628e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.4091e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.6819e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.5515e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00018318
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 7.4904e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00017136
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 8.833e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 5.5337e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 1.5145e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 7.9514e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 7.9977e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 9.2759e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.8853e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 2.7212e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 6.3709e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00023166
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 5.5901e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.1262e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.2316e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.618e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.9754e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0001324
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 8.1049e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 9.2701e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00054604
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0001146
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 9.9194e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00047037
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0001141
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.016907
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0053774
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.015678
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00066207
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.015037
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00041052
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0022503
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0021319
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.020399
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0052501
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0050105
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0056137
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.015268
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00030638
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00087635
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0023234
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0079313
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00033475
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.014897
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0084382
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0096514
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.05685
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.011931
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0010327
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.048971
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.010367
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.5404e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0010755
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.0411e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00013907
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00019208
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00053215
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00014078
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 9.931e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.9156e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00013897
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0006717
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.685e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00099415
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00050956
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00041855
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.001714
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00045113
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 4.7487e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0023162
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00017656
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.1833e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.2647e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.1182e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 9.072e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.3042e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.7025e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.3831e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.6543e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.9957e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.9872e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00011725
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 6.0657e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.9822e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00020403
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 5.3701e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 5.6527e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00027571
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00069476
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 1.329e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 9.0204e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00014202
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00036455
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 9.1582e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 6.7824e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.5831e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.3761e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00030818
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.5018e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00044261
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00023379
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00019203
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00078638
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00020698
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 2.1787e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0010627
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00032287
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00018529
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00063955
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 7.1994e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0029541
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 5.6369e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00039945
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00059237
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0012544
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00039906
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00019541
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00016744
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00064813
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 8.2064e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00034846
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00059862
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0028933
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.6111e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0044906
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.002195
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0018029
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.007383
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0019432
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00020455
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0099771
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00034585
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.8593e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.7597e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.0468e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 4.5708e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.2015e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.476e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.2142e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.8203e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.1883e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.3098e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.1658e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.3235e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 4.3641e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.7741e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.9443e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.1103e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.3141e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.3697e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.6758e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.0952e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 9.3236e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 4.9746e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 5.6899e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 3.3515e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 7.034e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.0883e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 2.887e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.6665e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.6212e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 8.5579e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.6557e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.2738e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 8.5423e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.5194e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 9.2559e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.8712e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.3978e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.6782e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.0425e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 2.5141e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.6532e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.7179e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.7252e-09
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.2304e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.1634e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0799e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.8648e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.1649e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.1489e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.3141e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 7.7403e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.6245e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.4061e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.6676e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.591e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 7.2793e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 7.949e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 2.2302e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 3.1724e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 4.4271e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 4.3677e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 4.4865e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.2088e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 5.1406e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.0942e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 1.7651e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 9.4813e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 6.3417e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 8.4786e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 1.6025e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.4165e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.8915e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.457e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.9576e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00013161
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 6.8697e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 7.8574e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00046282
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 9.7135e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 8.4077e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00039868
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 6.3346e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0074535
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 7.251e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00093839
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00034986
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00031814
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0019939
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.002214
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00073505
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.010522
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0029849
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0035401
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0073962
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.0068848
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00075025
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.4618e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00097282
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0023858
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0081443
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00040384
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.017971
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0086648
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0099106
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.058376
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.012252
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0010605
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.050286
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0081798
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.0958e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00010089
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 8.982e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 4.892e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00032944
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 9.1068e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.7197e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.5034e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00014202
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00068645
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.9171e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0011311
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00052075
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00042774
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0017516
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00046103
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 4.853e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0023671
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.7242e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.4835e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 8.0208e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 5.3101e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.4889e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 9.2975e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.9089e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.6507e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.9785e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.2402e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00013217
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 6.0527e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.9715e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00020359
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 5.3585e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 5.6406e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00027512
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 5.4837e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 3.9372e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.5057e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00020203
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 5.3152e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 4.3994e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.2702e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.4044e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00026121
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.4571e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00043997
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00019816
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00016276
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00066654
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00017543
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.8467e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00090073
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00014234
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 2.4189e-07
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 3.2335e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 1.4272e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 3.4595e-06
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0003917
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00030401
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00013048
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00064702
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00022688
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00013806
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00022061
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00029226
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 2.0095e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.4553e-08
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00038681
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0006147
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.002971
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.1819e-05
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0054173
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0022539
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0018513
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0075813
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0019954
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00021004
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.010245
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00027287
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.8474e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0001798
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 9.2543e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 7.827e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00014718
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 7.2313e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 3.7142e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 4.7672e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.36e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 5.5657e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 9.6922e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 9.8033e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 7.0535e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.4186e-09
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.3676e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.647e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.087e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.4804e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 7.3212e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 9.138e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.5773e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.0306e-10
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5723e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.9291e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3413e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.4051e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.8503e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.427e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.6322e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 9.6139e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.0177e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.7465e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 8.2816e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 9.774e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00011306
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 5.7314e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 5.381e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 8.8695e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 4.3546e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.2483e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.5652e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.3337e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.143e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.2204e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.2526e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.3776e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.8502e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.4924e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 5.443e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.0304e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.8078e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 4.3777e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 6.6399e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.6448e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.2064e-10
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7759e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.4287e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.2186e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5394e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 6.8502e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.4243e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.9167e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0002307
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.8419e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.191e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00019873
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.0176e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00042926
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 3.6149e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0003266
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00058357
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 2.7927e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.1343e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 1.4814e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00017278
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 1.9827e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 3.2282e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.6609e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 2.0922e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 8.1561e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00012588
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 3.5599e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 7.3736e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.612e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00013462
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00030676
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 9.2707e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 6.3268e-10
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.8618e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.3566e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0003194
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6222e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00072186
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00033982
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00038867
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0022894
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00048049
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 4.1589e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0019721
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00029062
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.072425
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0055682
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.037168
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.079552
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0037396
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00049304
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0054381
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.060876
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0075417
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.011919
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.010881
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0089345
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 7.1088e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.052495
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.017924
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.033817
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0059493
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.025684
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.036845
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.008847
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.6969e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0065696
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.016158
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.055158
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0027195
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.12102
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.058683
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.06712
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.39536
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.082976
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0071821
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.34057
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.046468
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.0906e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.6771e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 5.4827e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0024422
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00017725
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00039902
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00063178
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00056283
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.7335e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00062294
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00029034
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00027922
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.0058e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0002516
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0004074
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0019691
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.8607e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0034578
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0014938
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.001227
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0050246
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0013225
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00013921
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00679
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 4.5281e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 9.0597e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00053513
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.4348e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 6.6725e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00010549
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 9.548e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.6972e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00010712
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.829e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.6906e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.33e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.0408e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.9201e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0002378
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.0886e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00041823
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.0001804
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00014818
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00060681
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00015971
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.6812e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00082002
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.2528e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 4.6949e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0021693
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.000174
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00036622
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00047252
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00046003
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1337e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00049471
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00017293
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00018378
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.6257e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00017028
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00026733
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0012921
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.09e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0024131
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00098021
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00080513
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0032971
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0008678
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 9.1347e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0044555
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0013831
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00018575
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0012807
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0032452
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 4.0664e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00015322
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00026967
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.011959
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0010356
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0021158
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0030234
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0030739
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 1.5462e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0032282
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0013624
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0013188
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.3884e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0007661
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0015641
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00023696
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.8501e-09
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0026122
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0041631
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.020122
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00061832
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.036481
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.015265
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.012538
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.051345
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.013514
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0014225
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.069385
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0015501
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.1714e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00010138
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.1009e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.8767e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00015525
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 8.6792e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 8.1182e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 8.2721e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.6003e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.5837e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 7.0595e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.0514e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.1211e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.3588e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.9177e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.2912e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.9246e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.4298e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.5018e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 3.9244e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 8.7829e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.4843e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5037e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.8049e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.2989e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.047e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.6909e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.3819e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.5806e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 9.31e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.9539e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.6913e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 8.0198e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 4.0912e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 6.1916e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 6.481e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.1749e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 9.214e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 5.1763e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.8537e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.649e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 5.8752e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.0995e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.3651e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.5263e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.0116e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.6036e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.6317e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.7299e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 9.6583e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.7505e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.5516e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.7195e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 5.5818e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.3276e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.554e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.9989e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.0719e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4282e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 6.3553e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.2682e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.7381e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00022019
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.6212e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.9999e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00018967
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.1269e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00043918
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 4.787e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00027631
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00061971
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 3.8227e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.2785e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 3.7383e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 4.9775e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 7.7943e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.3146e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 3.9548e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8109e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.9464e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00015242
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 7.3912e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 9.397e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.6824e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00010613
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00017502
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 3.4616e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 1.0325e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.0333e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.7594e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00026488
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2058e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00053657
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00028181
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00032233
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0018986
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00039847
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.449e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0016355
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0001771
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.04412
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0053748
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.037481
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.082681
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0048096
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0014989
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0060299
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.018605
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0014322
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0091202
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.014691
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0069687
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0020963
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.060776
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.031591
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.035613
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0096553
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0097506
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.017173
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0039897
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.1617e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0060896
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.015481
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.052847
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0024368
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.10844
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.056225
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.064309
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.3788
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.079501
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0068813
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.3263
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.010071
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 9.3652e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 5.8514e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 9.5138e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00072913
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 8.2283e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00029063
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00067759
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00048843
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 6.8546e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00070139
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00040391
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00026453
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.0853e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00024062
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00039452
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0019068
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.5329e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0032644
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0014466
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0011882
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0048657
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0012807
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00013481
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0065753
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.0352e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.5333e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00013472
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.7623e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 4.9003e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00011437
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 8.0783e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1688e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00011712
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 6.858e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.3966e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.0663e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.8621e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.6958e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00022696
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.5765e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00038801
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00017218
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00014143
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00057915
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00015243
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.6046e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00078264
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 4.5254e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00011847
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00062493
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 6.84e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00026257
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0007023
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00039818
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 8.2658e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00059905
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00035904
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00023421
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.7053e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00013375
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0002217
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0010715
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.0401e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0017937
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00081289
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00066769
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0027343
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00071967
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 7.5755e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.003695
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00084255
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0001793
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0012915
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0033728
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 5.23e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0004658
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00029901
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.003655
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00019666
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0016189
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0040822
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0023975
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00045595
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0037374
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0024012
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0013889
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00015237
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00029084
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00072901
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00010686
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 5.3105e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0024214
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0039887
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.019279
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00055404
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.032688
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.014625
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.012013
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.049194
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.012948
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.001363
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.066479
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00033596
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.0721e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00012419
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 3.2321e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.9988e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00012974
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 5.5616e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.3171e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.3731e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.0504e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.6514e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.2162e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.7675e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.41e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.6821e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.4348e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.2112e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.0429e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 7.2327e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00011724
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.616e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 4.9776e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.3654e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.7667e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.4446e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.1044e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.3815e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.0048e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.1493e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 6.7696e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.4208e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.2298e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 5.8315e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00026283
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 9.6154e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.9331e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.7961e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 7.914e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 3.396e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 4.4766e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 8.1626e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.8813e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.2765e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 7.4605e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 9.4357e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.8645e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 9.3093e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.9511e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.0909e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.6277e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 4.5309e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 8.3734e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 2.3391e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.9695e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2798e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.743e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.3018e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.5435e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.3569e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.4489e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.801e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00016499
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.4627e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.9972e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00014212
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00018803
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00059973
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.2273e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00011826
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.001047
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 3.026e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 9.6282e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 7.6887e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.523e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.9788e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 6.8371e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.5058e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 4.4698e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 9.6407e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 4.732e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 6.7843e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.8227e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00028305
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00061174
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00014047
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 2.7598e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.3578e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.2867e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00024874
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.2798e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00032395
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00026464
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00030269
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0017829
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00037419
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.2388e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0015358
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00097413
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.04747
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0019781
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.015653
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.067966
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0030137
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0017054
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.026904
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0083356
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0087849
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.002904
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.004013
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0012873
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.037428
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.01962
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.016119
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00015813
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.022772
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.044555
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0092056
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.8921e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0039076
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.011002
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.037558
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0013855
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.061654
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.039959
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.045704
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.26921
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.056501
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0048905
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.2319
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.078029
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.624e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 9.4934e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0010813
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00033453
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00027383
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00014282
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00022083
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 7.113e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00038253
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00025294
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00010955
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.817e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00014986
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00028687
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0013865
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.8405e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0016759
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0010519
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00086398
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0035381
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00093123
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 9.8024e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0047812
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.6239e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00018717
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 7.8236e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 4.7167e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.4197e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.7892e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.235e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 6.6821e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.3926e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.8622e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.6822e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8359e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.5186e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00017007
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.4737e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00020495
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00012902
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00010597
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00043396
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00011422
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.2023e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00058644
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00019123
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00096532
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00022141
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00033792
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00012141
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00033109
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 6.2134e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00037889
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00022987
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00016909
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.8724e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00010396
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00020819
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0010062
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.8355e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0010829
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00076336
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00062701
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0025677
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00067582
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 7.1139e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0034698
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00090651
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 6.5988e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00053938
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0027725
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 3.2771e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00052999
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0052853
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0011446
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0015594
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00080692
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0013807
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00028
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0023016
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0014913
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00062863
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.4954e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00067924
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0018914
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00024657
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.178e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0015537
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0028348
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.013701
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00031501
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.018586
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.010394
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0085376
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.034962
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0092022
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00096865
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.047246
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.002603
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.7662e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.529e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.2175e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 9.4609e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.2963e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 9.7782e-09
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.0074e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 6.049e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 5.6585e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 7.9102e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.9188e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.6578e-09
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.2972e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.3337e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.357e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.8436e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.5116e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.5599e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 3.8793e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.1472e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.3452e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.8247e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.7811e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.9076e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.9413e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.2204e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.3079e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.7449e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.3759e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.1266e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.8691e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.5435e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.6858e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 5.718e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 7.9433e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.3533e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.3662e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.0107e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.9085e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.6417e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.4535e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 5.708e-09
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.3744e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.8246e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.123e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.3222e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 9.5463e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.5813e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 2.3501e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.1813e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2895e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.402e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.1195e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 9.4317e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.6834e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 5.3567e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 3.1553e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 6.6221e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 5.7318e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 2.718e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.1206e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00014512
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 5.3619e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 5.8944e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 6.169e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.5182e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 4.2977e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.8428e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.3231e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.8075e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.4807e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.0529e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 5.2535e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.7484e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 3.0203e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.8623e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00010669
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00015612
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 7.9031e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.8226e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.4199e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.847e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4306e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00010816
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 5.1568e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 5.8982e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00034742
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 7.2916e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 6.3113e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00029928
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 8.5033e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.011997
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0069523
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0051719
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00073715
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00013304
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.011026
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0059692
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0061691
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00088759
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.001348
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 2.4743e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.014896
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0065437
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0065395
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00025084
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0083331
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.013158
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00022762
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00081623
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0020102
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0068621
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00033744
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.015016
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0073007
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0083503
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.049186
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.010323
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00089351
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.042369
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0073762
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.193e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 7.0478e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00045902
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00019264
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00023295
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 5.0977e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 5.5209e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 8.363e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00018502
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 9.4027e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.75e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.7476e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4358e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.5422e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00026787
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.0346e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00047404
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00020322
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00016692
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00068354
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00017991
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.8938e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00092371
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.2164e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.7188e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.2226e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.9543e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 8.5678e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 9.8529e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.4491e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.1399e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.6188e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 9.664e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.1645e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.1726e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.7291e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.2524e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.76e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.7584e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.4673e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.0266e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 8.2992e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.1844e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.2993e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00011215
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 3.0152e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00053958
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00024948
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00026354
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 4.9856e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.2558e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 4.2437e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00020647
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.493e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 7.5279e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.8868e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5674e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.0568e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00019608
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.1283e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00036157
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00014875
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00012218
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00050034
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00013169
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.3862e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00067614
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00022911
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00023956
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00021098
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 8.0158e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 4.1346e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0021661
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00081965
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0010951
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00024663
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00046378
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 5.3817e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00091602
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00049738
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00025503
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.9584e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00024856
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00055857
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 6.0966e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00032455
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00051792
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0025033
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.6721e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0045266
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0018991
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0015598
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0063877
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0016813
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00017698
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0086321
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00024606
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.0787e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.8938e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 4.1465e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.3269e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.0748e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 7.2799e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.0507e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.7081e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.2835e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.0157e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.3258e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 4.4688e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.5823e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.4084e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 7.6663e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.3592e-09
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.0937e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9317e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.5941e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.4487e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.5347e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.0156e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 8.0242e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 4.7265e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 9.9198e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 8.5862e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.0715e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.4702e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.7335e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.6232e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.0027e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.2267e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 4.3168e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.0401e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 9.5644e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.5493e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 6.7887e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.6791e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.4794e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.6789e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 8.6059e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 4.8505e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 5.2884e-09
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.919e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.5783e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.5629e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.1797e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.64e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.6628e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.9018e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.1202e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.3511e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.035e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 9.6498e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 9.713e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 9.6091e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.9125e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 4.4441e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 6.2365e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 2.3038e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 9.367e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 8.1165e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 5.5365e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 5.8889e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 5.6702e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 1.1583e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 1.4465e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 5.2214e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 3.4726e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 5.8716e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5435e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.6229e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.2367e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.6785e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 2.9719e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 1.3158e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.5049e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 8.8645e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.8604e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.6103e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 7.636e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.982e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0092464
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 1.9144e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00029211
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0058705
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00022288
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0025937
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0026688
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0016387
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0018425
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0016653
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0035488
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0013036
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.0050327
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00034514
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.8594e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00022365
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00052538
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0017934
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.6695e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0043029
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0019081
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0021824
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.012855
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.002698
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00023353
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.011074
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0076366
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.6524e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.000139
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 8.6246e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 9.4011e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.8749e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 4.1001e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 4.042e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.2951e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.0029e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.6807e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.1555e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00018618
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.344e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 6.0322e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00024703
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 6.5018e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.844e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00033382
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.3849e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.533e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.5642e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.8729e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 6.8129e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 6.7345e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5454e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.3891e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.1547e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.7666e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.2223e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 8.7599e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 7.1952e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.9465e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 7.7553e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 8.1635e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 3.9818e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0001176
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 7.1228e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 6.2808e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.3144e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 2.7544e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 2.887e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.8059e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0351e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.003e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6839e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 9.9347e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 3.7954e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 3.1174e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00012766
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 3.3601e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 3.537e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00017252
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00017657
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 6.3864e-07
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 1.0066e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00023948
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 2.4237e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00050954
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00036647
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00029088
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0001133
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00012658
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0001384
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 3.8882e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00021364
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 9.2443e-06
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 6.4824e-08
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.8927e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00013536
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00065426
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.1985e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0012971
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00049633
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00040768
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0016695
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00043941
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 4.6254e-05
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0022561
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00025475
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.21e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 6.4678e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.6606e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.6425e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00018975
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 6.8292e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.5719e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.2954e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.3135e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.7615e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 9.7672e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 9.4384e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.7351e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 8.0896e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.5969e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.1884e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.0378e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.6385e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.6861e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 5.5318e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.1662e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5102e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.6141e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.2337e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.4182e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.8561e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.3126e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.5013e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 8.8431e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.856e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.6064e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 7.6176e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.1485e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 4.0512e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.0294e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.227e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00011943
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 4.3123e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 5.5412e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 4.5933e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.1806e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.8339e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.4484e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.3262e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.3647e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.8145e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.6154e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.1831e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 7.1781e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.2575e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.8733e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 3.5325e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 8.3857e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 7.6937e-12
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.8192e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.1422e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.1208e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6228e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.2216e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.3203e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.7977e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00022369
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.6948e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.0636e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00019269
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 4.8153e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00035404
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 6.8835e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00045391
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.001163
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 3.8125e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 4.2118e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 4.9894e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00017101
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 3.1734e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 3.8508e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 3.7022e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 2.7547e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 2.7543e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00022218
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 4.983e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 9.6904e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.2385e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00027404
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00030928
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 9.9234e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.363e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00010536
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00035966
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.8385e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00081815
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00038264
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00043766
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0025779
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00054105
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 4.6831e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0022207
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00051798
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.077537
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0018817
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.080306
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.23495
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0088056
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00037475
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.036367
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.094881
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.013021
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.028873
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.027669
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.020258
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0022773
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.12931
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.035514
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.06043
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.010034
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.020807
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.059315
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.01154
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.014447
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.034749
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.11862
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.006111
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.27194
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.1262
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.14435
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.85024
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.17845
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.015446
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.73241
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.061717
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.2188e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.1329e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00014898
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0015097
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00015164
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00040211
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00060826
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00053743
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 4.0809e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00065563
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.0002095
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00018432
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.3317e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00024165
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00037474
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0018112
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.8726e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0034648
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.001374
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0011286
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0046218
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0012165
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00012805
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0062456
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.01e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.6587e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00027071
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.9394e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.1447e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00010788
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 9.4962e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 7.1455e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00011595
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.7113e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.2676e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.3162e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.0756e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.7706e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00023058
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.4729e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.0004409
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00017492
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00014368
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00058838
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00015486
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.6301e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0007951
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 8.365e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00015812
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0021471
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00027849
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00043685
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00065744
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00060569
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.8287e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00087319
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00024206
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00024153
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.2491e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00019238
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00030102
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0014549
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.6355e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.002735
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0011038
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0009066
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0037126
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00097717
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00010286
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0050171
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0014807
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 6.2772e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0027672
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0095841
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 9.5753e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00011646
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0018034
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.018639
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.001788
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0051252
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0076883
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0069697
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00049531
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0079519
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0026994
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0023567
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00015835
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00062062
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0025179
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0003091
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0057445
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.008953
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.043273
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0013894
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.081977
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.032828
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.026964
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.11042
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.029063
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0030593
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.14922
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0020588
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.2544e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 9.3731e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.6194e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 8.8383e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00013587
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.0421e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 8.1253e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.9969e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.2127e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 3.3637e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.1012e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 9.9162e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 8.3331e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.3384e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.4447e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.4411e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.2574e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.3442e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 4.5989e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 5.7485e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.4634e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.4806e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.6015e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.5887e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.225e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.2136e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.2101e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.3033e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.4907e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 8.7808e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.8429e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.5951e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 7.5639e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.5741e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 5.6766e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 9.58e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 5.4471e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 8.5076e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 6.4311e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.7607e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 6.7229e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.5611e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.1273e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.8092e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.4532e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.9113e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.6837e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.5348e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.9291e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.1182e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.7867e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 2.7131e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 3.4494e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.4318e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.1389e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.9826e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.9237e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.0462e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7939e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.9828e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.2409e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.7069e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00021835
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.5826e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.9665e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00018809
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 4.5307e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00048046
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 7.3105e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00043897
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00076882
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 6.3854e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 3.0399e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00013106
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 8.3913e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 1.1354e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 5.0727e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 5.1993e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.7089e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 6.8262e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00018994
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 6.1122e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00014133
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.8564e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00013578
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00022077
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 6.2255e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 2.5204e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.8917e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00010951
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00037381
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.2051e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00098128
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0003977
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00045488
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0026794
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00056234
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 4.8674e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0023081
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0002104
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.092269
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0017852
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.097275
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.16966
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0125
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0021231
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.046893
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.05957
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0084954
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.034509
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.030092
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.027246
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.004162
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.12278
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.038825
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.093511
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.019225
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.030182
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.048079
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.014252
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0048178
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.01537
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.034438
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.11756
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0069237
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.3081
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.12507
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.14305
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.84264
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.17685
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.015307
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.72586
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.045964
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.8349e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 5.8565e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00022967
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0010082
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00010712
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00045334
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00063905
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00066494
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 6.7516e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00063393
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00025406
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00029463
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.054e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00025627
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0003721
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0017985
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.6004e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0038942
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0013643
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0011207
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0045892
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0012079
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00012715
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0062016
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.0014e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 3.8913e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00017338
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.8068e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.8923e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.000112
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00011691
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1891e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00011017
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.3731e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 5.09e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.133e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.2072e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.6566e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00022507
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.2606e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00048738
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00017074
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00014024
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00057431
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00015116
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.5912e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00077609
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 6.0376e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00041535
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0010535
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 9.9637e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00057547
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00092331
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00081551
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 9.4889e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0007465
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00029691
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00035225
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.8893e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00021569
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00031287
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0015122
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.5598e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0032803
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0011472
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00094229
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0038587
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0010156
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00010691
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0052145
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.001762
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 5.9554e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0033519
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.006921
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00013593
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00065978
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0023253
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.011703
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0011665
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0061257
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0083616
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0093737
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00090526
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0075504
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.002951
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0036469
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00030339
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00090026
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.002041
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00038174
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 8.0922e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0061116
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0088729
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.042886
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0015742
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.092878
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.032534
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.026723
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.10943
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.028803
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0030319
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.14788
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0015333
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.1507e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.4747e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.9621e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.5215e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.7899e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.0253e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.1225e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.2574e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.3345e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.2152e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.5e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.5633e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 7.9895e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.9544e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.3483e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.8247e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.9692e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.987e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 6.5069e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7355e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.3632e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.8549e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6837e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 7.4927e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.0374e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.474e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.0463e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.2947e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.7173e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.7627e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.7855e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 9.6022e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.074e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.6158e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.1739e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.3011e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.9704e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.9776e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.1971e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.0629e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.4859e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 9.396e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.8714e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.4324e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.2975e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.3559e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.2754e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.3154e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 4.0415e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.5215e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.1314e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.2759e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.2923e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.9101e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.7409e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 8.8538e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 5.2152e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.0945e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 9.4739e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 4.4924e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.9548e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00017148
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.0273e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00018179
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00012769
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 1.8125e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 8.6238e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 8.122e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.6184e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.1853e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 6.1491e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 2.2576e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 4.4947e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 2.5071e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 4.3207e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.1741e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00024877
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00017079
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 5.68e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.7478e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.9522e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00013491
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.8127e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00034766
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00014354
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00016417
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00096704
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00020296
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.7567e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00083302
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00021754
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.021702
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00063118
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.032345
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.024247
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0027736
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.029916
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.001689
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.010048
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.010119
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0051223
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00078075
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.023824
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.013811
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.022609
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0036857
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.022704
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.021166
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0063763
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0037268
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0083904
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.028642
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.001672
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.074405
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.030473
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.034854
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.2053
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.043087
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0037295
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.17685
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.024501
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 9.2758e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00051145
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.3113e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00013728
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0002072
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00011969
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.2931e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00011395
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 6.9711e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.7421e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.6785e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.9774e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.6715e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00041912
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5406e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00090896
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00031795
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00026116
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0010695
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00028149
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.9631e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0014452
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 9.1042e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.7724e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.4802e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.4472e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.203e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.3854e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.0611e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.2708e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.0458e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.1707e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.6678e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.1122e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.3757e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.9765e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00011661
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.0781e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.3497e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00013717
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.6105e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.8005e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00018537
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0010827
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 7.1276e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00029704
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00038807
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0001352
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.1382e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00017665
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00012179
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00010769
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.2098e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.7066e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00011292
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00054578
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.9698e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0011622
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00041404
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00034009
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0013927
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00036656
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 3.8585e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.001882
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00041443
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 2.1056e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0011146
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0009891
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 3.016e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0058771
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00023192
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0017836
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0028118
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0017623
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00016982
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.001465
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0010498
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00088172
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.8162e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0006772
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00089849
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00017079
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0014819
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0021618
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.010449
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00038016
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.022429
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0079266
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0065107
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.026662
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0070175
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00073869
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.03603
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00081732
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.1387e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.6527e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 3.3287e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.9099e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 6.1075e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.0402e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.292e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.8265e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.7146e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 4.5783e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.0537e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.3346e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 4.224e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.9485e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.1026e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 3.1333e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.9279e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 5.7693e-09
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.4797e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.0155e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.0535e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0404e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 4.6298e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.1847e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.4988e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.4719e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 3.0891e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.6738e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.2679e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.0884e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.0749e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.1949e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.2484e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 3.7756e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.3252e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.9787e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 7.6213e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.0068e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.5462e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 7.4731e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.9664e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.5188e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.1729e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.4399e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.0617e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.2842e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 4.2603e-09
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.3951e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.5482e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.2849e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.6885e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.1964e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 5.6227e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.4311e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 3.7881e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 7.9503e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 6.8815e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 3.2631e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.1966e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00010042
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.2632e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00011044
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 4.0688e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 1.2487e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.379e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00012393
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 1.4076e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 1.5033e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 8.4428e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 7.5611e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.7872e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 2.9642e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00013265
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00015588
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 1.3349e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 4.3117e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.8989e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9965e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.8152e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.1802e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00014152
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 7.2508e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 8.2933e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0004885
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00010252
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 8.8741e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0004208
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00019862
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.022043
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0053749
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.025976
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00662
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0028896
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.01647
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.030513
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0091684
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00086375
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0069187
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.041215
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.011851
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.020165
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.016522
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.024323
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0031356
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 9.3589e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0025533
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0061347
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.020942
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0010811
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.048109
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.02228
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.025483
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.15011
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.031503
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0027268
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.1293
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.028141
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.785e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00024112
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00058168
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00011176
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.9505e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00016387
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00019034
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.4464e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.3805e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.968e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2373e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00030147
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.5196e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00056166
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0002287
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00018785
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00076926
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00020247
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.1313e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0010395
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.5373e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00012215
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.0861e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.0149e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.0011e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.5648e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.3474e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 9.8913e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.1501e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.0787e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.9047e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.238e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.3042e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.9622e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.4331e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 9.9638e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.6225e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.7605e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00013465
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00029868
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0010876
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00015968
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.6695e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00018564
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00029716
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.6819e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 7.3881e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4829e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.7042e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0002757
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.0182e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00047307
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00020915
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00017179
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00070351
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00018517
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.9491e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00095069
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00042094
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0001793
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00089507
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00027005
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 3.1422e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0032356
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0041898
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0016275
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00024
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0023803
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0025345
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00090079
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00078644
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00049279
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0010325
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 8.3986e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.572e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0010152
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0015806
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0076396
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00024581
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.014503
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0057955
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0047603
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.019494
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0051309
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00054009
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.026343
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00093876
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 6.2155e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.347e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.9557e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 6.0932e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.259e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.8698e-10
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.8336e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 6.2004e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.9549e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.3644e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 9.8525e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.2961e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.8773e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.1018e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 5.6533e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.437e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.8587e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.3449e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.8533e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.7147e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 6.7505e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 7.721e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 4.5479e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 9.5449e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 8.2617e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 3.9176e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.5429e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 3.958e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 8.3429e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.8392e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 3.8821e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.175e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 6.5928e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.1424e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3741e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.7142e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.4443e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.6301e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.0391e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 6.8392e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 3.5727e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.1976e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.8406e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.6524e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0038e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 4.4667e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.758e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.0108e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.1844e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.4858e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.1516e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.0203e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 9.6131e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 5.4769e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 7.469e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 1.485e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 3.9637e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 9.8001e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 4.8308e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 9.0728e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.3208e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6778e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.1067e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 5.6095e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 4.3371e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 1.9528e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 6.6375e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 2.8557e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4265e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.5396e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.5738e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5664e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 6.9706e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 2.7383e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 3.1319e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00018448
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 3.8718e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.3513e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00015891
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0001046
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0069439
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.015415
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0038916
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00084811
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0083943
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 4.6907e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0050303
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0018534
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0014607
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00040782
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.023835
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0024963
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0086073
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.00092684
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.0055626
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00085281
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0018786
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.006413
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00038951
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.017333
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0068228
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0078038
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.045967
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0096473
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00083503
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.039596
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.010863
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00014849
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 5.9547e-08
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 7.5487e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.9959e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.1558e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 6.8826e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00014052
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.2862e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.6026e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.3501e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9272e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.3149e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.5257e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00020802
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.0665e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 5.8043e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00023769
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 6.2561e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.5853e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0003212
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.6942e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.366e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 6.9486e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.5182e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1968e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.19e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.3334e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.7301e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.7697e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.5259e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.2209e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.6222e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.7271e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 9.2617e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 7.6074e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 3.1153e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 8.1996e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 8.6312e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 4.2099e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00012304
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 4.2393e-07
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00010293
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 4.1213e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.6891e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 7.0986e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00022046
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 2.1068e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 4.8672e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5109e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.1542e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00010412
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.9494e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00023302
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 7.8986e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 6.4878e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00026568
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 6.9928e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 7.3608e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00035903
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0001326
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00053116
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00015875
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 9.2224e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0016491
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 6.441e-06
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00089292
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00051498
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00050257
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 8.8703e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0014657
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00018974
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00033568
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 2.7645e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00023613
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0003391
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00048403
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0023395
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.8561e-05
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0052251
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0017748
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0014578
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0059697
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0015712
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00016539
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0080671
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00036239
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.9147e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 6.973e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 9.3348e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 4.4776e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00014752
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 5.1402e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 8.7093e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 9.595e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.882e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 8.897e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 5.5474e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 5.9562e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.48e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 6.3338e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.2886e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 8.7962e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.4819e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.1306e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 4.4237e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 5.8501e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 9.5278e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.116e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.2838e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.5214e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.1934e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.6414e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.1754e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 5.5253e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 6.3197e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 3.7225e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 7.8126e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.7623e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 3.2066e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.4018e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 5.0332e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 6.1626e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.2682e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.0001025
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 3.5543e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.389e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 3.507e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.2059e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.197e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.2075e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.3698e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.325e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.429e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 8.9943e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.4054e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 5.6796e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.3145e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 3.2459e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 4.3864e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 7.9215e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.6578e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.7263e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.1657e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.422e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.2799e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.2395e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.5129e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.7304e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00010193
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.1392e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.8516e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 8.7803e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.8297e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00090706
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00010909
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0006074
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0021406
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 6.9064e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 8.8163e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 8.3207e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00036307
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 9.7665e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 5.704e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 6.324e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.5082e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.4526e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00022915
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.9971e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00014653
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.7556e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00045193
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00080519
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00011456
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 6.1118e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.9825e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.599e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00032767
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6812e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00074816
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00034862
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00039874
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0023487
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00049293
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 4.2667e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0020232
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00087954
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.22432
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.015269
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.15339
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.49221
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.017087
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0071131
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0657
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.26941
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.064611
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.043656
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.050458
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.029404
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0046929
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.18356
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.071989
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.11736
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0062063
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.10794
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.1992
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.028557
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0016181
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.016585
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.039613
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.13522
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0070622
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.31427
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.14387
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.16455
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.96925
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.20342
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.017607
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.83492
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.20807
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.6883e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 6.2774e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00011035
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0013131
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00028334
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00022838
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00038385
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00027769
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 3.1952e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00032642
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00015507
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00013404
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.3418e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00010055
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00015774
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00076243
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4169e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0014259
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0005784
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00047508
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0019455
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00051207
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.3902e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0026291
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.2293e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.0299e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00027651
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 6.7268e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 4.5738e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 7.6862e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.3211e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 6.1667e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 6.4561e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.0213e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.5854e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.1053e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.3902e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.1738e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00010507
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.3523e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00019778
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.9705e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.5468e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0002681
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 7.0564e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 7.4278e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0003623
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.0001751
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.0002637
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0045583
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00085708
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00064708
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.001123
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00077139
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 7.5795e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0009006
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00043705
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0003652
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.8218e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0001756
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00027426
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0013256
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.2389e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.002501
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0010056
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00082598
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0033825
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00089028
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 9.3714e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0045709
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0042838
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00050938
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0052855
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.020079
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00018581
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0022105
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0032579
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.052926
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.008872
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0077493
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.01402
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.010116
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0010207
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.011288
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0054718
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.004577
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.7939e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0032195
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0084559
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00076489
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.7178e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0065948
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.010206
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.04933
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0016057
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.094736
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.037423
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.030738
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.12588
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.033131
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0034875
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.1701
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.006941
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.7794e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.0668e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.9703e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.5372e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 6.9611e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9062e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.4156e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 2.7051e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.1114e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.9064e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 4.7436e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.024e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.0822e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 3.1606e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.3306e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.3217e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.0953e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.8604e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.8157e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.9758e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 3.1835e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.8067e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7786e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.6848e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9647e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6656e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 7.412e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.1542e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.6076e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.125e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.4599e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.8603e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.8305e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.3317e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 2.0796e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.3954e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.736e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 4.8376e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.013e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 9.073e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.0316e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.2557e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.1192e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.8066e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.181e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.1967e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1968e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 5.0617e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.0581e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.1745e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.2179e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.2226e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.3812e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 2.2189e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.1979e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.0603e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.4363e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.3166e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.6751e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.0804e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 8.8482e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.012e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 5.9612e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.2511e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.0829e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 5.135e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.5919e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00042967
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.8719e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00038756
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0011078
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 4.9077e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.8609e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 3.2843e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00010329
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.3743e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 5.7653e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 3.5807e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.8929e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 4.0042e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00015314
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 6.3415e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00013639
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.0157e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00021938
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00024546
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 4.1237e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.0823e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.7585e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.3633e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00021722
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2121e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00053938
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0002311
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00026433
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.001557
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00032677
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.8284e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0013412
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00024631
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.11417
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0075509
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.10591
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.30353
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.013353
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.002429
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.028778
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.083535
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.01946
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.04821
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.028983
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.032547
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0032495
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.12816
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.05213
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.11314
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0087058
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.049894
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.064459
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.011064
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0082017
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.011914
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.027377
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.093455
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0052529
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.23375
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.099428
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.11372
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.66986
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.14059
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.012169
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.57703
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.065228
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 7.6745e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.7411e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 3.1112e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00050638
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 9.2561e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00019529
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00019488
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00024594
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.5944e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00018977
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 9.3815e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 9.9068e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.2429e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.0463e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.005e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00043524
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.524e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00089917
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00033018
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00027121
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0011106
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00029232
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.077e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0015008
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.2911e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 5.9708e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 9.7585e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.7938e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.7431e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.8305e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.8058e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.0385e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.6332e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.826e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.9003e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.9274e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.5388e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2713e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.1447e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.1528e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00012702
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.6615e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.8289e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0001568
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.1269e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.3441e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00021189
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 5.6821e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00010409
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0012968
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00020836
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00065403
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00063587
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00085597
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.5662e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00060188
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00030805
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00033993
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.0244e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00012163
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00018181
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00087874
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.056e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0018031
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00066663
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00054756
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0022423
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00059018
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 6.2124e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0030301
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0021802
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00025189
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0036493
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.012382
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.0001452
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00075486
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.001427
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.01641
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0026722
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0085576
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0080533
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.011198
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00070679
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0078811
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0039624
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0044124
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00013738
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0014882
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0027363
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00029635
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00013776
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0047373
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0070536
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.034093
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0011943
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.070465
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.025863
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.021244
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.086995
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.022897
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0024102
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.11756
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.002176
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.2371e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.2419e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.227e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.9176e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.5972e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.2245e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.6203e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 7.1204e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 4.0773e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 9.8505e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.4303e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.4532e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 9.191e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.9044e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 7.7446e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.6996e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.7381e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.0815e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 5.3991e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.5726e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 9.9375e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 7.0488e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5268e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.6142e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.2338e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.5552e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.9171e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.3126e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.5013e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 8.8434e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.856e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.6065e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 7.6178e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.4758e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.5437e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 8.9781e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.4595e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.8038e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 8.8888e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 6.8147e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 3.3069e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.6131e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.3627e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 9.4786e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.7872e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.8657e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 7.4628e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.094e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 6.7166e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.7025e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.7293e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 3.6712e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.1749e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 7.3086e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 5.3016e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.373e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.03e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.5161e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.8861e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 8.3931e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.7408e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.2787e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.5203e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 5.2894e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.5783e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 2.171e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.0046e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00035827
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.394e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0002694
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00043997
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 2.211e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 2.7215e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 1.4681e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 4.5452e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 1.0809e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 3.4477e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 1.7324e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.304e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 2.3427e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 9.6567e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 2.5468e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 8.6954e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.5897e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 7.7508e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00021181
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 1.5124e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 1.2057e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.2924e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.0478e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00010404
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.568e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00024777
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00011069
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00012661
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00074575
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00015651
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.3547e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0006424
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00015167
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.080933
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00068064
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.057921
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.099508
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0056399
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0023734
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.012846
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.034687
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0084375
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.024551
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.013935
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.010992
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0019884
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.075376
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.019339
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.06654
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0084174
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.016669
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.041712
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0035773
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0032039
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0051222
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.012067
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.041193
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0022089
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.098294
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.043826
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.050127
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.29526
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.061969
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0053638
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.25434
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.03749
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.3354e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.1679e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 8.1891e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00018577
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 3.1371e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00010006
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 9.3649e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 7.3339e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 9.6068e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00011046
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.9962e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.0947e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.2258e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.4431e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.7475e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00018113
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.998e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00035388
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00013741
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00011286
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00046219
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00012165
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.2805e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00062458
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.472e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.9141e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.699e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 6.9924e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.9639e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.877e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.5524e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.8947e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.2209e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 5.959e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.2302e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.0273e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.5216e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.3749e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.5978e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.6852e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.1243e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.9708e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.6188e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 6.629e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.7448e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.8366e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 8.9581e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 5.4053e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 4.6525e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00057065
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 9.4854e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00039112
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00030765
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00028673
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.2565e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00037952
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00012372
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00021673
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.6716e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.6986e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.708e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00042089
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4039e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00082827
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00031929
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00026226
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.001074
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00028268
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 2.9756e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0014513
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0015455
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 2.2706e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0019958
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0040592
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 6.1329e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00073757
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00063703
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0068142
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0011586
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.004358
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0038721
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0037816
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0004325
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0046352
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00147
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.002595
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00013283
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00049718
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0017707
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 9.5816e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 5.3814e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0020367
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0031091
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.015027
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00050222
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.029631
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0114
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0093638
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.038346
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.010093
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0010624
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.051819
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0012506
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 6.4062e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.2182e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 5.4074e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.3388e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.0091e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.0388e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 4.1553e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.337e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.1638e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 4.6659e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.3066e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1135e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 5.2586e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.0898e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 4.282e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 5.2636e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 8.489e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.7743e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.0353e-09
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.0229e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.3162e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.9066e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.5675e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.0325e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 8.4119e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 9.6213e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 5.6673e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.1894e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.0295e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.8819e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.4994e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 8.931e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 3.4659e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.0025e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 7.2758e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 7.642e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.6595e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 5.2792e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 8.9261e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.9947e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 9.6257e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.808e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.1568e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 8.484e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.7313e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 3.7186e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 6.0721e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.295e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.4577e-09
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.954e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.6894e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.2835e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3189e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.869e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.4295e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.7787e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.6368e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.4352e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.9733e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.4099e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.0981e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00017262
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 9.9934e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00017978
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00012235
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 1.4601e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 3.7027e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 1.2689e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.0722e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 5.6257e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 2.038e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.2148e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 5.5701e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 2.1082e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 4.2349e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 6.6034e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00010346
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 2.1202e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 4.0887e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.311e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.6502e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.633e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.2731e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00014565
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 5.9931e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 6.8547e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00040376
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 8.474e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 7.3348e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00034781
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00018031
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.046216
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0019815
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.051435
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.03671
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0040247
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.029991
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.010641
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.017941
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0049397
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.017961
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0010955
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.04446
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.017492
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.034199
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.01615
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.027177
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0058032
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 9.8876e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0029897
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0067487
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.023038
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0013384
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.059559
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.02451
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.028034
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.16513
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.034656
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0029997
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.14224
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.046232
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.7629e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00018933
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.2578e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 8.908e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.007e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00018406
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.6171e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 7.5001e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.6841e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.8731e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.6369e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.4016e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00011608
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.1792e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00024657
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 8.8057e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 7.2329e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00029619
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 7.7959e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 8.2062e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00040026
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.8052e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 8.4614e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.8494e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 6.4693e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.8655e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.2207e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.5481e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.527e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 7.8812e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.3789e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.4906e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.6871e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.0733e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.5832e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.2799e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.0513e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 4.3051e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.1331e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.1928e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 5.8177e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00046488
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00011135
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00023508
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 9.9902e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00044812
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.6887e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00021891
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00010241
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00010555
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.2236e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.7147e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00022788
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.2525e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0004869
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00017287
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00014199
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00058148
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00015305
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.611e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00078578
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00088257
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 6.6101e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0017723
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0014975
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 4.3764e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0058918
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0014611
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0031846
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0013726
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0061796
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00023828
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0027341
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0013295
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0013337
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00048173
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0011537
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00015544
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.6607e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0011888
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0017388
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0084042
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00030431
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.017954
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0063756
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0052368
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.021445
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0056444
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00059415
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.02898
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0015423
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.754e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 8.8246e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.4189e-10
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.2816e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.1689e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.5453e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.7812e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 9.8033e-10
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.8519e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 7.6586e-09
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.1544e-09
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 9.8995e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.535e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 4.3112e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 7.3729e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.5813e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.0074e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.8605e-11
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.221e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.4294e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.5361e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4155e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 6.299e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.6982e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.0862e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.8178e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 3.8152e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.3023e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.5659e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.7439e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 6.0526e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.3341e-10
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 8.8027e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.4242e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.0724e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.6376e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.0321e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.6785e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.9156e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.2009e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.0467e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 6.2451e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.5787e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 6.6201e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.3566e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 2.8603e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.6895e-11
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.7627e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.0206e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.8975e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.8518e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.7141e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.3383e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 8.3934e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 4.9439e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.0376e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 8.9812e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 4.2588e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.3116e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 1.2782e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 4.4915e-09
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 1.8558e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 2.6061e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 2.5167e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.5665e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 8.3221e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 7.2408e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 8.4835e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.4942e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.5071e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.9211e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 4.1711e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 9.427e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 2.4205e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 5.1177e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 9.0547e-10
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5165e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.7708e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.9699e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1115e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 4.9463e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 2.0958e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.3972e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0001412
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.9634e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.565e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00012163
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 6.7799e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0030392
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 9.1777e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0046133
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0068001
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00056606
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0012182
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 5.6932e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0039677
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00068112
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00028054
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0081712
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.010601
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0031708
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0018071
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.0032949
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00013009
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.8502e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00077475
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0018022
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0061519
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00033794
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.015038
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0065451
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0074861
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.044096
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0092546
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00080104
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.037985
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0072434
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.1878e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 8.1157e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 3.1221e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.5858e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 4.9356e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.5171e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.4119e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.7061e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.8995e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.1542e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.7033e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.7233e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2952e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 7.6415e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.8245e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.32e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 9.5007e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.5006e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.6322e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00012839
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.7513e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.6542e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.4777e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 9.4564e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.8226e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.9047e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 5.5407e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 7.1864e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.0567e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0544e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.0961e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7737e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.0465e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.866e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.1755e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.3004e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.4227e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.6028e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.7573e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.9667e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 7.3032e-07
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.2142e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 1.5065e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 7.6829e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 5.9231e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 9.3321e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 1.0396e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1096e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.6488e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.9691e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.8025e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00016535
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 6.0455e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 4.9657e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00020335
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 5.3522e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 5.6339e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0002748
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 5.8039e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 3.0616e-08
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00015896
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0002774
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 6.1553e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00023932
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 7.8175e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00070429
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00018926
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 9.6519e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00050249
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00080578
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00012366
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 5.3901e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00013987
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 3.4845e-06
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.1077e-09
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00030806
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00046432
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0022442
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.6836e-05
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0045333
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0017025
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0013984
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0057267
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0015073
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00015866
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0077387
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00024163
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 8.8653e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.2413e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.0114e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.3451e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 3.5298e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.4912e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 4.587e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.4962e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 9.3275e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.5713e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.2211e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.307e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 7.8911e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 9.2992e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.5057e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.4103e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.722e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.8381e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 9.9211e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.784e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.4637e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.7294e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8415e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.2047e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.4353e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.164e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.633e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.5271e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.7466e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.0288e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.1592e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.8689e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 8.8623e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.544e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.6934e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 8.5638e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.0396e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 2.7191e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.1516e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.023e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 7.1942e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.0404e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.0527e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 9.4152e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.6452e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.3837e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.0104e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.7806e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.044e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.4343e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.9315e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 7.3221e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.3626e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.8911e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.0697e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.6044e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2788e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.3653e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4861e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.1063e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.6443e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 5.312e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 3.1289e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 6.5669e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 5.684e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 2.6953e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.9177e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0029644
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00011124
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0014359
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0042317
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00017331
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 3.7702e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 1.0868e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0009703
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00027867
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00018124
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00013659
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 6.9257e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.1392e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00058895
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00021818
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00049363
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.6362e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0018071
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0028989
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00036369
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 2.6696e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.7359e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00021931
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00074863
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.3661e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0019429
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00079648
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00091099
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.005366
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0011262
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 9.7479e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0046224
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0029638
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.83965
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.030803
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.40383
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 1.1689
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.047774
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.031202
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.009504
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.80987
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.23469
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.15147
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.11473
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.058623
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0043078
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.49328
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.18139
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.41414
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.014535
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.53902
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.78844
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.099028
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.007114
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.042161
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.095114
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.32468
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.018884
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.84032
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.34543
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.3951
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 2.3273
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.48843
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.042277
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 2.0047
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.81274
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.8235e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 3.3062e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.7208e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00042499
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 8.189e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 9.1442e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 8.423e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.2967e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 4.6911e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 9.2788e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 4.249e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.1756e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.7276e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.9467e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.3597e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00021072
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.47e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00044073
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00015985
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0001313
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00053769
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00014152
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.4897e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00072661
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 7.3382e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 4.1641e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 9.2648e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.6873e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.9508e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.8309e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3588e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0182e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.9959e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 9.2628e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.1081e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.2768e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.5133e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.6729e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.2252e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1448e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 6.7543e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.4467e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.0097e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 8.2299e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.1661e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.2802e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00011122
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00074881
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 3.4444e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.012182
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0024455
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.002056
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0024256
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015228
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 7.1438e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0023147
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0010598
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0012303
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.6501e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00042929
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00062659
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0030285
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00011008
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0064948
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0022975
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0018871
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0077279
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.002034
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00021411
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.010443
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.016034
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0010276
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.013915
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.047682
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.0005195
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0096965
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.00047129
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.1591
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.032227
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.026888
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.031881
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.020169
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00093697
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.030335
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.013787
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.016151
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00022938
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.016078
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.03347
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0026524
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00011949
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.016764
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.024506
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.11845
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0042935
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.25331
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.089855
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.073805
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.30224
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.07955
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0083737
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.40843
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.027112
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.0549e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 7.3238e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.4053e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 4.1117e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.4374e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 7.1048e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 7.4053e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 6.8888e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.5897e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.7272e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.0309e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 7.7422e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 7.6778e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 4.3364e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.9235e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.21e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.6758e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.0127e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.5214e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 3.0303e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 5.1942e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.6549e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.5431e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.519e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.1854e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.859e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.2723e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 5.5168e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 6.3099e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 3.7168e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 7.8006e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.7519e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 3.2017e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.0209e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 5.3873e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.1431e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.9179e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.0708e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 5.1117e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.8506e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.741e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 6.5689e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.1236e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 4.032e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.1746e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.0552e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.7415e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.1854e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.8035e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.4503e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.3497e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.8668e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.2342e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.9445e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.0921e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.9289e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.4859e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.5313e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.4149e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.7446e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.6292e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.8634e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.0976e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.3036e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.9939e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 9.455e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.2425e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00065106
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.5813e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00037448
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0010924
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 6.8332e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 5.6811e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 6.3672e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00014131
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 3.6419e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 9.0977e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 5.3139e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 5.8983e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.4552e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00023199
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.8813e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00027175
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.9243e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00012052
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00029178
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 5.8168e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00014436
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5334e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.8535e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00019982
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1117e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00049469
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00021259
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00024315
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0014322
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00030059
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.6018e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0012338
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0002724
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.17751
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0045598
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.10361
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.30117
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.018635
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0046175
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.052114
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.11944
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.03083
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.075082
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.044561
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.049008
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0011911
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.19346
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.073686
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.2244
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0077708
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.033155
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.079633
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.015981
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.038485
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.010912
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.025208
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.086052
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0047888
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.2131
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.091552
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.10472
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.6168
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.12945
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.011205
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.53133
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.075063
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.3175e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 5.3375e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 7.9228e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 7.2432e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 8.6855e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 4.2442e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 4.9895e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.1265e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.1876e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.1697e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.1331e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 3.3248e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.7065e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.047e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.575e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.6126e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.616e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00015434
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 5.775e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 4.7435e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00019425
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 5.1128e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.3819e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0002625
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.034e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 1.5865e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.5063e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.8009e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 8.3539e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.0296e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.2269e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 4.4213e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 8.5084e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.2617e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 6.6021e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.012e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5533e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.3408e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.1314e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.8749e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.2862e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 8.583e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 7.05e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.887e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 7.5987e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 7.9987e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 3.9014e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00011283
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00020179
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0017742
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0003196
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0010321
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00094365
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0012969
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 2.0228e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00091176
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00043143
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00067731
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.0005e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00011171
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00016724
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00080834
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.8028e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0016537
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00061322
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00050369
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0020627
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0005429
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 5.7147e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0027874
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0033897
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00015211
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0035702
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.012286
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00020263
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.001435
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.0025843
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.023463
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0042333
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.013328
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.012382
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.016861
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00025907
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.011897
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0056008
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0087513
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00012263
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00098894
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0033804
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00042805
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00064641
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0043389
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0064949
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.031392
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0010888
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.06424
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.023815
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.019561
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.080104
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.021084
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0022193
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.10825
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.002504
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.9197e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.396e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 4.2843e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.5439e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.0946e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 1.3301e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.3953e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.1321e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.9781e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.4052e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6292e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.8664e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 8.5547e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.793e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 8.0378e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.3855e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.4836e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.4225e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.3025e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 9.9584e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.3868e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.2289e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.1022e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.0436e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.6894e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.1727e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.3413e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 7.9005e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.6581e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.4352e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 6.8056e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.0322e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.668e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 3.6715e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.703e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.4515e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 9.3485e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.0832e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.0634e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.5537e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.7257e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 6.123e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 8.1365e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.1927e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.0178e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.1272e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.1151e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.7985e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 9.3639e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 8.5828e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 7.5001e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.9082e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.0748e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.0978e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7074e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.5981e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.2958e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.7696e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.2204e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.6601e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.0336e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.9127e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.5638e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.000155
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.8899e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00014066
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00015876
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 9.7996e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.4781e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.4935e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.4082e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 6.2542e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 9.7476e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 7.8008e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 4.8413e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.2806e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 5.022e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.0514e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 1.4718e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 5.1513e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 4.5988e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 5.5861e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.4509e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0287e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.5115e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.9525e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 8.6886e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 3.736e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 4.2731e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0002517
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 5.2825e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 4.5724e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00021682
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.6586e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.043629
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 5.9169e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.036351
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.043968
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0027084
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.021337
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0021322
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.02013
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0058361
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0081687
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 6.0141e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.040035
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.010501
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.041949
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0070638
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0040221
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.013288
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0013302
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0014903
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0019361
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00447
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.015259
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00085014
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.037831
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.016234
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.018568
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.10937
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.022955
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0019869
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.094215
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.016211
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 8.2793e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.4583e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 3.6053e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.6377e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.1945e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 9.415e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.2201e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.1608e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 7.2703e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.7311e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.219e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.3479e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.6182e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.5299e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.2626e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.2276e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.0083e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 4.1291e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.0868e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.144e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 5.5799e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.7768e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 6.5128e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.2192e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.5971e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.4589e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.0657e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.2917e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 6.2262e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.4235e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.679e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.1473e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.7354e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.2888e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.8625e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 4.6389e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.7363e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.4262e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 5.8403e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.5372e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.6181e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 7.8924e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00031113
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.1882e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00027319
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00011106
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00021433
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0844e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00019027
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 6.2208e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00012517
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.1201e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.9625e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.9391e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00014205
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.9229e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00029045
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00010777
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 8.8517e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00036248
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 9.5407e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.0043e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00048984
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00083317
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 1.9739e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0012526
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0017936
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 2.9452e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0041917
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00029278
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0035733
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0016216
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0028104
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 1.3081e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.002462
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00079818
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.001636
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00011147
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00011997
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00056407
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 3.5628e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.5032e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00076985
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0011517
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0055665
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00019329
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.011404
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0042229
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0034686
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.014204
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0037386
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00039353
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.019195
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0005408
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.003e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.072e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.0763e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.4798e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 3.082e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 4.6804e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.9814e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.7504e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.6327e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 4.3856e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.7193e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.93e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.0184e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.8625e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.8842e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.7883e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.3018e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 7.6253e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.0754e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.6727e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.1706e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.4097e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.3515e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.9364e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.8832e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 9.0166e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 5.3111e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.1147e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 9.6481e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.575e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.0096e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.5654e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.5053e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.7154e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.0474e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.695e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.5059e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.16e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 6.0321e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.5883e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8165e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 6.9898e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.3693e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.1455e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.2632e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.5102e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.5692e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 5.2337e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 8.7151e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.7671e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2217e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.1239e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2428e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.5303e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.2596e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.5845e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.5223e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.195e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.7655e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.3114e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.3635e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 5.5927e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 3.5925e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 5.5362e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 2.2799e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 1.7385e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.8999e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.4108e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.1316e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 7.5164e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 1.8346e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 2.4808e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 8.0203e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.6676e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 9.5499e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 2.3889e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.4818e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 9.5599e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 3.2292e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 6.3406e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 7.2425e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.249e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.1971e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.7741e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.8669e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 4.3908e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 1.8875e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.1589e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00012716
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.6688e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.3101e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00010954
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 6.2866e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.014102
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 1.2096e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.014004
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0061329
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0041971
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0013626
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.01006
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0017606
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0055475
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0013199
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0021109
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00057699
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.02108
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0072224
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.019168
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0054157
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0021574
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.0078766
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0017784
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.4385e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00095758
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0022092
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0075415
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00042073
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.018722
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0080235
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.009177
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.054056
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.011345
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00098198
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.046564
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.014758
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.7264e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 3.3735e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.8141e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 8.7591e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.7215e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.8263e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.9678e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 9.7363e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 8.5837e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.2834e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 5.3223e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.5452e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5478e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.2506e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0878e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.9816e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.3491e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 8.2523e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 6.7783e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.7758e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 7.3059e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 7.6904e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 3.751e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 6.1486e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.4532e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.8593e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.2498e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.1513e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 7.2947e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.7746e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.7007e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 6.3395e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.0302e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.1992e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2284e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.2466e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.5692e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.7228e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.3765e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.1904e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 9.778e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 4.0042e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.0539e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.1094e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 5.4111e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 3.7733e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00017712
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 1.8707e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.5269e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 3.258e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 5.4548e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1149e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00010484
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 4.639e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 5.954e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.5457e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.9164e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.4849e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.1769e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4877e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00014678
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 5.4446e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 4.4721e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00018313
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 4.8202e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 5.0739e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00024748
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0002693
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 4.0351e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00048256
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00025018
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 4.5639e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00042345
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0019762
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00024175
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00098472
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00036676
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00072626
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0001255
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0012963
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00054897
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00074753
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.5463e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 6.4351e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00033437
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 4.7633e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 4.0958e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00038076
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0005692
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0027512
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.5659e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0056439
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0020871
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0017143
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0070202
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0018477
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0001945
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0094867
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00049231
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.9956e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 4.455e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 5.2403e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 8.4648e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 4.087e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 4.5716e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 4.5237e-11
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.4082e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 9.6779e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 9.6677e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 5.9858e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 7.7024e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.6105e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.1229e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 6.4209e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.4713e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.7058e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 4.7564e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 3.2067e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.2325e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.0564e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7592e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.2914e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.8304e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7152e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 7.6329e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.0113e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.4442e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.0287e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.2578e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.6854e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.7476e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 6.2233e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 3.0246e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.136e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 6.0066e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 3.2394e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 3.3437e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.3914e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 5.6807e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.0314e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.9821e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.4848e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.2222e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 6.9104e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 8.155e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.5853e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 5.8725e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.2467e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 3.6489e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.2937e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.4848e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 8.338e-11
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.0703e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.3605e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.0578e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.8841e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.1734e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 8.5728e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 9.8053e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 5.7756e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.2122e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.0492e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 4.9752e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 4.3512e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 1.1038e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.4462e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 5.8412e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 2.4478e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 5.2627e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 3.8256e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.3231e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 1.4456e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 7.9245e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.3363e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 6.4527e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 6.6724e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.0416e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 6.193e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 1.6083e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.8044e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 4.9717e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 2.297e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 4.7145e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 2.1813e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4016e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.0867e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0537e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.4032e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 2.8494e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 1.121e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.2822e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 7.5526e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.5851e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.372e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 6.5059e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.5425e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.002975
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 6.6536e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.015675
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0071677
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0014405
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00032606
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.010936
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0012147
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0066527
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0019834
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0054535
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00057952
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.016609
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0051539
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.013377
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00047176
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0013659
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.0058948
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0012646
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 6.0029e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00058745
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0012937
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0044162
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00026837
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.011943
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0046985
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.005374
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.031654
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0066435
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00057504
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.027268
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0083417
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.1546e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 3.2606e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 6.416e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 3.0822e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.9801e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.8576e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.1461e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 8.1244e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 3.0278e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.1319e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.3308e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.2433e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.0153e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.597e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.1552e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5694e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 9.2597e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.1522e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.5892e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.0603e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.7907e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.9376e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.4328e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 5.0472e-09
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.3026e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 6.4615e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 8.2506e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 8.0591e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.294e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.7544e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 5.8536e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.2937e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.6732e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.6643e-10
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.6194e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2317e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.9534e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.249e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.3269e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.5164e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.7097e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.5191e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.9984e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.2089e-08
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 2.0529e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 7.5982e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00016611
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 1.2686e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.9899e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 4.1488e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00014188
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 9.2751e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 8.0237e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 3.0084e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 4.0085e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.854e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.1802e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.8191e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.2626e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6144e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 9.5252e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 3.2337e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.6561e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00010877
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.8628e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 3.0135e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00014699
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 5.6812e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 2.2196e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00054013
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00029239
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 1.5664e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00010133
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0021484
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00016679
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0011809
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00055112
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0018763
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00012605
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0010214
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00039175
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0005217
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.4447e-06
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 4.0742e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.00025024
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 3.3871e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.0083e-07
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00023358
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00033332
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.001611
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.1019e-05
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0036001
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0012222
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0010039
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0041109
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.001082
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0001139
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0055553
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00027827
HFTD - Distribution - Zone 1 - 1QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.673e-10
HFTD - Distribution - Zone 1 - 1QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.0154e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 8.8611e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.5888e-09
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 3.9502e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 5.5221e-09
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 6.0899e-09
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.7643e-09
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.0988e-10
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.3882e-10
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.128e-10
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 7.695e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.536e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.0138e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 5.219e-10
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.018e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.5302e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.4707e-09
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 6.8216e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 9.5362e-09
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 5.8386e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.6502e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.0122e-09
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 6.1246e-09
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.0402e-09
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.3289e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.6525e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.4777e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 9.0127e-10
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.2119e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 1.3457e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 3.9314e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 5.9988e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 8.386e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 6.8721e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 3.1194e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.3684e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 7.2087e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 2.4013e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 1.1686e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 2.3326e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 3.0583e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 7.9257e-09
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 4.5833e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.00040218
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 1.175e-05
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00017929
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 2.5063e-05
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0006259
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00028411
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 2.1571e-05
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 6.5656e-05
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 2.1871e-05
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.00034926
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.00069715
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 9.1402e-05
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.3688e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0013698
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.7747e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 8.8035e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 8.6404e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 9.1112e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.7514e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.3388e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.2477e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 4.169e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.3961e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.81e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 8.628e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.7375e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.6868e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.8331e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.1665e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 7.6802e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 3.9197e-07
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 6.1778e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 1.0224e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00012296
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 3.9012e-05
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 3.8289e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 4.0375e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 1.6624e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 1.0417e-05
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 2.9594e-05
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 2.4482e-06
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.9786e-08
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 4.5696e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.6147e-10
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 4.3395e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.2678e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.9345e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.7043e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.9824e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.3538e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.0278e-10
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 3.4804e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.592e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 3.7685e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 5.2133e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 9.8623e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.5559e-10
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 8.7537e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.5219e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.1976e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.3532e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 4.6875e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.87e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.3027e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 9.8908e-10
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.5211e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.5448e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 6.5321e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 6.9358e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.7095e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 4.4302e-10
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.1747e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 4.7884e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 3.8184e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 5.8263e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 8.1449e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00010072
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 3.0297e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.3003e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.1901e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 7.9218e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 1.135e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00013822
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 2.9703e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 7.6978e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00027418
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.013052
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 1.0819e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00016509
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 2.3078e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.081888
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00026161
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 1.9862e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0094962
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0061545
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.00032159
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.035292
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 8.4163e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.1811e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.07084
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.4216e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.3589e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.3113e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 4.2314e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.9639e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 6.3322e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 6.5809e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.088e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.0493e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.8097e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.2578e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0012645
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 2.6588e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.6095e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 4.6773e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 3.8482e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00024924
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 3.6092e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 5.6885e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 9.4143e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.016087
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 3.5922e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 3.5257e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00058397
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0004678
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 9.5923e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0014981
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 2.2543e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.6635e-08
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0023632
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.456e-10
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 1.9212e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.9212e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.9796e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0005132
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0001564
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0005288
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 6.2795e-09
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 7.5507e-07
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 9.8002e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 9.6176e-06
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.764e-05
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0066569
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.3772
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.004302
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.89003
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.018969
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.9246
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0027258
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.56394
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.042983
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 8.8926
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0098463
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 2.0371
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0074728
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 1.546
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.052161
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 10.7916
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0093086
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 1.9258
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0.012183
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 2.5205
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.092344
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 19.1049
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00025697
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.3419e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0033039
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.34195
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.9749e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2785e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0010253
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.10612
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00051394
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00014684
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0066078
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.6839
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.6583e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.5951e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00034178
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.035374
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00087724
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00025064
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.011279
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 1.1674
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00024811
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.0888e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0031899
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | dead | 0.33016
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00011519
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.2912e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.001481
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.15329
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00051394
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00014684
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0066078
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.6839
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0001595
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.5571e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0020507
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.21225
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00027469
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 7.8483e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.0035317
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.36553
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0022241
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00063546
non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.028596
non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 2.9596
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | other | all other | 6.1134e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | other | all other | 1.7467e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | other | all other | 0.00078601
non-HFTD - Distribution | Red Flag Warning - Small Fires | other | all other | 0.081352
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.5898e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 7.3995e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00033298
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.034463
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00031726
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 9.0644e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.004079
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.42218
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0018906
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00054017
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.024308
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 2.5158
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0007381
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00021089
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0094899
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.98221
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00010359
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.9598e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0013319
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.13785
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00020719
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.9196e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0026638
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.27571
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00016187
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.6247e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0020811
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.2154
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00012949
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.6998e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0016649
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.17232
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00079638
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00022754
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.010239
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 1.0597
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00025251
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.2146e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0032466
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.33602
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 5.8271e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 1.6649e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0.0007492
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0.077543
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 6.4746e-06
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 1.8499e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 8.3245e-05
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0.0086158
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 7.7695e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 2.2199e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0.00099894
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0.10339
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00054387
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00015539
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0069926
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.72373
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.8271e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.6649e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0007492
non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.077543
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00070741
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00020212
non-HFTD - Distribution | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0090953
non-HFTD - Distribution | Red Flag Warning - Small Fires | contact from object | animal contact | 0.94136
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0.00023289
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 6.6541e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0029943
non-HFTD - Distribution | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.30991
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00026783
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.6522e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0034435
non-HFTD - Distribution | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.3564
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00055312
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00015803
non-HFTD - Distribution | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0071115
non-HFTD - Distribution | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.73604
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.3289e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | contamination | contamination | 6.6541e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | contamination | contamination | 0.00029943
non-HFTD - Distribution | Red Flag Warning - Small Fires | contamination | contamination | 0.030991
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00017758
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | unknown | unknown | 5.0737e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | unknown | unknown | 0.0022832
non-HFTD - Distribution | Red Flag Warning - Small Fires | unknown | unknown | 0.23631
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.9112e-06
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 8.3176e-07
non-HFTD - Distribution | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 3.7429e-05
non-HFTD - Distribution | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0038739
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.2023e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 9.1493e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00041172
non-HFTD - Distribution | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.042613
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.3289e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 6.6541e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00029943
non-HFTD - Distribution | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.030991
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | other | all other | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | other | all other | 0.016441
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | other | all other | 3.4014
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.0030395
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.62883
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.037233
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 7.7032
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.22188
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 45.9047
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.086625
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 17.9217
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.012158
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 2.5153
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.024316
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 5.0306
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.018997
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 3.9302
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.015197
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 3.1442
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.093463
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 19.3365
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.029635
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 6.1311
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0.0068388
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 1.4149
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0.00075987
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0.15721
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0.0091184
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 1.8865
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.063829
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 13.2054
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0068388
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.4149
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.19024
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 39.3593
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.062632
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 12.9578
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.072026
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 14.9015
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.14875
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 30.7748
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0062632
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | contamination | contamination | 1.2958
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.047757
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | unknown | unknown | 9.8803
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.0007829
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.16197
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.0086119
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.7817
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0062632
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.2958
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | Red Flag Warning - Large Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | Red Flag Warning - Small Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | Red Flag Warning - Large Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | Red Flag Warning - Small Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | Contact from object | balloon contact | 1.8991e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | Contact from object | balloon contact | 5.426e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | Contact from object | balloon contact | 0.00024417
non-HFTD - Distribution | Red Flag Warning - Small Fires | Contact from object | balloon contact | 0.025272
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 9.4955e-06
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 2.713e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | Contact from object | other contact from object | 0.00012208
non-HFTD - Distribution | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.012636
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | conductor damage or failure | 0.00027537
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | Equipment / facility failure | conductor damage or failure | 7.8677e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | Equipment / facility failure | conductor damage or failure | 0.0035405
non-HFTD - Distribution | Red Flag Warning - Small Fires | Equipment / facility failure | conductor damage or failure | 0.36644
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | connection device damage or failure | 1.8991e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | Equipment / facility failure | connection device damage or failure | 5.426e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | Equipment / facility failure | connection device damage or failure | 0.00024417
non-HFTD - Distribution | Red Flag Warning - Small Fires | Equipment / facility failure | connection device damage or failure | 0.025272
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | crossarm damage or failure | 7.5964e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | Equipment / facility failure | crossarm damage or failure | 2.1704e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | Equipment / facility failure | crossarm damage or failure | 0.00097668
non-HFTD - Distribution | Red Flag Warning - Small Fires | Equipment / facility failure | crossarm damage or failure | 0.10109
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | insulator and brushing damage or failure | 9.4955e-06
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | Equipment / facility failure | insulator and brushing damage or failure | 2.713e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | Equipment / facility failure | insulator and brushing damage or failure | 0.00012208
non-HFTD - Distribution | Red Flag Warning - Small Fires | Equipment / facility failure | insulator and brushing damage or failure | 0.012636
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | other equipment / facility failure | 2.8486e-05
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | Equipment / facility failure | other equipment / facility failure | 8.139e-06
non-HFTD - Distribution | Red Flag Warning - Large Fires | Equipment / facility failure | other equipment / facility failure | 0.00036625
non-HFTD - Distribution | Red Flag Warning - Small Fires | Equipment / facility failure | other equipment / facility failure | 0.037907
non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | pole damage or failure | 0.00010445
non-HFTD - Distribution | Red Flag Warning - Destructive Fires | Equipment / facility failure | pole damage or failure | 2.9843e-05
non-HFTD - Distribution | Red Flag Warning - Large Fires | Equipment / facility failure | pole damage or failure | 0.0013429
non-HFTD - Distribution | Red Flag Warning - Small Fires | Equipment / facility failure | pole damage or failure | 0.13899
non-HFTD - Distribution | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 0
non-HFTD - Distribution | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.576e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.1868e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.1868e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.8681e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0049252
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4196e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4196e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.2776e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0021939
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0879e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0879e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.7907e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.016813
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.3736e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.3736e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.7362e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00098504
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.8362e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.8362e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00025526
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.043834
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.1574e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.1574e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00010416
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.017887
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.2023e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.2023e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00010821
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.018581
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 7.7975e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 7.7975e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00070177
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.12051
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.5731e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.5731e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00014158
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.024312
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.3616e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.3616e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.2255e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0021044
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 6.7169e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.7169e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00060452
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.10381
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.2408e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0344e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2064e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0008528
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.8272e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.896e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.1376e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00056853
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00034997
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.9996e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00029997
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0041219
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2068e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.724e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0344e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00014213
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00071201
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00010172
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00061029
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0083859
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00026549
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.7928e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00022757
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0031269
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00020515
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.9308e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00017585
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0024163
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00089303
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00012758
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00076545
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.010518
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00022929
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.2756e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00019654
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0027005
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.4136e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.448e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | grow into | 2.0688e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00028427
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0012068
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0001724
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0010344
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.014213
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.4508e-07
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.4508e-07
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.6057e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0013061
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7645e-07
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7645e-07
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.388e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0005818
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.8848e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.8848e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.5963e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0044585
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6902e-07
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6902e-07
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5211e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00026121
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 7.5212e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.5212e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 6.7691e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.011624
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.0692e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.0692e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 2.7623e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0047434
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.1883e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.1883e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.8694e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0049275
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.0678e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.0678e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0001861
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.031957
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.1716e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.1716e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 3.7545e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0064473
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.6108e-07
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.6108e-07
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.2497e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00055805
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.7812e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.7812e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00016031
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.027528
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.7193e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.8847e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.3308e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00032027
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8128e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5898e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5539e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00021351
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00013143
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.8776e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00011266
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.001548
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.5321e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.4744e-07
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.8847e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.3378e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00026739
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.8199e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00022919
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0031493
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 9.9706e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.4244e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | dead | 8.5462e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0011743
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 7.7046e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.1007e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 6.6039e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00090743
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00033538
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 4.7911e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00028746
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00395
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 8.611e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.2301e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 7.3809e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0010142
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 9.0642e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.2949e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | grow into | 7.7693e-06
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00010676
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00045321
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.4744e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00038847
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0053378
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.041e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.041e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.6369e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2453e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8001e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8001e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.6201e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.782e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3794e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3794e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.2415e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.1319e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.082e-10
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.082e-10
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.2738e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2491e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.5965e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.5965e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 3.2368e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 5.5584e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.4676e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.4676e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 1.3209e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 2.2682e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.5246e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.5246e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.3721e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 2.3562e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 9.8875e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 9.8875e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 8.8988e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00015281
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.9948e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.9948e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.7953e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 3.0829e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.7266e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.7266e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.5539e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 2.6685e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 8.5173e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 8.5173e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 7.6656e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00013163
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.022e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.6029e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.1617e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.0926e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.0147e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.7353e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4412e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.7284e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9106e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.1581e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.4948e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.4281e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0037e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4338e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.6029e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1821e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.9217e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 8.4595e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 5.0757e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 6.9744e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.2081e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.1544e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | dead | 1.8926e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | dead | 2.6006e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.7062e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.4375e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.4625e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 2.0096e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 7.4272e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.061e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 6.3661e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 8.7475e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.907e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.7242e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.6345e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 2.246e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.0073e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.8676e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.7206e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | grow into | 2.3642e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.0037e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.4338e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 8.6029e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.1821e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.62e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.4858e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 0.00033686
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 0.034832
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 8.7335e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.4953e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00011229
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.011611
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.4556e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.1588e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00018715
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.019351
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.1645e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 3.327e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00014972
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.015481
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9112e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contamination | contamination | 8.3176e-07
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contamination | contamination | 3.7429e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contamination | contamination | 0.0038702
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 6.4746e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.8499e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 8.3245e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0086075
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.2949e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.6998e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00016649
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.017215
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.4746e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.8499e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 8.3245e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0086075
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 8.7335e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 2.4953e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 0.00011229
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 0.011611
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0070461
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 1.4578
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0023487
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.48592
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0039145
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.80986
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0031316
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.64789
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0007829
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.16197
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00075987
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.15721
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015197
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.31442
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00075987
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.15721
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0023487
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.48592
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.7845e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.0813e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 0.00048658
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 0.050312
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 8.7335e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.4953e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00011229
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.011611
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.0378e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 5.8223e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.000262
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.027091
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9112e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contamination | contamination | 8.3176e-07
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contamination | contamination | 3.7429e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contamination | contamination | 0.0038702
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.9424e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 5.5497e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00024973
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.025823
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.4746e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.8499e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.3245e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0086075
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.4746e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8499e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 8.3245e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0086075
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.4746e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.8499e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 8.3245e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0086075
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 6.4746e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.8499e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.3245e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0086075
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.9112e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | unknown | unknown | 8.3176e-07
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | unknown | unknown | 3.7429e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | unknown | unknown | 0.0038702
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.010178
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 2.1056
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0023487
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.48592
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0054803
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 1.1338
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0007829
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.16197
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0022796
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.47162
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00075987
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.15721
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00075987
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.15721
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00075987
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.15721
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00075987
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.15721
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0007829
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.16197
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9112e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | contamination | contamination | 8.3176e-07
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | contamination | contamination | 3.7429e-05
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | contamination | contamination | 0.0038702
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.4746e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8499e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 8.3245e-05
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0086075
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.9112e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 8.3176e-07
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.7429e-05
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0038702
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0007829
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.16197
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00075987
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.15721
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.0007829
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.16197
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0034676
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0011928
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.3894e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00049537
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0001704
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 4.842e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0029722
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0010224
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 2.9052e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 0.040841
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 0.014049
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 3.992e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0.00028897
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 9.9402e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.8245e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.1281e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.42e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.035e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00024769
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 8.5202e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 2.421e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0034034
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0011707
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 3.3266e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.0008669
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00029821
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 8.4735e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00012384
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.2601e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.2105e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00074306
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00025561
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 7.263e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.01021
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0035122
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 9.9799e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0024819
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00085374
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.4259e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00035455
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00012196
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.4656e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0021273
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00073178
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.0793e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.029231
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.010055
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 2.8572e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0016546
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00056916
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6173e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00023637
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 8.1309e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.3104e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0014182
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00048785
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3862e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.019487
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0067035
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 1.9048e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0024819
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00085374
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.4259e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00035455
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00012196
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.4656e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0021273
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00073178
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.0793e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.029231
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.010055
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 2.8572e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00028897
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 9.9402e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.8245e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 4.1281e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 1.42e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 4.035e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 0.00024769
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 8.5202e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 2.421e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 0.0034034
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 0.0011707
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 3.3266e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00092467
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00031808
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 9.0382e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00092467
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00031808
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 9.0382e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.008322
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0028627
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 8.1343e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 1.4291
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.49159
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0013968
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 7.7056e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.6507e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 7.5318e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.7056e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.6507e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.5318e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0006935
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00023856
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 6.7786e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.11909
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.040966
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0001164
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00023117
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 7.952e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.2595e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00023117
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.952e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.2595e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0020805
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00071568
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 2.0336e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.35727
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.1229
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00034921
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00021687
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 7.4602e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.1198e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00021687
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.4602e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.1198e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0019518
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00067142
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.9078e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.33518
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.1153
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00032762
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00014458
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.9735e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.4132e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00014458
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.9735e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.4132e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0013012
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00044761
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.2719e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.22345
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.076865
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00021841
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00021687
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 7.4602e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.1198e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00021687
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.4602e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.1198e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0019518
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00067142
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.9078e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.33518
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.1153
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00032762
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 7.7056e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.6507e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 7.5318e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 7.7056e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.6507e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 7.5318e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0006935
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00023856
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 6.7786e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.11909
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.040966
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.0001164
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0.00029473
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 9.3401e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 5.1927e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.2104e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.3343e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.4181e-08
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00025263
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | balloon contact | 8.0058e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | balloon contact | 4.4509e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0034713
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0011001
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | balloon contact | 6.1158e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00029473
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 9.3401e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 5.1927e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.2104e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.3343e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.4181e-08
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00025263
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | other contact from object | 8.0058e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | other contact from object | 4.4509e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0034713
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0011001
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | other contact from object | 6.1158e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00084379
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0002674
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.4866e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00012054
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.82e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.1237e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00072325
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0002292
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.2742e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.009938
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0031494
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 1.7509e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0016876
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0005348
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.9732e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00024108
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.64e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.2475e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0014465
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0004584
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.5485e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.019876
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0062987
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 3.5018e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00058946
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.0001868
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.0385e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | unknown | unknown | 8.4209e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | unknown | unknown | 2.6686e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | unknown | unknown | 1.4836e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | unknown | unknown | 0.00050525
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | unknown | unknown | 0.00016012
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | unknown | unknown | 8.9017e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | unknown | unknown | 0.0069426
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | unknown | unknown | 0.0022001
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | unknown | unknown | 1.2232e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 7.8593e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.4906e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.3847e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.8593e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.4906e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.3847e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00070734
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00022416
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.2462e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.12147
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.038493
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.000214
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 7.8593e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.4906e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.3847e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.8593e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.4906e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.3847e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00070734
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00022416
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 1.2462e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.12147
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.038493
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.000214
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 7.3733e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.3366e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.299e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.3733e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.3366e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.299e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00066359
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00021029
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.1691e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.11395
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.036112
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00020077
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00014747
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.6732e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.5981e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00014747
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.6732e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.5981e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0013272
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00042059
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.3383e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.22791
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.072225
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00040154
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00015719
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 4.9813e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.7694e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00015719
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 4.9813e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.7694e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0014147
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00044831
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | unknown | unknown | 2.4924e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.24293
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.076985
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.000428
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0039895
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0010579
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 5.0588e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00056992
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00015113
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.2269e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0034195
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 0.00090681
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 4.3361e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 0.046987
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 0.01246
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 5.9582e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00092065
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00024414
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.1674e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00013152
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.4877e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.6677e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00078913
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00020926
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 1.0006e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.010843
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0028754
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 1.375e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0026357
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00069895
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.3422e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00037653
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 9.985e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.7746e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0022592
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0005991
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.8648e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.031043
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0082321
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 3.9364e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00087858
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00023298
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.1141e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00012551
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.3283e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.5915e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00075307
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0001997
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 9.5492e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.010348
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.002744
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 1.3121e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0017572
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00046597
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.2281e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00025102
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 6.6567e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.1831e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015061
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0003994
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.9098e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.020695
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0054881
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 2.6243e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0017572
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00046597
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.2281e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00025102
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 6.6567e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.1831e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0015061
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0003994
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.9098e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.020695
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0054881
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 2.6243e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00087858
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00023298
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.1141e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00012551
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.3283e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.5915e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00075307
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0001997
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 9.5492e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.010348
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.002744
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 1.3121e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | other | all other | 0.00030688
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | other | all other | 8.138e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | other | all other | 3.8914e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | other | all other | 4.384e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | other | all other | 1.1626e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | other | all other | 5.5591e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | other | all other | 0.00026304
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | other | all other | 6.9754e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | other | all other | 3.3355e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | other | all other | 0.0036144
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | other | all other | 0.00095848
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | other | all other | 4.5832e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0.00030688
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.138e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.8914e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 4.384e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.1626e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 5.5591e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00026304
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 6.9754e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.3355e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0036144
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00095848
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 4.5832e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0010638
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00028211
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.349e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0010638
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00028211
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.349e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0095745
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.002539
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 1.2141e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 1.6441
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.436
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0020849
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.0002455
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.5102e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 3.113e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.0002455
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 6.5102e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.113e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0022095
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00058592
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 2.8017e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.37942
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.10062
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00048112
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00023032
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 6.1076e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.9205e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00023032
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 6.1076e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.9205e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0020729
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00054969
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.6285e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.35596
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.094394
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00045137
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.6773e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.0359e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 9.7351e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 7.6773e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.0359e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 9.7351e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00069095
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00018323
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 8.7616e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.11865
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.031465
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00015046
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00015355
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.0718e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.947e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00015355
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.0718e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.947e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0013819
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00036646
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.7523e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.2373
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.062929
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00030091
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00015355
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.0718e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.947e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00015355
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.0718e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.947e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0013819
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00036646
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.7523e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.2373
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.062929
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00030091
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.6773e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.0359e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 9.7351e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.6773e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.0359e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 9.7351e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00069095
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00018323
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.7616e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.11865
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.031465
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00015046
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | other | all other | 8.1833e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.1701e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.0377e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | other | all other | 8.1833e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | other | all other | 2.1701e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | other | all other | 1.0377e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | other | all other | 0.0007365
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | other | all other | 0.00019531
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | other | all other | 9.3391e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | other | all other | 0.12647
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | other | all other | 0.033539
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | other | all other | 0.00016037
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.1833e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.1701e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.0377e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 8.1833e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.1701e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.0377e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.0007365
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00019531
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 9.3391e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.12647
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.033539
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00016037
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9552e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.5838e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.7931e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.9768e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.6759e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.7861e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00023028
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.5764e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.3035e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7225e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8621e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.3179e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1173e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.1907e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00015352
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.3843e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.4501e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6988e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.35e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.8554e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.1001e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.3133e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.001113
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00031786
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.2587e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.3063e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.6552e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3295e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.7931e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.9768e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.838e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0961e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00019226
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.4907e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.7466e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.8438e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00016479
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 4.7063e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0022644
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.00064668
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.169e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.0474e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.0241e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.9248e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | dead | 6.1449e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | dead | 1.7549e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00084435
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00024114
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 5.5397e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.5821e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 7.9139e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.2601e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 4.7483e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.3561e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00065246
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00018633
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00024114
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 6.8866e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 3.4449e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 9.838e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00020669
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 5.9028e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0028401
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00081109
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 6.1914e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.7682e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 8.8449e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.526e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 5.307e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.5156e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00072922
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00020825
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.5173e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.8613e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 9.3104e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.6589e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | grow into | 5.5863e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.5954e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | grow into | 7.6759e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | grow into | 2.1921e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00032587
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 9.3063e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 4.6552e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.3295e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00027931
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 7.9768e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.003838
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0010961
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.486e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.9096e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.1229e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.5851e-07
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2737e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.3511e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00017502
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.6046e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.9066e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.6064e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4152e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7234e-07
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.4914e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2341e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00011668
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.0698e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.1823e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.8896e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.026e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6995e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.1563e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.6197e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00084592
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00022256
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4767e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.516e-07
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.5381e-07
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.3085e-08
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.1229e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.5851e-07
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.917e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.6744e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00014612
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.8444e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.0875e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.492e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00012525
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 3.2952e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.001721
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.00045279
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 5.4487e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.4335e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.7838e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.0479e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | dead | 4.6703e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | dead | 1.2287e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00064173
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00016884
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 4.2103e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.1077e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.0148e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.5825e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 3.6089e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 9.4947e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00049588
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00013046
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00018327
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 4.8218e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.6182e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 6.8883e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00015709
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 4.133e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0021585
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0005679
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.7057e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.238e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 6.7224e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.7686e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 4.0334e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.0612e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00055422
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00014581
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 4.9533e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.3032e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 7.0762e-07
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.8617e-07
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | grow into | 4.2457e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.117e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | grow into | 5.8339e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | grow into | 1.5349e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00024767
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 6.516e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 3.5381e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 9.3085e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00021229
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 5.5851e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.002917
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00076744
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 0.00036171
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 0.0001033
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 0.00046096
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 5.1673e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.4757e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 6.5852e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | Contact from object | other contact from object | 0.00031004
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | Contact from object | other contact from object | 8.8542e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | Contact from object | other contact from object | 0.00039511
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0042602
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0012166
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0054291
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | other equipment / facility failure | 0.00041236
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | other equipment / facility failure | 0.00010849
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | other equipment / facility failure | 0.00040512
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | Equipment / facility failure | other equipment / facility failure | 5.8909e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | Equipment / facility failure | other equipment / facility failure | 1.5499e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | Equipment / facility failure | other equipment / facility failure | 5.7874e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | Equipment / facility failure | other equipment / facility failure | 0.00035346
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | Equipment / facility failure | other equipment / facility failure | 9.2992e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | Equipment / facility failure | other equipment / facility failure | 0.00034725
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | Equipment / facility failure | other equipment / facility failure | 0.0048567
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | Equipment / facility failure | other equipment / facility failure | 0.0012778
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | Equipment / facility failure | other equipment / facility failure | 0.0047714
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 4.3026e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 4.451e-07
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 4.7477e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.2293e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.2717e-07
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.3565e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | Contact from object | other contact from object | 5.532e-05
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | Contact from object | other contact from object | 5.7227e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | Contact from object | other contact from object | 6.1042e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0057201
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.00059173
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0063118
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.7114e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.5406e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1059e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2881e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.8766e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00010089
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.0075e-08
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4498e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 1.105e-06
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.00022861
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 2.5313e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 5.2369e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.9211e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 3.9746e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 1.341e-06
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00027743
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.393e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 4.9509e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.1319e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 6.4796e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 2.374e-06
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00049115
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.112e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.4606e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.5726e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.7961e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5865e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.5328e-10
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.0398e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.1091e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0224e-08
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9212e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3145e-07
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3592e-05
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.2883e-10
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5109e-10
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.7992e-09
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.0304e-07
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.7451e-08
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 4.9861e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 2.2437e-07
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 2.32e-05
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 4.9357e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.4102e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | dead | 6.346e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | dead | 6.5617e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.2916e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.5474e-10
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.9463e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 3.0465e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.0224e-08
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.9212e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 1.3145e-07
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.3592e-05
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 3.173e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 9.0657e-10
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 4.0795e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 4.2182e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.4646e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.5613e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | grow into | 7.0259e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | grow into | 7.2648e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.4245e-08
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.2642e-08
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 5.6887e-07
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 5.8821e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.7052e-09
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.7052e-09
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.1347e-08
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.8174e-06
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5414e-09
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5414e-09
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2873e-08
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.9278e-06
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.9476e-08
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.9476e-08
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.7528e-07
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.0099e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.141e-09
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.141e-09
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0269e-08
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7635e-06
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.0776e-08
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.0776e-08
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 4.5699e-07
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 7.8475e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.072e-08
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.072e-08
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 1.8648e-07
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 3.2023e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.1524e-08
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.1524e-08
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.9372e-07
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 3.3266e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.396e-07
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.396e-07
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 1.2564e-06
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00021575
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.8163e-08
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.8163e-08
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.5347e-07
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 4.3526e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.4377e-09
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.4377e-09
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.1939e-08
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 3.7674e-06
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.2025e-07
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.2025e-07
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 1.0823e-06
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00018585
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.5021e-08
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2146e-08
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.2875e-08
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0014e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.6681e-08
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.0973e-09
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.8584e-08
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.6757e-07
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.1094e-07
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.8705e-08
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.5223e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.8399e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.417e-08
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.0243e-09
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2146e-08
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6689e-07
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 8.3604e-07
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.1943e-07
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 7.1661e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 9.8467e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.1174e-07
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.4535e-08
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | dead | 2.6721e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | dead | 3.6717e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.4089e-07
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.4413e-08
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.0648e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 2.8372e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.0486e-06
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.498e-07
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 8.988e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.235e-05
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.6923e-07
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.8462e-08
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.3077e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 3.171e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.834e-08
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.0486e-09
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | grow into | 2.4292e-08
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | grow into | 3.3379e-07
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.417e-06
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 2.0243e-07
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 1.2146e-06
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.6689e-05
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.2949e-05
non-HFTD - Substation | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.6998e-06
non-HFTD - Substation | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00016649
non-HFTD - Substation | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.017215
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0015197
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.31442
HFTD - Substation | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0011127
HFTD - Substation | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00015895
HFTD - Substation | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00095372
HFTD - Substation | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.013105
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.7229e-05
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.7229e-05
HFTD - Substation | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00087506
HFTD - Substation | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.15027

## Ignition_to_Outage_Rate
Source file: | EO-WLDFR-5_Data_Pivots_DOVHD_outages_2015-2020.xlsb
Source file location: | WMP > 2022 > Risk Bow-Tie model support files
Sub-Driver | Associated with Ignition | Not associated with Ignition | Grand Total | Ignition to Outage rate
Capacitor/Booster/Regulator | 28 | 409 | 437 | 6.407%
Conductor | 214 | 5273 | 5487 | 3.9%
Connector/Splice/Jumper/Kearney | 138 | 7176 | 7314 | 1.887%
Cross-arm | 29 | 4499 | 4528 | 0.6405%
Cutout/Fuse | 25 | 4149 | 4174 | 0.5989%
Insulator/Woodpin | 23 | 1825 | 1848 | 1.245%
Other | 6 | 1705 | 1711 | 0.3507%
Pole | 81 | 4617 | 4698 | 1.724%
Recloser/Sectionalizer | 6 | 274 | 280 | 2.143%
Secondary/Service | 30 | 2129 | 2159 | 1.39%
Support Structure | 4 | 256 | 260 | 1.538%
Surge Arrestor | 11 | 748 | 759 | 1.449%
Switch | 5 | 351 | 356 | 1.404%
Transformer | 60 | 18330 | 18390 | 0.3263%
Grand Total | 660 | 51741 | 52401 | 1.26%
Animal contact | 52 | 6112 | 6164 | 0.8436%
Bird Contact | 140 | 6008 | 6148 | 2.277%
Grand Total | 192 | 12120 | 12312

## 7.3.3.1_Exposure
Source file: | 2022 WMP MASTER financials reach out v6_021122.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Non Enhanced Distribution Maintenance (Capacitor Maintenance only) |  | KAF, KBC, 2AE, 2BD, 17P, 06A, 06D, 06H, 06K | 444.6216 | 524.4233 | 524.8033 | 524.78 | 170.3654 | 263.2258 | 263.1054 | 263.1054
Distribution - All tier Split | 8.772% | Tier 3 |  |  | 39.004 | 46.0045 | 46.0379 | 46.0358 | 14.9451 | 23.0912 | 23.0807 | 23.0807
Distribution - All tier Split | 22.61% | Tier 2 |  |  | 100.5454 | 118.5915 | 118.6774 | 118.6722 | 38.5259 | 59.5251 | 59.4979 | 59.4979
Distribution - All tier Split | 0.01852% | Zone 1 |  |  | 0.082333 | 0.097111 | 0.097181 | 0.097177 | 0.031548 | 0.048743 | 0.048721 | 0.048721
Distribution - All tier Split | 68.6% | Tier 1 |  |  | 304.9899 | 359.7302 | 359.9908 | 359.9748 | 116.8628 | 180.5607 | 180.4781 | 180.4781

## 7.3.3.1_Financials
Source file: | 2022 WMP MASTER financials reach out v6_021122.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Non Enhanced Distribution Maintenance (Capacitor Maintenance only) |  | KAF, KBC, 2AE, 2BD, 17P, 06A, 06D, 06H, 06K | 2383379.68 | 2959176.0607 | 2369236.2738 | 2436159.7214 | 8248002.2642 | 11358483.6122 | 10549235.774 | 11964722.2018

## 7.3.3.2_Exposure
Source file: | 2022 WMP MASTER financials reach out v7_022222.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
A) Non Enhanced Substation Distribution Maintenance |  |  |  | GCB, GCM, GCS, GCV | 2253 | 2067 | 2817 | 2817 | 0 | 0 | 0 | 0
Distribution - All tier Split | 8.772% | Tier 3 |  |  | 197.6423 | 181.3256 | 247.1187 | 247.1187 | 0 | 0 | 0 | 0
Distribution - All tier Split | 22.61% | Tier 2 |  |  | 509.4866 | 467.4251 | 637.0279 | 637.0279 | 0 | 0 | 0 | 0
Distribution - All tier Split | 0.01852% | Zone 1 |  |  | 0.4172 | 0.38276 | 0.52164 | 0.52164 | 0 | 0 | 0 | 0
Distribution - All tier Split | 68.6% | Tier 1 |  |  | 1545.4539 | 1417.8665 | 1932.3318 | 1932.3318 | 0 | 0 | 0 | 0
Base or Preventative Substation Transmission Maintenance |  |  |  | AMB, AMM, AMS, AMV | 4639 | 3572 | 3416 | 3687 | 0 | 0 | 0 | 0
Transmission - All tier Split | 7.114% | Tier 3 |  |  | 330.0252 | 254.1173 | 243.0192 | 262.2986 | 0 | 0 | 0 | 0
Transmission - All tier Split | 23.29% | Tier 2 |  |  | 1080.5005 | 831.9784 | 795.6434 | 858.7638 | 0 | 0 | 0 | 0
Transmission - All tier Split | 0.03304% | Zone 1 |  |  | 1.5326 | 1.1801 | 1.1286 | 1.2181 | 0 | 0 | 0 | 0
Transmission - All tier Split | 69.56% | Tier 1 |  |  | 3226.9416 | 2484.7242 | 2376.2088 | 2564.7195 | 0 | 0 | 0 | 0

## 7.3.3.2_Financials
Source file: | 2022 WMP MASTER financials reach out v7_022222.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Base Substation Distribution Maintenance |  |  | 2368310 | 2638202 | 2585980.3424 | 2411392 | 0 | 0 | 0 | 0
|  | Base or Preventative Substation Transmission Maintenance |  |  | 2414211 | 2088398 | 2444531.6006 | 2444531.6006 | 0 | 0 | 0 | 0

## 7.3.3.4_Exposure
Source file: | 2022 WMP MASTER financials reach out v6_021122.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Covered Conductor (DO Maintenance) |  |  |  | 4455 | 3313 | 3313 |  | 1868 | 4516 | 4516
Distribution - HTFD Split | 27.93% | Tier 3 |  |  |  | 801.6911 | 783.255 | 783.255 |  | 193.8584 | 768.1709 | 768.1709
Distribution - HTFD Split | 72.01% | Tier 2 |  |  |  | 2066.6166 | 2019.0916 | 2019.0916 |  | 499.7324 | 1980.2076 | 1980.2076
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  |  | 1.6923 | 1.6534 | 1.6534 |  | 0.40921 | 1.6215 | 1.6215
Distribution - HTFD Split | 0% | Tier 1 |  |  |  | 1585 | 509 | 509 |  | 1174 | 1766 | 1766

## 7.3.3.4_Financials
Source file: | 2022 WMP MASTER financials reach out v7
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Covered Conductor (DO Maintenance) |  |  | 17027136 | 15281398 | 9013305 | 9013305 | 18576556 | 29052111 | 44386310 | 44386310

## 7.3.3.5_Exposure
Source file: | 2022 WMP MASTER financials reach out v7
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Crossarm (TO, DO, System Hardening) |  |  | 226.172 | 211 | 127 | 142 | 4571.9196 | 6832 | 7199 | 7199
|  | TO |  |  | 37 | 45 | 55 | 70 | 372 | 459 | 289 | 289
| SME driven | Tier 3 |  |  | 10.8097 | 7 | 9 | 11 | 84 | 130 | 85 | 85
| SME driven | Tier 2 |  |  | 21.9765 | 23 | 28 | 36 | 169 | 211 | 126 | 126
| SME driven | Zone 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SME driven | Tier 1 |  |  | 4.2138 | 15 | 18 | 23 | 119 | 118 | 78 | 78
|  | DO |  |  | 189.172 | 166 | 72 | 72 | 4199.9196 | 6373 | 6910 | 6910
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 25.2553 | 24.5815 | 13.9667 | 13.9667 | 550.1273 | 674.5937 | 869.2901 | 869.2901
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 65.1037 | 63.3666 | 36.0038 | 36.0038 | 1418.13 | 1738.9823 | 2240.8749 | 2240.8749
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 0.053311 | 0.051889 | 0.029482 | 0.029482 | 1.1613 | 1.424 | 1.835 | 1.835
Distribution - HTFD Split | 0% | Tier 1 |  |  | 98.7596 | 78 | 22 | 22 | 2230.501 | 3958 | 3798 | 3798

## 7.3.3.5_Financials
Source file: | 2022 WMP MASTER financials reach out v7
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Crossarm (TO, DO, System Hardening) |  |  | 966638.9894 | 2820125.7166 | 2567165.8314 | 2760698.0871 | 52085714.4211 | 80299618.481 | 71788164.6441 | 68996612.7609

## 7.3.3.6_Exposure
Source file: | 2022 WMP MASTER financials reach out v6_021122.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  |  | 07 | 07D, 07C, GAD | 4402 | 3371 | 4200 | 4500 | 9607 | 15898 | 18145 | 16522
|  | 07C (FRMMA WMPMA) |  |  | 0 | 0 | 0 | 0 | 0 | 393 | 958 | 270
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 0 | 0 | 0 | 0 | 0 | 109.7786 | 267.6028 | 75.4204
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 0 | 0 | 0 | 0 | 0 | 282.9897 | 689.8323 | 194.4204
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0.23173 | 0.56488 | 0.1592
| direct input from SME | Tier 1 |  |  | 0 | 0 | 0 | 0
|  | 07D (FRMMA WMPMA) |  |  | 0 | 0 | 0 | 0 | 7342 | 12990.7488 | 14400 | 15983
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 0 | 0 | 0 | 0 | 3058 | 3628.7693 | 4022.4223 | 4464.6094
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 0 | 0 | 0 | 0 | 4244 | 9354.3196 | 10369.0868 | 11508.9663
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 40 | 7.6599 | 8.4909 | 9.4243
| direct input from SME | Tier 1 |  |  | 0 | 0 | 0 | 0 | 2265 | 2514.2512 | 2787 | 269
|  | GAD |  |  | 4402 | 3371 | 4200 | 4500 | 0 | 0 | 0 | 0
Distribution - All tier Split | 8.772% | Tier 3 |  |  | 369.768 | 283.164 | 352.8 | 378 | 0 | 0 | 0 | 0
Distribution - All tier Split | 22.61% | Tier 2 |  |  | 893.606 | 684.313 | 852.6 | 913.5 | 0 | 0 | 0 | 0
Distribution - All tier Split | 0.01852% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution - All tier Split | 68.6% | Tier 1 |  |  | 3138.626 | 2403.523 | 2994.6 | 3208.5 | 0 | 0 | 0 | 0

## 7.3.3.6_Financials
Source file: | 2022 WMP MASTER financials reach out v6_021122.xlsx
Source file location: | WMP -> 2022 -> Financials
|  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
|  |  |  | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | 07 | 07D, 07C, GAD | 4783468.28 | 2800146.93 | 3460022.1071 | 3911424.0567 | 238929563 | 390886885.74 | 419170185 | 434217542.672

## 7.3.3.7_Exposure
Source file: | 2022 WMP MASTER financials reach out v6_021422.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023 | 2022 Revised allocation
|  | Non Exempt Fuse | 2A | 2AP | 0 | 0 | 0 | 0 | 643 | 1429 | 3000 | 3000
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 0 | 0 | 0 | 0 | 179.6123 | 399.1695 | 838.0046 | 838.0046 | 1046.4275
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 0 | 0 | 0 | 0 | 463.0085 | 1028.9879 | 2160.2264 | 2160.2264 | 1849.5629
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 0.37914 | 0.8426 | 1.7689 | 1.7689 | 104.0096
Distribution - HTFD Split | 0% | Tier 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Miles covered per expulsion fuse replacement calculation:
| 708 | Units of expulsion fuses replaced in 2019. Source file: "2021-Wildfire-Safety-Plan-Revised-060321", pg. 536
| 643 | Units of expulsion fuses replaced in 2020
| 1429 | Units of expulsion fuses replaced in 2021
| 3000 | Units of expulsion fuses replaced in 2022
| 13000 | Units of expulsion fuses planned to be replaced between 2023-2028. Source file: "Initiative 7.3.3.7" draft narrative, pg.10
18780
| 25461.6694 | Total miles in HFTD Distribution
Given the program is targeting 18,558 expulsion fuse replacements in HFTD only:
| 1.3558 | miles covered per expulsion fuse replacement
15.97%
For 2022, the Work plan for replacing approximately 3000 expulsion fuses was provided by the SME. Percentage allocation from this file was used to proportionately divide the work by tranche.
Source file: | TOL 2022 Work Plan 113021.xlsx
Source file location: | WMP -> 2022 -> Grid Design & System Hardening -> Source Data (RSE Input Template)
| Tier | 2022 allocation | Percentage allocation
| 0 | 67 | 2.02%
| Tier 2 | 2045 | 61.65%
| Tier 3 | 1157 | 34.88%
| Neither | 48 | 1.447%

## 7.3.3.7_Financials
Source file: | 2022 WMP MASTER financials reach out v6_021422.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Non Exempt Fuse | 2A | 2AP | 0 | 0 | 0 | 0 | 7846551 | 11295164.53 | 35000000 | 35000000

## 7.3.3.8.3_Exposure
Source file: | 2022 WMP MASTER financials reach out v6_021422.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | D Line Motorized Switch Operator Pilot (Subset of PSPS Sectionalizing) |  |  | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 100
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 0 | 0 | 0 | 0 | 0 | 13.9667 | 13.9667 | 27.9335
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 0 | 0 | 0 | 0 | 0 | 36.0038 | 36.0038 | 72.0075
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0.029482 | 0.029482 | 0.058965
Distribution - HTFD Split | 0% | Tier 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
From the draft narrative, we have the following scope of work:
50 | MSO switches replaced with SCADAMATE-SD and Viper reclosers in 2021 in HFTD areas
50 | MSO switches planned to be replaced in 2022 of the 104 remaining MSO switches that need to replaced in HFTD areas
54 | The remaining balance of MSO switches that will be replaced in 2023 and 2024 in HFTD areas
25461.6694 | Total HFTD Distribution miles
165.3355 | Estimate of the miles covered per MSO switch replacement in HFTD

## 7.3.3.8.3_Financials
Source file: | 2022 WMP MASTER financials reach out v6_021422.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | D Line Motorized Switch Operator Pilot (Subset of PSPS Sectionalizing) |  |  | 0 | 0 | 0 | 0 | 34977990.95 | 14912755.555 | 10452198.8726 | 5948759.85

## 7.3.3.9.2_Exposure
[5 empty] | HFTD | Non-HFTD
Average Fuse Zone Length Per Unit |  |  |  |  | 0.76208 | 0.40147 | miles
SME provided average FuseSaver protective zone by region in HFTD and non-HFTD. Took the average protective zone for each FuseSaver by region in HFTD and non-HFTD to estimate average protective zone length per unit.
From GRC Forecast
| Chapter | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Non-HFTD | 13 | 34 | 32 | 81 | 38 | 36 | 34 | 32 | Count of Fuse Savers
HFTD | 4.3 |  | 66 | 77 | 80 | 82 | 83 | 85
Total Distribution |  | 34 | 98 | 158 | 118 | 118 | 117 | 117
Exposure in Line Mile
| Chapter | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
OH in Non-HFTD Exposure | 13 | 13.65 | 12.8471 | 32.5192 | 15.2559 | 14.453 | 13.65 | 12.8471
OH in HFTD Exposure | 4.3 | 0 | 50.2974 | 58.6803 | 60.9666 | 62.4907 | 63.2528 | 64.777
From WMP 2022 Financial file (021422):
| Chapter | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Non-HFTD | WMP 2022 | 0 | 0 | 0 | 0
HFTD | WMP 2022 | 0 | 71 | 80 | 80
Total Distribution | WMP 2022 | 0 | 71 | 80 | 80
Exposure in Line Mile
| Chapter | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
OH in Non-HFTD Exposure | WMP 2022 | 0 | 0 | 0 | 0
OH in HFTD Exposure | WMP 2022 | 0 | 54.1078 | 60.9666 | 60.9666
Note on E25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Taken from Chris Wong's email to Yumi.
Note on E26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Taken from Chris Wong's email to Yumi.

## 7.3.3.9.2_Financials
Source file: | 2022 WMP MASTER financials reach out v6_021422.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Fuse Saver (now "Single Phase Reclosers") | 49 | 49T |  |  |  |  | 0 | 6730335.85 | 4400000 | 4400000

## 7.3.3.9.2_Effectiveness
From GRC 2023 filing:
Effectiveness Calculation
WLDFR Driver | Updated Subdriver | RAMP Subdriver | # wiredown | # outages | # ignitions | % wiredown | Est. % of outages where FuseSaver can potentially mitigate Wildfire ignition risk | Est. # of outages where FuseSaver can potentially mitigate Wildfire ignition risk | Outage to Ignition Rate | # of ignitions avoided | Effectiveness
Contact from object | Animal contact | Animal Contact | 192 | 6229 | 52 | 3.082% | 2.158% | 134.4 | 0.8436% | 1.1338 | 2.18%
Equipment / facility failure | Conductor damage or failure | Conductor | 4016 | 5517 | 214 | 72.79% | 50.96% | 2811.2 | 3.9% | 109.6404 | 51.23%
Equipment / facility failure | Connection device damage or failure | Connector | 1557 | 7331 | 138 | 21.24% | 14.87% | 1089.9 | 1.887% | 20.5642 | 14.9%
Equipment / facility failure | Crossarm damage or failure | Cross-Arm | 363 | 4528 | 29 | 8.017% | 5.612% | 254.1 | 0.6405% | 1.6274 | 5.612%
Equipment / facility failure | Fuse damage or failure | Fuse | 13 | 4359 | 25 | 0.2982% | 0.2088% | 9.1 | 0.5989% | 0.054504 | 0.218%
Equipment / facility failure | Insulator and brushing damage or failure | Insulator | 200 | 1847 | 23 | 10.83% | 7.58% | 140 | 1.245% | 1.7424 | 7.576%
Equipment / facility failure | Other equipment / facility failure | Equip-Other | 18 | 1832 | 6 | 0.9825% | 0.6878% | 12.6 | 0.3507% | 0.044185 | 0.7364%
Equipment / facility failure | Pole damage or failure | Pole | 912 | 4699 | 81 | 19.41% | 13.59% | 638.4 | 1.724% | 11.0069 | 13.59%
Equipment / facility failure | Lightning arrestor damage or failure | Surge/lightning Arrestor | 3 | 758 | 11 | 0.3958% | 0.277% | 2.1 | 1.449% | 0.030435 | 0.2767%
Equipment / facility failure | Switch damage or failure | Switch | 4 | 421 | 5 | 0.9501% | 0.6651% | 2.8 | 1.404% | 0.039326 | 0.7865%
Equipment / facility failure | Transformer damage or failure | Transformer | 192 | 19322 | 60 | 0.9937% | 0.6956% | 134.4 | 0.3263% | 0.4385 | 0.7308%
Vandalism / Theft | Vandalism / Theft | Vandalism | 28 | 181 | 7 | 15.47% | 10.83% | 19.6 | 4.242% | 0.83152 | 11.88%
Contact from object | Vehicle contact | Vehicle/car pole | 3805 | 10189 | 232 | 37.34% | 26.14% | 2663.5 | 2.291% | 61.0122 | 26.3%
Contact from object | Balloon contact | Metallic Balloon | 252 | 2587 | 12 | 9.741% | 6.819% | 176.4 | 2.091% | 3.6878 | 30.73%
Contact from object | Other contact from object | 3rd party-Other | 84 | 622 | 1 | 13.5% | 9.453% | 58.8 | 0.3507% | 0.2062 | 20.62%
Vegetation Contact | Branch (Not overhanging, > 12ft) | Branch (Not overhanging, > 12ft) | 200 | 615 | 9 | 32.52% | 22.76% | 140 | 1.466% | 2.0521 | 22.8%
Vegetation Contact | Branch (Not overhanging, 4-12ft) | Branch (Not overhanging, 4-12ft) | 106 | 343 | 2 | 30.9% | 21.63% | 74.2 | 0.5831% | 0.43265 | 21.63%
Vegetation Contact | Branch (Not overhanging, Distance Unknown) | Branch (Not overhanging, Distance Unknown) | 750 | 1861 | 74 | 40.3% | 28.21% | 525 | 3.976% | 20.8759 | 28.21%
Vegetation Contact | Branch (Not overhanging, within 4ft) | Branch (Not overhanging, within 4ft) | 76 | 195 |  | 38.97% | 27.28% | 53.2 | 0% | 0
Vegetation Contact | Branch (Overhanging) | Branch (Overhanging) | 1557 | 4436 | 96 | 35.1% | 24.57% | 1089.9 | 2.165% | 23.5973 | 24.58%
Vegetation Contact | Dead | Dead | 519 | 1381 | 25 | 37.58% | 26.31% | 363.3 | 1.812% | 6.5815 | 26.33%
Vegetation Contact | Fell into (Moderate-Severe defect) | Fell into (Moderate-Severe defect) | 757 | 1263 | 51 | 59.94% | 41.96% | 529.9 | 4.038% | 21.3974 | 41.96%
Vegetation Contact | Fell into (No defect) | Fell into (No defect) | 5384 | 8329 | 156 | 64.64% | 45.25% | 3768.8 | 1.873% | 70.5971 | 45.25%
Vegetation Contact | Fell into (slight defect) | Fell into (slight defect) | 1053 | 1627 | 54 | 64.72% | 45.3% | 737.1 | 3.323% | 24.4944 | 45.36%
Vegetation Contact | Grow Into | Grow Into | 104 | 786 | 8 | 13.23% | 9.262% | 72.8 | 1.02% | 0.74286 | 9.286%
Vegetation Contact | Other/Unknown | Other/Unknown | 3036 | 9973 | 91 | 30.44% | 21.31% | 2125.2 | 0.9129% | 19.4014 | 21.32%
SME Judgement: | If Driver/Sub Driver event creates a permanent fault condition that creates a wire down event the FuseSaver will lockout all phases and prevent backfeed condition on the faulted phase. In this instance, probably of mitigating an ignition is 70%.

## 7.3.3.10_Exposure
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Connectors, including hotline clamps Maintenance, repair, and replacement of |  |  | 8367.8453 | 7995 | 5941 | 5941 | 0 | 221 | 540 | 540
|  | Transmission component |  |  | 26 | 27 | 14 | 14 | 0 | 0 | 0 | 0
| 0% | Tier 3 |  |  | 10.724 | 3 | 2 | 2 | 0 | 0 | 0 | 0
| 0% | Tier 2 |  |  | 15.276 | 14 | 7 | 7 | 0 | 0 | 0 | 0
| 0% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0% | Tier 1 |  |  | 0 | 10 | 5 | 5 | 0 | 0 | 0 | 0
|  | Dist Maintenance component |  |  | 8341.8453 | 7968 | 5927 | 5927 |  | 221 | 540 | 540
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 2099.923 | 2043.8933 | 1523.7718 | 1523.7718 |  | 53.9116 | 142.7401 | 142.7401
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 5413.2268 | 5268.7922 | 3928.0117 | 3928.0117 |  | 138.9746 | 367.9586 | 367.9586
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 4.4327 | 4.3144 | 3.2165 | 3.2165 |  | 0.1138 | 0.30131 | 0.30131
| see Maintenance tab | Tier 1 |  |  | 824.2628 | 651 | 472 | 472 |  | 28 | 29 | 29

## 7.3.3.10_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Connectors, including hotline clamps Maintenance, repair, and replacement of |  |  | 24792900.6661 | 23651413.6307 | 14596800.5293 | 14597698.8379 | 0 | 1583868.2267 | 3134723.1192 | 3134723.1192

## 7.3.3.12.1_Exposure
Source file: | 2022 WMP MASTER financials reach out v3_020722
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
Animal Abatement - Distribution |  |  | 48 | 48X | 0 | 0 | 0 | 0 | 22.9814 | 21 | 0 | 0
Distribution - All tier Split | 8.772% | Tier 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8422
Distribution - All tier Split | 22.61% | Tier 2 |  |  | 0 | 0 | 0 | 0 | 1.0944 | 1 | 0 | 4.7489
Distribution - All tier Split | 0.01852% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 1.0944 | 1 | 0 | 0.0038887
Distribution - All tier Split | 68.6% | Tier 1 |  |  | 0 | 0 | 0 | 0 | 20.7927 | 19 | 0 | 14.405

## 7.3.3.12.1_Financials
Source file: | 2022 WMP MASTER financials reach out v3_020722
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
Animal Abatement - Distribution |  |  | 48 | 48X | 0 | 0 | 0 | 0 | 4960890.05 | 4533182.2 | 5308330.188 | 6421961.0162
Distribution - All tier Split | 8.772% | Tier 3 |  |  | 0 | 0 | 0 | 0 | 435189.4313 | 397669.1609 | 465668.2919 | 563360.5128
Distribution - All tier Split | 22.61% | Tier 2 |  |  | 0 | 0 | 0 | 0 | 1121840.6984 | 1025120.1365 | 1200409.7623 | 1452242.8756
Distribution - All tier Split | 0.01852% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 918.638 | 839.4367 | 982.9756 | 1189.1933
Distribution - All tier Split | 68.6% | Tier 1 |  |  | 0 | 0 | 0 | 0 | 3402941.2823 | 3109553.4658 | 3641269.1583 | 4405168.4345

## 7.3.3.12.3_Exposure
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Transmission |  |  | 10295 | 9617 | 10132 | 13260 | 5582 | 5384 | 5037 | 5838
| 25.44% | Tier 3 |  |  | 732.4013 | 684.1674 | 720.8052 | 943.3357 | 397.1116 | 383.0256 | 358.3395 | 415.3238
| 40.4% | Tier 2 |  |  | 2397.8773 | 2239.9598 | 2359.9119 | 3088.4753 | 1300.141 | 1254.0235 | 1173.2014 | 1359.7676
| 0% | Zone 1 |  |  | 3.4012 | 3.1772 | 3.3474 | 4.3808 | 1.8442 | 1.7788 | 1.6641 | 1.9287
| 34.16% | Tier 1 |  |  | 7161.3201 | 6689.6956 | 7047.9355 | 9223.8082 | 3882.9033 | 3745.1722 | 3503.795 | 4060.9798

## 7.3.3.12.3_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Transmission |  |  | 99945964.18 | 89135581.21 | 127975538.0805 | 139107312 | 449179013.8168 | 360362223.99 | 412054650.1115 | 381315733.3912

## 7.3.3.12.4_Exposure
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Enhanced - Maintenance Distribution (removed Poles) |  |  | 45669.8735 | 41331.3971 | 32272 | 33285 | 27207 | 24990.4662 | 18340 | 31642
|  | 8.772% |  |  | 9529.5286 | 8650.5601 | 6186.7112 | 6275.5757 | 3794.8565 | 3225.2391 | 2703.5319 | 5232.9819
|  | 22.61% |  |  | 24565.4244 | 22299.6004 | 15948.2375 | 16177.3143 | 9782.4628 | 8314.091 | 6969.2228 | 13489.6936
|  | 0.01852% |  |  | 20.1158 | 18.2604 | 13.0595 | 13.2471 | 8.0105 | 6.8081 | 5.7069 | 11.0463
|  | 68.6% |  |  | 11554.8047 | 10362.9761 | 10123.9918 | 10818.863 | 13621.6702 | 13444.328 | 8661.5384 | 12908.2782

## 7.3.3.12.4_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Enhanced - Maintenance Distribution (removed Poles) |  |  | 75248474.0009 | 74702949.0218 | 93704432.5808 | 73465810.1603 | 331098926.4 | 295107958.9417 | 196540836.8751 | 329592612.5273

## 7.3.3.13_Exposure
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Pole Loading replacement and wind loading | O7 | O7O |  |  |  |  | 288 | 559 | 269 | 262
| HFTD | [7 empty] | 143 | 391 | 223 | 217
| Non-HFTD | [7 empty] | 145 | 168 | 46 | 45

## 7.3.3.13_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Pole Loading replacement and wind loading | O7 | O7O | 61071.45 | 410.75 | 154455 | 158910 | 13793345.9 | 19998089.91 | 9236196 | 9220919

## 7.3.3.14_Exposure
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
[5 empty] | 37.7244 | 33 | 35 | 35 | 17 | 2865 | 1453 | 1653
|  | Dist Maintenance component | IG | IG# | 37.7244 | 33 | 35 | 35 |  | 2830 | 1253 | 1253
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 4.8789 | 4.7487 | 6.9834 | 6.9834 |  | 436.3211 | 206.1491 | 206.1491
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 12.5769 | 12.2413 | 18.0019 | 18.0019 |  | 1124.7579 | 531.4157 | 531.4157
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 0.010299 | 0.010024 | 0.014741 | 0.014741 |  | 0.92103 | 0.43516 | 0.43516
Distribution - HTFD Split | 100% | Tier 1 |  |  | 20.2584 | 16 | 10 | 10 |  | 1268 | 515 | 515
|  | Substation | 06 | 06B | 0 | 0 | 0 | 0 | 17 | 35 | 200 | 400
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 0 | 0 | 0 | 0 | 4.7487 | 9.7767 | 55.867 | 111.734
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 0 | 0 | 0 | 0 | 12.2413 | 25.2026 | 144.0151 | 288.0302
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 0.010024 | 0.020638 | 0.11793 | 0.23586
Distribution - HTFD Split | 0% | Tier 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 7.3.3.14_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
|  |  |  | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  |  |  | 129234.1601 | 108453.55 | 1335043.5552 | 1372543.5552 | 858930.12 | 48102836.8179 | 22485216.4745 | 17358716.4745

## 7.3.3.15_Exposure
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Transmission Maintenance | IC, 70 | ICQ, ICS, ICX, 70S | 8058 | 7462 | 6095 | 6387.9445 | 8 | 4 | 125 | 125
| 20.27% | Tier 3 |  |  | 1635.3972 | 1514.4371 | 1237 | 1296.454 | 1.6236 | 0.81181 | 25.3692 | 25.3692
| 43.14% | Tier 2 |  |  | 3481.0031 | 3223.535 | 2633 | 2759.5501 | 3.4559 | 1.728 | 53.9992 | 53.9992
| 0% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 36.6% | Tier 1 |  |  | 2941.5997 | 2724.0279 | 2225 | 2331.9404 | 2.9204 | 1.4602 | 45.6317 | 45.6317

## 7.3.3.15_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Transmission Maintenance | IC, 70 | ICQ, ICS, ICX, 70S | 51008442.53 | 57675555.1978 | 50261232.5 | 53422010 | 40848309.96 | 60006797.64 | 154981000 | 175000000

## 08W_Cost_Units
Source file: | Supplemental Forecast Update - 20220131.xlsx
Source file location: | WMP -> 2022 -> Financials
Updated Forecast (Un-Escalated)
|  | Year | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Overhead
|  | Planning Order | 5795518 | 5795520 | 5795522 | 5795524 | 5795526 | 5795528
|  | Forecast | 288000000 | 366000000 | 258400000 | 77277650 | 77472000 | 77667800
|  | Units (Miles) | 180 | 305 | 170 | 50 | 50 | 50
|  | Unit Cost (unescalated) | 1600000 | 1200000 | 1520000 | 1545553 | 1549440 | 1553356
|  | Unit Cost (escalated) | 0 | 1200000 | 1561040 | 1630139.5701 | 1678363.7629 | 1728035.9515
Underground
|  | Planning Order | 5795519 | 5795521 | 5795523 | 5795525 | 5795527 | 5795529
|  | Forecast | 86120000 | 611250000 | 1161225000 | 2290500000 | 2684275000 | 3000000000
|  | Units (Miles)**??? | 20 | 163 | 357.3 | 763.5 | 976.1 | 1200
|  | Unit Cost**??? | 4306000 | 3750000 | 3250000 | 3000000 | 2750000 | 2500000
|  | Unit Cost (escalated) | 4306000 | 3750000 | 3337750 | 3164187 | 2978818.3782 | 2781133.1586
Butte Rebuild (08W)
|  | Planning Order | 5791246/ 5793698 | 5795565 | 5795565 | 5795565 | 5795565
|  | Forecast | 41534000 | 52875000 | 52650000 | 41700000 | 25025000 | 0
|  | Units (Miles)** | 9.7 | 14.1 | 16.2 | 13.9 | 9.1 | 0
|  | Unit Cost** | 4281855.6701 | 3750000 | 3250000 | 3000000 | 2750000 | 0
|  | Unit Cost (escalated) | 4281855.6701 | 3750000 | 3337750 | 3164187 | 2978818.3782 | 0

## M002
| Source File | [9 empty] | Calculation
| Tranching analysis | [9 empty] | Overhead miles | [5 empty] | Underground miles | [5 empty] | remote grid
| Tranche | Exposure (miles) | Frequency | Total Risk Score | CoRE | Risk Score/Mile | % of Risk Score | % Miles | # of CS-Tiers | SH Miles Allocation | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
| HFTD - Distribution - 1QU CoRE ¦ 1QU LoRE | 222.3663 | 2.5095 | 1413.4 | 563 | 6.3562 | 6.192% | 0.8733% | 113 | 2.016% | 2.9658 | 6.1491 | 3.4274 | 1.008 | 1.008 | 1.008 | 1.0025 | 2.9132 | 6.0894 | 12.5945 | 15.9267 | 19.3545 | 0.020161 | 0.52418 | 0.52418 | 1.1492 | 1.5927 | 1.8145
| HFTD - Distribution - 1QU CoRE ¦ 2QU LoRE | 510.0995 | 3.1814 | 1776.5 | 558 | 3.4827 | 7.783% | 2.003% | 76 | 4.986% | 7.3346 | 15.207 | 8.4761 | 2.493 | 2.493 | 2.493 | 2.4793 | 7.2046 | 15.0595 | 31.147 | 39.3877 | 47.8648 | 0.049859 | 1.2963 | 1.2963 | 2.842 | 3.9389 | 4.4873
| HFTD - Distribution - 1QU CoRE ¦ 3QU LoRE | 1070.1922 | 5.1783 | 3124.8 | 603 | 2.9198 | 13.69% | 4.203% | 100 | 9.889% | 14.5476 | 30.1618 | 16.8115 | 4.9446 | 4.9446 | 4.9446 | 4.9174 | 14.2898 | 29.8691 | 61.7774 | 78.1221 | 94.9356 | 0.098891 | 2.5712 | 2.5712 | 5.6368 | 7.8124 | 8.9002
| HFTD - Distribution - 1QU CoRE ¦ 4QU LoRE | 1594.2882 | 6.052 | 4077.3 | 674 | 2.5574 | 17.86% | 6.262% | 115 | 14.34% | 21.0921 | 43.7307 | 24.3745 | 7.169 | 7.169 | 7.169 | 7.1296 | 20.7183 | 43.3063 | 89.5691 | 113.2668 | 137.6442 | 0.14338 | 3.7279 | 3.7279 | 8.1726 | 11.327 | 12.9041
| HFTD - Distribution - 1QU CoRE ¦ 5QU LoRE | 1667.6045 | 4.145 | 3168.3 | 764 | 1.8999 | 13.88% | 6.549% | 143 | 15.52% | 22.826 | 47.3256 | 26.3782 | 7.7583 | 7.7583 | 7.7583 | 7.7157 | 22.4215 | 46.8663 | 96.9321 | 122.5779 | 148.9592 | 0.15517 | 4.0343 | 4.0343 | 8.8445 | 12.2581 | 13.9649
| HFTD - Distribution - 2QU CoRE ¦ 1QU LoRE | 377.8964 | 3.669 | 812.1 | 221 | 2.149 | 3.558% | 1.484% | 120 | 2.207% | 3.2464 | 6.7309 | 3.7516 | 1.1034 | 1.1034 | 1.1034 | 1.0974 | 3.1889 | 6.6656 | 13.7862 | 17.4336 | 21.1857 | 0.022068 | 0.57378 | 0.57378 | 1.2579 | 1.7434 | 1.9862
| HFTD - Distribution - 2QU CoRE ¦ 2QU LoRE | 807.5613 | 4.9731 | 1084.3 | 218 | 1.3427 | 4.751% | 3.172% | 85 | 4.771% | 7.0186 | 14.5518 | 8.1109 | 2.3855 | 2.3855 | 2.3855 | 2.3724 | 6.8942 | 14.4106 | 29.805 | 37.6906 | 45.8025 | 0.047711 | 1.2405 | 1.2405 | 2.7195 | 3.7692 | 4.294
| HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | 1225.8696 | 5.9689 | 1364.8 | 229 | 1.1133 | 5.979% | 4.815% | 102 | 8.167% | 12.014 | 24.909 | 13.8837 | 4.0834 | 4.0834 | 4.0834 | 4.061 | 11.8011 | 24.6672 | 51.0185 | 64.5167 | 78.402 | 0.081669 | 2.1234 | 2.1234 | 4.6551 | 6.4518 | 7.3502
| HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | 1187.7252 | 4.5725 | 1023.3 | 224 | 0.86156 | 4.483% | 4.665% | 95 | 8.163% | 12.0083 | 24.897 | 13.877 | 4.0815 | 4.0815 | 4.0815 | 4.0591 | 11.7955 | 24.6554 | 50.994 | 64.4858 | 78.3644 | 0.08163 | 2.1224 | 2.1224 | 4.6529 | 6.4487 | 7.3467
| HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | 1487.6377 | 3.9614 | 989.8 | 250 | 0.66535 | 4.336% | 5.843% | 105 | 10.73% | 15.791 | 32.7397 | 18.2484 | 5.3672 | 5.3672 | 5.3672 | 5.3377 | 15.5111 | 32.422 | 67.0574 | 84.7991 | 103.0496 | 0.10734 | 2.7909 | 2.7909 | 6.1186 | 8.4801 | 9.6609
| HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | 912.8297 | 9.1445 | 833.7 | 91 | 0.91331 | 3.653% | 3.585% | 218 | 2.221% | 3.2675 | 6.7746 | 3.776 | 1.1106 | 1.1106 | 1.1106 | 1.1045 | 3.2096 | 6.7088 | 13.8756 | 17.5468 | 21.3232 | 0.022212 | 0.5775 | 0.5775 | 1.2661 | 1.7547 | 1.999
| HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | 1386.4856 | 8.689 | 878.2 | 101 | 0.6334 | 3.848% | 5.445% | 151 | 2.913% | 4.2854 | 8.8849 | 4.9523 | 1.4565 | 1.4565 | 1.4565 | 1.4485 | 4.2094 | 8.7987 | 18.1981 | 23.0128 | 27.9657 | 0.029131 | 0.7574 | 0.7574 | 1.6605 | 2.3013 | 2.6218
| HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | 1006.7138 | 4.9596 | 489.2 | 99 | 0.48594 | 2.143% | 3.954% | 98 | 2.469% | 3.6318 | 7.5298 | 4.1969 | 1.2344 | 1.2344 | 1.2344 | 1.2276 | 3.5674 | 7.4567 | 15.4225 | 19.5029 | 23.7003 | 0.024688 | 0.64188 | 0.64188 | 1.4072 | 1.9503 | 2.2219
| HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | 964.9333 | 3.5917 | 356.6 | 99 | 0.36956 | 1.562% | 3.79% | 92 | 1.804% | 2.654 | 5.5025 | 3.067 | 0.90206 | 0.90206 | 0.90206 | 0.8971 | 2.6069 | 5.4491 | 11.2703 | 14.2521 | 17.3195 | 0.018041 | 0.46907 | 0.46907 | 1.0283 | 1.4252 | 1.6237
| HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | 850.2029 | 2.149 | 215.7 | 100 | 0.2537 | 0.945% | 3.339% | 83 | 1.576% | 2.3186 | 4.8071 | 2.6794 | 0.78805 | 0.78805 | 0.78805 | 0.78372 | 2.2775 | 4.7605 | 9.8459 | 12.4509 | 15.1306 | 0.015761 | 0.40979 | 0.40979 | 0.89838 | 1.2451 | 1.4185
| HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | 1379.8545 | 14.2723 | 473.4 | 33 | 0.34308 | 2.074% | 5.419% | 313 | 1.232% | 1.8118 | 3.7565 | 2.0938 | 0.61583 | 0.61583 | 0.61583 | 0.61244 | 1.7797 | 3.7201 | 7.6941 | 9.7298 | 11.8239 | 0.012317 | 0.32023 | 0.32023 | 0.70204 | 0.97301 | 1.1085
| HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | 1094.2241 | 6.7895 | 217.5 | 32 | 0.19877 | 0.9529% | 4.298% | 132 | 0.8598% | 1.2648 | 2.6224 | 1.4617 | 0.4299 | 0.4299 | 0.4299 | 0.42754 | 1.2424 | 2.5969 | 5.3712 | 6.7922 | 8.2541 | 0.008598 | 0.22355 | 0.22355 | 0.49008 | 0.67924 | 0.77382
| HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | 1134.9991 | 5.6221 | 181.2 | 32 | 0.15965 | 0.7939% | 4.458% | 119 | 0.9186% | 1.3513 | 2.8018 | 1.5616 | 0.45931 | 0.45931 | 0.45931 | 0.45678 | 1.3274 | 2.7746 | 5.7386 | 7.2568 | 8.8187 | 0.0091861 | 0.23884 | 0.23884 | 0.52361 | 0.7257 | 0.82675
| HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | 899.0313 | 3.4511 | 115.3 | 33 | 0.12825 | 0.5052% | 3.531% | 100 | 0.7129% | 1.0487 | 2.1744 | 1.212 | 0.35646 | 0.35646 | 0.35646 | 0.3545 | 1.0302 | 2.1533 | 4.4536 | 5.6319 | 6.844 | 0.0071291 | 0.18536 | 0.18536 | 0.40636 | 0.5632 | 0.64162
| HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | 588.1638 | 1.481 | 54 | 36 | 0.091811 | 0.2366% | 2.31% | 70 | 0.459% | 0.67517 | 1.3999 | 0.78025 | 0.22948 | 0.22948 | 0.22948 | 0.22822 | 0.66321 | 1.3863 | 2.8672 | 3.6258 | 4.4061 | 0.0045897 | 0.11933 | 0.11933 | 0.26161 | 0.36258 | 0.41307
| HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | 2192.6678 | 24.1805 | 96.9 | 4 | 0.044193 | 0.4245% | 8.612% | 908 | 1.725% | 2.5378 | 5.2618 | 2.9328 | 0.86258 | 0.86258 | 0.86258 | 0.85785 | 2.4929 | 5.2107 | 10.7771 | 13.6285 | 16.5616 | 0.017252 | 0.44854 | 0.44854 | 0.98335 | 1.3629 | 1.5527
| HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | 1295.5943 | 8.1406 | 44.6 | 5 | 0.034424 | 0.1954% | 5.088% | 282 | 1.033% | 1.519 | 3.1494 | 1.7554 | 0.5163 | 0.5163 | 0.5163 | 0.51346 | 1.4921 | 3.1189 | 6.4507 | 8.1573 | 9.913 | 0.010326 | 0.26848 | 0.26848 | 0.58858 | 0.81575 | 0.92934
| HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | 657.7678 | 3.2436 | 17.6 | 5 | 0.026757 | 0.07711% | 2.583% | 178 | 0.5252% | 0.77256 | 1.6018 | 0.89279 | 0.26258 | 0.26258 | 0.26258 | 0.26114 | 0.75887 | 1.5862 | 3.2807 | 4.1487 | 5.0416 | 0.0052517 | 0.13654 | 0.13654 | 0.29935 | 0.41488 | 0.47265
| HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | 442.6987 | 1.6939 | 10.2 | 6 | 0.023041 | 0.04469% | 1.739% | 121 | 0.3688% | 0.54258 | 1.1249 | 0.62702 | 0.18442 | 0.18442 | 0.18442 | 0.1834 | 0.53297 | 1.114 | 2.3041 | 2.9137 | 3.5408 | 0.0036884 | 0.095897 | 0.095897 | 0.21024 | 0.29138 | 0.33195
| HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | 504.2618 | 1.1854 | 6.2 | 5 | 0.012295 | 0.02716% | 1.98% | 174 | 0.3953% | 0.58149 | 1.2056 | 0.67198 | 0.19764 | 0.19764 | 0.19764 | 0.19655 | 0.57118 | 1.1939 | 2.4693 | 3.1226 | 3.7947 | 0.0039528 | 0.10277 | 0.10277 | 0.22531 | 0.31227 | 0.35575
|  | 25461.6694 | 149.7056 | 22824.9 | 152.4652 | 0.9438 | 100% | 100% | 4093 | 100% | 147.107 | 305 | 170 | 50 | 50 | 50 | 49.7253 | 144.5 | 302.04 | 624.7 | 789.98 | 960 | 1 | 26 | 26 | 57 | 79 | 90
[10 empty] | previous miles | 180 | 423 | 423 | 405 | 405 | 405 | 29.7 | 61.1 | 63.2 | 58.9 | 54.1 | 45 | 16 | 26 | 26 | 57 | 79 | 90
[8 empty] | 1037.3364 |  | 1951.9273
[7 empty] | previous | 974 |  | 1757 | Underground miles 2021: 2021; Underground miles 2022: 2022; Underground miles 2023: 2023; Underground miles 2024: 2024; Underground miles 2025: 2025; Underground miles 2026: 2026
| Capital Costs Updated | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | Note |  | Overhead miles 2026: Underground; Underground miles 2021: UG Miles; Underground miles 2022: 163; Underground miles 2023: 357.3; Underground miles 2024: 763.5; Underground miles 2025: 976.1; Underground miles 2026: 1200
Capital Cost | System Hardening [Overhead] | 460714978.5021 | 286120000 | 366000000 | 265376800 | 81506978.5068 | 83918188.1454 | 86401797.5743 | used in 2-Program Cost tab |  | Underground miles 2021: OH Miles to UG; Underground miles 2022: 130.4; Underground miles 2023: 285.84; Underground miles 2024: 610.8; Underground miles 2025: 780.88; Underground miles 2026: 960
Capital Cost | System Hardening [Underground] | 24200434.3379 | 129534000 | 664125000 | 1246649625 | 2459838973.8 | 2934731866.2519 | 3337359790.323 | used in 2-Program Cost tab |  | Underground miles 2021: OH to UG Conversion Factor; Underground miles 2022: 1.25
Capital Cost | Butte Rebuild 08W |  |  | 52875000 | 54071550 | 43982199.3 | 27107247.2421 | 0
Unit Cost | System Hardening [Overhead] |  |  | 1200000 | 1561040 | 1630139.5701 | 1678363.7629 | 1728035.9515 |  |  | Overhead miles 2026: Butte Rebuild (08W)
Unit Cost | Undergrounding |  |  | 3750000 | 3337750 | 3164187 | 2978818.3782 | 2781133.1586 |  |  | Underground miles 2021: UG Miles; Underground miles 2022: 22.2; Underground miles 2023: 25.5064; Underground miles 2024: 21.8851; Underground miles 2025: 14.3277
Unit Cost | Butte Rebuild 08W (per OH mile) |  |  | 3750000 | 3337750 | 3164187 | 2978818.3782 | 0 |  |  | Underground miles 2021: OH Miles to UG; Underground miles 2022: 14.1; Underground miles 2023: 16.2; Underground miles 2024: 13.9; Underground miles 2025: 9.1
[17 empty] | OH to UG Conversion Factor | 1.5745
Capital Cost (Previous)
Capital Cost (Previous) | System Hardening [Overhead] | 460714978.5021 | 286120000 | 663264000 | 641241655.36 | 620774540.77 | 622753940.328 | 625056376.3 |  |  | Overhead miles 2026: System Hardening [Underground] - Total
Capital Cost (Previous) | System Hardening [Underground] | 24200434.3379 | 129534000 | 264684879.12 | 267705265 | 259196816.77 | 241699788.552 | 192152732.7 |  |  | Underground miles 2021: UG Miles; Underground miles 2022: 185.2; Underground miles 2023: 382.8064; Underground miles 2024: 785.3851; Underground miles 2025: 990.4277; Underground miles 2026: 1200
Unit Cost | System Hardening [Overhead] |  |  | 1568000 | 1515937.7195 | 1532776.6439 | 1537664.0502 | 1543349.0773 |  |  | Underground miles 2021: OH Miles to UG; Underground miles 2022: 144.5; Underground miles 2023: 302.04; Underground miles 2024: 624.7; Underground miles 2025: 789.98; Underground miles 2026: 960
Unit Cost | System Hardening [Underground] |  |  | 4331994.7483 | 4235842.8006 | 4400625.0725 | 4467648.5869 | 4270060.7267 |  |  | Underground miles 2021: OH to UG Conversion Factor; Underground miles 2022: 1.2817; Underground miles 2023: 1.2674; Underground miles 2024: 1.2572; Underground miles 2025: 1.2537; Underground miles 2026: 1.25
|  | Recorded Expense by Year (source: GRC MDR, expense by LOB, April 2021) |  |  |  | $ thousands |  |  |  |  | Overhead miles 2024: NPV of O&M Costs
| LOB | 2016 | 2017 | 2018 | 2019 | 2020 | average | Miles | O&M/mile |  | Underground miles 2021: 2021; Underground miles 2022: 2022; Underground miles 2023: 2023; Underground miles 2024: 2024; Underground miles 2025: 2025; Underground miles 2026: 2026
| Elec Dist | 565227.6519 | 717849.3052 | 1290595 | 1693862.9828 | 2215023.9967 | 1296511.7873 | 107370 | 12075.1773 |  | Overhead miles 2026: SH UG miles/OH mile; Underground miles 2021: 1; Underground miles 2022: 1.2817; Underground miles 2023: 1.2674; Underground miles 2024: 1.2572; Underground miles 2025: 1.2537; Underground miles 2026: 1.25
| UG | 96537.3264 | 132172.8728 | 162507.75 | 147818.1522 | 136511.5003 | 135109.5203 | 26980 | 5007.7658 |  | Overhead miles 2026: Net O&M for UG/mile/yr; Underground miles 2021: -9439.333; Underground miles 2022: -8028.8412; Underground miles 2023: -8100.2417; Underground miles 2024: -8151.2373; Underground miles 2025: -8168.6743; Underground miles 2026: -8187.3915
| OH | 468690.3254 | 585676.4324 | 1128087.25 | 1546044.8307 | 2078512.4964 | 1161402.267 | 80390 | 14447.0987 |  | Overhead miles 2026: NPV Net O&M for UG; Underground miles 2021: -6461778.7103; Underground miles 2022: -15971792.8846; Underground miles 2023: -33681808.0124; Underground miles 2024: -70101610.9705; Underground miles 2025: -88838380.7172; Underground miles 2026: -108205602.855; remote grid 2021: used in 2-Program Cost tab
Souce File: Supplemental Forecast Update - 20220131.xlsx
Updated Forecast (Un-Escalated)
[17 empty] | Year | 2022 | 2023 | 2024 | 2025 | 2026
Overhead
[17 empty] | Planning Order | 5795520 | 5795522 | 5795524 | 5795526 | 5795528
[17 empty] | Forecast | 366000000 | 258400000 | 77277650 | 77472000 | 77667800
[17 empty] | Units (Miles) | 305 | 170 | 50 | 50 | 50
[17 empty] | Unit Cost (unescalated) | 1200000 | 1520000 | 1545553 | 1549440 | 1553356
[17 empty] | Unit Cost (escalated) | 1200000 | 1561040 | 1630139.5701 | 1678363.7629 | 1728035.9515
Underground
[17 empty] | Planning Order | 5795521 | 5795523 | 5795525 | 5795527 | 5795529
[17 empty] | Forecast | 611250000 | 1161225000 | 2290500000 | 2684275000 | 3000000000
[17 empty] | Units (Miles)**??? | 163 | 357.3 | 763.5 | 976.1 | 1200
[17 empty] | Unit Cost**??? | 3750000 | 3250000 | 3000000 | 2750000 | 2500000
[17 empty] | Unit Cost (escalated) | 3750000 | 3337750 | 3164187 | 2978818.3782 | 2781133.1586
Butte Rebuild (08W)
[17 empty] | Planning Order | 5795565 | 5795565 | 5795565 | 5795565
[17 empty] | Forecast | 52875000 | 52650000 | 41700000 | 25025000 | 0
[15 empty] | trench mile |  | Units (Miles)** | 14.1 | 16.2 | 13.9 | 9.1 | 0
[17 empty] | Unit Cost** | 3750000 | 3250000 | 3000000 | 2750000 | 0
[17 empty] | Unit Cost (escalated) | 3750000 | 3337750 | 3164187 | 2978818.3782 | 0
[18 empty] | 52875000 | 54071550
CEMA UG Miles (95F)*
[17 empty] | Planning Order |  | 5546026 | 5546026 | 5546026
[17 empty] | Forecast | 85875000 | 86125000 | 67800000 | 40700000 | 0
[17 empty] | Units (Miles)** | 22.9 | 26.5 | 22.6 | 14.8 | 0
[17 empty] | Unit Cost** | 3750000 | 3250000 | 3000000 | 2750000 | 0
[17 empty] | Unit Cost (escalated) | 3750000 | 3337750 | 3164187 | 2978818.3782 | 0
[17 empty] | Total UG Miles (GRC & CEMA) | 200 | 400 | 800 | 1000 | 1200
[15 empty] | cable mile |  | UG mile | 22.137 | 25.434 | 21.823 | 14.287 | 0
185.137
1.1358

## 7.3.3.17.1_Exposure_CS
Source file: | tranching analysis_2022-02-09_SplitByTier.xlsx (for total miles, referred to GRC 2023 filing)
Source file location: | WMP > 2022 > 7.3.3 Grid Design & System Hardening > Source Data (RSE Input Template)
Calculation
[10 empty] | Overhead miles | [5 empty] | Underground miles | [5 empty] | Remote Grid
Tranche | Exposure (miles) | Frequency | Total Risk Score | CoRE | Risk Score/Mile | % of Risk Score | % Miles | # of CS-Tiers | SH Miles Allocation | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | 163.6441 | 1.9632 | 1105.0505 | 562.894 | 6.7528 | 4.841% | 0.6427% | 93 | 1.448% | 2.1301 | 4.4163 | 2.4615 | 0.72398 | 0.72398 | 0.72398 | 0.72 | 2.0923 | 4.3734 | 9.0454 | 11.4386 | 13.9004 | 0.01448 | 0.37647 | 0.37647 | 0.82534 | 1.1439 | 1.3032
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | 353.5334 | 2.1544 | 1307.3451 | 606.8142 | 3.6979 | 5.728% | 1.388% | 56 | 3.44% | 5.0607 | 10.4924 | 5.8482 | 1.7201 | 1.7201 | 1.7201 | 1.7106 | 4.971 | 10.3906 | 21.4905 | 27.1763 | 33.0252 | 0.034401 | 0.89443 | 0.89443 | 1.9609 | 2.7177 | 3.0961
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | 1013.9529 | 4.903 | 3014.2454 | 614.7808 | 2.9728 | 13.21% | 3.982% | 91 | 9.317% | 13.7063 | 28.4176 | 15.8393 | 4.6586 | 4.6586 | 4.6586 | 4.633 | 13.4634 | 28.1418 | 58.2048 | 73.6044 | 89.4456 | 0.093172 | 2.4225 | 2.4225 | 5.3108 | 7.3606 | 8.3855
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | 1483.0022 | 5.6549 | 3902.1909 | 690.0595 | 2.6313 | 17.1% | 5.824% | 106 | 13.2% | 19.4222 | 40.2685 | 22.4447 | 6.6014 | 6.6014 | 6.6014 | 6.5651 | 19.078 | 39.8777 | 82.4778 | 104.2993 | 126.7467 | 0.13203 | 3.4327 | 3.4327 | 7.5256 | 10.4302 | 11.8825
HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | 1601.5759 | 3.9602 | 3072.7217 | 775.9057 | 1.9186 | 13.46% | 6.29% | 131 | 14.88% | 21.8878 | 45.3803 | 25.294 | 7.4394 | 7.4394 | 7.4394 | 7.3985 | 21.4999 | 44.9399 | 92.9479 | 117.5395 | 142.8365 | 0.14879 | 3.8685 | 3.8685 | 8.4809 | 11.7543 | 13.3909
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | 193.7699 | 2.0503 | 443.9302 | 216.5202 | 2.291 | 1.945% | 0.761% | 87 | 1.323% | 1.9466 | 4.0358 | 2.2495 | 0.66161 | 0.66161 | 0.66161 | 0.65798 | 1.9121 | 3.9967 | 8.2662 | 10.4532 | 12.7029 | 0.013232 | 0.34404 | 0.34404 | 0.75424 | 1.0453 | 1.1909
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | 543.1039 | 3.329 | 719.9885 | 216.2746 | 1.3257 | 3.154% | 2.133% | 58 | 3.483% | 5.1237 | 10.6231 | 5.9211 | 1.7415 | 1.7415 | 1.7415 | 1.7319 | 5.0329 | 10.52 | 21.7583 | 27.5149 | 33.4367 | 0.03483 | 0.90558 | 0.90558 | 1.9853 | 2.7516 | 3.1347
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | 946.5765 | 4.5582 | 1058.1498 | 232.142 | 1.1179 | 4.636% | 3.718% | 80 | 6.406% | 9.4231 | 19.5372 | 10.8896 | 3.2028 | 3.2028 | 3.2028 | 3.1852 | 9.2561 | 19.3476 | 40.016 | 50.6032 | 61.494 | 0.064056 | 1.6655 | 1.6655 | 3.6512 | 5.0604 | 5.7651
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | 1078.9824 | 4.1356 | 925.2522 | 223.7264 | 0.85752 | 4.054% | 4.238% | 81 | 7.457% | 10.9692 | 22.7428 | 12.6763 | 3.7283 | 3.7283 | 3.7283 | 3.7078 | 10.7749 | 22.5221 | 46.5817 | 58.906 | 71.5838 | 0.074566 | 1.9387 | 1.9387 | 4.2503 | 5.8908 | 6.711
HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | 1464.9153 | 3.904 | 975.1431 | 249.7773 | 0.66567 | 4.272% | 5.753% | 101 | 10.58% | 15.5687 | 32.2789 | 17.9915 | 5.2916 | 5.2916 | 5.2916 | 5.2626 | 15.2928 | 31.9656 | 66.1135 | 83.6055 | 101.5991 | 0.10583 | 2.7516 | 2.7516 | 6.0324 | 8.3608 | 9.5249
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | 489.6273 | 5.5129 | 474.0261 | 85.9844 | 0.96814 | 2.077% | 1.923% | 154 | 1.146% | 1.6863 | 3.4962 | 1.9487 | 0.57315 | 0.57315 | 0.57315 | 0.57 | 1.6564 | 3.4623 | 7.1609 | 9.0555 | 11.0045 | 0.011463 | 0.29804 | 0.29804 | 0.65339 | 0.90558 | 1.0317
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | 791.1377 | 4.8722 | 495.9241 | 101.787 | 0.62685 | 2.173% | 3.107% | 99 | 1.501% | 2.2079 | 4.5777 | 2.5515 | 0.75044 | 0.75044 | 0.75044 | 0.74631 | 2.1688 | 4.5332 | 9.376 | 11.8566 | 14.4084 | 0.015009 | 0.39023 | 0.39023 | 0.8555 | 1.1857 | 1.3508
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | 791.1875 | 3.8995 | 390.4916 | 100.1388 | 0.49355 | 1.711% | 3.107% | 78 | 2.104% | 3.0955 | 6.4179 | 3.5772 | 1.0521 | 1.0521 | 1.0521 | 1.0463 | 3.0406 | 6.3556 | 13.1451 | 16.623 | 20.2006 | 0.021042 | 0.5471 | 0.5471 | 1.1994 | 1.6623 | 1.8938
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | 741.5879 | 2.7497 | 270.5632 | 98.3988 | 0.36484 | 1.185% | 2.913% | 72 | 1.4% | 2.0596 | 4.2702 | 2.3801 | 0.70003 | 0.70003 | 0.70003 | 0.69618 | 2.0231 | 4.2287 | 8.7461 | 11.0602 | 13.4405 | 0.014001 | 0.36401 | 0.36401 | 0.79803 | 1.106 | 1.26
HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | 715.8465 | 1.804 | 184.2215 | 102.1206 | 0.25735 | 0.8071% | 2.811% | 74 | 1.47% | 2.1629 | 4.4845 | 2.4995 | 0.73516 | 0.73516 | 0.73516 | 0.73112 | 2.1246 | 4.441 | 9.1851 | 11.6152 | 14.1151 | 0.014703 | 0.38228 | 0.38228 | 0.83808 | 1.1616 | 1.3233
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | 772.1066 | 8.9035 | 290.0455 | 32.5767 | 0.37565 | 1.271% | 3.032% | 209 | 0.7197% | 1.0587 | 2.1951 | 1.2235 | 0.35986 | 0.35986 | 0.35986 | 0.35788 | 1.04 | 2.1738 | 4.496 | 5.6856 | 6.9092 | 0.0071971 | 0.18713 | 0.18713 | 0.41024 | 0.56857 | 0.64774
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | 522.2177 | 3.2633 | 114.4667 | 35.0773 | 0.21919 | 0.5015% | 2.051% | 78 | 0.4102% | 0.60343 | 1.2511 | 0.69734 | 0.2051 | 0.2051 | 0.2051 | 0.20397 | 0.59274 | 1.239 | 2.5625 | 3.2405 | 3.9379 | 0.004102 | 0.10665 | 0.10665 | 0.23381 | 0.32406 | 0.36918
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | 750.2287 | 3.7595 | 127.8881 | 34.0175 | 0.17047 | 0.5603% | 2.947% | 84 | 0.5893% | 0.8669 | 1.7974 | 1.0018 | 0.29465 | 0.29465 | 0.29465 | 0.29303 | 0.85154 | 1.7799 | 3.6814 | 4.6554 | 5.6573 | 0.005893 | 0.15322 | 0.15322 | 0.3359 | 0.46555 | 0.53037
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | 696.1473 | 2.6565 | 87.3293 | 32.8733 | 0.12545 | 0.3826% | 2.734% | 78 | 0.5533% | 0.81396 | 1.6876 | 0.94063 | 0.27666 | 0.27666 | 0.27666 | 0.27514 | 0.79953 | 1.6712 | 3.4565 | 4.371 | 5.3118 | 0.0055331 | 0.14386 | 0.14386 | 0.31539 | 0.43712 | 0.49798
HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | 470.836 | 1.1708 | 43.6781 | 37.3062 | 0.092767 | 0.1914% | 1.849% | 58 | 0.3698% | 0.54406 | 1.128 | 0.62873 | 0.18492 | 0.18492 | 0.18492 | 0.1839 | 0.53442 | 1.1171 | 2.3104 | 2.9217 | 3.5505 | 0.0036984 | 0.096158 | 0.096158 | 0.21081 | 0.29217 | 0.33286
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | 752.6401 | 8.387 | 36.8628 | 4.3952 | 0.048978 | 0.1615% | 2.956% | 479 | 0.5918% | 0.87064 | 1.8051 | 1.0061 | 0.29592 | 0.29592 | 0.29592 | 0.2943 | 0.85521 | 1.7876 | 3.6972 | 4.6754 | 5.6817 | 0.0059184 | 0.15388 | 0.15388 | 0.33735 | 0.46756 | 0.53266
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | 768.4668 | 4.8133 | 28.4752 | 5.916 | 0.037055 | 0.1248% | 3.018% | 181 | 0.6036% | 0.88798 | 1.8411 | 1.0262 | 0.30181 | 0.30181 | 0.30181 | 0.30016 | 0.87224 | 1.8232 | 3.7709 | 4.7685 | 5.7948 | 0.0060363 | 0.15694 | 0.15694 | 0.34407 | 0.47686 | 0.54326
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | 467.0501 | 2.3087 | 11.3062 | 4.8971 | 0.024208 | 0.04953% | 1.834% | 134 | 0.3685% | 0.54213 | 1.124 | 0.62649 | 0.18426 | 0.18426 | 0.18426 | 0.18325 | 0.53252 | 1.1131 | 2.3022 | 2.9113 | 3.5378 | 0.0036852 | 0.095816 | 0.095816 | 0.21006 | 0.29113 | 0.33167
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | 347.2658 | 1.3241 | 7.9106 | 5.9743 | 0.02278 | 0.03466% | 1.364% | 99 | 0.2938% | 0.43213 | 0.89595 | 0.49938 | 0.14688 | 0.14688 | 0.14688 | 0.14607 | 0.42448 | 0.88726 | 1.8351 | 2.3206 | 2.82 | 0.0029376 | 0.076376 | 0.076376 | 0.16744 | 0.23207 | 0.26438
HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | 406.8993 | 0.93819 | 4.8164 | 5.1337 | 0.011837 | 0.0211% | 1.598% | 150 | 0.3199% | 0.47066 | 0.97582 | 0.5439 | 0.15997 | 0.15997 | 0.15997 | 0.15909 | 0.46232 | 0.96635 | 1.9987 | 2.5275 | 3.0714 | 0.0031994 | 0.083185 | 0.083185 | 0.18237 | 0.25275 | 0.28795
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | 58.7222 | 0.54636 | 308.3087 | 564.2942 | 5.2503 | 1.351% | 0.2306% | 20 | 0.568% | 0.83561 | 1.7325 | 0.96565 | 0.28402 | 0.28402 | 0.28402 | 0.28246 | 0.82081 | 1.7157 | 3.5485 | 4.4873 | 5.4531 | 0.0056803 | 0.14769 | 0.14769 | 0.32378 | 0.44874 | 0.51123
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | 156.5661 | 1.027 | 469.1296 | 456.7939 | 2.9964 | 2.055% | 0.6149% | 20 | 1.546% | 2.2736 | 4.7139 | 2.6274 | 0.77278 | 0.77278 | 0.77278 | 0.76853 | 2.2333 | 4.6682 | 9.6551 | 12.2096 | 14.8373 | 0.015456 | 0.40184 | 0.40184 | 0.88097 | 1.221 | 1.391
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | 56.2394 | 0.27532 | 110.5648 | 401.5838 | 1.966 | 0.4844% | 0.2209% | 9 | 0.5714% | 0.84059 | 1.7428 | 0.9714 | 0.28571 | 0.28571 | 0.28571 | 0.28414 | 0.82569 | 1.7259 | 3.5696 | 4.5141 | 5.4856 | 0.0057141 | 0.14857 | 0.14857 | 0.32571 | 0.45142 | 0.51427
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | 111.286 | 0.39711 | 175.1398 | 441.0332 | 1.5738 | 0.7673% | 0.4371% | 9 | 1.134% | 1.6689 | 3.4601 | 1.9286 | 0.56723 | 0.56723 | 0.56723 | 0.56412 | 1.6393 | 3.4265 | 7.087 | 8.9621 | 10.8909 | 0.011345 | 0.29496 | 0.29496 | 0.64665 | 0.89623 | 1.021
HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | 65.8407 | 0.18486 | 95.6268 | 517.2966 | 1.4524 | 0.419% | 0.2586% | 12 | 0.6408% | 0.9427 | 1.9545 | 1.0894 | 0.32041 | 0.32041 | 0.32041 | 0.31865 | 0.92599 | 1.9355 | 4.0032 | 5.0624 | 6.1519 | 0.0064082 | 0.16661 | 0.16661 | 0.36527 | 0.50625 | 0.57674
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | 184.1265 | 1.6187 | 368.1642 | 227.4412 | 1.9995 | 1.613% | 0.7232% | 33 | 0.8835% | 1.2997 | 2.6946 | 1.5019 | 0.44174 | 0.44174 | 0.44174 | 0.43932 | 1.2766 | 2.6685 | 5.5191 | 6.9794 | 8.4815 | 0.0088348 | 0.22971 | 0.22971 | 0.50359 | 0.69795 | 0.79514
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | 264.4574 | 1.6441 | 364.3104 | 221.5896 | 1.3776 | 1.596% | 1.039% | 27 | 1.288% | 1.8944 | 3.9278 | 2.1893 | 0.6439 | 0.6439 | 0.6439 | 0.64036 | 1.8609 | 3.8897 | 8.0449 | 10.1734 | 12.3629 | 0.012878 | 0.33483 | 0.33483 | 0.73405 | 1.0174 | 1.159
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | 279.2931 | 1.4107 | 306.6034 | 217.3411 | 1.0978 | 1.343% | 1.097% | 22 | 1.761% | 2.5902 | 5.3704 | 2.9933 | 0.88039 | 0.88039 | 0.88039 | 0.87555 | 2.5443 | 5.3182 | 10.9995 | 13.9097 | 16.9034 | 0.017608 | 0.4578 | 0.4578 | 1.0036 | 1.391 | 1.5847
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | 108.7427 | 0.43681 | 98.002 | 224.358 | 0.90123 | 0.4294% | 0.4271% | 14 | 0.7059% | 1.0384 | 2.1529 | 1.2 | 0.35293 | 0.35293 | 0.35293 | 0.35099 | 1.02 | 2.132 | 4.4095 | 5.5761 | 6.7762 | 0.0070585 | 0.18352 | 0.18352 | 0.40234 | 0.55763 | 0.63527
HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | 22.7224 | 0.057392 | 14.6173 | 254.6938 | 0.6433 | 0.06404% | 0.08924% | 4 | 0.1505% | 0.22139 | 0.45902 | 0.25585 | 0.075249 | 0.075249 | 0.075249 | 0.074835 | 0.21747 | 0.45456 | 0.94016 | 1.1889 | 1.4448 | 0.001505 | 0.039129 | 0.039129 | 0.085784 | 0.11889 | 0.13545
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | 423.2024 | 3.6315 | 359.6654 | 99.0396 | 0.84987 | 1.576% | 1.662% | 64 | 1.075% | 1.5808 | 3.2775 | 1.8268 | 0.5373 | 0.5373 | 0.5373 | 0.53434 | 1.5528 | 3.2457 | 6.713 | 8.4891 | 10.3161 | 0.010746 | 0.27939 | 0.27939 | 0.61252 | 0.84893 | 0.96713
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | 595.3479 | 3.8168 | 382.2893 | 100.1603 | 0.64213 | 1.675% | 2.338% | 52 | 1.412% | 2.0769 | 4.306 | 2.4001 | 0.70591 | 0.70591 | 0.70591 | 0.70203 | 2.0401 | 4.2642 | 8.8196 | 11.153 | 13.5534 | 0.014118 | 0.36707 | 0.36707 | 0.80473 | 1.1153 | 1.2706
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | 215.5262 | 1.0601 | 98.7146 | 93.1182 | 0.45802 | 0.4325% | 0.8465% | 20 | 0.3643% | 0.53584 | 1.111 | 0.61923 | 0.18213 | 0.18213 | 0.18213 | 0.18112 | 0.52634 | 1.1002 | 2.2755 | 2.8775 | 3.4968 | 0.0036425 | 0.094705 | 0.094705 | 0.20762 | 0.28776 | 0.32783
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | 223.3454 | 0.84201 | 86.0301 | 102.1725 | 0.38519 | 0.3769% | 0.8772% | 20 | 0.4038% | 0.59399 | 1.2315 | 0.68643 | 0.20189 | 0.20189 | 0.20189 | 0.20078 | 0.58346 | 1.2196 | 2.5224 | 3.1898 | 3.8763 | 0.0040378 | 0.10498 | 0.10498 | 0.23015 | 0.31899 | 0.3634
HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | 134.3564 | 0.34507 | 31.4684 | 91.1952 | 0.23422 | 0.1379% | 0.5277% | 9 | 0.1055% | 0.15525 | 0.32189 | 0.17941 | 0.052768 | 0.052768 | 0.052768 | 0.052478 | 0.1525 | 0.31876 | 0.65928 | 0.83372 | 1.0131 | 0.0010554 | 0.027439 | 0.027439 | 0.060156 | 0.083374 | 0.094983
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | 607.6135 | 5.3645 | 183.2705 | 34.1633 | 0.30162 | 0.8029% | 2.386% | 103 | 0.5115% | 0.7524 | 1.56 | 0.86949 | 0.25573 | 0.25573 | 0.25573 | 0.25433 | 0.73907 | 1.5448 | 3.1951 | 4.0405 | 4.9101 | 0.0051146 | 0.13298 | 0.13298 | 0.29153 | 0.40406 | 0.46032
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | 572.0063 | 3.5262 | 102.9918 | 29.2076 | 0.18005 | 0.4512% | 2.247% | 54 | 0.4493% | 0.66096 | 1.3704 | 0.76382 | 0.22465 | 0.22465 | 0.22465 | 0.22342 | 0.64925 | 1.3571 | 2.8068 | 3.5494 | 4.3134 | 0.0044931 | 0.11682 | 0.11682 | 0.25611 | 0.35495 | 0.40438
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | 384.7705 | 1.8626 | 53.3248 | 28.6287 | 0.13859 | 0.2336% | 1.511% | 35 | 0.329% | 0.484 | 1.0035 | 0.55932 | 0.1645 | 0.1645 | 0.1645 | 0.1636 | 0.47542 | 0.99374 | 2.0553 | 2.5991 | 3.1585 | 0.0032901 | 0.085542 | 0.085542 | 0.18754 | 0.25992 | 0.29611
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | 202.884 | 0.79451 | 27.9367 | 35.162 | 0.1377 | 0.1224% | 0.7968% | 22 | 0.1594% | 0.23444 | 0.48606 | 0.27092 | 0.079682 | 0.079682 | 0.079682 | 0.079244 | 0.23028 | 0.48134 | 0.99555 | 1.2589 | 1.5299 | 0.0015936 | 0.041435 | 0.041435 | 0.090838 | 0.1259 | 0.14343
HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | 117.3278 | 0.3102 | 10.3374 | 33.3251 | 0.088107 | 0.04529% | 0.4608% | 12 | 0.09216% | 0.13557 | 0.28109 | 0.15667 | 0.04608 | 0.04608 | 0.04608 | 0.045827 | 0.13317 | 0.27836 | 0.57573 | 0.72805 | 0.88474 | 0.0009216 | 0.023962 | 0.023962 | 0.052531 | 0.072807 | 0.082944
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | 1430.0123 | 15.5593 | 59.8849 | 3.8488 | 0.041877 | 0.2624% | 5.616% | 425 | 1.125% | 1.6548 | 3.4309 | 1.9123 | 0.56244 | 0.56244 | 0.56244 | 0.55935 | 1.6254 | 3.3976 | 7.0271 | 8.8863 | 10.7988 | 0.011249 | 0.29247 | 0.29247 | 0.64118 | 0.88865 | 1.0124
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | 527.1275 | 3.3273 | 16.1522 | 4.8544 | 0.030642 | 0.07077% | 2.07% | 101 | 0.4286% | 0.63054 | 1.3073 | 0.72867 | 0.21431 | 0.21431 | 0.21431 | 0.21314 | 0.61937 | 1.2946 | 2.6777 | 3.3861 | 4.1148 | 0.0042863 | 0.11144 | 0.11144 | 0.24432 | 0.33862 | 0.38577
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | 190.7177 | 0.93485 | 6.3225 | 6.7631 | 0.033151 | 0.0277% | 0.749% | 44 | 0.1565% | 0.23018 | 0.47723 | 0.266 | 0.078235 | 0.078235 | 0.078235 | 0.077805 | 0.2261 | 0.4726 | 0.97746 | 1.2361 | 1.5021 | 0.0015647 | 0.040682 | 0.040682 | 0.089187 | 0.12361 | 0.14082
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | 95.1547 | 0.36861 | 2.2603 | 6.132 | 0.023754 | 0.009903% | 0.3737% | 21 | 0.07474% | 0.10995 | 0.22797 | 0.12706 | 0.037372 | 0.037372 | 0.037372 | 0.037166 | 0.108 | 0.22576 | 0.46692 | 0.59046 | 0.71754 | 0.00074743 | 0.019433 | 0.019433 | 0.042604 | 0.059047 | 0.067269
HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | 97.3625 | 0.24722 | 1.3516 | 5.4671 | 0.013882 | 0.005922% | 0.3824% | 24 | 0.07648% | 0.1125 | 0.23326 | 0.13001 | 0.038239 | 0.038239 | 0.038239 | 0.038029 | 0.11051 | 0.23099 | 0.47776 | 0.60416 | 0.73419 | 0.00076478 | 0.019884 | 0.019884 | 0.043592 | 0.060417 | 0.06883
HFTD - Distribution - Zone 1 - 1QU CoRE ¦ 5QU LoRE | 0.18783 | 2.0448e-08 | 0.00028925 | 14146 | 0.00154 | 1.267e-06% | 0.0007377% | 0 | 0.0001475% | 0.00021704 | 0.00045 | 0.00025082 | 7.377e-05 | 7.377e-05 | 7.377e-05 | 7.3365e-05 | 0.0002132 | 0.00044563 | 0.00092169 | 0.0011655 | 0.0014164 | 1.4754e-06 | 3.8361e-05 | 3.8361e-05 | 8.4098e-05 | 0.00011656 | 0.00013279
HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | 0.13442 | 0.0043134 | 0.091293 | 21.1651 | 0.67918 | 0.0004% | 0.0005279% | 1 | 0.0001056% | 0.00015532 | 0.00032203 | 0.00017949 | 5.2792e-05 | 5.2792e-05 | 5.2792e-05 | 5.2502e-05 | 0.00015257 | 0.00031891 | 0.00065958 | 0.00083409 | 0.0010136 | 1.0558e-06 | 2.7452e-05 | 2.7452e-05 | 6.0183e-05 | 8.3411e-05 | 9.5025e-05
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | 10.0154 | 0.23423 | 0.12016 | 0.51301 | 0.011998 | 0.0005265% | 0.03934% | 4 | 0.007867% | 0.011573 | 0.023994 | 0.013374 | 0.0039335 | 0.0039335 | 0.0039335 | 0.0039119 | 0.011368 | 0.023762 | 0.049145 | 0.062148 | 0.075524 | 7.867e-05 | 0.0020454 | 0.0020454 | 0.0044842 | 0.006215 | 0.0070803
HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | 0.27822 | 0.0011987 | 0.00021167 | 0.17659 | 0.00076079 | 9.274e-07% | 0.001093% | 1 | 0.0002185% | 0.00032149 | 0.00066654 | 0.00037152 | 0.00010927 | 0.00010927 | 0.00010927 | 0.00010867 | 0.00031579 | 0.00066007 | 0.0013652 | 0.0017264 | 0.002098 | 2.1854e-06 | 5.682e-05 | 5.682e-05 | 0.00012457 | 0.00017265 | 0.00019668
| 25461.6694 | 142.8049 | 22824.7023 | 23443.0098 | 51.5807 | 100% | 100% | 4093 | 100% | 147.107 | 305 | 170 | 50 | 50 | 50 | 49.7253 | 144.5 | 302.04 | 624.7 | 789.98 | 960 | 1 | 26 | 26 | 57 | 79 | 90
Capital Costs as of 6/9
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
System Hardening [Overhead] | 460714978.5021 | 286120000 | 663264000 | 641241655.36 | 620774540.77 | 622753940.328 | 625056376.3
System Hardening [Underground] | 24200434.3379 | 129534000 | 264684879.12 | 267705265 | 259196816.77 | 241699788.552 | 192152732.7
| Recorded Expense by Year (source: GRC MDR, expense by LOB, April 2021) |  |  |  | $ thousands
LOB | 2016 | 2017 | 2018 | 2019 | 2020 | average | Miles | O&M/mile
Elec Dist | 565227.6519 | 717849.3052 | 1290595 | 1693862.9828 | 2215023.9967 | 1296511.7873 | 107370 | 12075.1773 |  | Overhead miles 2025: SH UG miles/OH mile; Overhead miles 2026: 1
UG | 96537.3264 | 132172.8728 | 162507.75 | 147818.1522 | 136511.5003 | 135109.5203 | 26980 | 5007.7658 |  | Overhead miles 2025: Net O&M for UG/mile; Overhead miles 2026: -9439.333; Underground miles 2021: 2021; Underground miles 2022: 2022; Underground miles 2023: 2023; Underground miles 2024: 2024; Underground miles 2025: 2025; Underground miles 2026: 2026
OH | 468690.3254 | 585676.4324 | 1128087.25 | 1546044.8307 | 2078512.4964 | 1161402.267 | 80390 | 14447.0987 |  | Overhead miles 2025: NPV Net O&M for UG/mile; Overhead miles 2026: -129949.3952; Underground miles 2021: -6461778.7103; Underground miles 2022: -18777687.6122; Underground miles 2023: -39249915.3383; Underground miles 2024: -81179387.2064; Underground miles 2025: -102657423.2517; Underground miles 2026: -124751419.4304

## 7.3.3.17.1_Financials
Source file: | EO-WLDFR-3_RSE Input File.xlsx (GRC 2023 filing)
Source file location: | WMP > 2022 > GRC 2023 filing
| Program | MAT (optional) | CapEx USD 2020 | CapEx USD 2021 | CapEx USD 2022 | CapEx USD 2023 | CapEx USD 2024 | CapEx USD 2025 | CapEx USD 2026 | OpEx USD 2020 | OpEx USD 2021 | OpEx USD 2022 | OpEx USD 2023 | OpEx USD 2024 | OpEx USD 2025 | OpEx USD 2026
| System Hardening [Overhead] | 08W |  | 286120000 | 663264000 | 641241655.36 | 620774540.77 | 622753940.328 | 625056376.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| System Hardening [Underground] | 08W |  | 129534000 | 264684879.12 | 267705265 | 259196816.77 | 241699788.552 | 192152732.7 |  | -6461778.7103 | -18777687.6122 | -39249915.3383 | -81179387.2064 | -102657423.2517 | -124751419.4304
| System Hardening [Remote Grid] | 08W, KAT, AB# |  | 5100000 | 8500000 | 8500000 | 18200000 | 25400000 | 28800000 |  | 1782468 | 2040084 | 2417387 | 3346293 | 4542680 | 5910846
Capital Costs as of 6/9:
|  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
| System Hardening [Overhead] | 460714978.5021 | 286120000 | 663264000 | 641241655.36 | 620774540.77 | 622753940.328 | 625056376.3
| System Hardening [Underground] | 24200434.3379 | 129534000 | 264684879.12 | 267705265 | 259196816.77 | 241699788.552 | 192152732.7
| Recorded Expense by Year (source: GRC MDR, expense by LOB, April 2021): |  |  |  |  | $ thousands
| LOB | 2016 | 2017 | 2018 | 2019 | 2020 | average | Miles | O&M/mile
| Elec Dist | 565227.6519 | 717849.3052 | 1290595 | 1693862.9828 | 2215023.9967 | 1296511.7873 | 107370 | 12075.1773
| UG | 96537.3264 | 132172.8728 | 162507.75 | 147818.1522 | 136511.5003 | 135109.5203 | 26980 | 5007.7658
| OH | 468690.3254 | 585676.4324 | 1128087.25 | 1546044.8307 | 2078512.4964 | 1161402.267 | 80390 | 14447.0987
| SH UG miles/OH mile | 1
| Net O&M for UG/mile | -9439.333 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
| NPV Net O&M for UG/mile | -129949.3952 | -6461778.7103 | -18777687.6122 | -39249915.3383 | -81179387.2064 | -102657423.2517 | -124751419.4304

## 7.3.3.17.1_SME_Input
Pacific Gas and Electric Company
Failure of Electric Distribution Overhead Assets: Mitigation Effectiveness Workpaper - System Hardening SME Input
Line No. | Basic Cause | Supplemental Cause | Failed/Involved Equipment | Equipment Condition | System Hardening Effectiveness | Narrative
1 | 3rd Party |  | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage. | None / N/A: 0%
2 | 3rd Party |  | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage. | Low = 20%
3 | 3rd Party |  | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage. | Medium = 40%
4 | 3rd Party |  | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk. | High = 70%
5 | 3rd Party |  | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk. | All = 90%
6 | 3rd Party | Aircraft | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage. (Assumed Broken does not refer to conductor, this would be wire down/object),
7 | 3rd Party | Aircraft | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
8 | 3rd Party | Aircraft | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
9 | 3rd Party | Aircraft | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
10 | 3rd Party | Aircraft | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
11 | 3rd Party | Aircraft | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
12 | 3rd Party | Aircraft | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
13 | 3rd Party | Aircraft | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
14 | 3rd Party | Aircraft | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
15 | 3rd Party | Aircraft- crop dusting | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage. (Assumed Broken does not refer to conductor, this would be wire down/object),
16 | 3rd Party | Aircraft- crop dusting | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
17 | 3rd Party | Aircraft- crop dusting | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
18 | 3rd Party | Aircraft- crop dusting | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
19 | 3rd Party | Aircraft- crop dusting | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
20 | 3rd Party | Aircraft- crop dusting | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
21 | 3rd Party | Aircraft- crop dusting | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
22 | 3rd Party | Aircraft- crop dusting | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
23 | 3rd Party | Contact with High Voltage- 3rd party |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
24 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
25 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
26 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage. (Assumed Broken does not refer to conductor, this would be wire down/object),
27 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
28 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
29 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
30 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
31 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
32 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
33 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Underground | Broken | None | Underground facilities = no ignition risk
34 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Underground | Burned/flashed | None | Underground facilities = no ignition risk
35 | 3rd Party | Contact with High Voltage- 3rd party | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
36 | 3rd Party | Contact with High Voltage- 3rd party | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
37 | 3rd Party | Contact with High Voltage- 3rd party | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
38 | 3rd Party | Contact with High Voltage- 3rd party | Fuse | Normal | All | New covered wire would prevent wire contact
39 | 3rd Party | Contact with High Voltage- 3rd party | Other | Malfunctioning | None | Unknown equipment. Assume impact is great enough to cause outage.
40 | 3rd Party | Contact with High Voltage- 3rd party | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
41 | 3rd Party | Contact with High Voltage- 3rd party | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
42 | 3rd Party | Contact with High Voltage- 3rd party | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
43 | 3rd Party | Contact with High Voltage- 3rd party | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
44 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
45 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
46 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
47 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
48 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
49 | 3rd Party | Contact with High Voltage- 3rd party | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
50 | 3rd Party | Contact with High Voltage- 3rd party | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
51 | 3rd Party | Contact with High Voltage- 3rd party | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
52 | 3rd Party | Contact with High Voltage- 3rd party | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
53 | 3rd Party | Contact with High Voltage- 3rd party | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
54 | 3rd Party | Customer Equipment |  |  | None | No work is being completed on customer equipment.
55 | 3rd Party | Customer Equipment |  | Blown/failed | None | No work is being completed on customer equipment.
56 | 3rd Party | Customer Equipment |  | Normal | None | No work is being completed on customer equipment.
57 | 3rd Party | Customer Equipment | Anchor or Guy | Broken | None | No work is being completed on customer equipment.
58 | 3rd Party | Customer Equipment | Bus | Arcing | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
59 | 3rd Party | Customer Equipment | Bus | Blown/failed | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
60 | 3rd Party | Customer Equipment | Bus | Burned Open | None | No work is being completed on customer equipment.
61 | 3rd Party | Customer Equipment | Bus | Burned/flashed | None | No work is being completed on customer equipment.
62 | 3rd Party | Customer Equipment | Circuit Breaker | Arcing | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
63 | 3rd Party | Customer Equipment | Circuit Breaker | Blown/failed | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
64 | 3rd Party | Customer Equipment | Circuit Breaker | Broken | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
65 | 3rd Party | Customer Equipment | Circuit Breaker | Burned/flashed | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
66 | 3rd Party | Customer Equipment | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
67 | 3rd Party | Customer Equipment | Circuit Breaker | Normal | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
68 | 3rd Party | Customer Equipment | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
69 | 3rd Party | Customer Equipment | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
70 | 3rd Party | Customer Equipment | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
71 | 3rd Party | Customer Equipment | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
72 | 3rd Party | Customer Equipment | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
73 | 3rd Party | Customer Equipment | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
74 | 3rd Party | Customer Equipment | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
75 | 3rd Party | Customer Equipment | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
76 | 3rd Party | Customer Equipment | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
77 | 3rd Party | Customer Equipment | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
78 | 3rd Party | Customer Equipment | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
79 | 3rd Party | Customer Equipment | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
80 | 3rd Party | Customer Equipment | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
81 | 3rd Party | Customer Equipment | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
82 | 3rd Party | Customer Equipment | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
83 | 3rd Party | Customer Equipment | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
84 | 3rd Party | Customer Equipment | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
85 | 3rd Party | Customer Equipment | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
86 | 3rd Party | Customer Equipment | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
87 | 3rd Party | Customer Equipment | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
88 | 3rd Party | Customer Equipment | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
89 | 3rd Party | Customer Equipment | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
90 | 3rd Party | Customer Equipment | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
91 | 3rd Party | Customer Equipment | Customer Equipment | Bent or Twisted | None | No work is being completed on customer equipment.
92 | 3rd Party | Customer Equipment | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
93 | 3rd Party | Customer Equipment | Customer Equipment | Broken | None | No work is being completed on customer equipment.
94 | 3rd Party | Customer Equipment | Customer Equipment | Burned Open | None | No work is being completed on customer equipment.
95 | 3rd Party | Customer Equipment | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
96 | 3rd Party | Customer Equipment | Customer Equipment | Contaminated | None | No work is being completed on customer equipment.
97 | 3rd Party | Customer Equipment | Customer Equipment | Deteriorated | None | No work is being completed on customer equipment.
98 | 3rd Party | Customer Equipment | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
99 | 3rd Party | Customer Equipment | Customer Equipment | Normal | None | No work is being completed on customer equipment.
100 | 3rd Party | Customer Equipment | Customer Equipment | On Ground | None | No work is being completed on customer equipment.
101 | 3rd Party | Customer Equipment | Customer Equipment | Together | None | No work is being completed on customer equipment.
102 | 3rd Party | Customer Equipment | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
103 | 3rd Party | Customer Equipment | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
104 | 3rd Party | Customer Equipment | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
105 | 3rd Party | Customer Equipment | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
106 | 3rd Party | Customer Equipment | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
107 | 3rd Party | Customer Equipment | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
108 | 3rd Party | Customer Equipment | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
109 | 3rd Party | Customer Equipment | Generator | Malfunctioning | None | No work is being completed on customer equipment.
110 | 3rd Party | Customer Equipment | Generator | Normal | None | No work is being completed on customer equipment.
111 | 3rd Party | Customer Equipment | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
112 | 3rd Party | Customer Equipment | Interrupter | Normal | All | Underground facilities = no ignition risk
113 | 3rd Party | Customer Equipment | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
114 | 3rd Party | Customer Equipment | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
115 | 3rd Party | Customer Equipment | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
116 | 3rd Party | Customer Equipment | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
117 | 3rd Party | Customer Equipment | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
118 | 3rd Party | Customer Equipment | Metering Equipment | Arcing | None | System Hardening does not address Metering facilities.
119 | 3rd Party | Customer Equipment | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
120 | 3rd Party | Customer Equipment | Metering Equipment | Broken | None | System Hardening does not address Metering facilities.
121 | 3rd Party | Customer Equipment | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
122 | 3rd Party | Customer Equipment | Metering Equipment | Deteriorated | None | System Hardening does not address Metering facilities.
123 | 3rd Party | Customer Equipment | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
124 | 3rd Party | Customer Equipment | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
125 | 3rd Party | Customer Equipment | Other | Arcing | None | No work is being completed on customer equipment.
126 | 3rd Party | Customer Equipment | Other | Blown/failed | None | No work is being completed on customer equipment.
127 | 3rd Party | Customer Equipment | Other | Broken | None | No work is being completed on customer equipment.
128 | 3rd Party | Customer Equipment | Other | Burned/flashed | None | No work is being completed on customer equipment.
129 | 3rd Party | Customer Equipment | Other | Contaminated | None | No work is being completed on customer equipment.
130 | 3rd Party | Customer Equipment | Other | Deteriorated | None | No work is being completed on customer equipment.
131 | 3rd Party | Customer Equipment | Other | Malfunctioning | None | No work is being completed on customer equipment.
132 | 3rd Party | Customer Equipment | Other | Normal | None | No work is being completed on customer equipment.
133 | 3rd Party | Customer Equipment | Other | Together | None | No work is being completed on customer equipment.
134 | 3rd Party | Customer Equipment | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
135 | 3rd Party | Customer Equipment | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
136 | 3rd Party | Customer Equipment | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
137 | 3rd Party | Customer Equipment | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
138 | 3rd Party | Customer Equipment | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
139 | 3rd Party | Customer Equipment | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
140 | 3rd Party | Customer Equipment | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
141 | 3rd Party | Customer Equipment | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
142 | 3rd Party | Customer Equipment | PT/CCVT | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
143 | 3rd Party | Customer Equipment | Recloser | Arcing | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
144 | 3rd Party | Customer Equipment | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
145 | 3rd Party | Customer Equipment | Recloser | Broken | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
146 | 3rd Party | Customer Equipment | Recloser | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
147 | 3rd Party | Customer Equipment | Recloser | Normal | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
148 | 3rd Party | Customer Equipment | Riser | Burned/flashed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
149 | 3rd Party | Customer Equipment | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
150 | 3rd Party | Customer Equipment | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
151 | 3rd Party | Customer Equipment | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
152 | 3rd Party | Customer Equipment | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
153 | 3rd Party | Customer Equipment | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
154 | 3rd Party | Customer Equipment | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
155 | 3rd Party | Customer Equipment | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
156 | 3rd Party | Customer Equipment | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
157 | 3rd Party | Customer Equipment | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
158 | 3rd Party | Customer Equipment | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
159 | 3rd Party | Customer Equipment | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
160 | 3rd Party | Customer Equipment | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
161 | 3rd Party | Customer Equipment | Service conductor | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
162 | 3rd Party | Customer Equipment | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
163 | 3rd Party | Customer Equipment | Switch | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
164 | 3rd Party | Customer Equipment | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
165 | 3rd Party | Customer Equipment | Switch (OH) | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
166 | 3rd Party | Customer Equipment | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
167 | 3rd Party | Customer Equipment | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
168 | 3rd Party | Customer Equipment | Switch (UG) | Blown/failed | All | Underground facilities = no ignition risk
169 | 3rd Party | Customer Equipment | Switch (UG) | Normal | All | Underground facilities = no ignition risk
170 | 3rd Party | Customer Equipment | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
171 | 3rd Party | Customer Equipment | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
172 | 3rd Party | Customer Equipment | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
173 | 3rd Party | Customer Equipment | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
174 | 3rd Party | Customer Equipment | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
175 | 3rd Party | Customer Equipment | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
176 | 3rd Party | Customer Equipment | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
177 | 3rd Party | Customer Equipment | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
178 | 3rd Party | Customer Equipment | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
179 | 3rd Party | Customer Equipment | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
180 | 3rd Party | Customer Equipment | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
181 | 3rd Party | Customer Equipment | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
182 | 3rd Party | Customer Equipment | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
183 | 3rd Party | Customer Equipment | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
184 | 3rd Party | Customer Equipment | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
185 | 3rd Party | Customer Equipment | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
186 | 3rd Party | Customer Equipment | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
187 | 3rd Party | Customer Equipment | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
188 | 3rd Party | Customer Equipment | Transformer (UG) | Deteriorated | All | Underground facilities = no ignition risk
189 | 3rd Party | Customer Equipment | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
190 | 3rd Party | Dig in- 3rd party | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
191 | 3rd Party | Dig in- 3rd party | Bushing | Broken | All | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
192 | 3rd Party | Dig in- 3rd party | Cable Termination(live front | Broken | All | Underground facilities = no ignition risk
193 | 3rd Party | Dig in- 3rd party | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
194 | 3rd Party | Dig in- 3rd party | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
195 | 3rd Party | Dig in- 3rd party | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
196 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Bent or Twisted | All | Underground facilities = no ignition risk
197 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
198 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
199 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
200 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
201 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
202 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
203 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
204 | 3rd Party | Dig in- 3rd party | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
205 | 3rd Party | Dig in- 3rd party | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
206 | 3rd Party | Dig in- 3rd party | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
207 | 3rd Party | Dig in- 3rd party | Connector or Splice (UG) | Broken | All | Underground facilities = no ignition risk
208 | 3rd Party | Dig in- 3rd party | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
209 | 3rd Party | Dig in- 3rd party | Customer Equipment | Broken | None | No work is being completed on customer equipment.
210 | 3rd Party | Dig in- 3rd party | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
211 | 3rd Party | Dig in- 3rd party | Cutout- fuse holder | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
212 | 3rd Party | Dig in- 3rd party | Elbow | Broken | All | Underground facilities = no ignition risk
213 | 3rd Party | Dig in- 3rd party | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
214 | 3rd Party | Dig in- 3rd party | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
215 | 3rd Party | Dig in- 3rd party | Other | Bent or Twisted | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
216 | 3rd Party | Dig in- 3rd party | Other | Blown/failed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
217 | 3rd Party | Dig in- 3rd party | Other | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
218 | 3rd Party | Dig in- 3rd party | Other | Leaking | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
219 | 3rd Party | Dig in- 3rd party | Other | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
220 | 3rd Party | Dig in- 3rd party | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
221 | 3rd Party | Dig in- 3rd party | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
222 | 3rd Party | Dig in- 3rd party | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
223 | 3rd Party | Dig in- 3rd party | Pole-Wood | Malfunctioning | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
224 | 3rd Party | Dig in- 3rd party | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
225 | 3rd Party | Dig in- 3rd party | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
226 | 3rd Party | Dig in- 3rd party | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
227 | 3rd Party | Dig in- 3rd party | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
228 | 3rd Party | Dig in- 3rd party | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
229 | 3rd Party | Dig in- 3rd party | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
230 | 3rd Party | Dig in- 3rd party | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
231 | 3rd Party | Dig in- 3rd party | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
232 | 3rd Party | Dig in- 3rd party | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
233 | 3rd Party | Dig in- 3rd party | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
234 | 3rd Party | Dig in- 3rd party | Switch (UG) | Broken | All | Underground facilities = no ignition risk.
235 | 3rd Party | Dig in- 3rd party | Switch (UG) | Normal | All | Underground facilities = no ignition risk.
236 | 3rd Party | Dig in- 3rd party | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
237 | 3rd Party | Dig in- 3rd party | Transformer | Burned Open | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
238 | 3rd Party | Dig in- 3rd party | Transformer | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
239 | 3rd Party | Dig in- 3rd party | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
240 | 3rd Party | Dig in- 3rd party | Transformer | Malfunctioning | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
241 | 3rd Party | Dig in- 3rd party | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
242 | 3rd Party | Dig in- 3rd party | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
243 | 3rd Party | Dig in- 3rd party | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
244 | 3rd Party | Dig in- 3rd party | Transformer (UG) | Leaking | All | Underground facilities = no ignition risk
245 | 3rd Party | Dig in- 3rd party | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
246 | 3rd Party | Fire- house or bldg. |  |  | All | 3rd party fire impacting PGE equipment. Not enough outage information or correct information in ILIS to determine effect of System Hardening
247 | 3rd Party | Fire- house or bldg. |  | Blown/failed | All | 3rd party fire impacting PGE equipment. Not enough outage information or correct information in ILIS to determine effect of System Hardening
248 | 3rd Party | Fire- house or bldg. | Circuit Breaker | Normal | None | 3rd party fire impacting PGE equipment
249 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Broken | None | 3rd party fire impacting PGE equipment
250 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
251 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
252 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Burned/flashed | None | 3rd party fire impacting PGE equipment
253 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Normal | None | 3rd party fire impacting PGE equipment
254 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
255 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Together | None | 3rd party fire impacting PGE equipment
256 | 3rd Party | Fire- house or bldg. | Conductor- Underground | Broken | None | 3rd party fire impacting PGE equipment
257 | 3rd Party | Fire- house or bldg. | Conductor- Underground | Burned/flashed | None | 3rd party fire impacting PGE equipment
258 | 3rd Party | Fire- house or bldg. | Conductor- Underground | Normal | None | 3rd party fire impacting PGE equipment
259 | 3rd Party | Fire- house or bldg. | Connector or Splice (OH) | Burned Open | None | 3rd party fire impacting PGE equipment
260 | 3rd Party | Fire- house or bldg. | Crossarm- Wood | Broken | None | 3rd party fire impacting PGE equipment
261 | 3rd Party | Fire- house or bldg. | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
262 | 3rd Party | Fire- house or bldg. | Crossarm- Wood | Burned/flashed | None | 3rd party fire impacting PGE equipment
263 | 3rd Party | Fire- house or bldg. | Customer Equipment | Arcing | None | 3rd party fire impacting PGE equipment
264 | 3rd Party | Fire- house or bldg. | Customer Equipment | Burned Open | None | 3rd party fire impacting PGE equipment
265 | 3rd Party | Fire- house or bldg. | Customer Equipment | Burned/flashed | None | 3rd party fire impacting PGE equipment
266 | 3rd Party | Fire- house or bldg. | Customer Equipment | Malfunctioning | None | 3rd party fire impacting PGE equipment
267 | 3rd Party | Fire- house or bldg. | Customer Equipment | Normal | None | 3rd party fire impacting PGE equipment
268 | 3rd Party | Fire- house or bldg. | Cutout- fuse holder | Blown/failed | None | 3rd party fire impacting PGE equipment
269 | 3rd Party | Fire- house or bldg. | Cutout- fuse holder | Broken | None | 3rd party fire impacting PGE equipment
270 | 3rd Party | Fire- house or bldg. | Cutout- fuse holder | Burned/flashed | None | 3rd party fire impacting PGE equipment
271 | 3rd Party | Fire- house or bldg. | Cutout- Fused- Distribution | Blown/failed | None | 3rd party fire impacting PGE equipment
272 | 3rd Party | Fire- house or bldg. | Fuse | Blown/failed | None | 3rd party fire impacting PGE equipment
273 | 3rd Party | Fire- house or bldg. | Fuse | Normal | None | 3rd party fire impacting PGE equipment
274 | 3rd Party | Fire- house or bldg. | Jumper | Broken | None | 3rd party fire impacting PGE equipment
275 | 3rd Party | Fire- house or bldg. | Jumper | Normal | None | 3rd party fire impacting PGE equipment
276 | 3rd Party | Fire- house or bldg. | Other | Arcing | None | 3rd party fire impacting PGE equipment
277 | 3rd Party | Fire- house or bldg. | Other | Burned/flashed | None | 3rd party fire impacting PGE equipment
278 | 3rd Party | Fire- house or bldg. | Other | Normal | None | 3rd party fire impacting PGE equipment
279 | 3rd Party | Fire- house or bldg. | Pole-Wood | Broken | None | 3rd party fire impacting PGE equipment
280 | 3rd Party | Fire- house or bldg. | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
281 | 3rd Party | Fire- house or bldg. | Pole-Wood | Burned/flashed | None | 3rd party fire impacting PGE equipment
282 | 3rd Party | Fire- house or bldg. | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
283 | 3rd Party | Fire- house or bldg. | Pothead(Riser Termination) | Burned/flashed | None | 3rd party fire impacting PGE equipment
284 | 3rd Party | Fire- house or bldg. | Secondary | Arcing | None | 3rd party fire impacting PGE equipment
285 | 3rd Party | Fire- house or bldg. | Secondary | Broken | None | 3rd party fire impacting PGE equipment
286 | 3rd Party | Fire- house or bldg. | Secondary | Broken- wire on ground | None | 3rd party fire impacting PGE equipment
287 | 3rd Party | Fire- house or bldg. | Secondary | Burned Open | None | 3rd party fire impacting PGE equipment
288 | 3rd Party | Fire- house or bldg. | Secondary | Burned/flashed | None | 3rd party fire impacting PGE equipment
289 | 3rd Party | Fire- house or bldg. | Secondary | Normal | None | 3rd party fire impacting PGE equipment
290 | 3rd Party | Fire- house or bldg. | Secondary | On Ground | None | 3rd party fire impacting PGE equipment
291 | 3rd Party | Fire- house or bldg. | Secondary | Together | None | 3rd party fire impacting PGE equipment
292 | 3rd Party | Fire- house or bldg. | Service conductor | Arcing | None | 3rd party fire impacting PGE equipment
293 | 3rd Party | Fire- house or bldg. | Service conductor | Broken | None | 3rd party fire impacting PGE equipment
294 | 3rd Party | Fire- house or bldg. | Service conductor | Broken- wire on ground | None | 3rd party fire impacting PGE equipment
295 | 3rd Party | Fire- house or bldg. | Service conductor | Broken- wire on object | None | 3rd party fire impacting PGE equipment
296 | 3rd Party | Fire- house or bldg. | Service conductor | Burned Open | None | 3rd party fire impacting PGE equipment
297 | 3rd Party | Fire- house or bldg. | Service conductor | Burned/flashed | None | 3rd party fire impacting PGE equipment
298 | 3rd Party | Fire- house or bldg. | Service conductor | Normal | None | 3rd party fire impacting PGE equipment
299 | 3rd Party | Fire- house or bldg. | Service conductor | Together | None | 3rd party fire impacting PGE equipment
300 | 3rd Party | Fire- house or bldg. | Switch | Blown/failed | None | 3rd party fire impacting PGE equipment
301 | 3rd Party | Fire- house or bldg. | Switch (OH) | Normal | None | 3rd party fire impacting PGE equipment
302 | 3rd Party | Fire- house or bldg. | Switch (UG) | Normal | All | 3rd party fire impacting PGE equipment. Underground facilities = no ignition risk
303 | 3rd Party | Fire- house or bldg. | Transformer | Blown/failed | None | 3rd party fire impacting PGE equipment
304 | 3rd Party | Fire- house or bldg. | Transformer | Burned Open | None | 3rd party fire impacting PGE equipment
305 | 3rd Party | Fire- house or bldg. | Transformer | Burned/flashed | None | 3rd party fire impacting PGE equipment
306 | 3rd Party | Fire- house or bldg. | Transformer | Normal | None | 3rd party fire impacting PGE equipment
307 | 3rd Party | Fire- house or bldg. | Transformer (OH) | Arcing | None | 3rd party fire impacting PGE equipment
308 | 3rd Party | Fire- house or bldg. | Transformer (OH) | Blown/failed | None | 3rd party fire impacting PGE equipment
309 | 3rd Party | Fire- house or bldg. | Transformer (OH) | Broken | None | 3rd party fire impacting PGE equipment
310 | 3rd Party | Fire- house or bldg. | Transformer (OH) | Burned/flashed | None | 3rd party fire impacting PGE equipment
311 | 3rd Party | Fire- house or bldg. | Transformer (OH) | Normal | None | 3rd party fire impacting PGE equipment
312 | 3rd Party | Fire- house or bldg. | Transformer (UG) | Burned/flashed | All | 3rd party fire impacting PGE equipment. Underground facilities = no ignition risk
313 | 3rd Party | Fire- house or bldg. | Transformer (UG) | Contaminated | All | 3rd party fire impacting PGE equipment. Underground facilities = no ignition risk
314 | 3rd Party | Fire- house or bldg. | Transformer (UG) | Normal | All | 3rd party fire impacting PGE equipment. Underground facilities = no ignition risk
315 | 3rd Party | Gun Shot | Booster | Leaking | None | Covered wire will not prevent gun shot damage
316 | 3rd Party | Gun Shot | Conductor- Overhead | Annealed | None | Covered wire will not prevent gun shot damage
317 | 3rd Party | Gun Shot | Conductor- Overhead | Broken | None | Covered wire will not prevent gun shot damage
318 | 3rd Party | Gun Shot | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
319 | 3rd Party | Gun Shot | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
320 | 3rd Party | Gun Shot | Conductor- Overhead | Deteriorated | None | Covered wire will not prevent gun shot damage
321 | 3rd Party | Gun Shot | Conductor- Overhead | Normal | None | Covered wire will not prevent gun shot damage
322 | 3rd Party | Gun Shot | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
323 | 3rd Party | Gun Shot | Conductor- Overhead | Together | None | Covered wire will not prevent gun shot damage
324 | 3rd Party | Gun Shot | Conductor- Underground | Broken | None | Covered wire will not prevent gun shot damage
325 | 3rd Party | Gun Shot | Conductor- Underground | Burned/flashed | None | Covered wire will not prevent gun shot damage
326 | 3rd Party | Gun Shot | Connector or Splice (OH) | Broken- wire on ground | None | Covered wire will not prevent gun shot damage
327 | 3rd Party | Gun Shot | Crossarm- Wood | Broken | None | Covered wire will not prevent gun shot damage
328 | 3rd Party | Gun Shot | Fuse | Blown/failed | None | Covered wire will not prevent gun shot damage
329 | 3rd Party | Gun Shot | Fuse | Normal | None | Covered wire will not prevent gun shot damage
330 | 3rd Party | Gun Shot | Insulator | Blown/failed | None | Covered wire will not prevent gun shot damage
331 | 3rd Party | Gun Shot | Insulator | Broken | None | Covered wire will not prevent gun shot damage
332 | 3rd Party | Gun Shot | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
333 | 3rd Party | Gun Shot | Jumper | Broken | None | Covered wire will not prevent gun shot damage
334 | 3rd Party | Gun Shot | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
335 | 3rd Party | Gun Shot | Pothead(Riser Termination) | Blown/failed | None | Covered wire will not prevent gun shot damage
336 | 3rd Party | Gun Shot | Recloser | Broken | None | Covered wire will not prevent gun shot damage
337 | 3rd Party | Gun Shot | Regulator | Leaking | None | Covered wire will not prevent gun shot damage
338 | 3rd Party | Gun Shot | Secondary | Broken | None | Covered wire will not prevent gun shot damage
339 | 3rd Party | Gun Shot | Secondary | Broken- wire on ground | None | Covered wire will not prevent gun shot damage
340 | 3rd Party | Gun Shot | Secondary | On Ground | None | Covered wire will not prevent gun shot damage
341 | 3rd Party | Gun Shot | Transformer | Blown/failed | None | Covered wire will not prevent gun shot damage
342 | 3rd Party | Gun Shot | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
343 | 3rd Party | Gun Shot | Transformer | Burned/flashed | None | Covered wire will not prevent gun shot damage
344 | 3rd Party | Gun Shot | Transformer | Deteriorated | None | Covered wire will not prevent gun shot damage
345 | 3rd Party | Gun Shot | Transformer | Leaking | None | Covered wire will not prevent gun shot damage
346 | 3rd Party | Gun Shot | Transformer (OH) | Blown/failed | None | Covered wire will not prevent gun shot damage
347 | 3rd Party | Gun Shot | Transformer (OH) | Leaking | None | Covered wire will not prevent gun shot damage
348 | 3rd Party | Kite | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
349 | 3rd Party | Kite | Conductor- Overhead | Bent or Twisted | All | New covered conductor will eliminate these contact type outages.
350 | 3rd Party | Kite | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
351 | 3rd Party | Kite | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
352 | 3rd Party | Kite | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
353 | 3rd Party | Kite | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
354 | 3rd Party | Kite | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
355 | 3rd Party | Kite | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
356 | 3rd Party | Kite | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
357 | 3rd Party | Kite | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
358 | 3rd Party | Kite | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
359 | 3rd Party | Kite | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
360 | 3rd Party | Kite | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
361 | 3rd Party | Kite | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
362 | 3rd Party | Kite | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
363 | 3rd Party | Kite | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
364 | 3rd Party | Kite | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
365 | 3rd Party | Kite | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
366 | 3rd Party | Metallic Balloon |  | Blown/failed | None | Unknown what failed
367 | 3rd Party | Metallic Balloon |  | Normal | All | New covered conductor will eliminate these contact type outages.
368 | 3rd Party | Metallic Balloon | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
369 | 3rd Party | Metallic Balloon | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
370 | 3rd Party | Metallic Balloon | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
371 | 3rd Party | Metallic Balloon | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
372 | 3rd Party | Metallic Balloon | Capacitor | Burned/flashed | None | System Hardening would not address this outage
373 | 3rd Party | Metallic Balloon | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
374 | 3rd Party | Metallic Balloon | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
375 | 3rd Party | Metallic Balloon | Conductor- Overhead | Bent or Twisted | All | New covered conductor will eliminate these contact type outages.
376 | 3rd Party | Metallic Balloon | Conductor- Overhead | Blown/failed | All | New covered conductor will eliminate these contact type outages.
377 | 3rd Party | Metallic Balloon | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
378 | 3rd Party | Metallic Balloon | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
379 | 3rd Party | Metallic Balloon | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
380 | 3rd Party | Metallic Balloon | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
381 | 3rd Party | Metallic Balloon | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
382 | 3rd Party | Metallic Balloon | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
383 | 3rd Party | Metallic Balloon | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
384 | 3rd Party | Metallic Balloon | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
385 | 3rd Party | Metallic Balloon | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
386 | 3rd Party | Metallic Balloon | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
387 | 3rd Party | Metallic Balloon | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
388 | 3rd Party | Metallic Balloon | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
389 | 3rd Party | Metallic Balloon | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
390 | 3rd Party | Metallic Balloon | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
391 | 3rd Party | Metallic Balloon | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
392 | 3rd Party | Metallic Balloon | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
393 | 3rd Party | Metallic Balloon | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
394 | 3rd Party | Metallic Balloon | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
395 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Arcing | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
396 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
397 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
398 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
399 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
400 | 3rd Party | Metallic Balloon | Cutout- Fused- Distribution | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
401 | 3rd Party | Metallic Balloon | Fuse | Arcing | High | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
402 | 3rd Party | Metallic Balloon | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
403 | 3rd Party | Metallic Balloon | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
404 | 3rd Party | Metallic Balloon | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
405 | 3rd Party | Metallic Balloon | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
406 | 3rd Party | Metallic Balloon | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
407 | 3rd Party | Metallic Balloon | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
408 | 3rd Party | Metallic Balloon | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
409 | 3rd Party | Metallic Balloon | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
410 | 3rd Party | Metallic Balloon | Interrupter | Normal | All | Underground facilities = no ignition risk
411 | 3rd Party | Metallic Balloon | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
412 | 3rd Party | Metallic Balloon | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
413 | 3rd Party | Metallic Balloon | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
414 | 3rd Party | Metallic Balloon | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
415 | 3rd Party | Metallic Balloon | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
416 | 3rd Party | Metallic Balloon | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
417 | 3rd Party | Metallic Balloon | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
418 | 3rd Party | Metallic Balloon | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
419 | 3rd Party | Metallic Balloon | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
420 | 3rd Party | Metallic Balloon | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
421 | 3rd Party | Metallic Balloon | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
422 | 3rd Party | Metallic Balloon | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
423 | 3rd Party | Metallic Balloon | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
424 | 3rd Party | Metallic Balloon | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
425 | 3rd Party | Metallic Balloon | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
426 | 3rd Party | Metallic Balloon | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
427 | 3rd Party | Metallic Balloon | Riser | Burned/flashed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
428 | 3rd Party | Metallic Balloon | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
429 | 3rd Party | Metallic Balloon | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
430 | 3rd Party | Metallic Balloon | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
431 | 3rd Party | Metallic Balloon | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
432 | 3rd Party | Metallic Balloon | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
433 | 3rd Party | Metallic Balloon | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
434 | 3rd Party | Metallic Balloon | Switch (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
435 | 3rd Party | Metallic Balloon | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
436 | 3rd Party | Metallic Balloon | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
437 | 3rd Party | Metallic Balloon | Transformer | Arcing | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
438 | 3rd Party | Metallic Balloon | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
439 | 3rd Party | Metallic Balloon | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
440 | 3rd Party | Metallic Balloon | Transformer | Burned Open | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
441 | 3rd Party | Metallic Balloon | Transformer | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
442 | 3rd Party | Metallic Balloon | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
443 | 3rd Party | Metallic Balloon | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
444 | 3rd Party | Metallic Balloon | Transformer (OH) | Arcing | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
445 | 3rd Party | Metallic Balloon | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
446 | 3rd Party | Metallic Balloon | Transformer (OH) | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
447 | 3rd Party | Metallic Balloon | Transformer (OH) | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
448 | 3rd Party | Metallic Balloon | Transformer (OH) | Contaminated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
449 | 3rd Party | Metallic Balloon | Transformer (OH) | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
450 | 3rd Party | Metallic Balloon | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
451 | 3rd Party | Metallic Balloon | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
452 | 3rd Party | Other | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
453 | 3rd Party | Other | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
454 | 3rd Party | Other | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
455 | 3rd Party | Other | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
456 | 3rd Party | Other | Cable Termination(live front | Normal | All | Underground facilities = no ignition risk
457 | 3rd Party | Other | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
458 | 3rd Party | Other | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
459 | 3rd Party | Other | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
460 | 3rd Party | Other | Conductor- Overhead | Bent or Twisted | All | New covered conductor will eliminate these contact type outages.
461 | 3rd Party | Other | Conductor- Overhead | Blown/failed | All | New covered conductor will eliminate these contact type outages.
462 | 3rd Party | Other | Conductor- Overhead | Broken | All | New covered conductor will eliminate these contact type outages.
463 | 3rd Party | Other | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
464 | 3rd Party | Other | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
465 | 3rd Party | Other | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
466 | 3rd Party | Other | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
467 | 3rd Party | Other | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
468 | 3rd Party | Other | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
469 | 3rd Party | Other | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
470 | 3rd Party | Other | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
471 | 3rd Party | Other | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
472 | 3rd Party | Other | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
473 | 3rd Party | Other | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
474 | 3rd Party | Other | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
475 | 3rd Party | Other | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
476 | 3rd Party | Other | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
477 | 3rd Party | Other | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
478 | 3rd Party | Other | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
479 | 3rd Party | Other | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
480 | 3rd Party | Other | Customer Equipment | Broken | None | No work is being completed on customer equipment.
481 | 3rd Party | Other | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
482 | 3rd Party | Other | Customer Equipment | Leaking | None | No work is being completed on customer equipment.
483 | 3rd Party | Other | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
484 | 3rd Party | Other | Customer Equipment | Normal | None | No work is being completed on customer equipment.
485 | 3rd Party | Other | Customer Equipment | On Ground | None | No work is being completed on customer equipment.
486 | 3rd Party | Other | Cutout- fuse holder | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
487 | 3rd Party | Other | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
488 | 3rd Party | Other | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
489 | 3rd Party | Other | Cutout- fuse holder | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
490 | 3rd Party | Other | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
491 | 3rd Party | Other | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
492 | 3rd Party | Other | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
493 | 3rd Party | Other | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
494 | 3rd Party | Other | Interrupter | Normal | All | Underground facilities = no ignition risk
495 | 3rd Party | Other | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
496 | 3rd Party | Other | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
497 | 3rd Party | Other | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
498 | 3rd Party | Other | Metering Equipment | Blown/failed | None | No work is being completed on customer equipment.
499 | 3rd Party | Other | Metering Equipment | Normal | None | No work is being completed on customer equipment.
500 | 3rd Party | Other | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
501 | 3rd Party | Other | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
502 | 3rd Party | Other | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
503 | 3rd Party | Other | Pole - Tower- steel | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
504 | 3rd Party | Other | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
505 | 3rd Party | Other | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
506 | 3rd Party | Other | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
507 | 3rd Party | Other | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
508 | 3rd Party | Other | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
509 | 3rd Party | Other | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
510 | 3rd Party | Other | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
511 | 3rd Party | Other | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
512 | 3rd Party | Other | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
513 | 3rd Party | Other | Recloser | Broken | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
514 | 3rd Party | Other | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
515 | 3rd Party | Other | Regulator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
516 | 3rd Party | Other | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
517 | 3rd Party | Other | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
518 | 3rd Party | Other | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
519 | 3rd Party | Other | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
520 | 3rd Party | Other | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
521 | 3rd Party | Other | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
522 | 3rd Party | Other | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
523 | 3rd Party | Other | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
524 | 3rd Party | Other | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
525 | 3rd Party | Other | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
526 | 3rd Party | Other | Switch (UG) | Broken | All | Underground facilities = no ignition risk
527 | 3rd Party | Other | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
528 | 3rd Party | Other | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
529 | 3rd Party | Other | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
530 | 3rd Party | Other | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
531 | 3rd Party | Other | Transformer (OH) | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
532 | 3rd Party | Other | Transformer (OH) | Contaminated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
533 | 3rd Party | Other | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
534 | 3rd Party | Other | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
535 | 3rd Party | Other | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
536 | 3rd Party | Other | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
537 | 3rd Party | Thrown Object | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
538 | 3rd Party | Thrown Object | Conductor- Overhead | Broken | All | New covered conductor will eliminate these contact type outages.
539 | 3rd Party | Thrown Object | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
540 | 3rd Party | Thrown Object | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
541 | 3rd Party | Thrown Object | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
542 | 3rd Party | Thrown Object | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
543 | 3rd Party | Thrown Object | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
544 | 3rd Party | Thrown Object | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
545 | 3rd Party | Thrown Object | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
546 | 3rd Party | Thrown Object | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
547 | 3rd Party | Thrown Object | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
548 | 3rd Party | Thrown Object | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
549 | 3rd Party | Thrown Object | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
550 | 3rd Party | Thrown Object | Transformer | Arcing | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
551 | 3rd Party | Thrown Object | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
552 | 3rd Party | Thrown Object | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
553 | 3rd Party | Thrown Object | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
554 | 3rd Party | Tree - cutting- 3rd party | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
555 | 3rd Party | Tree - cutting- 3rd party | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
556 | 3rd Party | Tree - cutting- 3rd party | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
557 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
558 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Bent or Twisted | All | New covered conductor will eliminate these contact type outages.
559 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Broken | All | New covered conductor will eliminate these contact type outages.
560 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
561 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
562 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
563 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
564 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
565 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
566 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
567 | 3rd Party | Tree - cutting- 3rd party | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
568 | 3rd Party | Tree - cutting- 3rd party | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
569 | 3rd Party | Tree - cutting- 3rd party | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
570 | 3rd Party | Tree - cutting- 3rd party | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
571 | 3rd Party | Tree - cutting- 3rd party | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
572 | 3rd Party | Tree - cutting- 3rd party | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
573 | 3rd Party | Tree - cutting- 3rd party | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
574 | 3rd Party | Tree - cutting- 3rd party | Cutout- Fused- Distribution | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
575 | 3rd Party | Tree - cutting- 3rd party | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
576 | 3rd Party | Tree - cutting- 3rd party | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
577 | 3rd Party | Tree - cutting- 3rd party | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
578 | 3rd Party | Tree - cutting- 3rd party | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
579 | 3rd Party | Tree - cutting- 3rd party | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
580 | 3rd Party | Tree - cutting- 3rd party | Metering Equipment | Malfunctioning | None | No work is being completed on customer equipment.
581 | 3rd Party | Tree - cutting- 3rd party | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
582 | 3rd Party | Tree - cutting- 3rd party | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
583 | 3rd Party | Tree - cutting- 3rd party | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
584 | 3rd Party | Tree - cutting- 3rd party | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
585 | 3rd Party | Tree - cutting- 3rd party | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
586 | 3rd Party | Tree - cutting- 3rd party | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
587 | 3rd Party | Tree - cutting- 3rd party | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
588 | 3rd Party | Tree - cutting- 3rd party | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
589 | 3rd Party | Tree - cutting- 3rd party | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
590 | 3rd Party | Tree - cutting- 3rd party | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
591 | 3rd Party | Tree - cutting- 3rd party | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
592 | 3rd Party | Tree - cutting- 3rd party | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
593 | 3rd Party | Tree - cutting- 3rd party | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
594 | 3rd Party | Tree - cutting- 3rd party | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
595 | 3rd Party | Tree - cutting- 3rd party | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
596 | 3rd Party | Tree - cutting- 3rd party | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
597 | 3rd Party | Tree - cutting- 3rd party | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
598 | 3rd Party | Tree - cutting- 3rd party | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
599 | 3rd Party | Tree - cutting- 3rd party | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
600 | 3rd Party | Tree - cutting- 3rd party | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
601 | 3rd Party | Tree - cutting- 3rd party | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
602 | 3rd Party | Tree - cutting- 3rd party | Transformer | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
603 | 3rd Party | Tree - cutting- 3rd party | Transformer | Contaminated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
604 | 3rd Party | Tree - cutting- 3rd party | Transformer | Deteriorated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
605 | 3rd Party | Tree - cutting- 3rd party | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
606 | 3rd Party | Tree - cutting- 3rd party | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
607 | 3rd Party | Tree - cutting- 3rd party | Transformer (OH) | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
608 | 3rd Party | Tree - cutting- 3rd party | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
609 | 3rd Party | Tree - cutting- 3rd party | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
610 | 3rd Party | Tree - cutting- 3rd party | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
611 | 3rd Party | Vandalism |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
612 | 3rd Party | Vandalism | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
613 | 3rd Party | Vandalism | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
614 | 3rd Party | Vandalism | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
615 | 3rd Party | Vandalism | Conductor- Overhead | Broken | All | New covered conductor will eliminate these contact type outages.
616 | 3rd Party | Vandalism | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
617 | 3rd Party | Vandalism | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
618 | 3rd Party | Vandalism | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
619 | 3rd Party | Vandalism | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
620 | 3rd Party | Vandalism | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
621 | 3rd Party | Vandalism | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
622 | 3rd Party | Vandalism | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
623 | 3rd Party | Vandalism | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
624 | 3rd Party | Vandalism | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
625 | 3rd Party | Vandalism | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
626 | 3rd Party | Vandalism | Connector or Splice (UG) | Broken | All | Underground facilities = no ignition risk
627 | 3rd Party | Vandalism | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
628 | 3rd Party | Vandalism | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
629 | 3rd Party | Vandalism | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
630 | 3rd Party | Vandalism | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
631 | 3rd Party | Vandalism | CT | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
632 | 3rd Party | Vandalism | Customer Equipment | Bent or Twisted | None | No work is being completed on customer equipment.
633 | 3rd Party | Vandalism | Customer Equipment | Broken | None | No work is being completed on customer equipment.
634 | 3rd Party | Vandalism | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
635 | 3rd Party | Vandalism | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
636 | 3rd Party | Vandalism | Cutout- Fused- Distribution | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
637 | 3rd Party | Vandalism | Elbow | Blown/failed | All | Underground facilities = no ignition risk
638 | 3rd Party | Vandalism | Elbow | Malfunctioning | All | Underground facilities = no ignition risk
639 | 3rd Party | Vandalism | Elbow | Normal | All | Underground facilities = no ignition risk
640 | 3rd Party | Vandalism | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
641 | 3rd Party | Vandalism | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
642 | 3rd Party | Vandalism | Metering Equipment | Broken | None | No work is being completed on customer equipment.
643 | 3rd Party | Vandalism | Metering Equipment | Malfunctioning | None | No work is being completed on customer equipment.
644 | 3rd Party | Vandalism | Metering Equipment | Normal | None | No work is being completed on customer equipment.
645 | 3rd Party | Vandalism | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
646 | 3rd Party | Vandalism | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
647 | 3rd Party | Vandalism | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
648 | 3rd Party | Vandalism | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
649 | 3rd Party | Vandalism | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
650 | 3rd Party | Vandalism | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
651 | 3rd Party | Vandalism | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
652 | 3rd Party | Vandalism | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
653 | 3rd Party | Vandalism | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
654 | 3rd Party | Vandalism | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
655 | 3rd Party | Vandalism | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
656 | 3rd Party | Vandalism | Recloser | Broken | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
657 | 3rd Party | Vandalism | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
658 | 3rd Party | Vandalism | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
659 | 3rd Party | Vandalism | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
660 | 3rd Party | Vandalism | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
661 | 3rd Party | Vandalism | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
662 | 3rd Party | Vandalism | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
663 | 3rd Party | Vandalism | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
664 | 3rd Party | Vandalism | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
665 | 3rd Party | Vandalism | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
666 | 3rd Party | Vandalism | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
667 | 3rd Party | Vandalism | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
668 | 3rd Party | Vandalism | Switch (UG) | Broken | All | Underground facilities = no ignition risk
669 | 3rd Party | Vandalism | Switch (UG) | Normal | All | Underground facilities = no ignition risk
670 | 3rd Party | Vandalism | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
671 | 3rd Party | Vandalism | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
672 | 3rd Party | Vandalism | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
673 | 3rd Party | Vandalism | Transformer | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
674 | 3rd Party | Vandalism | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
675 | 3rd Party | Vandalism | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
676 | 3rd Party | Vandalism | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
677 | 3rd Party | Vandalism | Transformer (OH) | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
678 | 3rd Party | Vandalism | Transformer (OH) | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
679 | 3rd Party | Vandalism | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
680 | 3rd Party | Vandalism | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
681 | 3rd Party | Vandalism | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
682 | 3rd Party | Vandalism | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
683 | 3rd Party | Vandalism | Transformer (UG) | Deteriorated | All | Underground facilities = no ignition risk
684 | 3rd Party | Vandalism | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
685 | 3rd Party | Vehicle |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
686 | 3rd Party | Vehicle |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
687 | 3rd Party | Vehicle |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
688 | 3rd Party | Vehicle |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
689 | 3rd Party | Vehicle | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
690 | 3rd Party | Vehicle | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
691 | 3rd Party | Vehicle | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
692 | 3rd Party | Vehicle | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
693 | 3rd Party | Vehicle | Anchor or Guy | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
694 | 3rd Party | Vehicle | Anchor or Guy | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
695 | 3rd Party | Vehicle | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
696 | 3rd Party | Vehicle | Anchor or Guy | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
697 | 3rd Party | Vehicle | Bushing | Broken | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
698 | 3rd Party | Vehicle | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
699 | 3rd Party | Vehicle | Capacitor | Broken | None | System Hardening would not address this outage
700 | 3rd Party | Vehicle | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
701 | 3rd Party | Vehicle | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
702 | 3rd Party | Vehicle | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
703 | 3rd Party | Vehicle | Conductor- Overhead | Bent or Twisted | All | New covered conductor will eliminate these contact type outages.
704 | 3rd Party | Vehicle | Conductor- Overhead | Broken | All | New covered conductor will eliminate these contact type outages.
705 | 3rd Party | Vehicle | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
706 | 3rd Party | Vehicle | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
707 | 3rd Party | Vehicle | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
708 | 3rd Party | Vehicle | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
709 | 3rd Party | Vehicle | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
710 | 3rd Party | Vehicle | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
711 | 3rd Party | Vehicle | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
712 | 3rd Party | Vehicle | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
713 | 3rd Party | Vehicle | Conductor- Underground | Arcing | All | Underground facilities = no ignition risk
714 | 3rd Party | Vehicle | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
715 | 3rd Party | Vehicle | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
716 | 3rd Party | Vehicle | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
717 | 3rd Party | Vehicle | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
718 | 3rd Party | Vehicle | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
719 | 3rd Party | Vehicle | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
720 | 3rd Party | Vehicle | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
721 | 3rd Party | Vehicle | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
722 | 3rd Party | Vehicle | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
723 | 3rd Party | Vehicle | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
724 | 3rd Party | Vehicle | Connector or Splice (UG) | Broken | All | Underground facilities = no ignition risk
725 | 3rd Party | Vehicle | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
726 | 3rd Party | Vehicle | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
727 | 3rd Party | Vehicle | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
728 | 3rd Party | Vehicle | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
729 | 3rd Party | Vehicle | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
730 | 3rd Party | Vehicle | Customer Equipment | Broken | None | No work is being completed on customer equipment.
731 | 3rd Party | Vehicle | Customer Equipment | On Ground | None | No work is being completed on customer equipment.
732 | 3rd Party | Vehicle | Cutout- fuse holder | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
733 | 3rd Party | Vehicle | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
734 | 3rd Party | Vehicle | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
735 | 3rd Party | Vehicle | Elbow | Blown/failed | All | Underground facilities = no ignition risk
736 | 3rd Party | Vehicle | Footings- Tower or Pole | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
737 | 3rd Party | Vehicle | Footings- Tower or Pole | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
738 | 3rd Party | Vehicle | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
739 | 3rd Party | Vehicle | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
740 | 3rd Party | Vehicle | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
741 | 3rd Party | Vehicle | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
742 | 3rd Party | Vehicle | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
743 | 3rd Party | Vehicle | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
744 | 3rd Party | Vehicle | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
745 | 3rd Party | Vehicle | Interrupter | Broken | All | Underground facilities = no ignition risk
746 | 3rd Party | Vehicle | Interrupter | Normal | All | Underground facilities = no ignition risk
747 | 3rd Party | Vehicle | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
748 | 3rd Party | Vehicle | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
749 | 3rd Party | Vehicle | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
750 | 3rd Party | Vehicle | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
751 | 3rd Party | Vehicle | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
752 | 3rd Party | Vehicle | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
753 | 3rd Party | Vehicle | Metering Equipment | Broken | None | No work is being completed on customer equipment.
754 | 3rd Party | Vehicle | Other | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
755 | 3rd Party | Vehicle | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
756 | 3rd Party | Vehicle | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
757 | 3rd Party | Vehicle | Other | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
758 | 3rd Party | Vehicle | Other | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
759 | 3rd Party | Vehicle | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
760 | 3rd Party | Vehicle | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
761 | 3rd Party | Vehicle | Other | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
762 | 3rd Party | Vehicle | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
763 | 3rd Party | Vehicle | Pole - Tower- steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
764 | 3rd Party | Vehicle | Pole - Tower- steel | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
765 | 3rd Party | Vehicle | Pole - Tower- steel | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
766 | 3rd Party | Vehicle | Pole - Tower- steel | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
767 | 3rd Party | Vehicle | Pole-Wood |  | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
768 | 3rd Party | Vehicle | Pole-Wood | Arcing | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
769 | 3rd Party | Vehicle | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
770 | 3rd Party | Vehicle | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
771 | 3rd Party | Vehicle | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
772 | 3rd Party | Vehicle | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
773 | 3rd Party | Vehicle | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
774 | 3rd Party | Vehicle | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
775 | 3rd Party | Vehicle | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
776 | 3rd Party | Vehicle | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
777 | 3rd Party | Vehicle | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
778 | 3rd Party | Vehicle | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
779 | 3rd Party | Vehicle | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
780 | 3rd Party | Vehicle | Pothead/Riser Termination | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
781 | 3rd Party | Vehicle | Recloser | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
782 | 3rd Party | Vehicle | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
783 | 3rd Party | Vehicle | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
784 | 3rd Party | Vehicle | Regulator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
785 | 3rd Party | Vehicle | Regulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
786 | 3rd Party | Vehicle | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
787 | 3rd Party | Vehicle | Riser | Bent or Twisted | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
788 | 3rd Party | Vehicle | Riser | Broken | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
789 | 3rd Party | Vehicle | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
790 | 3rd Party | Vehicle | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
791 | 3rd Party | Vehicle | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
792 | 3rd Party | Vehicle | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
793 | 3rd Party | Vehicle | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
794 | 3rd Party | Vehicle | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
795 | 3rd Party | Vehicle | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
796 | 3rd Party | Vehicle | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
797 | 3rd Party | Vehicle | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
798 | 3rd Party | Vehicle | Sectionalizer | Blown/failed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
799 | 3rd Party | Vehicle | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
800 | 3rd Party | Vehicle | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
801 | 3rd Party | Vehicle | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
802 | 3rd Party | Vehicle | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
803 | 3rd Party | Vehicle | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
804 | 3rd Party | Vehicle | Service conductor | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
805 | 3rd Party | Vehicle | Splice box | Broken | All | Underground facilities = no ignition risk
806 | 3rd Party | Vehicle | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
807 | 3rd Party | Vehicle | Switch | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
808 | 3rd Party | Vehicle | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
809 | 3rd Party | Vehicle | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
810 | 3rd Party | Vehicle | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
811 | 3rd Party | Vehicle | Switch (UG) | Broken | All | Underground facilities = no ignition risk
812 | 3rd Party | Vehicle | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
813 | 3rd Party | Vehicle | Switch (UG) | Normal | All | Underground facilities = no ignition risk
814 | 3rd Party | Vehicle | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
815 | 3rd Party | Vehicle | Transformer | Arcing | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
816 | 3rd Party | Vehicle | Transformer | Bent or Twisted | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
817 | 3rd Party | Vehicle | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
818 | 3rd Party | Vehicle | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
819 | 3rd Party | Vehicle | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
820 | 3rd Party | Vehicle | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
821 | 3rd Party | Vehicle | Transformer | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
822 | 3rd Party | Vehicle | Transformer | Deteriorated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
823 | 3rd Party | Vehicle | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
824 | 3rd Party | Vehicle | Transformer | Malfunctioning | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
825 | 3rd Party | Vehicle | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
826 | 3rd Party | Vehicle | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
827 | 3rd Party | Vehicle | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
828 | 3rd Party | Vehicle | Transformer (OH) | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
829 | 3rd Party | Vehicle | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
830 | 3rd Party | Vehicle | Transformer (OH) | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
831 | 3rd Party | Vehicle | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
832 | 3rd Party | Vehicle | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
833 | 3rd Party | Vehicle | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
834 | 3rd Party | Vehicle | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
835 | 3rd Party | Vehicle | Transformer (UG) | Broken- wire on ground | All | Underground facilities = no ignition risk
836 | 3rd Party | Vehicle | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
837 | 3rd Party | Vehicle | Transformer (UG) | Deteriorated | All | Underground facilities = no ignition risk
838 | 3rd Party | Vehicle | Transformer (UG) | Leaking | All | Underground facilities = no ignition risk
839 | 3rd Party | Vehicle | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
840 | 3rd Party | Vehicle | Transformer (UG) | On Ground | All | Underground facilities = no ignition risk
841 | 3rd Party | Vehicle | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
842 | 3rd Party | Vehicle | Woodpin | Broken- wire on object | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
843 | 3rd Party | Vehicle | Woodpin | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
844 | Animal | Bird found |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
845 | Animal | Bird found |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
846 | Animal | Bird found |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
847 | Animal | Bird found |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
848 | Animal | Bird found |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
849 | Animal | Bird found | Booster | Blown/failed | All | Circuit Hardening replaces boosters with voltage regulators. Work will cover leads and jumpers.
850 | Animal | Bird found | Booster | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
851 | Animal | Bird found | Booster | Burned/flashed | All | Circuit Hardening replaces boosters with voltage regulators. Leads covered.
852 | Animal | Bird found | Booster | Normal | All | Circuit Hardening replaces boosters with voltage regulators. Leads covered.
853 | Animal | Bird found | Bus | Normal | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
854 | Animal | Bird found | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
855 | Animal | Bird found | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
856 | Animal | Bird found | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
857 | Animal | Bird found | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
858 | Animal | Bird found | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
859 | Animal | Bird found | Capacitor | Normal | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
860 | Animal | Bird found | Circuit Breaker | Blown/failed | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
861 | Animal | Bird found | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
862 | Animal | Bird found | Conductor- Overhead | Arcing | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
863 | Animal | Bird found | Conductor- Overhead | Bent or Twisted | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
864 | Animal | Bird found | Conductor- Overhead | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
865 | Animal | Bird found | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
866 | Animal | Bird found | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
867 | Animal | Bird found | Conductor- Overhead | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
868 | Animal | Bird found | Conductor- Overhead | Contaminated | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
869 | Animal | Bird found | Conductor- Overhead | Deteriorated | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
870 | Animal | Bird found | Conductor- Overhead | Malfunctioning | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
871 | Animal | Bird found | Conductor- Overhead | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
872 | Animal | Bird found | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
873 | Animal | Bird found | Conductor- Overhead | Together | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
874 | Animal | Bird found | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
875 | Animal | Bird found | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
876 | Animal | Bird found | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
877 | Animal | Bird found | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
878 | Animal | Bird found | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
879 | Animal | Bird found | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
880 | Animal | Bird found | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
881 | Animal | Bird found | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
882 | Animal | Bird found | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
883 | Animal | Bird found | Crossarm- Steel | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
884 | Animal | Bird found | Crossarm- Wood | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
885 | Animal | Bird found | Crossarm- Wood | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
886 | Animal | Bird found | Crossarm- Wood | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
887 | Animal | Bird found | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
888 | Animal | Bird found | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
889 | Animal | Bird found | Customer Equipment | Normal | None | No work is being completed on customer equipment.
890 | Animal | Bird found | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
891 | Animal | Bird found | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
892 | Animal | Bird found | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
893 | Animal | Bird found | Cutout- fuse holder | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
894 | Animal | Bird found | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
895 | Animal | Bird found | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
896 | Animal | Bird found | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
897 | Animal | Bird found | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
898 | Animal | Bird found | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
899 | Animal | Bird found | Elbow | Blown/failed | All | Underground facilities = no ignition risk
900 | Animal | Bird found | Footings- Tower or Pole | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
901 | Animal | Bird found | Fuse | Arcing | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
902 | Animal | Bird found | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
903 | Animal | Bird found | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
904 | Animal | Bird found | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
905 | Animal | Bird found | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
906 | Animal | Bird found | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
907 | Animal | Bird found | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
908 | Animal | Bird found | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
909 | Animal | Bird found | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
910 | Animal | Bird found | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
911 | Animal | Bird found | Interrupter | Normal | All | Underground facilities = no ignition risk
912 | Animal | Bird found | Jumper |  | High | Larger covered conductor to mostly eliminate cause and risk.
913 | Animal | Bird found | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
914 | Animal | Bird found | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
915 | Animal | Bird found | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
916 | Animal | Bird found | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
917 | Animal | Bird found | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
918 | Animal | Bird found | Jumper | Deteriorated | High | Larger covered conductor to mostly eliminate cause and risk.
919 | Animal | Bird found | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
920 | Animal | Bird found | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
921 | Animal | Bird found | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
922 | Animal | Bird found | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
923 | Animal | Bird found | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
924 | Animal | Bird found | Other | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
925 | Animal | Bird found | Other | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
926 | Animal | Bird found | Other | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
927 | Animal | Bird found | PGs- Kearneys | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
928 | Animal | Bird found | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
929 | Animal | Bird found | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
930 | Animal | Bird found | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
931 | Animal | Bird found | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
932 | Animal | Bird found | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
933 | Animal | Bird found | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
934 | Animal | Bird found | Pothead(Riser Termination) | Arcing | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
935 | Animal | Bird found | Pothead(Riser Termination) | Blown/failed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
936 | Animal | Bird found | Pothead(Riser Termination) | Broken | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
937 | Animal | Bird found | Pothead(Riser Termination) | Burned/flashed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
938 | Animal | Bird found | Pothead(Riser Termination) | Normal | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
939 | Animal | Bird found | Pothead/Riser Termination | Burned/flashed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
940 | Animal | Bird found | Pothead/Riser Termination | Normal | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
941 | Animal | Bird found | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
942 | Animal | Bird found | PT/CCVT | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
943 | Animal | Bird found | Recloser | Blown/failed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
944 | Animal | Bird found | Recloser | Broken | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
945 | Animal | Bird found | Recloser | Burned/flashed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
946 | Animal | Bird found | Recloser | Normal | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
947 | Animal | Bird found | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
948 | Animal | Bird found | Regulator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
949 | Animal | Bird found | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
950 | Animal | Bird found | Regulator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
951 | Animal | Bird found | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
952 | Animal | Bird found | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
953 | Animal | Bird found | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
954 | Animal | Bird found | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
955 | Animal | Bird found | Sectionalizer | Blown/failed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
956 | Animal | Bird found | Stepdown | Blown/failed | All | Underground facilities = no ignition risk
957 | Animal | Bird found | Stepdown | Burned/flashed | All | Underground facilities = no ignition risk
958 | Animal | Bird found | Street Light Equipment | Blown/failed | Medium | System Hardening will not address Street Lights but will address their transformers.
959 | Animal | Bird found | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
960 | Animal | Bird found | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
961 | Animal | Bird found | Switch (OH) | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
962 | Animal | Bird found | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
963 | Animal | Bird found | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
964 | Animal | Bird found | Switch (UG) | Normal | All | Underground facilities = no ignition risk
965 | Animal | Bird found | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
966 | Animal | Bird found | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
967 | Animal | Bird found | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
968 | Animal | Bird found | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
969 | Animal | Bird found | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
970 | Animal | Bird found | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
971 | Animal | Bird found | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
972 | Animal | Bird found | Transformer (OH) |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
973 | Animal | Bird found | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
974 | Animal | Bird found | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
975 | Animal | Bird found | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
976 | Animal | Bird found | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
977 | Animal | Bird found | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
978 | Animal | Bird found | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
979 | Animal | Bird found | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
980 | Animal | Bird found | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
981 | Animal | Bird found | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
982 | Animal | Bird found | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
983 | Animal | Bird found | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
984 | Animal | Bird found | Woodpin | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
985 | Animal | Bird found | Woodpin | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
986 | Animal | Other |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
987 | Animal | Other |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
988 | Animal | Other |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
989 | Animal | Other |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
990 | Animal | Other | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
991 | Animal | Other | Anchor or Guy | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
992 | Animal | Other | Booster | Burned/flashed | All | Circuit Hardening replaces boosters with voltage regulators. Leads covered.
993 | Animal | Other | Booster | Contaminated | All | Circuit Hardening replaces boosters with voltage regulators. Leads covered.
994 | Animal | Other | Bus | Normal | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
995 | Animal | Other | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
996 | Animal | Other | Bushing | Broken | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
997 | Animal | Other | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
998 | Animal | Other | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
999 | Animal | Other | Cable Termination(live front | Normal | All | Underground facilities = no ignition risk
1000 | Animal | Other | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
1001 | Animal | Other | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
1002 | Animal | Other | Capacitor | Normal | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
1003 | Animal | Other | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1004 | Animal | Other | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1005 | Animal | Other | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1006 | Animal | Other | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1007 | Animal | Other | Conductor- Overhead | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1008 | Animal | Other | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1009 | Animal | Other | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1010 | Animal | Other | Conductor- Overhead | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1011 | Animal | Other | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1012 | Animal | Other | Conductor- Overhead | Deteriorated | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1013 | Animal | Other | Conductor- Overhead | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1014 | Animal | Other | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1015 | Animal | Other | Conductor- Overhead | Together | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1016 | Animal | Other | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
1017 | Animal | Other | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
1018 | Animal | Other | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
1019 | Animal | Other | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
1020 | Animal | Other | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1021 | Animal | Other | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1022 | Animal | Other | Connector or Splice (OH) | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1023 | Animal | Other | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1024 | Animal | Other | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1025 | Animal | Other | Crossarm- Steel | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1026 | Animal | Other | Crossarm- Wood | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1027 | Animal | Other | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1028 | Animal | Other | Crossarm- Wood | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1029 | Animal | Other | Crossarm- Wood | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1030 | Animal | Other | Crossarm- Wood | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1031 | Animal | Other | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
1032 | Animal | Other | Customer Equipment | Normal | None | No work is being completed on customer equipment.
1033 | Animal | Other | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1034 | Animal | Other | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1035 | Animal | Other | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1036 | Animal | Other | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1037 | Animal | Other | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1038 | Animal | Other | Cutout- Fused- Distribution | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1039 | Animal | Other | Elbow | Blown/failed | All | Underground facilities = no ignition risk
1040 | Animal | Other | Fuse | Arcing | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1041 | Animal | Other | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1042 | Animal | Other | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1043 | Animal | Other | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1044 | Animal | Other | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1045 | Animal | Other | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1046 | Animal | Other | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1047 | Animal | Other | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1048 | Animal | Other | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1049 | Animal | Other | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1050 | Animal | Other | Jumper | Arcing | High | Larger covered conductor to mostly eliminate cause and risk.
1051 | Animal | Other | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
1052 | Animal | Other | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
1053 | Animal | Other | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
1054 | Animal | Other | Jumper | Contaminated | High | Larger covered conductor to mostly eliminate cause and risk.
1055 | Animal | Other | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
1056 | Animal | Other | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1057 | Animal | Other | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1058 | Animal | Other | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1059 | Animal | Other | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1060 | Animal | Other | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
1061 | Animal | Other | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
1062 | Animal | Other | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
1063 | Animal | Other | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1064 | Animal | Other | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1065 | Animal | Other | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1066 | Animal | Other | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1067 | Animal | Other | Pole - Tower- steel | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1068 | Animal | Other | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1069 | Animal | Other | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1070 | Animal | Other | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1071 | Animal | Other | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1072 | Animal | Other | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1073 | Animal | Other | Pole-Wood | Together | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1074 | Animal | Other | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1075 | Animal | Other | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1076 | Animal | Other | Pothead(Riser Termination) | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1077 | Animal | Other | Pothead(Riser Termination) | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1078 | Animal | Other | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1079 | Animal | Other | Pothead/Riser Termination | Arcing | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1080 | Animal | Other | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1081 | Animal | Other | Pothead/Riser Termination | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1082 | Animal | Other | PT/CCVT | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1083 | Animal | Other | PT/CCVT | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1084 | Animal | Other | Recloser | Blown/failed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1085 | Animal | Other | Recloser | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1086 | Animal | Other | Recloser | Burned/flashed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1087 | Animal | Other | Recloser | Malfunctioning | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1088 | Animal | Other | Recloser | Normal | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1089 | Animal | Other | Regulator | Arcing | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1090 | Animal | Other | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1091 | Animal | Other | Regulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1092 | Animal | Other | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1093 | Animal | Other | Regulator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1094 | Animal | Other | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
1095 | Animal | Other | Secondary | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1096 | Animal | Other | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1097 | Animal | Other | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1098 | Animal | Other | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1099 | Animal | Other | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1100 | Animal | Other | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1101 | Animal | Other | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1102 | Animal | Other | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1103 | Animal | Other | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1104 | Animal | Other | Sectionalizer | Burned/flashed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1105 | Animal | Other | Sectionalizer | Normal | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1106 | Animal | Other | Stepdown | Burned/flashed | All | Underground facilities = no ignition risk
1107 | Animal | Other | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1108 | Animal | Other | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1109 | Animal | Other | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1110 | Animal | Other | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1111 | Animal | Other | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1112 | Animal | Other | Switch (UG) | Arcing | All | Underground facilities = no ignition risk
1113 | Animal | Other | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1114 | Animal | Other | Switch (UG) | Normal | All | Underground facilities = no ignition risk
1115 | Animal | Other | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1116 | Animal | Other | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1117 | Animal | Other | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1118 | Animal | Other | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1119 | Animal | Other | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1120 | Animal | Other | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1121 | Animal | Other | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1122 | Animal | Other | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1123 | Animal | Other | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1124 | Animal | Other | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1125 | Animal | Other | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1126 | Animal | Other | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1127 | Animal | Other | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1128 | Animal | Other | Transformer (UG) | Arcing | All | UG Facilities = no ignition risk
1129 | Animal | Other | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
1130 | Animal | Other | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
1131 | Animal | Other | Transformer (UG) | Burned/flashed | All | UG Facilities = no ignition risk
1132 | Animal | Other | Transformer (UG) | Deteriorated | All | UG Facilities = no ignition risk
1133 | Animal | Other | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
1134 | Animal | Other | Woodpin | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1135 | Animal | Squirrel |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1136 | Animal | Squirrel |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1137 | Animal | Squirrel |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1138 | Animal | Squirrel |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1139 | Animal | Squirrel |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1140 | Animal | Squirrel | Bus | Normal | Medium | Transforemers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
1141 | Animal | Squirrel | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
1142 | Animal | Squirrel | Bushing | Broken | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
1143 | Animal | Squirrel | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
1144 | Animal | Squirrel | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
1145 | Animal | Squirrel | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
1146 | Animal | Squirrel | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1147 | Animal | Squirrel | Conductor- Overhead | Arcing | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1148 | Animal | Squirrel | Conductor- Overhead | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1149 | Animal | Squirrel | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1150 | Animal | Squirrel | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1151 | Animal | Squirrel | Conductor- Overhead | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1152 | Animal | Squirrel | Conductor- Overhead | Deteriorated | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1153 | Animal | Squirrel | Conductor- Overhead | Malfunctioning | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1154 | Animal | Squirrel | Conductor- Overhead | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1155 | Animal | Squirrel | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1156 | Animal | Squirrel | Conductor- Overhead | Together | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1157 | Animal | Squirrel | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
1158 | Animal | Squirrel | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
1159 | Animal | Squirrel | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
1160 | Animal | Squirrel | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
1161 | Animal | Squirrel | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1162 | Animal | Squirrel | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1163 | Animal | Squirrel | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1164 | Animal | Squirrel | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1165 | Animal | Squirrel | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
1166 | Animal | Squirrel | Crossarm- Steel | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1167 | Animal | Squirrel | Crossarm- Wood | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1168 | Animal | Squirrel | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1169 | Animal | Squirrel | Crossarm- Wood | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1170 | Animal | Squirrel | Crossarm- Wood | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1171 | Animal | Squirrel | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
1172 | Animal | Squirrel | Customer Equipment | Normal | None | No work is being completed on customer equipment.
1173 | Animal | Squirrel | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1174 | Animal | Squirrel | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1175 | Animal | Squirrel | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1176 | Animal | Squirrel | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1177 | Animal | Squirrel | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1178 | Animal | Squirrel | Cutout- Fused- Distribution | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1179 | Animal | Squirrel | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1180 | Animal | Squirrel | Fuse |  | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1181 | Animal | Squirrel | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1182 | Animal | Squirrel | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1183 | Animal | Squirrel | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1184 | Animal | Squirrel | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1185 | Animal | Squirrel | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1186 | Animal | Squirrel | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1187 | Animal | Squirrel | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1188 | Animal | Squirrel | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1189 | Animal | Squirrel | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1190 | Animal | Squirrel | Interrupter | Normal | All | Underground facilities = no ignition risk
1191 | Animal | Squirrel | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
1192 | Animal | Squirrel | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
1193 | Animal | Squirrel | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
1194 | Animal | Squirrel | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
1195 | Animal | Squirrel | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
1196 | Animal | Squirrel | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1197 | Animal | Squirrel | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1198 | Animal | Squirrel | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1199 | Animal | Squirrel | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1200 | Animal | Squirrel | Other | Arcing | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1201 | Animal | Squirrel | Other | Blown/failed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1202 | Animal | Squirrel | Other | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1203 | Animal | Squirrel | Other | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1204 | Animal | Squirrel | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1205 | Animal | Squirrel | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1206 | Animal | Squirrel | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1207 | Animal | Squirrel | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1208 | Animal | Squirrel | Pothead(Riser Termination) | Blown/failed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1209 | Animal | Squirrel | Pothead(Riser Termination) | Broken | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1210 | Animal | Squirrel | Pothead(Riser Termination) | Burned/flashed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1211 | Animal | Squirrel | Pothead(Riser Termination) | Normal | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1212 | Animal | Squirrel | Pothead/Riser Termination | Blown/failed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1213 | Animal | Squirrel | Pothead/Riser Termination | Broken | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1214 | Animal | Squirrel | Pothead/Riser Termination | Burned/flashed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1215 | Animal | Squirrel | Pothead/Riser Termination | Contaminated | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1216 | Animal | Squirrel | Pothead/Riser Termination | Normal | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1217 | Animal | Squirrel | Pothead/Riser Termination | Together | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1218 | Animal | Squirrel | PT/CCVT | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1219 | Animal | Squirrel | Recloser | Blown/failed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1220 | Animal | Squirrel | Recloser | Broken | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1221 | Animal | Squirrel | Recloser | Burned/flashed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1222 | Animal | Squirrel | Recloser | Malfunctioning | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1223 | Animal | Squirrel | Recloser | Normal | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1224 | Animal | Squirrel | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1225 | Animal | Squirrel | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1226 | Animal | Squirrel | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
1227 | Animal | Squirrel | Secondary |  | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1228 | Animal | Squirrel | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1229 | Animal | Squirrel | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1230 | Animal | Squirrel | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1231 | Animal | Squirrel | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1232 | Animal | Squirrel | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1233 | Animal | Squirrel | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1234 | Animal | Squirrel | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1235 | Animal | Squirrel | Sectionalizer | Normal | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1236 | Animal | Squirrel | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1237 | Animal | Squirrel | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1238 | Animal | Squirrel | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1239 | Animal | Squirrel | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1240 | Animal | Squirrel | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1241 | Animal | Squirrel | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1242 | Animal | Squirrel | Switch (UG) | Leaking | All | Underground facilities = no ignition risk
1243 | Animal | Squirrel | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1244 | Animal | Squirrel | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1245 | Animal | Squirrel | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1246 | Animal | Squirrel | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1247 | Animal | Squirrel | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1248 | Animal | Squirrel | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1249 | Animal | Squirrel | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1250 | Animal | Squirrel | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1251 | Animal | Squirrel | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1252 | Animal | Squirrel | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1253 | Animal | Squirrel | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1254 | Animal | Squirrel | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1255 | Animal | Squirrel | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1256 | Animal | Squirrel | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1257 | Animal | Squirrel | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1258 | Animal | Squirrel | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1259 | Animal | Squirrel | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
1260 | Animal | Squirrel | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
1261 | Company Initiated | Construction Activity/equip- company | Anchor or Guy | Deteriorated | None | Company Initiated Outage. Not outage related.
1262 | Company Initiated | Construction Activity/equip- company | Anchor or Guy | Normal | None | Company Initiated Outage. Not outage related.
1263 | Company Initiated | Construction Activity/equip- company | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
1264 | Company Initiated | Construction Activity/equip- company | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
1265 | Company Initiated | Construction Activity/equip- company | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1266 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
1267 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
1268 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1269 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1270 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
1271 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1272 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | On Ground | None | Company Initiated Outage. Not outage related.
1273 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1274 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1275 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1276 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
1277 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1278 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
1279 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1280 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken- wire on object | None | Company Initiated Outage. Not outage related.
1281 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Burned Open | None | Company Initiated Outage. Not outage related.
1282 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
1283 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1284 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Broken | None | Company Initiated Outage. Not outage related.
1285 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
1286 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
1287 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1288 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
1289 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
1290 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
1291 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
1292 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
1293 | Company Initiated | Construction Activity/equip- company | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
1294 | Company Initiated | Construction Activity/equip- company | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
1295 | Company Initiated | Construction Activity/equip- company | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
1296 | Company Initiated | Construction Activity/equip- company | Elbow | Normal | None | Company Initiated Outage. Not outage related.
1297 | Company Initiated | Construction Activity/equip- company | Footings- Tower or Pole | Normal | None | Company Initiated Outage. Not outage related.
1298 | Company Initiated | Construction Activity/equip- company | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
1299 | Company Initiated | Construction Activity/equip- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1300 | Company Initiated | Construction Activity/equip- company | Fuse | Burned Open | None | Company Initiated Outage. Not outage related.
1301 | Company Initiated | Construction Activity/equip- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1302 | Company Initiated | Construction Activity/equip- company | Generator | Malfunctioning | None | Company Initiated Outage. Not outage related.
1303 | Company Initiated | Construction Activity/equip- company | Insulator | Broken | None | Company Initiated Outage. Not outage related.
1304 | Company Initiated | Construction Activity/equip- company | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
1305 | Company Initiated | Construction Activity/equip- company | Jumper | Broken | None | Company Initiated Outage. Not outage related.
1306 | Company Initiated | Construction Activity/equip- company | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
1307 | Company Initiated | Construction Activity/equip- company | Jumper | Burned/flashed | None | Company Initiated Outage. Not outage related.
1308 | Company Initiated | Construction Activity/equip- company | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1309 | Company Initiated | Construction Activity/equip- company | Lightning Arrestor | Normal | None | Company Initiated Outage. Not outage related.
1310 | Company Initiated | Construction Activity/equip- company | Other | Broken | None | Company Initiated Outage. Not outage related.
1311 | Company Initiated | Construction Activity/equip- company | Other | Normal | None | Company Initiated Outage. Not outage related.
1312 | Company Initiated | Construction Activity/equip- company | Pole - Tower- steel | Normal | None | Company Initiated Outage. Not outage related.
1313 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
1314 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1315 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1316 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1317 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
1318 | Company Initiated | Construction Activity/equip- company | Pole-Wood | On Ground | None | Company Initiated Outage. Not outage related.
1319 | Company Initiated | Construction Activity/equip- company | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
1320 | Company Initiated | Construction Activity/equip- company | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
1321 | Company Initiated | Construction Activity/equip- company | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1322 | Company Initiated | Construction Activity/equip- company | Regulator | Normal | None | Company Initiated Outage. Not outage related.
1323 | Company Initiated | Construction Activity/equip- company | Relay | Malfunctioning | None | Company Initiated Outage. Not outage related.
1324 | Company Initiated | Construction Activity/equip- company | Riser | Normal | None | Company Initiated Outage. Not outage related.
1325 | Company Initiated | Construction Activity/equip- company | Secondary | Bent or Twisted | None | Company Initiated Outage. Not outage related.
1326 | Company Initiated | Construction Activity/equip- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
1327 | Company Initiated | Construction Activity/equip- company | Secondary | Deteriorated | None | Company Initiated Outage. Not outage related.
1328 | Company Initiated | Construction Activity/equip- company | Secondary | Normal | None | Company Initiated Outage. Not outage related.
1329 | Company Initiated | Construction Activity/equip- company | Secondary | Together | None | Company Initiated Outage. Not outage related.
1330 | Company Initiated | Construction Activity/equip- company | Service conductor | Broken | None | Company Initiated Outage. Not outage related.
1331 | Company Initiated | Construction Activity/equip- company | Switch | Normal | None | Company Initiated Outage. Not outage related.
1332 | Company Initiated | Construction Activity/equip- company | Switch (OH) | Broken | None | Company Initiated Outage. Not outage related.
1333 | Company Initiated | Construction Activity/equip- company | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1334 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1335 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
1336 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1337 | Company Initiated | Construction Activity/equip- company | Transformer | Broken | None | Company Initiated Outage. Not outage related.
1338 | Company Initiated | Construction Activity/equip- company | Transformer | Deteriorated | None | Company Initiated Outage. Not outage related.
1339 | Company Initiated | Construction Activity/equip- company | Transformer | Leaking | None | Company Initiated Outage. Not outage related.
1340 | Company Initiated | Construction Activity/equip- company | Transformer | Normal | None | Company Initiated Outage. Not outage related.
1341 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
1342 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
1343 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
1344 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1345 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
1346 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
1347 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1348 | Company Initiated | Contact with High Voltage- company |  | Blown/failed | None | Company Initiated Outage. Not outage related.
1349 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1350 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1351 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1352 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | On Ground | None | Company Initiated Outage. Not outage related.
1353 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1354 | Company Initiated | Contact with High Voltage- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1355 | Company Initiated | Contact with High Voltage- company | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
1356 | Company Initiated | Contact with High Voltage- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1357 | Company Initiated | Contact with High Voltage- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1358 | Company Initiated | Contact with High Voltage- company | Pothead(Riser Termination) | Burned/flashed | None | Company Initiated Outage. Not outage related.
1359 | Company Initiated | Contact with High Voltage- company | Secondary | Burned/flashed | None | Company Initiated Outage. Not outage related.
1360 | Company Initiated | Contact with High Voltage- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
1361 | Company Initiated | Coordination failure |  | Normal | None | Company Initiated Outage. Not outage related.
1362 | Company Initiated | Coordination failure | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
1363 | Company Initiated | Coordination failure | Circuit Breaker | Malfunctioning | None | Company Initiated Outage. Not outage related.
1364 | Company Initiated | Coordination failure | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1365 | Company Initiated | Coordination failure | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1366 | Company Initiated | Coordination failure | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1367 | Company Initiated | Coordination failure | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1368 | Company Initiated | Coordination failure | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1369 | Company Initiated | Coordination failure | Crossarm- Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1370 | Company Initiated | Coordination failure | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
1371 | Company Initiated | Coordination failure | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1372 | Company Initiated | Coordination failure | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1373 | Company Initiated | Coordination failure | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
1374 | Company Initiated | Coordination failure | Other | Normal | None | Company Initiated Outage. Not outage related.
1375 | Company Initiated | Coordination failure | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1376 | Company Initiated | Coordination failure | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1377 | Company Initiated | Coordination failure | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
1378 | Company Initiated | Coordination failure | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1379 | Company Initiated | Coordination failure | Relay | Malfunctioning | None | Company Initiated Outage. Not outage related.
1380 | Company Initiated | Coordination failure | SCADA | Malfunctioning | None | Company Initiated Outage. Not outage related.
1381 | Company Initiated | Coordination failure | Stepdown | Normal | None | Company Initiated Outage. Not outage related.
1382 | Company Initiated | Coordination failure | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1383 | Company Initiated | Coordination failure | Transformer |  | None | Company Initiated Outage. Not outage related.
1384 | Company Initiated | Coordination failure | Transformer | Normal | None | Company Initiated Outage. Not outage related.
1385 | Company Initiated | Dig in- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1386 | Company Initiated | Dig in- company | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1387 | Company Initiated | Dig in- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1388 | Company Initiated | Dig in- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
1389 | Company Initiated | Dig in- company | Service conductor | Broken | None | Company Initiated Outage. Not outage related.
1390 | Company Initiated | Improper Construction | Anchor or Guy | Broken | None | Company Initiated Outage. Not outage related.
1391 | Company Initiated | Improper Construction | Booster | Normal | None | Company Initiated Outage. Not outage related.
1392 | Company Initiated | Improper Construction | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
1393 | Company Initiated | Improper Construction | Conductor- Overhead | Annealed | None | Company Initiated Outage. Not outage related.
1394 | Company Initiated | Improper Construction | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
1395 | Company Initiated | Improper Construction | Conductor- Overhead | Bent or Twisted | None | Company Initiated Outage. Not outage related.
1396 | Company Initiated | Improper Construction | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
1397 | Company Initiated | Improper Construction | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1398 | Company Initiated | Improper Construction | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1399 | Company Initiated | Improper Construction | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
1400 | Company Initiated | Improper Construction | Conductor- Overhead | Malfunctioning | None | Company Initiated Outage. Not outage related.
1401 | Company Initiated | Improper Construction | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1402 | Company Initiated | Improper Construction | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1403 | Company Initiated | Improper Construction | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1404 | Company Initiated | Improper Construction | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1405 | Company Initiated | Improper Construction | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
1406 | Company Initiated | Improper Construction | Connector or Splice (OH) | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1407 | Company Initiated | Improper Construction | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
1408 | Company Initiated | Improper Construction | Connector or Splice (UG) | Broken | None | Company Initiated Outage. Not outage related.
1409 | Company Initiated | Improper Construction | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
1410 | Company Initiated | Improper Construction | Connector or Splice (UG) | Together | None | Company Initiated Outage. Not outage related.
1411 | Company Initiated | Improper Construction | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1412 | Company Initiated | Improper Construction | Crossarm- Wood | Contaminated | None | Company Initiated Outage. Not outage related.
1413 | Company Initiated | Improper Construction | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
1414 | Company Initiated | Improper Construction | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
1415 | Company Initiated | Improper Construction | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
1416 | Company Initiated | Improper Construction | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
1417 | Company Initiated | Improper Construction | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
1418 | Company Initiated | Improper Construction | Elbow | Normal | None | Company Initiated Outage. Not outage related.
1419 | Company Initiated | Improper Construction | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
1420 | Company Initiated | Improper Construction | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1421 | Company Initiated | Improper Construction | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1422 | Company Initiated | Improper Construction | Insulator | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1423 | Company Initiated | Improper Construction | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
1424 | Company Initiated | Improper Construction | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
1425 | Company Initiated | Improper Construction | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1426 | Company Initiated | Improper Construction | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
1427 | Company Initiated | Improper Construction | Other | Normal | None | Company Initiated Outage. Not outage related.
1428 | Company Initiated | Improper Construction | Other | Together | None | Company Initiated Outage. Not outage related.
1429 | Company Initiated | Improper Construction | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
1430 | Company Initiated | Improper Construction | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1431 | Company Initiated | Improper Construction | Regulator | Burned/flashed | None | Company Initiated Outage. Not outage related.
1432 | Company Initiated | Improper Construction | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
1433 | Company Initiated | Improper Construction | Regulator | Normal | None | Company Initiated Outage. Not outage related.
1434 | Company Initiated | Improper Construction | Secondary | Bent or Twisted | None | Company Initiated Outage. Not outage related.
1435 | Company Initiated | Improper Construction | Secondary | Broken | None | Company Initiated Outage. Not outage related.
1436 | Company Initiated | Improper Construction | Secondary | Burned Open | None | Company Initiated Outage. Not outage related.
1437 | Company Initiated | Improper Construction | Secondary | Normal | None | Company Initiated Outage. Not outage related.
1438 | Company Initiated | Improper Construction | Secondary | Together | None | Company Initiated Outage. Not outage related.
1439 | Company Initiated | Improper Construction | Switch | Normal | None | Company Initiated Outage. Not outage related.
1440 | Company Initiated | Improper Construction | Switch (OH) | Arcing | None | Company Initiated Outage. Not outage related.
1441 | Company Initiated | Improper Construction | Switch (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
1442 | Company Initiated | Improper Construction | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1443 | Company Initiated | Improper Construction | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1444 | Company Initiated | Improper Construction | Transformer |  | None | Company Initiated Outage. Not outage related.
1445 | Company Initiated | Improper Construction | Transformer | Blown/failed | None | Company Initiated Outage. Not outage related.
1446 | Company Initiated | Improper Construction | Transformer | Normal | None | Company Initiated Outage. Not outage related.
1447 | Company Initiated | Improper Construction | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
1448 | Company Initiated | Improper Construction | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1449 | Company Initiated | Improper Construction | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1450 | Company Initiated | Insulator washing | Bushing | Broken | None | Company Initiated Outage. Not outage related.
1451 | Company Initiated | Insulator washing | Circuit Breaker | Burned/flashed | None | Company Initiated Outage. Not outage related.
1452 | Company Initiated | Insulator washing | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1453 | Company Initiated | Operating error |  |  | None | Company Initiated Outage. Not outage related.
1454 | Company Initiated | Operating error | Capacitor | Blown/failed | None | Company Initiated Outage. Not outage related.
1455 | Company Initiated | Operating error | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1456 | Company Initiated | Operating error | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1457 | Company Initiated | Operating error | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1458 | Company Initiated | Operating error | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1459 | Company Initiated | Operating error | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1460 | Company Initiated | Operating error | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1461 | Company Initiated | Operating error | Customer Equipment | Malfunctioning | None | Company Initiated Outage. Not outage related.
1462 | Company Initiated | Operating error | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
1463 | Company Initiated | Operating error | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
1464 | Company Initiated | Operating error | Fuse |  | None | Company Initiated Outage. Not outage related.
1465 | Company Initiated | Operating error | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1466 | Company Initiated | Operating error | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1467 | Company Initiated | Operating error | Jumper | Broken | None | Company Initiated Outage. Not outage related.
1468 | Company Initiated | Operating error | Jumper | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1469 | Company Initiated | Operating error | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1470 | Company Initiated | Operating error | Other | Burned/flashed | None | Company Initiated Outage. Not outage related.
1471 | Company Initiated | Operating error | Other | Normal | None | Company Initiated Outage. Not outage related.
1472 | Company Initiated | Operating error | Recloser | Blown/failed | None | Company Initiated Outage. Not outage related.
1473 | Company Initiated | Operating error | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1474 | Company Initiated | Operating error | Regulator | Normal | None | Company Initiated Outage. Not outage related.
1475 | Company Initiated | Operating error | Relay | Normal | None | Company Initiated Outage. Not outage related.
1476 | Company Initiated | Operating error | SCADA | Normal | None | Company Initiated Outage. Not outage related.
1477 | Company Initiated | Operating error | Secondary | Arcing | None | Company Initiated Outage. Not outage related.
1478 | Company Initiated | Operating error | Switch |  | None | Company Initiated Outage. Not outage related.
1479 | Company Initiated | Operating error | Switch | Contaminated | None | Company Initiated Outage. Not outage related.
1480 | Company Initiated | Operating error | Switch (OH) | Burned/flashed | None | Company Initiated Outage. Not outage related.
1481 | Company Initiated | Operating error | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1482 | Company Initiated | Operating error | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1483 | Company Initiated | Operating error | Transformer (UG) |  | None | Company Initiated Outage. Not outage related.
1484 | Company Initiated | Operating error | Transformer (UG) | Burned/flashed | None | Company Initiated Outage. Not outage related.
1485 | Company Initiated | Operating error | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1486 | Company Initiated | Other Circuits |  |  | None | Company Initiated Outage. Not outage related.
1487 | Company Initiated | Other Circuits | Booster | Deteriorated | None | Company Initiated Outage. Not outage related.
1488 | Company Initiated | Other Circuits | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1489 | Company Initiated | Other Circuits | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
1490 | Company Initiated | Other Circuits | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1491 | Company Initiated | Other Circuits | Conductor- Overhead | Broken- wire on object | None | Company Initiated Outage. Not outage related.
1492 | Company Initiated | Other Circuits | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
1493 | Company Initiated | Other Circuits | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1494 | Company Initiated | Other Circuits | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1495 | Company Initiated | Other Circuits | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1496 | Company Initiated | Other Circuits | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1497 | Company Initiated | Other Circuits | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1498 | Company Initiated | Other Circuits | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
1499 | Company Initiated | Other Circuits | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
1500 | Company Initiated | Other Circuits | Footings- Tower or Pole | Bent or Twisted | None | Company Initiated Outage. Not outage related.
1501 | Company Initiated | Other Circuits | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1502 | Company Initiated | Other Circuits | Fuse | Deteriorated | None | Company Initiated Outage. Not outage related.
1503 | Company Initiated | Other Circuits | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1504 | Company Initiated | Other Circuits | Generator | Contaminated | None | Company Initiated Outage. Not outage related.
1505 | Company Initiated | Other Circuits | Generator | Malfunctioning | None | Company Initiated Outage. Not outage related.
1506 | Company Initiated | Other Circuits | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
1507 | Company Initiated | Other Circuits | Jumper | Malfunctioning | None | Company Initiated Outage. Not outage related.
1508 | Company Initiated | Other Circuits | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1509 | Company Initiated | Other Circuits | Lightning Arrestor | Blown/failed | None | Company Initiated Outage. Not outage related.
1510 | Company Initiated | Other Circuits | Other |  | None | Company Initiated Outage. Not outage related.
1511 | Company Initiated | Other Circuits | Other | Broken | None | Company Initiated Outage. Not outage related.
1512 | Company Initiated | Other Circuits | Other | Normal | None | Company Initiated Outage. Not outage related.
1513 | Company Initiated | Other Circuits | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1514 | Company Initiated | Other Circuits | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1515 | Company Initiated | Other Circuits | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
1516 | Company Initiated | Other Circuits | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1517 | Company Initiated | Other Circuits | Regulator | Broken | None | Company Initiated Outage. Not outage related.
1518 | Company Initiated | Other Circuits | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
1519 | Company Initiated | Other Circuits | Regulator- LTC substation | Normal | None | Company Initiated Outage. Not outage related.
1520 | Company Initiated | Other Circuits | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1521 | Company Initiated | Other Circuits | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1522 | Company Initiated | Other Circuits | Transformer | Blown/failed | None | Company Initiated Outage. Not outage related.
1523 | Company Initiated | Other Circuits | Transformer | Broken | None | Company Initiated Outage. Not outage related.
1524 | Company Initiated | Other Circuits | Transformer | Deteriorated | None | Company Initiated Outage. Not outage related.
1525 | Company Initiated | Other Circuits | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
1526 | Company Initiated | Other Circuits | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1527 | Company Initiated | Personnel- company |  |  | None | Company Initiated Outage. Not outage related.
1528 | Company Initiated | Personnel- company |  | Blown/failed | None | Company Initiated Outage. Not outage related.
1529 | Company Initiated | Personnel- company |  | Broken | None | Company Initiated Outage. Not outage related.
1530 | Company Initiated | Personnel- company |  | Normal | None | Company Initiated Outage. Not outage related.
1531 | Company Initiated | Personnel- company | Bus | Normal | None | Company Initiated Outage. Not outage related.
1532 | Company Initiated | Personnel- company | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
1533 | Company Initiated | Personnel- company | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1534 | Company Initiated | Personnel- company | Conductor- Overhead |  | None | Company Initiated Outage. Not outage related.
1535 | Company Initiated | Personnel- company | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
1536 | Company Initiated | Personnel- company | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
1537 | Company Initiated | Personnel- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1538 | Company Initiated | Personnel- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1539 | Company Initiated | Personnel- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1540 | Company Initiated | Personnel- company | Conductor- Underground | Blown/failed | None | Company Initiated Outage. Not outage related.
1541 | Company Initiated | Personnel- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1542 | Company Initiated | Personnel- company | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
1543 | Company Initiated | Personnel- company | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1544 | Company Initiated | Personnel- company | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
1545 | Company Initiated | Personnel- company | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
1546 | Company Initiated | Personnel- company | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
1547 | Company Initiated | Personnel- company | Cutout- fuse holder | Arcing | None | Company Initiated Outage. Not outage related.
1548 | Company Initiated | Personnel- company | Cutout- Fused- Distribution | Normal | None | Company Initiated Outage. Not outage related.
1549 | Company Initiated | Personnel- company | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
1550 | Company Initiated | Personnel- company | Elbow | Broken | None | Company Initiated Outage. Not outage related.
1551 | Company Initiated | Personnel- company | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
1552 | Company Initiated | Personnel- company | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
1553 | Company Initiated | Personnel- company | Elbow | Normal | None | Company Initiated Outage. Not outage related.
1554 | Company Initiated | Personnel- company | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
1555 | Company Initiated | Personnel- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1556 | Company Initiated | Personnel- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1557 | Company Initiated | Personnel- company | Interrupter | Malfunctioning | None | Company Initiated Outage. Not outage related.
1558 | Company Initiated | Personnel- company | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
1559 | Company Initiated | Personnel- company | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
1560 | Company Initiated | Personnel- company | Jumper | Burned/flashed | None | Company Initiated Outage. Not outage related.
1561 | Company Initiated | Personnel- company | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1562 | Company Initiated | Personnel- company | Metering Equipment |  | None | Company Initiated Outage. Not outage related.
1563 | Company Initiated | Personnel- company | Other | Deteriorated | None | Company Initiated Outage. Not outage related.
1564 | Company Initiated | Personnel- company | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
1565 | Company Initiated | Personnel- company | Other | Normal | None | Company Initiated Outage. Not outage related.
1566 | Company Initiated | Personnel- company | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
1567 | Company Initiated | Personnel- company | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1568 | Company Initiated | Personnel- company | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
1569 | Company Initiated | Personnel- company | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
1570 | Company Initiated | Personnel- company | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
1571 | Company Initiated | Personnel- company | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1572 | Company Initiated | Personnel- company | Regulator | Blown/failed | None | Company Initiated Outage. Not outage related.
1573 | Company Initiated | Personnel- company | Regulator | Broken | None | Company Initiated Outage. Not outage related.
1574 | Company Initiated | Personnel- company | Relay | Normal | None | Company Initiated Outage. Not outage related.
1575 | Company Initiated | Personnel- company | SCADA | Normal | None | Company Initiated Outage. Not outage related.
1576 | Company Initiated | Personnel- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
1577 | Company Initiated | Personnel- company | Secondary | Burned Open | None | Company Initiated Outage. Not outage related.
1578 | Company Initiated | Personnel- company | Secondary | Deteriorated | None | Company Initiated Outage. Not outage related.
1579 | Company Initiated | Personnel- company | Secondary | Normal | None | Company Initiated Outage. Not outage related.
1580 | Company Initiated | Personnel- company | Secondary | Together | None | Company Initiated Outage. Not outage related.
1581 | Company Initiated | Personnel- company | Sectionalizer | Normal | None | Company Initiated Outage. Not outage related.
1582 | Company Initiated | Personnel- company | Service conductor | Together | None | Company Initiated Outage. Not outage related.
1583 | Company Initiated | Personnel- company | Switch (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
1584 | Company Initiated | Personnel- company | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1585 | Company Initiated | Personnel- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
1586 | Company Initiated | Personnel- company | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1587 | Company Initiated | Personnel- company | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
1588 | Company Initiated | Personnel- company | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
1589 | Company Initiated | Personnel- company | Transformer (OH) | Contaminated | None | Company Initiated Outage. Not outage related.
1590 | Company Initiated | Personnel- company | Transformer (OH) | Leaking | None | Company Initiated Outage. Not outage related.
1591 | Company Initiated | Personnel- company | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
1592 | Company Initiated | Personnel- company | Transformer (UG) |  | None | Company Initiated Outage. Not outage related.
1593 | Company Initiated | Personnel- company | Transformer (UG) | Arcing | None | Company Initiated Outage. Not outage related.
1594 | Company Initiated | Personnel- company | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1595 | Company Initiated | Personnel- company | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
1596 | Company Initiated | Personnel- company | Transformer (UG) | Deteriorated | None | Company Initiated Outage. Not outage related.
1597 | Company Initiated | Personnel- company | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
1598 | Company Initiated | Personnel- company | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1599 | Company Initiated | Return Circuit Normal | Booster | Burned/flashed | None | Company Initiated Outage. Not outage related.
1600 | Company Initiated | Return Circuit Normal | Bushing | Normal | None | Company Initiated Outage. Not outage related.
1601 | Company Initiated | Return Circuit Normal | Cable Termination(live front | Blown/failed | None | Company Initiated Outage. Not outage related.
1602 | Company Initiated | Return Circuit Normal | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
1603 | Company Initiated | Return Circuit Normal | Circuit Breaker | Burned/flashed | None | Company Initiated Outage. Not outage related.
1604 | Company Initiated | Return Circuit Normal | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1605 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
1606 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Bent or Twisted | None | Company Initiated Outage. Not outage related.
1607 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
1608 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1609 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken- wire on object | None | Company Initiated Outage. Not outage related.
1610 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
1611 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1612 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1613 | Company Initiated | Return Circuit Normal | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1614 | Company Initiated | Return Circuit Normal | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1615 | Company Initiated | Return Circuit Normal | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
1616 | Company Initiated | Return Circuit Normal | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1617 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Arcing | None | Company Initiated Outage. Not outage related.
1618 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
1619 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
1620 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1621 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Burned/flashed | None | Company Initiated Outage. Not outage related.
1622 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
1623 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
1624 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1625 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
1626 | Company Initiated | Return Circuit Normal | Customer Equipment | Normal | None | Company Initiated Outage. Not outage related.
1627 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Arcing | None | Company Initiated Outage. Not outage related.
1628 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
1629 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
1630 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
1631 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
1632 | Company Initiated | Return Circuit Normal | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
1633 | Company Initiated | Return Circuit Normal | Elbow | Broken | None | Company Initiated Outage. Not outage related.
1634 | Company Initiated | Return Circuit Normal | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
1635 | Company Initiated | Return Circuit Normal | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
1636 | Company Initiated | Return Circuit Normal | Elbow | Normal | None | Company Initiated Outage. Not outage related.
1637 | Company Initiated | Return Circuit Normal | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1638 | Company Initiated | Return Circuit Normal | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1639 | Company Initiated | Return Circuit Normal | Generator | Normal | None | Company Initiated Outage. Not outage related.
1640 | Company Initiated | Return Circuit Normal | Insulator | Broken | None | Company Initiated Outage. Not outage related.
1641 | Company Initiated | Return Circuit Normal | Insulator | Broken- wire on object | None | Company Initiated Outage. Not outage related.
1642 | Company Initiated | Return Circuit Normal | Insulator | Burned/flashed | None | Company Initiated Outage. Not outage related.
1643 | Company Initiated | Return Circuit Normal | Insulator | Normal | None | Company Initiated Outage. Not outage related.
1644 | Company Initiated | Return Circuit Normal | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
1645 | Company Initiated | Return Circuit Normal | Jumper | Broken | None | Company Initiated Outage. Not outage related.
1646 | Company Initiated | Return Circuit Normal | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
1647 | Company Initiated | Return Circuit Normal | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1648 | Company Initiated | Return Circuit Normal | Lightning Arrestor | Blown/failed | None | Company Initiated Outage. Not outage related.
1649 | Company Initiated | Return Circuit Normal | Other | Blown/failed | None | Company Initiated Outage. Not outage related.
1650 | Company Initiated | Return Circuit Normal | Other | Broken | None | Company Initiated Outage. Not outage related.
1651 | Company Initiated | Return Circuit Normal | Other | Deteriorated | None | Company Initiated Outage. Not outage related.
1652 | Company Initiated | Return Circuit Normal | Other | Normal | None | Company Initiated Outage. Not outage related.
1653 | Company Initiated | Return Circuit Normal | PGs- Kearneys | Normal | None | Company Initiated Outage. Not outage related.
1654 | Company Initiated | Return Circuit Normal | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
1655 | Company Initiated | Return Circuit Normal | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1656 | Company Initiated | Return Circuit Normal | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1657 | Company Initiated | Return Circuit Normal | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1658 | Company Initiated | Return Circuit Normal | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
1659 | Company Initiated | Return Circuit Normal | Pole-Wood | On Ground | None | Company Initiated Outage. Not outage related.
1660 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Blown/failed | None | Company Initiated Outage. Not outage related.
1661 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Broken | None | Company Initiated Outage. Not outage related.
1662 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Burned/flashed | None | Company Initiated Outage. Not outage related.
1663 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
1664 | Company Initiated | Return Circuit Normal | Recloser | Broken | None | Company Initiated Outage. Not outage related.
1665 | Company Initiated | Return Circuit Normal | Recloser | Burned/flashed | None | Company Initiated Outage. Not outage related.
1666 | Company Initiated | Return Circuit Normal | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
1667 | Company Initiated | Return Circuit Normal | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1668 | Company Initiated | Return Circuit Normal | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
1669 | Company Initiated | Return Circuit Normal | Regulator | Normal | None | Company Initiated Outage. Not outage related.
1670 | Company Initiated | Return Circuit Normal | SCADA | Normal | None | Company Initiated Outage. Not outage related.
1671 | Company Initiated | Return Circuit Normal | Secondary | Broken | None | Company Initiated Outage. Not outage related.
1672 | Company Initiated | Return Circuit Normal | Secondary | Burned/flashed | None | Company Initiated Outage. Not outage related.
1673 | Company Initiated | Return Circuit Normal | Secondary | Normal | None | Company Initiated Outage. Not outage related.
1674 | Company Initiated | Return Circuit Normal | Sectionalizer | Normal | None | Company Initiated Outage. Not outage related.
1675 | Company Initiated | Return Circuit Normal | Stepdown | Normal | None | Company Initiated Outage. Not outage related.
1676 | Company Initiated | Return Circuit Normal | Switch (OH) | Arcing | None | Company Initiated Outage. Not outage related.
1677 | Company Initiated | Return Circuit Normal | Switch (OH) | Broken | None | Company Initiated Outage. Not outage related.
1678 | Company Initiated | Return Circuit Normal | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1679 | Company Initiated | Return Circuit Normal | Switch (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1680 | Company Initiated | Return Circuit Normal | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1681 | Company Initiated | Return Circuit Normal | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
1682 | Company Initiated | Return Circuit Normal | Transformer (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
1683 | Company Initiated | Return Circuit Normal | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
1684 | Company Initiated | Return Circuit Normal | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
1685 | Company Initiated | Return Circuit Normal | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1686 | Company Initiated | Return Circuit Normal | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
1687 | Company Initiated | Return Circuit Normal | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
1688 | Company Initiated | Return Circuit Normal | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1689 | Company Initiated | Return Circuit Normal | Woodpin | Broken | None | Company Initiated Outage. Not outage related.
1690 | Environmental/ External | Earthquake | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1691 | Environmental/ External | Earthquake | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1692 | Environmental/ External | Earthquake | Other | Deteriorated | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
1693 | Environmental/ External | Earthquake | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1694 | Environmental/ External | Earthquake | Transformer |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1695 | Environmental/ External | Fire- Forest/Grass | Anchor or Guy | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1696 | Environmental/ External | Fire- Forest/Grass | Circuit Breaker | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1697 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Annealed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1698 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Broken | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1699 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1700 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1701 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Contaminated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1702 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Deteriorated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1703 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1704 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | On Ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1705 | Environmental/ External | Fire- Forest/Grass | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
1706 | Environmental/ External | Fire- Forest/Grass | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
1707 | Environmental/ External | Fire- Forest/Grass | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
1708 | Environmental/ External | Fire- Forest/Grass | Connector or Splice (OH) | Broken- wire on ground | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1709 | Environmental/ External | Fire- Forest/Grass | Connector or Splice (OH) | Broken- wire on object | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1710 | Environmental/ External | Fire- Forest/Grass | Connector or Splice (OH) | Burned/flashed | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1711 | Environmental/ External | Fire- Forest/Grass | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
1712 | Environmental/ External | Fire- Forest/Grass | Crossarm- Wood | Broken | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1713 | Environmental/ External | Fire- Forest/Grass | Crossarm- Wood | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1714 | Environmental/ External | Fire- Forest/Grass | Crossarm- Wood | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1715 | Environmental/ External | Fire- Forest/Grass | Customer Equipment | Broken | None | System hardening does not address customer equipment
1716 | Environmental/ External | Fire- Forest/Grass | Customer Equipment | Burned/flashed | None | System hardening does not address customer equipment
1717 | Environmental/ External | Fire- Forest/Grass | Customer Equipment | Malfunctioning | None | System hardening does not address customer equipment
1718 | Environmental/ External | Fire- Forest/Grass | Cutout- fuse holder | Broken | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
1719 | Environmental/ External | Fire- Forest/Grass | Cutout- fuse holder | Normal | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
1720 | Environmental/ External | Fire- Forest/Grass | Elbow | Blown/failed | All | Underground facilities = no ignition risk
1721 | Environmental/ External | Fire- Forest/Grass | Footings- Tower or Pole | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1722 | Environmental/ External | Fire- Forest/Grass | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1723 | Environmental/ External | Fire- Forest/Grass | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1724 | Environmental/ External | Fire- Forest/Grass | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1725 | Environmental/ External | Fire- Forest/Grass | Insulator | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1726 | Environmental/ External | Fire- Forest/Grass | Insulator | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1727 | Environmental/ External | Fire- Forest/Grass | Jumper | Broken | High | SECONDARY IGNITION RISK - Larger covered conductor to mostly eliminate cause and risk.
1728 | Environmental/ External | Fire- Forest/Grass | Jumper | Normal | High | SECONDARY IGNITION RISK - Larger covered conductor to mostly eliminate cause and risk.
1729 | Environmental/ External | Fire- Forest/Grass | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent.
1730 | Environmental/ External | Fire- Forest/Grass | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
1731 | Environmental/ External | Fire- Forest/Grass | Other | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1732 | Environmental/ External | Fire- Forest/Grass | Other | Burned Open | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1733 | Environmental/ External | Fire- Forest/Grass | Other | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1734 | Environmental/ External | Fire- Forest/Grass | Other | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1735 | Environmental/ External | Fire- Forest/Grass | Pole - Tower- steel | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1736 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Broken | High | SECONDARY IGNITION RISK - We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1737 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1738 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Broken- wire on object | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1739 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Burned/flashed | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1740 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Contaminated | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1741 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Deteriorated | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1742 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Normal | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1743 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | On Ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1744 | Environmental/ External | Fire- Forest/Grass | Pothead(Riser Termination) | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1745 | Environmental/ External | Fire- Forest/Grass | Pothead(Riser Termination) | Deteriorated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1746 | Environmental/ External | Fire- Forest/Grass | Recloser | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1747 | Environmental/ External | Fire- Forest/Grass | Recloser | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1748 | Environmental/ External | Fire- Forest/Grass | Recloser | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1749 | Environmental/ External | Fire- Forest/Grass | Regulator | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1750 | Environmental/ External | Fire- Forest/Grass | Regulator | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1751 | Environmental/ External | Fire- Forest/Grass | Relay | Normal | All | Covered conductor will eliminate "smoke arcing" and risk associated with this outage.
1752 | Environmental/ External | Fire- Forest/Grass | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1753 | Environmental/ External | Fire- Forest/Grass | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1754 | Environmental/ External | Fire- Forest/Grass | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1755 | Environmental/ External | Fire- Forest/Grass | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1756 | Environmental/ External | Fire- Forest/Grass | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1757 | Environmental/ External | Fire- Forest/Grass | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1758 | Environmental/ External | Fire- Forest/Grass | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1759 | Environmental/ External | Fire- Forest/Grass | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1760 | Environmental/ External | Fire- Forest/Grass | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1761 | Environmental/ External | Fire- Forest/Grass | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1762 | Environmental/ External | Fire- Forest/Grass | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1763 | Environmental/ External | Fire- Forest/Grass | Switch | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1764 | Environmental/ External | Fire- Forest/Grass | Switch | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1765 | Environmental/ External | Fire- Forest/Grass | Switch (OH) | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1766 | Environmental/ External | Fire- Forest/Grass | Switch (UG) | Normal | All | Underground facilities = no ignition risk
1767 | Environmental/ External | Fire- Forest/Grass | Transformer | Blown/failed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1768 | Environmental/ External | Fire- Forest/Grass | Transformer | Broken | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1769 | Environmental/ External | Fire- Forest/Grass | Transformer | Burned/flashed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1770 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Blown/failed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1771 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Broken | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1772 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Burned/flashed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1773 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Deteriorated | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1774 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Leaking | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1775 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Normal | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1776 | Environmental/ External | Fire- Forest/Grass | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
1777 | Environmental/ External | Fire- Forest/Grass | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
1778 | Environmental/ External | Fire- Forest/Grass | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1779 | Environmental/ External | Fire- Forest/Grass | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
1780 | Environmental/ External | Flood/Erosion | Anchor or Guy | Broken | Low | Water and Moisture limit ignition risk
1781 | Environmental/ External | Flood/Erosion | Anchor or Guy | Deteriorated | Low | Water and Moisture limit ignition risk
1782 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Arcing | Low | Water and Moisture limit ignition risk
1783 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Bent or Twisted | Low | Water and Moisture limit ignition risk
1784 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Broken | Low | Water and Moisture limit ignition risk
1785 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1786 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1787 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Burned/flashed | Low | Water and Moisture limit ignition risk
1788 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Deteriorated | Low | Water and Moisture limit ignition risk
1789 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Normal | Low | Water and Moisture limit ignition risk
1790 | Environmental/ External | Flood/Erosion | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1791 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Together | Low | Water and Moisture limit ignition risk
1792 | Environmental/ External | Flood/Erosion | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
1793 | Environmental/ External | Flood/Erosion | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
1794 | Environmental/ External | Flood/Erosion | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
1795 | Environmental/ External | Flood/Erosion | Connector or Splice (UG) | Deteriorated | All | Underground facilities = no ignition risk
1796 | Environmental/ External | Flood/Erosion | Crossarm- Wood | Broken | Low | Water and Moisture limit ignition risk
1797 | Environmental/ External | Flood/Erosion | Crossarm- Wood | Deteriorated | Low | Water and Moisture limit ignition risk
1798 | Environmental/ External | Flood/Erosion | Customer Equipment | Contaminated | None | System hardening does not address customer equipment
1799 | Environmental/ External | Flood/Erosion | Customer Equipment | Normal | None | System hardening does not address customer equipment
1800 | Environmental/ External | Flood/Erosion | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1801 | Environmental/ External | Flood/Erosion | Fuse | Blown/failed | High | Moisture and Water should eliminate Ignition Risk. Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1802 | Environmental/ External | Flood/Erosion | Fuse | Normal | High | Moisture and Water should eliminate Ignition Risk. Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1803 | Environmental/ External | Flood/Erosion | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
1804 | Environmental/ External | Flood/Erosion | Other | Arcing | Low | Water and Moisture limit ignition risk
1805 | Environmental/ External | Flood/Erosion | Other | Deteriorated | Low | Water and Moisture limit ignition risk
1806 | Environmental/ External | Flood/Erosion | Other | Normal | Low | Water and Moisture limit ignition risk
1807 | Environmental/ External | Flood/Erosion | Pole - Tower- steel | Deteriorated | Low | Water and Moisture limit ignition risk
1808 | Environmental/ External | Flood/Erosion | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1809 | Environmental/ External | Flood/Erosion | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1810 | Environmental/ External | Flood/Erosion | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1811 | Environmental/ External | Flood/Erosion | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1812 | Environmental/ External | Flood/Erosion | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1813 | Environmental/ External | Flood/Erosion | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1814 | Environmental/ External | Flood/Erosion | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1815 | Environmental/ External | Flood/Erosion | Switch | Broken | Low | Water and Moisture limit ignition risk
1816 | Environmental/ External | Flood/Erosion | Switch (OH) | Normal | Low | Water and Moisture limit ignition risk
1817 | Environmental/ External | Flood/Erosion | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1818 | Environmental/ External | Flood/Erosion | Switch (UG) | Normal | All | Underground facilities = no ignition risk
1819 | Environmental/ External | Flood/Erosion | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1820 | Environmental/ External | Flood/Erosion | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1821 | Environmental/ External | Flood/Erosion | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1822 | Environmental/ External | Flood/Erosion | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1823 | Environmental/ External | Flood/Erosion | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1824 | Environmental/ External | Flood/Erosion | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
1825 | Environmental/ External | Flood/Erosion | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
1826 | Environmental/ External | Flood/Erosion | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
1827 | Environmental/ External | Ice or snow |  | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
1828 | Environmental/ External | Ice or snow | Conductor- Overhead | Arcing | All | Ice and Snow conditions should have no ignition risk.
1829 | Environmental/ External | Ice or snow | Conductor- Overhead | Bent or Twisted | All | Ice and Snow conditions should have no ignition risk.
1830 | Environmental/ External | Ice or snow | Conductor- Overhead | Broken | All | Ice and Snow conditions should have no ignition risk.
1831 | Environmental/ External | Ice or snow | Conductor- Overhead | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1832 | Environmental/ External | Ice or snow | Conductor- Overhead | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
1833 | Environmental/ External | Ice or snow | Conductor- Overhead | Burned/flashed | All | Ice and Snow conditions should have no ignition risk.
1834 | Environmental/ External | Ice or snow | Conductor- Overhead | Normal | All | Ice and Snow conditions should have no ignition risk.
1835 | Environmental/ External | Ice or snow | Conductor- Overhead | On Ground | All | Ice and Snow conditions should have no ignition risk.
1836 | Environmental/ External | Ice or snow | Conductor- Overhead | Together | All | Ice and Snow conditions should have no ignition risk.
1837 | Environmental/ External | Ice or snow | Connector or Splice (OH) | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1838 | Environmental/ External | Ice or snow | Connector or Splice (OH) | Normal | All | Ice and Snow conditions should have no ignition risk.
1839 | Environmental/ External | Ice or snow | Crossarm- Wood | Broken | All | Ice and Snow conditions should have no ignition risk.
1840 | Environmental/ External | Ice or snow | Crossarm- Wood | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1841 | Environmental/ External | Ice or snow | Crossarm- Wood | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
1842 | Environmental/ External | Ice or snow | Fuse | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
1843 | Environmental/ External | Ice or snow | Fuse | Normal | All | Ice and Snow conditions should have no ignition risk.
1844 | Environmental/ External | Ice or snow | Insulator | Broken | All | Ice and Snow conditions should have no ignition risk.
1845 | Environmental/ External | Ice or snow | Insulator | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1846 | Environmental/ External | Ice or snow | Insulator | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
1847 | Environmental/ External | Ice or snow | Jumper | Broken | All | Ice and Snow conditions should have no ignition risk.
1848 | Environmental/ External | Ice or snow | Other | Annealed | All | Ice and Snow conditions should have no ignition risk.
1849 | Environmental/ External | Ice or snow | Pole-Wood | Broken | All | Ice and Snow conditions should have no ignition risk.
1850 | Environmental/ External | Ice or snow | Pole-Wood | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1851 | Environmental/ External | Ice or snow | Pole-Wood | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
1852 | Environmental/ External | Ice or snow | Recloser | Normal | All | Ice and Snow conditions should have no ignition risk.
1853 | Environmental/ External | Ice or snow | Secondary | Broken | All | Ice and Snow conditions should have no ignition risk.
1854 | Environmental/ External | Ice or snow | Secondary | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1855 | Environmental/ External | Ice or snow | Secondary | Deteriorated | All | Ice and Snow conditions should have no ignition risk.
1856 | Environmental/ External | Ice or snow | Service conductor | Broken | All | Ice and Snow conditions should have no ignition risk.
1857 | Environmental/ External | Ice or snow | Service conductor | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1858 | Environmental/ External | Ice or snow | Transformer | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
1859 | Environmental/ External | Ice or snow | Transformer | Broken | All | Ice and Snow conditions should have no ignition risk.
1860 | Environmental/ External | Ice or snow | Transformer | Normal | All | Ice and Snow conditions should have no ignition risk.
1861 | Environmental/ External | Ice or snow | Transformer (OH) | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
1862 | Environmental/ External | Ice or snow | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
1863 | Environmental/ External | Lightning |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1864 | Environmental/ External | Lightning |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1865 | Environmental/ External | Lightning |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1866 | Environmental/ External | Lightning |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1867 | Environmental/ External | Lightning |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1868 | Environmental/ External | Lightning | Anchor or Guy | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1869 | Environmental/ External | Lightning | Booster | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1870 | Environmental/ External | Lightning | Bushing | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1871 | Environmental/ External | Lightning | Bushing | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1872 | Environmental/ External | Lightning | Bushing | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1873 | Environmental/ External | Lightning | Capacitor | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1874 | Environmental/ External | Lightning | Capacitor | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1875 | Environmental/ External | Lightning | Circuit Breaker | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
1876 | Environmental/ External | Lightning | Circuit Breaker | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1877 | Environmental/ External | Lightning | Conductor- Overhead | Arcing | None | System Hardening will not mitigate for Environmental factors for this outage.
1878 | Environmental/ External | Lightning | Conductor- Overhead | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1879 | Environmental/ External | Lightning | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1880 | Environmental/ External | Lightning | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1881 | Environmental/ External | Lightning | Conductor- Overhead | Burned Open | None | System Hardening will not mitigate for Environmental factors for this outage.
1882 | Environmental/ External | Lightning | Conductor- Overhead | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1883 | Environmental/ External | Lightning | Conductor- Overhead | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1884 | Environmental/ External | Lightning | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1885 | Environmental/ External | Lightning | Conductor- Overhead | Together | None | System Hardening will not mitigate for Environmental factors for this outage.
1886 | Environmental/ External | Lightning | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
1887 | Environmental/ External | Lightning | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1888 | Environmental/ External | Lightning | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1889 | Environmental/ External | Lightning | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1890 | Environmental/ External | Lightning | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
1891 | Environmental/ External | Lightning | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1892 | Environmental/ External | Lightning | Crossarm- Steel | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1893 | Environmental/ External | Lightning | Crossarm- Wood | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1894 | Environmental/ External | Lightning | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1895 | Environmental/ External | Lightning | Crossarm- Wood | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1896 | Environmental/ External | Lightning | Customer Equipment | Blown/failed | None | System hardening does not address customer equipment
1897 | Environmental/ External | Lightning | Customer Equipment | Burned/flashed | None | System hardening does not address customer equipment
1898 | Environmental/ External | Lightning | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1899 | Environmental/ External | Lightning | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1900 | Environmental/ External | Lightning | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1901 | Environmental/ External | Lightning | Cutout- fuse holder | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1902 | Environmental/ External | Lightning | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1903 | Environmental/ External | Lightning | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1904 | Environmental/ External | Lightning | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1905 | Environmental/ External | Lightning | Elbow | Blown/failed | All | Underground facilities = no ignition risk
1906 | Environmental/ External | Lightning | Fuse | Arcing | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1907 | Environmental/ External | Lightning | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1908 | Environmental/ External | Lightning | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1909 | Environmental/ External | Lightning | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1910 | Environmental/ External | Lightning | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1911 | Environmental/ External | Lightning | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1912 | Environmental/ External | Lightning | Insulator | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1913 | Environmental/ External | Lightning | Insulator | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1914 | Environmental/ External | Lightning | Insulator | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1915 | Environmental/ External | Lightning | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
1916 | Environmental/ External | Lightning | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1917 | Environmental/ External | Lightning | Jumper | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1918 | Environmental/ External | Lightning | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
1919 | Environmental/ External | Lightning | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
1920 | Environmental/ External | Lightning | Lightning Arrestor | Arcing | All | We are replacing lightning arrestors with their exempt equivalent.
1921 | Environmental/ External | Lightning | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent.
1922 | Environmental/ External | Lightning | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent.
1923 | Environmental/ External | Lightning | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent.
1924 | Environmental/ External | Lightning | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
1925 | Environmental/ External | Lightning | Other | Bent or Twisted | None | System Hardening will not mitigate for Environmental factors for this outage.
1926 | Environmental/ External | Lightning | Other | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1927 | Environmental/ External | Lightning | Other | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1928 | Environmental/ External | Lightning | Other | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1929 | Environmental/ External | Lightning | Other | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
1930 | Environmental/ External | Lightning | Other | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1931 | Environmental/ External | Lightning | PGs- Kearneys | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1932 | Environmental/ External | Lightning | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1933 | Environmental/ External | Lightning | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1934 | Environmental/ External | Lightning | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1935 | Environmental/ External | Lightning | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1936 | Environmental/ External | Lightning | Pothead(Riser Termination) | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1937 | Environmental/ External | Lightning | Pothead(Riser Termination) | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1938 | Environmental/ External | Lightning | Pothead(Riser Termination) | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1939 | Environmental/ External | Lightning | Pothead/Riser Termination | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1940 | Environmental/ External | Lightning | Recloser | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1941 | Environmental/ External | Lightning | Recloser | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1942 | Environmental/ External | Lightning | Recloser | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1943 | Environmental/ External | Lightning | Recloser | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
1944 | Environmental/ External | Lightning | Recloser | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1945 | Environmental/ External | Lightning | Regulator | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1946 | Environmental/ External | Lightning | Regulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1947 | Environmental/ External | Lightning | Regulator | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1948 | Environmental/ External | Lightning | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1949 | Environmental/ External | Lightning | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1950 | Environmental/ External | Lightning | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1951 | Environmental/ External | Lightning | Sectionalizer | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1952 | Environmental/ External | Lightning | Sectionalizer | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1953 | Environmental/ External | Lightning | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1954 | Environmental/ External | Lightning | Stepdown | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1955 | Environmental/ External | Lightning | Street Light Equipment | Blown/failed | Medium | System Hardening will not address Street Lights but will address their transformers.
1956 | Environmental/ External | Lightning | Switch | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1957 | Environmental/ External | Lightning | Switch | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1958 | Environmental/ External | Lightning | Switch (OH) | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1959 | Environmental/ External | Lightning | Switch (OH) | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1960 | Environmental/ External | Lightning | Switch (UG) | Blown/failed | All | Underground facilities = no ignition risk
1961 | Environmental/ External | Lightning | Transformer |  | None | System Hardening will not mitigate for Environmental factors for this outage.
1962 | Environmental/ External | Lightning | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1963 | Environmental/ External | Lightning | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1964 | Environmental/ External | Lightning | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1965 | Environmental/ External | Lightning | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1966 | Environmental/ External | Lightning | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1967 | Environmental/ External | Lightning | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1968 | Environmental/ External | Lightning | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1969 | Environmental/ External | Lightning | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1970 | Environmental/ External | Lightning | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1971 | Environmental/ External | Lightning | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1972 | Environmental/ External | Lightning | Transformer (OH) |  | None | System Hardening will not mitigate for Environmental factors for this outage.
1973 | Environmental/ External | Lightning | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1974 | Environmental/ External | Lightning | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1975 | Environmental/ External | Lightning | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1976 | Environmental/ External | Lightning | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1977 | Environmental/ External | Lightning | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1978 | Environmental/ External | Lightning | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1979 | Environmental/ External | Lightning | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1980 | Environmental/ External | Lightning | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
1981 | Environmental/ External | Lightning | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
1982 | Environmental/ External | Lightning | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1983 | Environmental/ External | Lightning | Transformer (UG) | Deteriorated | All | Underground facilities = no ignition risk
1984 | Environmental/ External | Water | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1985 | Environmental/ External | Water | Conductor- Overhead | Contaminated | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1986 | Environmental/ External | Water | Conductor- Overhead | Normal | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1987 | Environmental/ External | Water | Conductor- Overhead | Together | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1988 | Environmental/ External | Water | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
1989 | Environmental/ External | Water | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
1990 | Environmental/ External | Water | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
1991 | Environmental/ External | Water | Crossarm- Wood | Burned/flashed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1992 | Environmental/ External | Water | Customer Equipment | Normal | None | System hardening does not address customer equipment
1993 | Environmental/ External | Water | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1994 | Environmental/ External | Water | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1995 | Environmental/ External | Water | Insulator | Arcing | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1996 | Environmental/ External | Water | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
1997 | Environmental/ External | Water | Other | Leaking | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1998 | Environmental/ External | Water | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1999 | Environmental/ External | Water | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2000 | Environmental/ External | Water | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2001 | Environmental/ External | Water | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2002 | Environmental/ External | Water | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2003 | Environmental/ External | Water | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2004 | Environmental/ External | Water | Secondary | Burned/flashed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
2005 | Environmental/ External | Water | Secondary | Normal | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
2006 | Environmental/ External | Water | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2007 | Environmental/ External | Water | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2008 | Environmental/ External | Water | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2009 | Environmental/ External | Water | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2010 | Environmental/ External | Water | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2011 | Environmental/ External | Water | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2012 | Environmental/ External | Water | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
2013 | Environmental/ External | Water | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
2014 | Environmental/ External | Water | Transformer (UG) | Leaking | All | Underground facilities = no ignition risk
2015 | Environmental/ External | Water | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
2016 | Equipment Failure/Involved | Electrical Overload |  | Arcing | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2017 | Equipment Failure/Involved | Electrical Overload |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2018 | Equipment Failure/Involved | Electrical Overload |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2019 | Equipment Failure/Involved | Electrical Overload |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2020 | Equipment Failure/Involved | Electrical Overload |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2021 | Equipment Failure/Involved | Electrical Overload | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2022 | Equipment Failure/Involved | Electrical Overload | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2023 | Equipment Failure/Involved | Electrical Overload | Booster | Broken | All | Circuit Hardening replaces boosters with voltage regulators.
2024 | Equipment Failure/Involved | Electrical Overload | Bushing |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2025 | Equipment Failure/Involved | Electrical Overload | Bushing | Broken | None | Significant external force broke the bushing. Ignition risk not mitigated.
2026 | Equipment Failure/Involved | Electrical Overload | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2027 | Equipment Failure/Involved | Electrical Overload | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2028 | Equipment Failure/Involved | Electrical Overload | Capacitor | Arcing | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2029 | Equipment Failure/Involved | Electrical Overload | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2030 | Equipment Failure/Involved | Electrical Overload | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2031 | Equipment Failure/Involved | Electrical Overload | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2032 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2033 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2034 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2035 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2036 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2037 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2038 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2039 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2040 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2041 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2042 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
2043 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
2044 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
2045 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
2046 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
2047 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2048 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2049 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2050 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2051 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2052 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2053 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2054 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2055 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | On Ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2056 | Equipment Failure/Involved | Electrical Overload | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2057 | Equipment Failure/Involved | Electrical Overload | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2058 | Equipment Failure/Involved | Electrical Overload | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2059 | Equipment Failure/Involved | Electrical Overload | CT | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2060 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
2061 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Burned Open | None | No work is being completed on customer equipment.
2062 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
2063 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
2064 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Normal | None | No work is being completed on customer equipment.
2065 | Equipment Failure/Involved | Electrical Overload | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2066 | Equipment Failure/Involved | Electrical Overload | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2067 | Equipment Failure/Involved | Electrical Overload | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2068 | Equipment Failure/Involved | Electrical Overload | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2069 | Equipment Failure/Involved | Electrical Overload | Elbow | Blown/failed | All | Underground facilities = no ignition risk
2070 | Equipment Failure/Involved | Electrical Overload | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2071 | Equipment Failure/Involved | Electrical Overload | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2072 | Equipment Failure/Involved | Electrical Overload | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2073 | Equipment Failure/Involved | Electrical Overload | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2074 | Equipment Failure/Involved | Electrical Overload | Generator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2075 | Equipment Failure/Involved | Electrical Overload | Generator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2076 | Equipment Failure/Involved | Electrical Overload | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2077 | Equipment Failure/Involved | Electrical Overload | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2078 | Equipment Failure/Involved | Electrical Overload | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2079 | Equipment Failure/Involved | Electrical Overload | Interrupter | Malfunctioning | All | Underground facilities = no ignition risk
2080 | Equipment Failure/Involved | Electrical Overload | Interrupter | Normal | All | Underground facilities = no ignition risk
2081 | Equipment Failure/Involved | Electrical Overload | Jumper | Arcing | High | Larger covered conductor to mostly eliminate cause and risk.
2082 | Equipment Failure/Involved | Electrical Overload | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
2083 | Equipment Failure/Involved | Electrical Overload | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
2084 | Equipment Failure/Involved | Electrical Overload | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
2085 | Equipment Failure/Involved | Electrical Overload | Jumper | Deteriorated | High | Larger covered conductor to mostly eliminate cause and risk.
2086 | Equipment Failure/Involved | Electrical Overload | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2087 | Equipment Failure/Involved | Electrical Overload | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2088 | Equipment Failure/Involved | Electrical Overload | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
2089 | Equipment Failure/Involved | Electrical Overload | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
2090 | Equipment Failure/Involved | Electrical Overload | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
2091 | Equipment Failure/Involved | Electrical Overload | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2092 | Equipment Failure/Involved | Electrical Overload | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2093 | Equipment Failure/Involved | Electrical Overload | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2094 | Equipment Failure/Involved | Electrical Overload | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2095 | Equipment Failure/Involved | Electrical Overload | Other | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2096 | Equipment Failure/Involved | Electrical Overload | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2097 | Equipment Failure/Involved | Electrical Overload | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2098 | Equipment Failure/Involved | Electrical Overload | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2099 | Equipment Failure/Involved | Electrical Overload | PGs- Kearneys | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2100 | Equipment Failure/Involved | Electrical Overload | PGs- Kearneys | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2101 | Equipment Failure/Involved | Electrical Overload | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2102 | Equipment Failure/Involved | Electrical Overload | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2103 | Equipment Failure/Involved | Electrical Overload | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2104 | Equipment Failure/Involved | Electrical Overload | Pothead(Riser Termination) | Arcing | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2105 | Equipment Failure/Involved | Electrical Overload | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2106 | Equipment Failure/Involved | Electrical Overload | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2107 | Equipment Failure/Involved | Electrical Overload | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2108 | Equipment Failure/Involved | Electrical Overload | Recloser | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2109 | Equipment Failure/Involved | Electrical Overload | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2110 | Equipment Failure/Involved | Electrical Overload | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2111 | Equipment Failure/Involved | Electrical Overload | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2112 | Equipment Failure/Involved | Electrical Overload | Regulator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2113 | Equipment Failure/Involved | Electrical Overload | Relay | Normal | None | Circuit Hardening will not affect substation equipment.
2114 | Equipment Failure/Involved | Electrical Overload | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2115 | Equipment Failure/Involved | Electrical Overload | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2116 | Equipment Failure/Involved | Electrical Overload | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2117 | Equipment Failure/Involved | Electrical Overload | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2118 | Equipment Failure/Involved | Electrical Overload | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2119 | Equipment Failure/Involved | Electrical Overload | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2120 | Equipment Failure/Involved | Electrical Overload | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2121 | Equipment Failure/Involved | Electrical Overload | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2122 | Equipment Failure/Involved | Electrical Overload | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2123 | Equipment Failure/Involved | Electrical Overload | Sectionalizer | Arcing | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
2124 | Equipment Failure/Involved | Electrical Overload | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2125 | Equipment Failure/Involved | Electrical Overload | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2126 | Equipment Failure/Involved | Electrical Overload | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2127 | Equipment Failure/Involved | Electrical Overload | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2128 | Equipment Failure/Involved | Electrical Overload | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2129 | Equipment Failure/Involved | Electrical Overload | Stepdown | Blown/failed | All | Underground facilities = no ignition risk
2130 | Equipment Failure/Involved | Electrical Overload | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2131 | Equipment Failure/Involved | Electrical Overload | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2132 | Equipment Failure/Involved | Electrical Overload | Switch (OH) | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2133 | Equipment Failure/Involved | Electrical Overload | Switch (OH) | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2134 | Equipment Failure/Involved | Electrical Overload | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2135 | Equipment Failure/Involved | Electrical Overload | Switch (UG) | Normal | All | Underground facilities = no ignition risk
2136 | Equipment Failure/Involved | Electrical Overload | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2137 | Equipment Failure/Involved | Electrical Overload | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2138 | Equipment Failure/Involved | Electrical Overload | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2139 | Equipment Failure/Involved | Electrical Overload | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2140 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2141 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2142 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2143 | Equipment Failure/Involved | Electrical Overload | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2144 | Equipment Failure/Involved | Electrical Overload | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2145 | Equipment Failure/Involved | Electrical Overload | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2146 | Equipment Failure/Involved | Electrical Overload | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2147 | Equipment Failure/Involved | Electrical Overload | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2148 | Equipment Failure/Involved | Electrical Overload | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2149 | Equipment Failure/Involved | Electrical Overload | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2150 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2151 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2152 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2153 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2154 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2155 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2156 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2157 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
2158 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
2159 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Deteriorated | All | UG Facilities = no ignition risk
2160 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Leaking | All | UG Facilities = no ignition risk
2161 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
2162 | Equipment Failure/Involved | Fire- pole | Anchor or Guy | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2163 | Equipment Failure/Involved | Fire- pole | Anchor or Guy | Deteriorated | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2164 | Equipment Failure/Involved | Fire- pole | Bushing | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2165 | Equipment Failure/Involved | Fire- pole | Bushing | Burned/flashed | High | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2166 | Equipment Failure/Involved | Fire- pole | Capacitor | Arcing | Low | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2167 | Equipment Failure/Involved | Fire- pole | Capacitor | Blown/failed | Low | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2168 | Equipment Failure/Involved | Fire- pole | Capacitor | Broken | Low | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2169 | Equipment Failure/Involved | Fire- pole | Capacitor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2170 | Equipment Failure/Involved | Fire- pole | Capacitor | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2171 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2172 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2173 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2174 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2175 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2176 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Normal | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2177 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2178 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Together | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2179 | Equipment Failure/Involved | Fire- pole | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
2180 | Equipment Failure/Involved | Fire- pole | Connector or Splice (OH) | Broken | High | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2181 | Equipment Failure/Involved | Fire- pole | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2182 | Equipment Failure/Involved | Fire- pole | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2183 | Equipment Failure/Involved | Fire- pole | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2184 | Equipment Failure/Involved | Fire- pole | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2185 | Equipment Failure/Involved | Fire- pole | Crossarm- Steel | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2186 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Broken | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2187 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Broken- wire on ground | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2188 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Broken- wire on object | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2189 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Burned/flashed | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2190 | Equipment Failure/Involved | Fire- pole | Cutout- fuse holder | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2191 | Equipment Failure/Involved | Fire- pole | Cutout- fuse holder | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2192 | Equipment Failure/Involved | Fire- pole | Cutout- fuse holder | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2193 | Equipment Failure/Involved | Fire- pole | Fuse | Arcing | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2194 | Equipment Failure/Involved | Fire- pole | Fuse | Blown/failed | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2195 | Equipment Failure/Involved | Fire- pole | Fuse | Burned Open | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2196 | Equipment Failure/Involved | Fire- pole | Fuse | Normal | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2197 | Equipment Failure/Involved | Fire- pole | Insulator | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2198 | Equipment Failure/Involved | Fire- pole | Insulator | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2199 | Equipment Failure/Involved | Fire- pole | Insulator | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2200 | Equipment Failure/Involved | Fire- pole | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2201 | Equipment Failure/Involved | Fire- pole | Insulator | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2202 | Equipment Failure/Involved | Fire- pole | Jumper | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2203 | Equipment Failure/Involved | Fire- pole | Jumper | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2204 | Equipment Failure/Involved | Fire- pole | Lightning Arrestor | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2205 | Equipment Failure/Involved | Fire- pole | Other | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2206 | Equipment Failure/Involved | Fire- pole | Other | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2207 | Equipment Failure/Involved | Fire- pole | Other | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2208 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2209 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2210 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2211 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2212 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2213 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Contaminated | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2214 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Deteriorated | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2215 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Normal | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2216 | Equipment Failure/Involved | Fire- pole | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2217 | Equipment Failure/Involved | Fire- pole | Pothead(Riser Termination) | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2218 | Equipment Failure/Involved | Fire- pole | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2219 | Equipment Failure/Involved | Fire- pole | Pothead/Riser Termination | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2220 | Equipment Failure/Involved | Fire- pole | Recloser | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2221 | Equipment Failure/Involved | Fire- pole | Recloser | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2222 | Equipment Failure/Involved | Fire- pole | Recloser | Malfunctioning | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2223 | Equipment Failure/Involved | Fire- pole | Recloser | Normal | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2224 | Equipment Failure/Involved | Fire- pole | Regulator | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2225 | Equipment Failure/Involved | Fire- pole | Regulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2226 | Equipment Failure/Involved | Fire- pole | Regulator | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2227 | Equipment Failure/Involved | Fire- pole | Riser | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2228 | Equipment Failure/Involved | Fire- pole | Secondary | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2229 | Equipment Failure/Involved | Fire- pole | Secondary | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2230 | Equipment Failure/Involved | Fire- pole | Secondary | Normal | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2231 | Equipment Failure/Involved | Fire- pole | Service conductor | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2232 | Equipment Failure/Involved | Fire- pole | Street Light Equipment | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2233 | Equipment Failure/Involved | Fire- pole | Switch (OH) | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2234 | Equipment Failure/Involved | Fire- pole | Switch (OH) | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2235 | Equipment Failure/Involved | Fire- pole | Transformer | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2236 | Equipment Failure/Involved | Fire- pole | Transformer | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2237 | Equipment Failure/Involved | Fire- pole | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2238 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2239 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2240 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2241 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2242 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2243 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2244 | Equipment Failure/Involved | Fire- pole | Transformer (UG) | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2245 | Equipment Failure/Involved | Fire- pole | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2246 | Equipment Failure/Involved | Other |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2247 | Equipment Failure/Involved | Other |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2248 | Equipment Failure/Involved | Other |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2249 | Equipment Failure/Involved | Other |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2250 | Equipment Failure/Involved | Other |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2251 | Equipment Failure/Involved | Other | Anchor or Guy | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2252 | Equipment Failure/Involved | Other | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2253 | Equipment Failure/Involved | Other | Anchor or Guy | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2254 | Equipment Failure/Involved | Other | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2255 | Equipment Failure/Involved | Other | Booster | Burned/flashed | All | Circuit Hardening replaces boosters with voltage regulators.
2256 | Equipment Failure/Involved | Other | Booster | Malfunctioning | All | Circuit Hardening replaces boosters with voltage regulators.
2257 | Equipment Failure/Involved | Other | Bus | Broken | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2258 | Equipment Failure/Involved | Other | Bus | Burned/flashed | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2259 | Equipment Failure/Involved | Other | Bus | Deteriorated | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2260 | Equipment Failure/Involved | Other | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2261 | Equipment Failure/Involved | Other | Bushing | Broken | None | Significant external force broke the bushing. Ignition risk not mitigated.
2262 | Equipment Failure/Involved | Other | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2263 | Equipment Failure/Involved | Other | Bushing | Deteriorated | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2264 | Equipment Failure/Involved | Other | Bushing | Leaking | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2265 | Equipment Failure/Involved | Other | Cable Termination(live front | Burned/flashed | All | Underground facilities = no ignition risk
2266 | Equipment Failure/Involved | Other | Capacitor | Arcing | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2267 | Equipment Failure/Involved | Other | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2268 | Equipment Failure/Involved | Other | Capacitor | Broken | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2269 | Equipment Failure/Involved | Other | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2270 | Equipment Failure/Involved | Other | Capacitor | Malfunctioning | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2271 | Equipment Failure/Involved | Other | Capacitor | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2272 | Equipment Failure/Involved | Other | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2273 | Equipment Failure/Involved | Other | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2274 | Equipment Failure/Involved | Other | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2275 | Equipment Failure/Involved | Other | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2276 | Equipment Failure/Involved | Other | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2277 | Equipment Failure/Involved | Other | Conductor- Overhead | Burned Open | All | Covered conductor will likely eliminate the temporary fault condition that caused this outage.
2278 | Equipment Failure/Involved | Other | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2279 | Equipment Failure/Involved | Other | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2280 | Equipment Failure/Involved | Other | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2281 | Equipment Failure/Involved | Other | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2282 | Equipment Failure/Involved | Other | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2283 | Equipment Failure/Involved | Other | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2284 | Equipment Failure/Involved | Other | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
2285 | Equipment Failure/Involved | Other | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
2286 | Equipment Failure/Involved | Other | Conductor- Underground | Broken- wire on ground | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2287 | Equipment Failure/Involved | Other | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
2288 | Equipment Failure/Involved | Other | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
2289 | Equipment Failure/Involved | Other | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
2290 | Equipment Failure/Involved | Other | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
2291 | Equipment Failure/Involved | Other | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
2292 | Equipment Failure/Involved | Other | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
2293 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2294 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Bent or Twisted | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2295 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2296 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2297 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2298 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2299 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2300 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2301 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2302 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2303 | Equipment Failure/Involved | Other | Connector or Splice (OH) | On Ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2304 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Arcing | All | Underground facilities = no ignition risk
2305 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
2306 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Broken | All | Underground facilities = no ignition risk
2307 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Burned Open | All | Underground facilities = no ignition risk
2308 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2309 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Deteriorated | All | Underground facilities = no ignition risk
2310 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Malfunctioning | All | Underground facilities = no ignition risk
2311 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
2312 | Equipment Failure/Involved | Other | Crossarm- Steel | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2313 | Equipment Failure/Involved | Other | Crossarm- Steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2314 | Equipment Failure/Involved | Other | Crossarm- Steel | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2315 | Equipment Failure/Involved | Other | Crossarm- Wood |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2316 | Equipment Failure/Involved | Other | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2317 | Equipment Failure/Involved | Other | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2318 | Equipment Failure/Involved | Other | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2319 | Equipment Failure/Involved | Other | Crossarm- Wood | Burned Open | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2320 | Equipment Failure/Involved | Other | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2321 | Equipment Failure/Involved | Other | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2322 | Equipment Failure/Involved | Other | Crossarm- Wood | Malfunctioning | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2323 | Equipment Failure/Involved | Other | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
2324 | Equipment Failure/Involved | Other | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
2325 | Equipment Failure/Involved | Other | Customer Equipment | Broken | None | No work is being completed on customer equipment.
2326 | Equipment Failure/Involved | Other | Customer Equipment | Burned Open | None | No work is being completed on customer equipment.
2327 | Equipment Failure/Involved | Other | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
2328 | Equipment Failure/Involved | Other | Customer Equipment | Deteriorated | None | No work is being completed on customer equipment.
2329 | Equipment Failure/Involved | Other | Customer Equipment | Leaking | None | No work is being completed on customer equipment.
2330 | Equipment Failure/Involved | Other | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
2331 | Equipment Failure/Involved | Other | Customer Equipment | Normal | None | No work is being completed on customer equipment.
2332 | Equipment Failure/Involved | Other | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2333 | Equipment Failure/Involved | Other | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2334 | Equipment Failure/Involved | Other | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2335 | Equipment Failure/Involved | Other | Cutout- fuse holder | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2336 | Equipment Failure/Involved | Other | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2337 | Equipment Failure/Involved | Other | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2338 | Equipment Failure/Involved | Other | Cutout- fuse holder | Deteriorated | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2339 | Equipment Failure/Involved | Other | Cutout- fuse holder | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2340 | Equipment Failure/Involved | Other | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2341 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2342 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2343 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2344 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2345 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Deteriorated | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2346 | Equipment Failure/Involved | Other | Elbow | Arcing | All | Underground facilities = no ignition risk
2347 | Equipment Failure/Involved | Other | Elbow | Blown/failed | All | Underground facilities = no ignition risk
2348 | Equipment Failure/Involved | Other | Elbow | Broken | All | Underground facilities = no ignition risk
2349 | Equipment Failure/Involved | Other | Elbow | Burned Open | All | Underground facilities = no ignition risk
2350 | Equipment Failure/Involved | Other | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
2351 | Equipment Failure/Involved | Other | Elbow | Malfunctioning | All | Underground facilities = no ignition risk
2352 | Equipment Failure/Involved | Other | Fuse | Arcing | All | Covered conductor will eliminate the line to ground connection that likely caused this outage/risk.
2353 | Equipment Failure/Involved | Other | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2354 | Equipment Failure/Involved | Other | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2355 | Equipment Failure/Involved | Other | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2356 | Equipment Failure/Involved | Other | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2357 | Equipment Failure/Involved | Other | Fuse | Deteriorated | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2358 | Equipment Failure/Involved | Other | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2359 | Equipment Failure/Involved | Other | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2360 | Equipment Failure/Involved | Other | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2361 | Equipment Failure/Involved | Other | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2362 | Equipment Failure/Involved | Other | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2363 | Equipment Failure/Involved | Other | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2364 | Equipment Failure/Involved | Other | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2365 | Equipment Failure/Involved | Other | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2366 | Equipment Failure/Involved | Other | Insulator | Contaminated | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2367 | Equipment Failure/Involved | Other | Insulator | Deteriorated | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2368 | Equipment Failure/Involved | Other | Insulator | Leaking | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2369 | Equipment Failure/Involved | Other | Insulator | Malfunctioning | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2370 | Equipment Failure/Involved | Other | Interrupter | Blown/failed | All | Underground facilities = no ignition risk
2371 | Equipment Failure/Involved | Other | Interrupter | Broken | All | Underground facilities = no ignition risk
2372 | Equipment Failure/Involved | Other | Interrupter | Burned/flashed | All | Underground facilities = no ignition risk
2373 | Equipment Failure/Involved | Other | Interrupter | Malfunctioning | All | Underground facilities = no ignition risk
2374 | Equipment Failure/Involved | Other | Jumper | Arcing | High | Larger covered conductor to mostly eliminate cause and risk.
2375 | Equipment Failure/Involved | Other | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
2376 | Equipment Failure/Involved | Other | Jumper | Blown/failed | High | Larger covered conductor to mostly eliminate cause and risk.
2377 | Equipment Failure/Involved | Other | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
2378 | Equipment Failure/Involved | Other | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2379 | Equipment Failure/Involved | Other | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
2380 | Equipment Failure/Involved | Other | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
2381 | Equipment Failure/Involved | Other | Jumper | Deteriorated | High | Larger covered conductor to mostly eliminate cause and risk.
2382 | Equipment Failure/Involved | Other | Jumper | Malfunctioning | High | Larger covered conductor to mostly eliminate cause and risk.
2383 | Equipment Failure/Involved | Other | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
2384 | Equipment Failure/Involved | Other | Lightning Arrestor | Arcing | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2385 | Equipment Failure/Involved | Other | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2386 | Equipment Failure/Involved | Other | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2387 | Equipment Failure/Involved | Other | Lightning Arrestor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2388 | Equipment Failure/Involved | Other | Lightning Arrestor | Burned Open | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2389 | Equipment Failure/Involved | Other | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2390 | Equipment Failure/Involved | Other | Lightning Arrestor | Deteriorated | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2391 | Equipment Failure/Involved | Other | Lightning Arrestor | Malfunctioning | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2392 | Equipment Failure/Involved | Other | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
2393 | Equipment Failure/Involved | Other | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
2394 | Equipment Failure/Involved | Other | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
2395 | Equipment Failure/Involved | Other | Other | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2396 | Equipment Failure/Involved | Other | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2397 | Equipment Failure/Involved | Other | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2398 | Equipment Failure/Involved | Other | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2399 | Equipment Failure/Involved | Other | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2400 | Equipment Failure/Involved | Other | Other | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2401 | Equipment Failure/Involved | Other | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2402 | Equipment Failure/Involved | Other | Other | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2403 | Equipment Failure/Involved | Other | Other | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2404 | Equipment Failure/Involved | Other | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2405 | Equipment Failure/Involved | Other | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2406 | Equipment Failure/Involved | Other | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2407 | Equipment Failure/Involved | Other | PGs- Kearneys | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2408 | Equipment Failure/Involved | Other | PGs- Kearneys | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2409 | Equipment Failure/Involved | Other | PGs- Kearneys | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2410 | Equipment Failure/Involved | Other | PGs- Kearneys | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2411 | Equipment Failure/Involved | Other | PGs- Kearneys | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2412 | Equipment Failure/Involved | Other | Pole-Wood | Arcing | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2413 | Equipment Failure/Involved | Other | Pole-Wood | Bent or Twisted | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2414 | Equipment Failure/Involved | Other | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2415 | Equipment Failure/Involved | Other | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2416 | Equipment Failure/Involved | Other | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2417 | Equipment Failure/Involved | Other | Pole-Wood | Burned Open | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2418 | Equipment Failure/Involved | Other | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2419 | Equipment Failure/Involved | Other | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2420 | Equipment Failure/Involved | Other | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2421 | Equipment Failure/Involved | Other | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2422 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Arcing | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2423 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2424 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2425 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Burned Open | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2426 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2427 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2428 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Malfunctioning | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2429 | Equipment Failure/Involved | Other | Recloser | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2430 | Equipment Failure/Involved | Other | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2431 | Equipment Failure/Involved | Other | Regulator | Arcing | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2432 | Equipment Failure/Involved | Other | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2433 | Equipment Failure/Involved | Other | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2434 | Equipment Failure/Involved | Other | Regulator | Leaking | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2435 | Equipment Failure/Involved | Other | Regulator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2436 | Equipment Failure/Involved | Other | Riser | Blown/failed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
2437 | Equipment Failure/Involved | Other | Riser | Malfunctioning | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
2438 | Equipment Failure/Involved | Other | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2439 | Equipment Failure/Involved | Other | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2440 | Equipment Failure/Involved | Other | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2441 | Equipment Failure/Involved | Other | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2442 | Equipment Failure/Involved | Other | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2443 | Equipment Failure/Involved | Other | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2444 | Equipment Failure/Involved | Other | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2445 | Equipment Failure/Involved | Other | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2446 | Equipment Failure/Involved | Other | Secondary | Leaking | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2447 | Equipment Failure/Involved | Other | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2448 | Equipment Failure/Involved | Other | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2449 | Equipment Failure/Involved | Other | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2450 | Equipment Failure/Involved | Other | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2451 | Equipment Failure/Involved | Other | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2452 | Equipment Failure/Involved | Other | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2453 | Equipment Failure/Involved | Other | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2454 | Equipment Failure/Involved | Other | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2455 | Equipment Failure/Involved | Other | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2456 | Equipment Failure/Involved | Other | Service conductor | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2457 | Equipment Failure/Involved | Other | Service conductor | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2458 | Equipment Failure/Involved | Other | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2459 | Equipment Failure/Involved | Other | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2460 | Equipment Failure/Involved | Other | Splice box | Burned Open | All | Underground facilities = no ignition risk
2461 | Equipment Failure/Involved | Other | Splice box | Leaking | All | Underground facilities = no ignition risk
2462 | Equipment Failure/Involved | Other | Switch | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2463 | Equipment Failure/Involved | Other | Switch | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2464 | Equipment Failure/Involved | Other | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2465 | Equipment Failure/Involved | Other | Switch | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2466 | Equipment Failure/Involved | Other | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2467 | Equipment Failure/Involved | Other | Switch | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2468 | Equipment Failure/Involved | Other | Switch | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2469 | Equipment Failure/Involved | Other | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2470 | Equipment Failure/Involved | Other | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2471 | Equipment Failure/Involved | Other | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2472 | Equipment Failure/Involved | Other | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2473 | Equipment Failure/Involved | Other | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2474 | Equipment Failure/Involved | Other | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2475 | Equipment Failure/Involved | Other | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2476 | Equipment Failure/Involved | Other | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2477 | Equipment Failure/Involved | Other | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2478 | Equipment Failure/Involved | Other | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2479 | Equipment Failure/Involved | Other | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2480 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2481 | Equipment Failure/Involved | Other | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2482 | Equipment Failure/Involved | Other | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2483 | Equipment Failure/Involved | Other | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2484 | Equipment Failure/Involved | Other | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2485 | Equipment Failure/Involved | Other | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2486 | Equipment Failure/Involved | Other | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2487 | Equipment Failure/Involved | Other | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2488 | Equipment Failure/Involved | Other | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
2489 | Equipment Failure/Involved | Other | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
2490 | Equipment Failure/Involved | Other | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2491 | Equipment Failure/Involved | Other | Woodpin | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
2492 | Equipment Failure/Involved | Other | Woodpin | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2493 | Equipment Failure/Involved | Overhead |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2494 | Equipment Failure/Involved | Overhead |  | Arcing | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2495 | Equipment Failure/Involved | Overhead |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2496 | Equipment Failure/Involved | Overhead |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2497 | Equipment Failure/Involved | Overhead |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2498 | Equipment Failure/Involved | Overhead |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2499 | Equipment Failure/Involved | Overhead | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2500 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2501 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2502 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2503 | Equipment Failure/Involved | Overhead | Anchor or Guy | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2504 | Equipment Failure/Involved | Overhead | Anchor or Guy | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2505 | Equipment Failure/Involved | Overhead | Anchor or Guy | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2506 | Equipment Failure/Involved | Overhead | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2507 | Equipment Failure/Involved | Overhead | Booster | Arcing | All | Circuit Hardening replaces boosters with voltage regulators.
2508 | Equipment Failure/Involved | Overhead | Booster | Blown/failed | All | Circuit Hardening replaces boosters with voltage regulators.
2509 | Equipment Failure/Involved | Overhead | Booster | Broken | All | Circuit Hardening replaces boosters with voltage regulators.
2510 | Equipment Failure/Involved | Overhead | Booster | Burned/flashed | All | Circuit Hardening replaces boosters with voltage regulators.
2511 | Equipment Failure/Involved | Overhead | Booster | Malfunctioning | All | Circuit Hardening replaces boosters with voltage regulators.
2512 | Equipment Failure/Involved | Overhead | Booster | Normal | All | Circuit Hardening replaces boosters with voltage regulators.
2513 | Equipment Failure/Involved | Overhead | Bus | Arcing | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2514 | Equipment Failure/Involved | Overhead | Bus | Blown/failed | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2515 | Equipment Failure/Involved | Overhead | Bus | Burned Open | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2516 | Equipment Failure/Involved | Overhead | Bus | Burned/flashed | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2517 | Equipment Failure/Involved | Overhead | Bus | Deteriorated | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2518 | Equipment Failure/Involved | Overhead | Bushing | Arcing | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2519 | Equipment Failure/Involved | Overhead | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2520 | Equipment Failure/Involved | Overhead | Bushing | Broken | None | Significant external force broke the bushing. Ignition risk not mitigated.
2521 | Equipment Failure/Involved | Overhead | Bushing | Burned Open | None | Significant external force broke the bushing. Ignition risk not mitigated.
2522 | Equipment Failure/Involved | Overhead | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2523 | Equipment Failure/Involved | Overhead | Bushing | Contaminated | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2524 | Equipment Failure/Involved | Overhead | Bushing | Deteriorated | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2525 | Equipment Failure/Involved | Overhead | Bushing | Leaking | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2526 | Equipment Failure/Involved | Overhead | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2527 | Equipment Failure/Involved | Overhead | Capacitor | Arcing | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2528 | Equipment Failure/Involved | Overhead | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2529 | Equipment Failure/Involved | Overhead | Capacitor | Broken | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2530 | Equipment Failure/Involved | Overhead | Capacitor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2531 | Equipment Failure/Involved | Overhead | Capacitor | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2532 | Equipment Failure/Involved | Overhead | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2533 | Equipment Failure/Involved | Overhead | Capacitor | Leaking | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2534 | Equipment Failure/Involved | Overhead | Capacitor | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2535 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2536 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2537 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2538 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2539 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2540 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2541 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2542 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2543 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2544 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2545 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2546 | Equipment Failure/Involved | Overhead | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2547 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2548 | Equipment Failure/Involved | Overhead | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
2549 | Equipment Failure/Involved | Overhead | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
2550 | Equipment Failure/Involved | Overhead | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
2551 | Equipment Failure/Involved | Overhead | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
2552 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) |  | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2553 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2554 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2555 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2556 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2557 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2558 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2559 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2560 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2561 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2562 | Equipment Failure/Involved | Overhead | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
2563 | Equipment Failure/Involved | Overhead | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2564 | Equipment Failure/Involved | Overhead | Crossarm- Steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2565 | Equipment Failure/Involved | Overhead | Crossarm- Steel | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2566 | Equipment Failure/Involved | Overhead | Crossarm- Steel | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2567 | Equipment Failure/Involved | Overhead | Crossarm- Steel | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2568 | Equipment Failure/Involved | Overhead | Crossarm- Wood |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2569 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Blown/failed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2570 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2571 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2572 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2573 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2574 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Contaminated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2575 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2576 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2577 | Equipment Failure/Involved | Overhead | CT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2578 | Equipment Failure/Involved | Overhead | CT | Deteriorated | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2579 | Equipment Failure/Involved | Overhead | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
2580 | Equipment Failure/Involved | Overhead | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
2581 | Equipment Failure/Involved | Overhead | Customer Equipment | Broken | None | No work is being completed on customer equipment.
2582 | Equipment Failure/Involved | Overhead | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
2583 | Equipment Failure/Involved | Overhead | Customer Equipment | Deteriorated | None | No work is being completed on customer equipment.
2584 | Equipment Failure/Involved | Overhead | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
2585 | Equipment Failure/Involved | Overhead | Customer Equipment | Together | None | No work is being completed on customer equipment.
2586 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2587 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2588 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2589 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2590 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2591 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2592 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2593 | Equipment Failure/Involved | Overhead | Footings- Tower or Pole | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2594 | Equipment Failure/Involved | Overhead | Footings- Tower or Pole | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2595 | Equipment Failure/Involved | Overhead | Footings- Tower or Pole | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2596 | Equipment Failure/Involved | Overhead | Fuse | Arcing | All | Covered conductor will eliminate the line to ground connection that likely caused this outage/risk.
2597 | Equipment Failure/Involved | Overhead | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2598 | Equipment Failure/Involved | Overhead | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2599 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2600 | Equipment Failure/Involved | Overhead | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2601 | Equipment Failure/Involved | Overhead | Generator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2602 | Equipment Failure/Involved | Overhead | Generator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2603 | Equipment Failure/Involved | Overhead | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2604 | Equipment Failure/Involved | Overhead | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2605 | Equipment Failure/Involved | Overhead | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2606 | Equipment Failure/Involved | Overhead | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2607 | Equipment Failure/Involved | Overhead | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2608 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2609 | Equipment Failure/Involved | Overhead | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2610 | Equipment Failure/Involved | Overhead | Jumper | Arcing | High | Larger covered conductor to mostly eliminate cause and risk.
2611 | Equipment Failure/Involved | Overhead | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
2612 | Equipment Failure/Involved | Overhead | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
2613 | Equipment Failure/Involved | Overhead | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2614 | Equipment Failure/Involved | Overhead | Jumper | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2615 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
2616 | Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
2617 | Equipment Failure/Involved | Overhead | Jumper | Deteriorated | High | Larger covered conductor to mostly eliminate cause and risk.
2618 | Equipment Failure/Involved | Overhead | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
2619 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Arcing | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2620 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2621 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2622 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2623 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2624 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2625 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2626 | Equipment Failure/Involved | Overhead | Metering Equipment |  | None | System Hardening does not address Metering facilities.
2627 | Equipment Failure/Involved | Overhead | Metering Equipment | Arcing | None | System Hardening does not address Metering facilities.
2628 | Equipment Failure/Involved | Overhead | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
2629 | Equipment Failure/Involved | Overhead | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
2630 | Equipment Failure/Involved | Overhead | Metering Equipment | Deteriorated | None | System Hardening does not address Metering facilities.
2631 | Equipment Failure/Involved | Overhead | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
2632 | Equipment Failure/Involved | Overhead | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2633 | Equipment Failure/Involved | Overhead | Other | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2634 | Equipment Failure/Involved | Overhead | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2635 | Equipment Failure/Involved | Overhead | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2636 | Equipment Failure/Involved | Overhead | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2637 | Equipment Failure/Involved | Overhead | Other | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2638 | Equipment Failure/Involved | Overhead | Other | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2639 | Equipment Failure/Involved | Overhead | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2640 | Equipment Failure/Involved | Overhead | Other | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2641 | Equipment Failure/Involved | Overhead | Other | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2642 | Equipment Failure/Involved | Overhead | Other | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2643 | Equipment Failure/Involved | Overhead | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2644 | Equipment Failure/Involved | Overhead | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2645 | Equipment Failure/Involved | Overhead | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2646 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2647 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2648 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2649 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2650 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2651 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2652 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2653 | Equipment Failure/Involved | Overhead | Pole - Tower- steel | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2654 | Equipment Failure/Involved | Overhead | Pole - Tower- steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2655 | Equipment Failure/Involved | Overhead | Pole - Tower- steel | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
2656 | Equipment Failure/Involved | Overhead | Pole - Tower- steel | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2657 | Equipment Failure/Involved | Overhead | Pole - Tower- steel | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2658 | Equipment Failure/Involved | Overhead | Pole-Wood | Blown/failed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2659 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2660 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2661 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2662 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2663 | Equipment Failure/Involved | Overhead | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2664 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2665 | Equipment Failure/Involved | Overhead | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2666 | Equipment Failure/Involved | Overhead | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2667 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Arcing | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2668 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2669 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2670 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Burned Open | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2671 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2672 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2673 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2674 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2675 | Equipment Failure/Involved | Overhead | Pothead/Riser Termination |  | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2676 | Equipment Failure/Involved | Overhead | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2677 | Equipment Failure/Involved | Overhead | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2678 | Equipment Failure/Involved | Overhead | PT/CCVT | Arcing | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2679 | Equipment Failure/Involved | Overhead | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2680 | Equipment Failure/Involved | Overhead | PT/CCVT | Burned Open | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2681 | Equipment Failure/Involved | Overhead | PT/CCVT | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2682 | Equipment Failure/Involved | Overhead | PT/CCVT | Contaminated | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2683 | Equipment Failure/Involved | Overhead | Recloser | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2684 | Equipment Failure/Involved | Overhead | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
2685 | Equipment Failure/Involved | Overhead | Recloser | Broken | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
2686 | Equipment Failure/Involved | Overhead | Recloser | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2687 | Equipment Failure/Involved | Overhead | Recloser | Leaking | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2688 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2689 | Equipment Failure/Involved | Overhead | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2690 | Equipment Failure/Involved | Overhead | Regulator | Arcing | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2691 | Equipment Failure/Involved | Overhead | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2692 | Equipment Failure/Involved | Overhead | Regulator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2693 | Equipment Failure/Involved | Overhead | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2694 | Equipment Failure/Involved | Overhead | Regulator | Leaking | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2695 | Equipment Failure/Involved | Overhead | Regulator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2696 | Equipment Failure/Involved | Overhead | Regulator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2697 | Equipment Failure/Involved | Overhead | Regulator- LTC substation | Malfunctioning | None | Circuit Hardening will not affect substation equipment.
2698 | Equipment Failure/Involved | Overhead | Relay | Malfunctioning | None | Circuit Hardening will not affect substation equipment.
2699 | Equipment Failure/Involved | Overhead | SCADA | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2700 | Equipment Failure/Involved | Overhead | Secondary |  | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2701 | Equipment Failure/Involved | Overhead | Secondary | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2702 | Equipment Failure/Involved | Overhead | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2703 | Equipment Failure/Involved | Overhead | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2704 | Equipment Failure/Involved | Overhead | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2705 | Equipment Failure/Involved | Overhead | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2706 | Equipment Failure/Involved | Overhead | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2707 | Equipment Failure/Involved | Overhead | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2708 | Equipment Failure/Involved | Overhead | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2709 | Equipment Failure/Involved | Overhead | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2710 | Equipment Failure/Involved | Overhead | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2711 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2712 | Equipment Failure/Involved | Overhead | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2713 | Equipment Failure/Involved | Overhead | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2714 | Equipment Failure/Involved | Overhead | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2715 | Equipment Failure/Involved | Overhead | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2716 | Equipment Failure/Involved | Overhead | Sectionalizer | Blown/failed | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
2717 | Equipment Failure/Involved | Overhead | Sectionalizer | Broken | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
2718 | Equipment Failure/Involved | Overhead | Sectionalizer | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
2719 | Equipment Failure/Involved | Overhead | Sectionalizer | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
2720 | Equipment Failure/Involved | Overhead | Sectionalizer | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2721 | Equipment Failure/Involved | Overhead | Service conductor |  | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2722 | Equipment Failure/Involved | Overhead | Service conductor | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2723 | Equipment Failure/Involved | Overhead | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2724 | Equipment Failure/Involved | Overhead | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2725 | Equipment Failure/Involved | Overhead | Service conductor | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2726 | Equipment Failure/Involved | Overhead | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2727 | Equipment Failure/Involved | Overhead | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2728 | Equipment Failure/Involved | Overhead | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2729 | Equipment Failure/Involved | Overhead | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2730 | Equipment Failure/Involved | Overhead | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2731 | Equipment Failure/Involved | Overhead | Service conductor | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2732 | Equipment Failure/Involved | Overhead | Service conductor | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2733 | Equipment Failure/Involved | Overhead | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2734 | Equipment Failure/Involved | Overhead | Service conductor | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2735 | Equipment Failure/Involved | Overhead | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2736 | Equipment Failure/Involved | Overhead | Stepdown | Arcing | All | Underground facilities = no ignition risk
2737 | Equipment Failure/Involved | Overhead | Stepdown | Blown/failed | All | Underground facilities = no ignition risk
2738 | Equipment Failure/Involved | Overhead | Stepdown | Broken | All | Underground facilities = no ignition risk
2739 | Equipment Failure/Involved | Overhead | Stepdown | Burned/flashed | All | Underground facilities = no ignition risk
2740 | Equipment Failure/Involved | Overhead | Stepdown | Deteriorated | All | Underground facilities = no ignition risk
2741 | Equipment Failure/Involved | Overhead | Stepdown | Normal | All | Underground facilities = no ignition risk
2742 | Equipment Failure/Involved | Overhead | Street Light Equipment | Arcing | Medium | System Hardening will not address Street Lights but will address their transformers.
2743 | Equipment Failure/Involved | Overhead | Street Light Equipment | Blown/failed | Medium | System Hardening will not address Street Lights but will address their transformers.
2744 | Equipment Failure/Involved | Overhead | Street Light Equipment | Broken | Medium | System Hardening will not address Street Lights but will address their transformers.
2745 | Equipment Failure/Involved | Overhead | Street Light Equipment | Burned/flashed | Medium | System Hardening will not address Street Lights but will address their transformers.
2746 | Equipment Failure/Involved | Overhead | Street Light Equipment | Malfunctioning | Medium | System Hardening will not address Street Lights but will address their transformers.
2747 | Equipment Failure/Involved | Overhead | Switch | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2748 | Equipment Failure/Involved | Overhead | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2749 | Equipment Failure/Involved | Overhead | Switch | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2750 | Equipment Failure/Involved | Overhead | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2751 | Equipment Failure/Involved | Overhead | Switch | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2752 | Equipment Failure/Involved | Overhead | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2753 | Equipment Failure/Involved | Overhead | Switch (OH) | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2754 | Equipment Failure/Involved | Overhead | Switch (OH) | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2755 | Equipment Failure/Involved | Overhead | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2756 | Equipment Failure/Involved | Overhead | Switch (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2757 | Equipment Failure/Involved | Overhead | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2758 | Equipment Failure/Involved | Overhead | Switch (OH) | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2759 | Equipment Failure/Involved | Overhead | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2760 | Equipment Failure/Involved | Overhead | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2761 | Equipment Failure/Involved | Overhead | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2762 | Equipment Failure/Involved | Overhead | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2763 | Equipment Failure/Involved | Overhead | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2764 | Equipment Failure/Involved | Overhead | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2765 | Equipment Failure/Involved | Overhead | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2766 | Equipment Failure/Involved | Overhead | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2767 | Equipment Failure/Involved | Overhead | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2768 | Equipment Failure/Involved | Overhead | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2769 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2770 | Equipment Failure/Involved | Overhead | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2771 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2772 | Equipment Failure/Involved | Overhead | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2773 | Equipment Failure/Involved | Overhead | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2774 | Equipment Failure/Involved | Overhead | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2775 | Equipment Failure/Involved | Overhead | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2776 | Equipment Failure/Involved | Overhead | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2777 | Equipment Failure/Involved | Overhead | Transformer (OH) |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2778 | Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2779 | Equipment Failure/Involved | Overhead | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2780 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2781 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2782 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2783 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2784 | Equipment Failure/Involved | Overhead | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2785 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2786 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2787 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2788 | Equipment Failure/Involved | Overhead | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2789 | Equipment Failure/Involved | Overhead | Transformer (UG) | Deteriorated | All | UG Facilities = no ignition risk
2790 | Equipment Failure/Involved | Overhead | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
2791 | Equipment Failure/Involved | Overhead | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2792 | Equipment Failure/Involved | Overhead | Woodpin | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
2793 | Equipment Failure/Involved | Overhead | Woodpin | Broken- wire on object | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
2794 | Equipment Failure/Involved | Overhead | Woodpin | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2795 | Equipment Failure/Involved | Overhead | Woodpin | Contaminated | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2796 | Equipment Failure/Involved | Overhead | Woodpin | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2797 | Equipment Failure/Involved | Overhead | Woodpin | Normal | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2798 | Equipment Failure/Involved | Substation | Circuit Breaker | Blown/failed | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
2799 | Equipment Failure/Involved | Substation | Circuit Breaker | Broken | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
2800 | Equipment Failure/Involved | Substation | Circuit Breaker | Contaminated | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2801 | Equipment Failure/Involved | Substation | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
2802 | Equipment Failure/Involved | Substation | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2803 | Equipment Failure/Involved | Substation | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
2804 | Equipment Failure/Involved | Substation | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2805 | Equipment Failure/Involved | Substation | CT | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2806 | Equipment Failure/Involved | Substation | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2807 | Equipment Failure/Involved | Substation | Generator | Leaking | None | Circuit Hardening will not affect substation equipment.
2808 | Equipment Failure/Involved | Substation | Generator | Normal | None | Circuit Hardening will not affect substation equipment.
2809 | Equipment Failure/Involved | Substation | Insulator | Blown/failed | none | Circuit hardening does not address substation equipment.
2810 | Equipment Failure/Involved | Substation | Insulator | Broken | none | System Hardening does not address substation equipment..
2811 | Equipment Failure/Involved | Substation | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2812 | Equipment Failure/Involved | Substation | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
2813 | Equipment Failure/Involved | Substation | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2814 | Equipment Failure/Involved | Substation | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2815 | Equipment Failure/Involved | Substation | Other | Burned Open | None | Circuit Hardening will not affect substation equipment.
2816 | Equipment Failure/Involved | Substation | Other | Burned/flashed | None | Circuit Hardening will not affect substation equipment.
2817 | Equipment Failure/Involved | Substation | Other | Leaking | None | Circuit Hardening will not affect substation equipment.
2818 | Equipment Failure/Involved | Substation | Other | Malfunctioning | None | Circuit Hardening will not affect substation equipment.
2819 | Equipment Failure/Involved | Substation | Other | Normal | None | Circuit Hardening will not affect substation equipment.
2820 | Equipment Failure/Involved | Substation | Pothead(Riser Termination) | Blown/failed | None | Substation equipment is not addressed with system hardening.
2821 | Equipment Failure/Involved | Substation | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2822 | Equipment Failure/Involved | Substation | Recloser | Normal | All | Circuit hardening does not address substation equipment.
2823 | Equipment Failure/Involved | Substation | Relay | Malfunctioning | None | Circuit Hardening will not affect substation equipment.
2824 | Equipment Failure/Involved | Substation | Relay | Normal | None | Circuit Hardening will not affect substation equipment.
2825 | Equipment Failure/Involved | Substation | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2826 | Equipment Failure/Involved | Substation | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2827 | Equipment Failure/Involved | Substation | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2828 | Equipment Failure/Involved | Substation | Stepdown | Blown/failed | None | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
2829 | Equipment Failure/Involved | Substation | Transformer | Blown/failed | None | Circuit Hardening will not affect substation equipment.
2830 | Equipment Failure/Involved | Substation | Transformer | Broken | None | Circuit Hardening will not affect substation equipment.
2831 | Equipment Failure/Involved | Substation | Transformer | Leaking | None | Circuit Hardening will not affect substation equipment.
2832 | Equipment Failure/Involved | Underground |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2833 | Equipment Failure/Involved | Underground |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2834 | Equipment Failure/Involved | Underground |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2835 | Equipment Failure/Involved | Underground | Bus | Arcing | All | UG Facilities = no ignition risk
2836 | Equipment Failure/Involved | Underground | Bus | Bent or Twisted | All | UG Facilities = no ignition risk
2837 | Equipment Failure/Involved | Underground | Bus | Blown/failed | All | UG Facilities = no ignition risk
2838 | Equipment Failure/Involved | Underground | Bus | Burned/flashed | All | UG Facilities = no ignition risk
2839 | Equipment Failure/Involved | Underground | Bus | Contaminated | All | UG Facilities = no ignition risk
2840 | Equipment Failure/Involved | Underground | Bus | Deteriorated | All | UG Facilities = no ignition risk
2841 | Equipment Failure/Involved | Underground | Bus | Normal | All | UG Facilities = no ignition risk
2842 | Equipment Failure/Involved | Underground | Bushing | Arcing | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2843 | Equipment Failure/Involved | Underground | Bushing | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2844 | Equipment Failure/Involved | Underground | Bushing | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2845 | Equipment Failure/Involved | Underground | Bushing | Burned/flashed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2846 | Equipment Failure/Involved | Underground | Bushing | Deteriorated | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2847 | Equipment Failure/Involved | Underground | Bushing | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2848 | Equipment Failure/Involved | Underground | Cable Termination(live front | Arcing | All | Underground facilities = no ignition risk
2849 | Equipment Failure/Involved | Underground | Cable Termination(live front | Blown/failed | All | Underground facilities = no ignition risk
2850 | Equipment Failure/Involved | Underground | Cable Termination(live front | Broken | All | Underground facilities = no ignition risk
2851 | Equipment Failure/Involved | Underground | Cable Termination(live front | Burned/flashed | All | Underground facilities = no ignition risk
2852 | Equipment Failure/Involved | Underground | Cable Termination(live front | Contaminated | All | Underground facilities = no ignition risk
2853 | Equipment Failure/Involved | Underground | Cable Termination(live front | Deteriorated | All | Underground facilities = no ignition risk
2854 | Equipment Failure/Involved | Underground | Cable Termination(live front | Normal | All | Underground facilities = no ignition risk
2855 | Equipment Failure/Involved | Underground | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2856 | Equipment Failure/Involved | Underground | Capacitor | Broken | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2857 | Equipment Failure/Involved | Underground | Capacitor | Burned/flashed | All | Underground facilities = no ignition risk
2858 | Equipment Failure/Involved | Underground | Capacitor | Leaking | All | Underground facilities = no ignition risk
2859 | Equipment Failure/Involved | Underground | Conductor- Overhead | Burned/flashed | All | Underground facilities = no ignition risk
2860 | Equipment Failure/Involved | Underground | Conductor- Underground |  | All | Underground facilities = no ignition risk
2861 | Equipment Failure/Involved | Underground | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
2862 | Equipment Failure/Involved | Underground | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
2863 | Equipment Failure/Involved | Underground | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
2864 | Equipment Failure/Involved | Underground | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
2865 | Equipment Failure/Involved | Underground | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
2866 | Equipment Failure/Involved | Underground | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
2867 | Equipment Failure/Involved | Underground | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2868 | Equipment Failure/Involved | Underground | Connector or Splice (UG) |  | All | Underground facilities = no ignition risk
2869 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Arcing | All | Underground facilities = no ignition risk
2870 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
2871 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Broken | All | Underground facilities = no ignition risk
2872 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2873 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Contaminated | All | Underground facilities = no ignition risk
2874 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Deteriorated | All | Underground facilities = no ignition risk
2875 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
2876 | Equipment Failure/Involved | Underground | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
2877 | Equipment Failure/Involved | Underground | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
2878 | Equipment Failure/Involved | Underground | Customer Equipment | Broken | None | No work is being completed on customer equipment.
2879 | Equipment Failure/Involved | Underground | Customer Equipment | Burned Open | None | No work is being completed on customer equipment.
2880 | Equipment Failure/Involved | Underground | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
2881 | Equipment Failure/Involved | Underground | Customer Equipment | Deteriorated | None | No work is being completed on customer equipment.
2882 | Equipment Failure/Involved | Underground | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
2883 | Equipment Failure/Involved | Underground | Customer Equipment | Normal | None | No work is being completed on customer equipment.
2884 | Equipment Failure/Involved | Underground | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2885 | Equipment Failure/Involved | Underground | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2886 | Equipment Failure/Involved | Underground | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2887 | Equipment Failure/Involved | Underground | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2888 | Equipment Failure/Involved | Underground | Elbow | Blown/failed | All | Underground facilities = no ignition risk
2889 | Equipment Failure/Involved | Underground | Elbow | Broken | All | Underground facilities = no ignition risk
2890 | Equipment Failure/Involved | Underground | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
2891 | Equipment Failure/Involved | Underground | Elbow | Contaminated | All | Underground facilities = no ignition risk
2892 | Equipment Failure/Involved | Underground | Elbow | Deteriorated | All | Underground facilities = no ignition risk
2893 | Equipment Failure/Involved | Underground | Elbow | Normal | All | Underground facilities = no ignition risk
2894 | Equipment Failure/Involved | Underground | Fuse | Arcing | All | Underground facilities = no ignition risk
2895 | Equipment Failure/Involved | Underground | Fuse | Blown/failed | All | Underground facilities = no ignition risk
2896 | Equipment Failure/Involved | Underground | Fuse | Broken | All | Underground facilities = no ignition risk
2897 | Equipment Failure/Involved | Underground | Fuse | Burned Open | All | Underground facilities = no ignition risk
2898 | Equipment Failure/Involved | Underground | Fuse | Normal | All | Underground facilities = no ignition risk
2899 | Equipment Failure/Involved | Underground | Generator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2900 | Equipment Failure/Involved | Underground | Generator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2901 | Equipment Failure/Involved | Underground | Generator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2902 | Equipment Failure/Involved | Underground | Interrupter | Arcing | All | Underground facilities = no ignition risk
2903 | Equipment Failure/Involved | Underground | Interrupter | Blown/failed | All | Underground facilities = no ignition risk
2904 | Equipment Failure/Involved | Underground | Interrupter | Broken | All | Underground facilities = no ignition risk
2905 | Equipment Failure/Involved | Underground | Interrupter | Leaking | All | Underground facilities = no ignition risk
2906 | Equipment Failure/Involved | Underground | Interrupter | Malfunctioning | All | Underground facilities = no ignition risk
2907 | Equipment Failure/Involved | Underground | Interrupter | Normal | All | Underground facilities = no ignition risk
2908 | Equipment Failure/Involved | Underground | Metering Equipment |  | None | System Hardening does not address Metering facilities.
2909 | Equipment Failure/Involved | Underground | Metering Equipment | Arcing | None | System Hardening does not address Metering facilities.
2910 | Equipment Failure/Involved | Underground | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
2911 | Equipment Failure/Involved | Underground | Metering Equipment | Broken | None | System Hardening does not address Metering facilities.
2912 | Equipment Failure/Involved | Underground | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
2913 | Equipment Failure/Involved | Underground | Other | Arcing | All | Underground facilities = no ignition risk
2914 | Equipment Failure/Involved | Underground | Other | Bent or Twisted | All | Underground facilities = no ignition risk
2915 | Equipment Failure/Involved | Underground | Other | Blown/failed | All | Underground facilities = no ignition risk
2916 | Equipment Failure/Involved | Underground | Other | Broken | All | Underground facilities = no ignition risk
2917 | Equipment Failure/Involved | Underground | Other | Burned Open | All | Underground facilities = no ignition risk
2918 | Equipment Failure/Involved | Underground | Other | Burned/flashed | All | Underground facilities = no ignition risk
2919 | Equipment Failure/Involved | Underground | Other | Contaminated | All | Underground facilities = no ignition risk
2920 | Equipment Failure/Involved | Underground | Other | Deteriorated | All | Underground facilities = no ignition risk
2921 | Equipment Failure/Involved | Underground | Other | Leaking | All | Underground facilities = no ignition risk
2922 | Equipment Failure/Involved | Underground | Other | Malfunctioning | All | Underground facilities = no ignition risk
2923 | Equipment Failure/Involved | Underground | Other | Normal | All | Underground facilities = no ignition risk
2924 | Equipment Failure/Involved | Underground | Other | Together | All | Underground facilities = no ignition risk
2925 | Equipment Failure/Involved | Underground | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2926 | Equipment Failure/Involved | Underground | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2927 | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2928 | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2929 | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2930 | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2931 | Equipment Failure/Involved | Underground | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2932 | Equipment Failure/Involved | Underground | PT/CCVT | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2933 | Equipment Failure/Involved | Underground | Recloser | Burned/flashed | None | Underground facilities = no ignition risk
2934 | Equipment Failure/Involved | Underground | Recloser | Malfunctioning | All | Underground facilities = no ignition risk
2935 | Equipment Failure/Involved | Underground | Relay | Malfunctioning | All | Underground facilities = no ignition risk
2936 | Equipment Failure/Involved | Underground | Relay | Normal | All | Underground facilities = no ignition risk
2937 | Equipment Failure/Involved | Underground | SCADA | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2938 | Equipment Failure/Involved | Underground | Secondary |  | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2939 | Equipment Failure/Involved | Underground | Secondary | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2940 | Equipment Failure/Involved | Underground | Secondary | Arcing | All | Underground facilities = no ignition risk
2941 | Equipment Failure/Involved | Underground | Secondary | Bent or Twisted | All | Underground facilities = no ignition risk
2942 | Equipment Failure/Involved | Underground | Secondary | Broken | All | Underground facilities = no ignition risk
2943 | Equipment Failure/Involved | Underground | Secondary | Burned Open | All | Underground facilities = no ignition risk
2944 | Equipment Failure/Involved | Underground | Secondary | Burned/flashed | All | Underground facilities = no ignition risk
2945 | Equipment Failure/Involved | Underground | Secondary | Contaminated | All | Underground facilities = no ignition risk
2946 | Equipment Failure/Involved | Underground | Secondary | Deteriorated | All | Underground facilities = no ignition risk
2947 | Equipment Failure/Involved | Underground | Secondary | Normal | All | Underground facilities = no ignition risk
2948 | Equipment Failure/Involved | Underground | Secondary | Together | All | Underground facilities = no ignition risk
2949 | Equipment Failure/Involved | Underground | Service conductor | Arcing | All | Underground facilities = no ignition risk
2950 | Equipment Failure/Involved | Underground | Service conductor | Blown/failed | All | Underground facilities = no ignition risk
2951 | Equipment Failure/Involved | Underground | Service conductor | Broken | All | Underground facilities = no ignition risk
2952 | Equipment Failure/Involved | Underground | Service conductor | Burned Open | All | Underground facilities = no ignition risk
2953 | Equipment Failure/Involved | Underground | Service conductor | Burned/flashed | All | Underground facilities = no ignition risk
2954 | Equipment Failure/Involved | Underground | Service conductor | Deteriorated | All | Underground facilities = no ignition risk
2955 | Equipment Failure/Involved | Underground | Service conductor | Normal | All | Underground facilities = no ignition risk
2956 | Equipment Failure/Involved | Underground | Stepdown | Arcing | All | Underground facilities = no ignition risk
2957 | Equipment Failure/Involved | Underground | Stepdown | Blown/failed | All | Underground facilities = no ignition risk
2958 | Equipment Failure/Involved | Underground | Stepdown | Broken | All | Underground facilities = no ignition risk
2959 | Equipment Failure/Involved | Underground | Stepdown | Normal | All | Underground facilities = no ignition risk
2960 | Equipment Failure/Involved | Underground | Switch | Arcing | All | Underground facilities = no ignition risk
2961 | Equipment Failure/Involved | Underground | Switch | Blown/failed | All | Underground facilities = no ignition risk
2962 | Equipment Failure/Involved | Underground | Switch | Broken | All | Underground facilities = no ignition risk
2963 | Equipment Failure/Involved | Underground | Switch | Burned/flashed | All | Underground facilities = no ignition risk
2964 | Equipment Failure/Involved | Underground | Switch | Leaking | All | Underground facilities = no ignition risk
2965 | Equipment Failure/Involved | Underground | Switch | Normal | All | Underground facilities = no ignition risk
2966 | Equipment Failure/Involved | Underground | Switch (UG) | Arcing | All | Underground facilities = no ignition risk
2967 | Equipment Failure/Involved | Underground | Switch (UG) | Blown/failed | All | Underground facilities = no ignition risk
2968 | Equipment Failure/Involved | Underground | Switch (UG) | Broken | All | Underground facilities = no ignition risk
2969 | Equipment Failure/Involved | Underground | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2970 | Equipment Failure/Involved | Underground | Switch (UG) | Leaking | All | Underground facilities = no ignition risk
2971 | Equipment Failure/Involved | Underground | Switch (UG) | Normal | All | Underground facilities = no ignition risk
2972 | Equipment Failure/Involved | Underground | Transformer | Arcing | All | Underground facilities = no ignition risk
2973 | Equipment Failure/Involved | Underground | Transformer | Blown/failed | All | Underground facilities = no ignition risk
2974 | Equipment Failure/Involved | Underground | Transformer | Broken | All | Underground facilities = no ignition risk
2975 | Equipment Failure/Involved | Underground | Transformer | Burned Open | All | Underground facilities = no ignition risk
2976 | Equipment Failure/Involved | Underground | Transformer | Burned/flashed | All | Underground facilities = no ignition risk
2977 | Equipment Failure/Involved | Underground | Transformer | Deteriorated | All | Underground facilities = no ignition risk
2978 | Equipment Failure/Involved | Underground | Transformer | Leaking | All | Underground facilities = no ignition risk
2979 | Equipment Failure/Involved | Underground | Transformer | Malfunctioning | All | Underground facilities = no ignition risk
2980 | Equipment Failure/Involved | Underground | Transformer | Normal | All | Underground facilities = no ignition risk
2981 | Equipment Failure/Involved | Underground | Transformer (OH) | Blown/failed | All | Underground facilities = no ignition risk
2982 | Equipment Failure/Involved | Underground | Transformer (OH) | Broken | All | Underground facilities = no ignition risk
2983 | Equipment Failure/Involved | Underground | Transformer (OH) | Leaking | All | Underground facilities = no ignition risk
2984 | Equipment Failure/Involved | Underground | Transformer (UG) | Arcing | All | UG Facilities = no ignition risk
2985 | Equipment Failure/Involved | Underground | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
2986 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
2987 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken- wire on ground | All | UG Facilities = no ignition risk
2988 | Equipment Failure/Involved | Underground | Transformer (UG) | Burned/flashed | All | UG Facilities = no ignition risk
2989 | Equipment Failure/Involved | Underground | Transformer (UG) | Contaminated | All | UG Facilities = no ignition risk
2990 | Equipment Failure/Involved | Underground | Transformer (UG) | Deteriorated | All | UG Facilities = no ignition risk
2991 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | All | UG Facilities = no ignition risk
2992 | Equipment Failure/Involved | Underground | Transformer (UG) | Malfunctioning | All | UG Facilities = no ignition risk
2993 | Equipment Failure/Involved | Underground | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
2994 | Unknown Cause |  |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2995 | Unknown Cause | Patrol - found nothing |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2996 | Unknown Cause | Patrol - found nothing |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2997 | Unknown Cause | Patrol - found nothing |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2998 | Unknown Cause | Patrol - found nothing |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2999 | Unknown Cause | Patrol - found nothing |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3000 | Unknown Cause | Patrol - found nothing | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3001 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3002 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3003 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3004 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3005 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3006 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3007 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3008 | Unknown Cause | Patrol - found nothing | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
3009 | Unknown Cause | Patrol - found nothing | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
3010 | Unknown Cause | Patrol - found nothing | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
3011 | Unknown Cause | Patrol - found nothing | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3012 | Unknown Cause | Patrol - found nothing | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3013 | Unknown Cause | Patrol - found nothing | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3014 | Unknown Cause | Patrol - found nothing | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
3015 | Unknown Cause | Patrol - found nothing | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3016 | Unknown Cause | Patrol - found nothing | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3017 | Unknown Cause | Patrol - found nothing | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3018 | Unknown Cause | Patrol - found nothing | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3019 | Unknown Cause | Patrol - found nothing | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3020 | Unknown Cause | Patrol - found nothing | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3021 | Unknown Cause | Patrol - found nothing | Interrupter |  | All | Underground facilities = no ignition risk
3022 | Unknown Cause | Patrol - found nothing | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
3023 | Unknown Cause | Patrol - found nothing | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3024 | Unknown Cause | Patrol - found nothing | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3025 | Unknown Cause | Patrol - found nothing | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3026 | Unknown Cause | Patrol - found nothing | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3027 | Unknown Cause | Patrol - found nothing | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3028 | Unknown Cause | Patrol - found nothing | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3029 | Unknown Cause | Patrol - found nothing | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3030 | Unknown Cause | Patrol - found nothing | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3031 | Unknown Cause | Patrol - found nothing | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3032 | Unknown Cause | Patrol - found nothing | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
3033 | Unknown Cause | Patrol - found nothing | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3034 | Unknown Cause | Patrol - found nothing | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3035 | Unknown Cause | Patrol - found nothing | Sectionalizer | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3036 | Unknown Cause | Patrol - found nothing | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3037 | Unknown Cause | Patrol - found nothing | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3038 | Unknown Cause | Patrol - found nothing | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3039 | Unknown Cause | Patrol - found nothing | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3040 | Unknown Cause | Patrol - found nothing | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3041 | Unknown Cause | Patrol - found nothing | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3042 | Unknown Cause | Patrol - found nothing | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3043 | Unknown Cause | Patrol - found nothing | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3044 | Unknown Cause | Patrol - found nothing | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3045 | Unknown Cause | Patrol - found nothing | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3046 | Unknown Cause | Patrol - not conducted |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3047 | Unknown Cause | Patrol - not conducted |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3048 | Unknown Cause | Patrol - not conducted |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3049 | Unknown Cause | Patrol - not conducted |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3050 | Unknown Cause | Patrol - not conducted |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3051 | Unknown Cause | Patrol - not conducted | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
3052 | Unknown Cause | Patrol - not conducted | Circuit Breaker | Normal | All | Covered conductor will likely eliminate the temporary fault condition that caused this outage.
3053 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3054 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3055 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3056 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3057 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3058 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3059 | Unknown Cause | Patrol - not conducted | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
3060 | Unknown Cause | Patrol - not conducted | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3061 | Unknown Cause | Patrol - not conducted | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3062 | Unknown Cause | Patrol - not conducted | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3063 | Unknown Cause | Patrol - not conducted | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3064 | Unknown Cause | Patrol - not conducted | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3065 | Unknown Cause | Patrol - not conducted | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3066 | Unknown Cause | Patrol - not conducted | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3067 | Unknown Cause | Patrol - not conducted | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3068 | Unknown Cause | Patrol - not conducted | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3069 | Unknown Cause | Patrol - not conducted | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3070 | Unknown Cause | Patrol - not conducted | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3071 | Unknown Cause | Patrol - not conducted | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3072 | Unknown Cause | Patrol - not conducted | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3073 | Unknown Cause | Patrol - not conducted | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3074 | Vegetation | Other ground vegetation |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3075 | Vegetation | Other ground vegetation | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3076 | Vegetation | Other ground vegetation | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3077 | Vegetation | Other ground vegetation | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3078 | Vegetation | Other ground vegetation | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3079 | Vegetation | Other ground vegetation | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3080 | Vegetation | Other ground vegetation | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3081 | Vegetation | Other ground vegetation | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3082 | Vegetation | Other ground vegetation | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
3083 | Vegetation | Other ground vegetation | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
3084 | Vegetation | Other ground vegetation | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3085 | Vegetation | Other ground vegetation | Crossarm- Wood | Contaminated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3086 | Vegetation | Other ground vegetation | Customer Equipment | Contaminated | None | No work is being completed on customer equipment.
3087 | Vegetation | Other ground vegetation | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3088 | Vegetation | Other ground vegetation | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3089 | Vegetation | Other ground vegetation | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3090 | Vegetation | Other ground vegetation | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3091 | Vegetation | Other ground vegetation | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3092 | Vegetation | Other ground vegetation | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3093 | Vegetation | Other ground vegetation | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3094 | Vegetation | Other ground vegetation | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3095 | Vegetation | Other ground vegetation | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3096 | Vegetation | Other ground vegetation | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3097 | Vegetation | Other ground vegetation | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3098 | Vegetation | Other ground vegetation | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3099 | Vegetation | Other ground vegetation | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3100 | Vegetation | Other ground vegetation | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3101 | Vegetation | Other ground vegetation | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3102 | Vegetation | Other ground vegetation | Street Light Equipment | Blown/failed | Medium | System Hardening will not address Street Lights but will address their transformers.
3103 | Vegetation | Other ground vegetation | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3104 | Vegetation | Other ground vegetation | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3105 | Vegetation | Other ground vegetation | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3106 | Vegetation | Other ground vegetation | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3107 | Vegetation | Other ground vegetation | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
3108 | Vegetation | Other ground vegetation | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
3109 | Vegetation | Other ground vegetation | Transformer (UG) | Burned/flashed | All | UG Facilities = no ignition risk
3110 | Vegetation | Other ground vegetation | Transformer (UG) | Contaminated | All | UG Facilities = no ignition risk
3111 | Vegetation | Other ground vegetation | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
3112 | Vegetation | Tree - bark fell into line |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3113 | Vegetation | Tree - bark fell into line |  | Arcing | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3114 | Vegetation | Tree - bark fell into line |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3115 | Vegetation | Tree - bark fell into line |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3116 | Vegetation | Tree - bark fell into line | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3117 | Vegetation | Tree - bark fell into line | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3118 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3119 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3120 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3121 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3122 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3123 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3124 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3125 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3126 | Vegetation | Tree - bark fell into line | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3127 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3128 | Vegetation | Tree - bark fell into line | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
3129 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3130 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3131 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3132 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3133 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3134 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3135 | Vegetation | Tree - bark fell into line | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3136 | Vegetation | Tree - bark fell into line | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3137 | Vegetation | Tree - bark fell into line | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3138 | Vegetation | Tree - bark fell into line | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3139 | Vegetation | Tree - bark fell into line | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3140 | Vegetation | Tree - bark fell into line | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3141 | Vegetation | Tree - bark fell into line | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3142 | Vegetation | Tree - bark fell into line | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3143 | Vegetation | Tree - bark fell into line | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3144 | Vegetation | Tree - bark fell into line | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3145 | Vegetation | Tree - bark fell into line | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3146 | Vegetation | Tree - bark fell into line | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3147 | Vegetation | Tree - bark fell into line | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3148 | Vegetation | Tree - bark fell into line | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3149 | Vegetation | Tree - bark fell into line | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3150 | Vegetation | Tree - bark fell into line | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3151 | Vegetation | Tree - bark fell into line | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3152 | Vegetation | Tree - bark fell into line | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3153 | Vegetation | Tree - bark fell into line | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3154 | Vegetation | Tree - bark fell into line | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3155 | Vegetation | Tree - bark fell into line | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3156 | Vegetation | Tree - bark fell into line | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
3157 | Vegetation | Tree - bark fell into line | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3158 | Vegetation | Tree - bark fell into line | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3159 | Vegetation | Tree - bark fell into line | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3160 | Vegetation | Tree - bark fell into line | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3161 | Vegetation | Tree - bark fell into line | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3162 | Vegetation | Tree - bark fell into line | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3163 | Vegetation | Tree - bark fell into line | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3164 | Vegetation | Tree - bark fell into line | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3165 | Vegetation | Tree - bark fell into line | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3166 | Vegetation | Tree - bark fell into line | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3167 | Vegetation | Tree - bark fell into line | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3168 | Vegetation | Tree - bark fell into line | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3169 | Vegetation | Tree - bark fell into line | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3170 | Vegetation | Tree - bark fell into line | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3171 | Vegetation | Tree - bark fell into line | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3172 | Vegetation | Tree - bark fell into line | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3173 | Vegetation | Tree - bark fell into line | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3174 | Vegetation | Tree - bark fell into line | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3175 | Vegetation | Tree - bark fell into line | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3176 | Vegetation | Tree - bark fell into line | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3177 | Vegetation | Tree - bark fell into line | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3178 | Vegetation | Tree - branch fell on line |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3179 | Vegetation | Tree - branch fell on line |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3180 | Vegetation | Tree - branch fell on line |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3181 | Vegetation | Tree - branch fell on line |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3182 | Vegetation | Tree - branch fell on line |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3183 | Vegetation | Tree - branch fell on line | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3184 | Vegetation | Tree - branch fell on line | Anchor or Guy | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3185 | Vegetation | Tree - branch fell on line | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3186 | Vegetation | Tree - branch fell on line | Bushing | Broken | None | Significant external force broke the bushing. Ignition risk not mitigated.
3187 | Vegetation | Tree - branch fell on line | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
3188 | Vegetation | Tree - branch fell on line | Capacitor | Arcing | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
3189 | Vegetation | Tree - branch fell on line | Capacitor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3190 | Vegetation | Tree - branch fell on line | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
3191 | Vegetation | Tree - branch fell on line | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3192 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3193 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3194 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3195 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3196 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3197 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3198 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3199 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3200 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3201 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3202 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3203 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3204 | Vegetation | Tree - branch fell on line | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3205 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3206 | Vegetation | Tree - branch fell on line | Conductor- Underground |  | All | Underground facilities = no ignition risk
3207 | Vegetation | Tree - branch fell on line | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
3208 | Vegetation | Tree - branch fell on line | Conductor- Underground | Together | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3209 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3210 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3211 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3212 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3213 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3214 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3215 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3216 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3217 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3218 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3219 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3220 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3221 | Vegetation | Tree - branch fell on line | Customer Equipment | Broken | None | No work is being completed on customer equipment.
3222 | Vegetation | Tree - branch fell on line | Customer Equipment | Broken- wire on ground | None | No work is being completed on customer equipment.
3223 | Vegetation | Tree - branch fell on line | Customer Equipment | Normal | None | No work is being completed on customer equipment.
3224 | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3225 | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3226 | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3227 | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3228 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3229 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3230 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3231 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3232 | Vegetation | Tree - branch fell on line | Elbow |  | All | Underground facilities = no ignition risk
3233 | Vegetation | Tree - branch fell on line | Fuse | Arcing | All | Covered conductor will eliminate the line to ground connection that likely caused this outage/risk.
3234 | Vegetation | Tree - branch fell on line | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3235 | Vegetation | Tree - branch fell on line | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3236 | Vegetation | Tree - branch fell on line | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3237 | Vegetation | Tree - branch fell on line | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3238 | Vegetation | Tree - branch fell on line | Fuse | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3239 | Vegetation | Tree - branch fell on line | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3240 | Vegetation | Tree - branch fell on line | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3241 | Vegetation | Tree - branch fell on line | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3242 | Vegetation | Tree - branch fell on line | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3243 | Vegetation | Tree - branch fell on line | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3244 | Vegetation | Tree - branch fell on line | Jumper |  | High | Larger covered conductor to mostly eliminate cause and risk.
3245 | Vegetation | Tree - branch fell on line | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
3246 | Vegetation | Tree - branch fell on line | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
3247 | Vegetation | Tree - branch fell on line | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3248 | Vegetation | Tree - branch fell on line | Jumper | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3249 | Vegetation | Tree - branch fell on line | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3250 | Vegetation | Tree - branch fell on line | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
3251 | Vegetation | Tree - branch fell on line | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3252 | Vegetation | Tree - branch fell on line | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3253 | Vegetation | Tree - branch fell on line | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3254 | Vegetation | Tree - branch fell on line | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3255 | Vegetation | Tree - branch fell on line | Other | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3256 | Vegetation | Tree - branch fell on line | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3257 | Vegetation | Tree - branch fell on line | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3258 | Vegetation | Tree - branch fell on line | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3259 | Vegetation | Tree - branch fell on line | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3260 | Vegetation | Tree - branch fell on line | Other | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3261 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3262 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3263 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3264 | Vegetation | Tree - branch fell on line | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3265 | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3266 | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3267 | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3268 | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3269 | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3270 | Vegetation | Tree - branch fell on line | Pothead/Riser Termination | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3271 | Vegetation | Tree - branch fell on line | Recloser | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3272 | Vegetation | Tree - branch fell on line | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3273 | Vegetation | Tree - branch fell on line | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3274 | Vegetation | Tree - branch fell on line | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3275 | Vegetation | Tree - branch fell on line | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3276 | Vegetation | Tree - branch fell on line | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3277 | Vegetation | Tree - branch fell on line | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3278 | Vegetation | Tree - branch fell on line | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3279 | Vegetation | Tree - branch fell on line | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3280 | Vegetation | Tree - branch fell on line | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3281 | Vegetation | Tree - branch fell on line | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3282 | Vegetation | Tree - branch fell on line | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3283 | Vegetation | Tree - branch fell on line | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3284 | Vegetation | Tree - branch fell on line | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3285 | Vegetation | Tree - branch fell on line | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3286 | Vegetation | Tree - branch fell on line | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3287 | Vegetation | Tree - branch fell on line | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3288 | Vegetation | Tree - branch fell on line | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3289 | Vegetation | Tree - branch fell on line | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3290 | Vegetation | Tree - branch fell on line | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3291 | Vegetation | Tree - branch fell on line | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3292 | Vegetation | Tree - branch fell on line | Service conductor | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3293 | Vegetation | Tree - branch fell on line | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3294 | Vegetation | Tree - branch fell on line | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3295 | Vegetation | Tree - branch fell on line | Switch (OH) | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3296 | Vegetation | Tree - branch fell on line | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3297 | Vegetation | Tree - branch fell on line | Switch (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3298 | Vegetation | Tree - branch fell on line | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3299 | Vegetation | Tree - branch fell on line | Switch (UG) | Normal | All | Underground facilities = no ignition risk
3300 | Vegetation | Tree - branch fell on line | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3301 | Vegetation | Tree - branch fell on line | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3302 | Vegetation | Tree - branch fell on line | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3303 | Vegetation | Tree - branch fell on line | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3304 | Vegetation | Tree - branch fell on line | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3305 | Vegetation | Tree - branch fell on line | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3306 | Vegetation | Tree - branch fell on line | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3307 | Vegetation | Tree - branch fell on line | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3308 | Vegetation | Tree - branch fell on line | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3309 | Vegetation | Tree - branch fell on line | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3310 | Vegetation | Tree - branch fell on line | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3311 | Vegetation | Tree - branch fell on line | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3312 | Vegetation | Tree - branch fell on line | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3313 | Vegetation | Tree - branch fell on line | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3314 | Vegetation | Tree - branch fell on line | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3315 | Vegetation | Tree - branch fell on line | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3316 | Vegetation | Tree - branch fell on line | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3317 | Vegetation | Tree - branch fell on line | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3318 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3319 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3320 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3321 | Vegetation | Tree - branch fell on line | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3322 | Vegetation | Tree - branch fell on line | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3323 | Vegetation | Tree - branch fell on line | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3324 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3325 | Vegetation | Tree - branch fell on line | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
3326 | Vegetation | Tree - branch fell on line | Transformer (UG) | Leaking | All | UG Facilities = no ignition risk
3327 | Vegetation | Tree - branch fell on line | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3328 | Vegetation | Tree - branch fell on line | Woodpin | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
3329 | Vegetation | Tree - cutting- 3rd party | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3330 | Vegetation | Tree - cutting- 3rd party | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3331 | Vegetation | Tree - cutting- 3rd party | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3332 | Vegetation | Tree - cutting- PG&E contractor | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3333 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3334 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3335 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3336 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3337 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3338 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3339 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3340 | Vegetation | Tree - cutting- PG&E contractor | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3341 | Vegetation | Tree - cutting- PG&E contractor | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3342 | Vegetation | Tree - cutting- PG&E contractor | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3343 | Vegetation | Tree - cutting- PG&E contractor | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3344 | Vegetation | Tree - cutting- PG&E contractor | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3345 | Vegetation | Tree - cutting- PG&E contractor | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3346 | Vegetation | Tree - cutting- PG&E contractor | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3347 | Vegetation | Tree - cutting- PG&E contractor | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3348 | Vegetation | Tree - cutting- PG&E contractor | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3349 | Vegetation | Tree - cutting- PG&E contractor | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3350 | Vegetation | Tree - cutting- PG&E contractor | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3351 | Vegetation | Tree - cutting- PG&E contractor | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3352 | Vegetation | Tree - cutting- PG&E contractor | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3353 | Vegetation | Tree - cutting- PG&E contractor | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3354 | Vegetation | Tree - cutting- PG&E contractor | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3355 | Vegetation | Tree - cutting- PG&E contractor | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3356 | Vegetation | Tree - cutting- PG&E contractor | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3357 | Vegetation | Tree - cutting- PG&E contractor | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3358 | Vegetation | Tree - cutting- PG&E contractor | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3359 | Vegetation | Tree - cutting- PG&E contractor | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3360 | Vegetation | Tree - cutting- PG&E contractor | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3361 | Vegetation | Tree - fell into line |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3362 | Vegetation | Tree - fell into line |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3363 | Vegetation | Tree - fell into line |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3364 | Vegetation | Tree - fell into line |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3365 | Vegetation | Tree - fell into line |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3366 | Vegetation | Tree - fell into line | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3367 | Vegetation | Tree - fell into line | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3368 | Vegetation | Tree - fell into line | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3369 | Vegetation | Tree - fell into line | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3370 | Vegetation | Tree - fell into line | Bushing | Broken | None | Significant external force broke the bushing. Ignition risk not mitigated.
3371 | Vegetation | Tree - fell into line | Bushing | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3372 | Vegetation | Tree - fell into line | Capacitor | Broken | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
3373 | Vegetation | Tree - fell into line | Capacitor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3374 | Vegetation | Tree - fell into line | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
3375 | Vegetation | Tree - fell into line | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
3376 | Vegetation | Tree - fell into line | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3377 | Vegetation | Tree - fell into line | Conductor- Overhead |  | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3378 | Vegetation | Tree - fell into line | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3379 | Vegetation | Tree - fell into line | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3380 | Vegetation | Tree - fell into line | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3381 | Vegetation | Tree - fell into line | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3382 | Vegetation | Tree - fell into line | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3383 | Vegetation | Tree - fell into line | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3384 | Vegetation | Tree - fell into line | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3385 | Vegetation | Tree - fell into line | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3386 | Vegetation | Tree - fell into line | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3387 | Vegetation | Tree - fell into line | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3388 | Vegetation | Tree - fell into line | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3389 | Vegetation | Tree - fell into line | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3390 | Vegetation | Tree - fell into line | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3391 | Vegetation | Tree - fell into line | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3392 | Vegetation | Tree - fell into line | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
3393 | Vegetation | Tree - fell into line | Conductor- Underground | Broken- wire on ground | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3394 | Vegetation | Tree - fell into line | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
3395 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3396 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3397 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3398 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3399 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3400 | Vegetation | Tree - fell into line | Crossarm- Steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3401 | Vegetation | Tree - fell into line | Crossarm- Steel | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3402 | Vegetation | Tree - fell into line | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3403 | Vegetation | Tree - fell into line | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3404 | Vegetation | Tree - fell into line | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3405 | Vegetation | Tree - fell into line | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3406 | Vegetation | Tree - fell into line | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3407 | Vegetation | Tree - fell into line | Customer Equipment | Broken | None | No work is being completed on customer equipment.
3408 | Vegetation | Tree - fell into line | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
3409 | Vegetation | Tree - fell into line | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
3410 | Vegetation | Tree - fell into line | Customer Equipment | On Ground | None | No work is being completed on customer equipment.
3411 | Vegetation | Tree - fell into line | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3412 | Vegetation | Tree - fell into line | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3413 | Vegetation | Tree - fell into line | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3414 | Vegetation | Tree - fell into line | Cutout- fuse holder | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3415 | Vegetation | Tree - fell into line | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3416 | Vegetation | Tree - fell into line | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3417 | Vegetation | Tree - fell into line | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3418 | Vegetation | Tree - fell into line | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3419 | Vegetation | Tree - fell into line | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3420 | Vegetation | Tree - fell into line | Footings- Tower or Pole | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3421 | Vegetation | Tree - fell into line | Fuse | Arcing | All | Covered conductor will eliminate the line to ground connection that likely caused this outage/risk.
3422 | Vegetation | Tree - fell into line | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3423 | Vegetation | Tree - fell into line | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3424 | Vegetation | Tree - fell into line | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3425 | Vegetation | Tree - fell into line | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3426 | Vegetation | Tree - fell into line | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3427 | Vegetation | Tree - fell into line | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3428 | Vegetation | Tree - fell into line | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3429 | Vegetation | Tree - fell into line | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3430 | Vegetation | Tree - fell into line | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
3431 | Vegetation | Tree - fell into line | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3432 | Vegetation | Tree - fell into line | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3433 | Vegetation | Tree - fell into line | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
3434 | Vegetation | Tree - fell into line | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
3435 | Vegetation | Tree - fell into line | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3436 | Vegetation | Tree - fell into line | Metering Equipment | Broken | None | System Hardening does not address Metering facilities.
3437 | Vegetation | Tree - fell into line | Other | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3438 | Vegetation | Tree - fell into line | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3439 | Vegetation | Tree - fell into line | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3440 | Vegetation | Tree - fell into line | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3441 | Vegetation | Tree - fell into line | Other | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3442 | Vegetation | Tree - fell into line | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3443 | Vegetation | Tree - fell into line | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3444 | Vegetation | Tree - fell into line | PGs- Kearneys | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3445 | Vegetation | Tree - fell into line | Pole - Tower- steel | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
3446 | Vegetation | Tree - fell into line | Pole - Tower- steel | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3447 | Vegetation | Tree - fell into line | Pole - Tower- steel | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3448 | Vegetation | Tree - fell into line | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3449 | Vegetation | Tree - fell into line | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3450 | Vegetation | Tree - fell into line | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3451 | Vegetation | Tree - fell into line | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3452 | Vegetation | Tree - fell into line | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3453 | Vegetation | Tree - fell into line | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3454 | Vegetation | Tree - fell into line | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3455 | Vegetation | Tree - fell into line | Pole-Wood | Together | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3456 | Vegetation | Tree - fell into line | Pothead(Riser Termination) | Arcing | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3457 | Vegetation | Tree - fell into line | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3458 | Vegetation | Tree - fell into line | Recloser | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3459 | Vegetation | Tree - fell into line | Recloser | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3460 | Vegetation | Tree - fell into line | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3461 | Vegetation | Tree - fell into line | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3462 | Vegetation | Tree - fell into line | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3463 | Vegetation | Tree - fell into line | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3464 | Vegetation | Tree - fell into line | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3465 | Vegetation | Tree - fell into line | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3466 | Vegetation | Tree - fell into line | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3467 | Vegetation | Tree - fell into line | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3468 | Vegetation | Tree - fell into line | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3469 | Vegetation | Tree - fell into line | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3470 | Vegetation | Tree - fell into line | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3471 | Vegetation | Tree - fell into line | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3472 | Vegetation | Tree - fell into line | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3473 | Vegetation | Tree - fell into line | Sectionalizer | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3474 | Vegetation | Tree - fell into line | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3475 | Vegetation | Tree - fell into line | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3476 | Vegetation | Tree - fell into line | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3477 | Vegetation | Tree - fell into line | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3478 | Vegetation | Tree - fell into line | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3479 | Vegetation | Tree - fell into line | Service conductor | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3480 | Vegetation | Tree - fell into line | Service conductor | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3481 | Vegetation | Tree - fell into line | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3482 | Vegetation | Tree - fell into line | Service conductor | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3483 | Vegetation | Tree - fell into line | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3484 | Vegetation | Tree - fell into line | Switch | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3485 | Vegetation | Tree - fell into line | Switch | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3486 | Vegetation | Tree - fell into line | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3487 | Vegetation | Tree - fell into line | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3488 | Vegetation | Tree - fell into line | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3489 | Vegetation | Tree - fell into line | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3490 | Vegetation | Tree - fell into line | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3491 | Vegetation | Tree - fell into line | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3492 | Vegetation | Tree - fell into line | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3493 | Vegetation | Tree - fell into line | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3494 | Vegetation | Tree - fell into line | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3495 | Vegetation | Tree - fell into line | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3496 | Vegetation | Tree - fell into line | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3497 | Vegetation | Tree - fell into line | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3498 | Vegetation | Tree - fell into line | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3499 | Vegetation | Tree - fell into line | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3500 | Vegetation | Tree - fell into line | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3501 | Vegetation | Tree - fell into line | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3502 | Vegetation | Tree - fell into line | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3503 | Vegetation | Tree - fell into line | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3504 | Vegetation | Tree - fell into line | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3505 | Vegetation | Tree - fell into line | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3506 | Vegetation | Tree - fell into line | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3507 | Vegetation | Tree - fell into line | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3508 | Vegetation | Tree - fell into line | Transformer (OH) | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3509 | Vegetation | Tree - fell into line | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3510 | Vegetation | Tree - fell into line | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3511 | Vegetation | Tree - fell into line | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3512 | Vegetation | Tree - fell into line | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3513 | Vegetation | Tree - fell into line | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3514 | Vegetation | Tree - fell into line | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
3515 | Vegetation | Tree - fell into line | Transformer (UG) | Leaking | All | UG Facilities = no ignition risk
3516 | Vegetation | Tree - fell into line | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
3517 | Vegetation | Tree - fell into line | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3518 | Vegetation | Tree - fell into line | Woodpin | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
3519 | Vegetation | Tree - fell into line | Woodpin | Broken- wire on object | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
3520 | Vegetation | Tree - fell into line | Woodpin | Normal | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3521 | Vegetation | Tree - grew into line |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3522 | Vegetation | Tree - grew into line |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3523 | Vegetation | Tree - grew into line |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3524 | Vegetation | Tree - grew into line | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3525 | Vegetation | Tree - grew into line | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3526 | Vegetation | Tree - grew into line | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3527 | Vegetation | Tree - grew into line | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3528 | Vegetation | Tree - grew into line | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3529 | Vegetation | Tree - grew into line | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3530 | Vegetation | Tree - grew into line | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3531 | Vegetation | Tree - grew into line | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3532 | Vegetation | Tree - grew into line | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3533 | Vegetation | Tree - grew into line | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3534 | Vegetation | Tree - grew into line | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3535 | Vegetation | Tree - grew into line | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3536 | Vegetation | Tree - grew into line | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3537 | Vegetation | Tree - grew into line | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3538 | Vegetation | Tree - grew into line | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3539 | Vegetation | Tree - grew into line | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3540 | Vegetation | Tree - grew into line | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3541 | Vegetation | Tree - grew into line | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3542 | Vegetation | Tree - grew into line | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3543 | Vegetation | Tree - grew into line | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
3544 | Vegetation | Tree - grew into line | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3545 | Vegetation | Tree - grew into line | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3546 | Vegetation | Tree - grew into line | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3547 | Vegetation | Tree - grew into line | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3548 | Vegetation | Tree - grew into line | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3549 | Vegetation | Tree - grew into line | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3550 | Vegetation | Tree - grew into line | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
3551 | Vegetation | Tree - grew into line | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3552 | Vegetation | Tree - grew into line | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3553 | Vegetation | Tree - grew into line | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3554 | Vegetation | Tree - grew into line | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3555 | Vegetation | Tree - grew into line | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3556 | Vegetation | Tree - grew into line | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3557 | Vegetation | Tree - grew into line | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3558 | Vegetation | Tree - grew into line | Secondary | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3559 | Vegetation | Tree - grew into line | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3560 | Vegetation | Tree - grew into line | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3561 | Vegetation | Tree - grew into line | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3562 | Vegetation | Tree - grew into line | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3563 | Vegetation | Tree - grew into line | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3564 | Vegetation | Tree - grew into line | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3565 | Vegetation | Tree - grew into line | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3566 | Vegetation | Tree - grew into line | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3567 | Vegetation | Tree - grew into line | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3568 | Vegetation | Tree - grew into line | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3569 | Vegetation | Tree - grew into line | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3570 | Vegetation | Tree - grew into line | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3571 | Vegetation | Tree - grew into line | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3572 | Vegetation | Tree - grew into line | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3573 | Vegetation | Tree - grew into line | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3574 | Vegetation | Tree - grew into line | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3575 | Vegetation | Tree - grew into line | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3576 | Vegetation | Tree - grew into line | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3577 | Vegetation | Tree - grew into line | Service conductor | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3578 | Vegetation | Tree - grew into line | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3579 | Vegetation | Tree - grew into line | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3580 | Vegetation | Tree - grew into line | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3581 | Vegetation | Tree - grew into line | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3582 | Vegetation | Tree - grew into line | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3583 | Vegetation | Tree - grew into line | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3584 | Vegetation | Tree - grew into line | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3585 | Vegetation | Tree - grew into line | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3586 | Vegetation | Tree - grew into line | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3587 | Vegetation | Tree - grew into line | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3588 | Vegetation | Tree - grew into line | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3589 | Vegetation | Tree - grew into line | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3590 | Vegetation | Tree - grew into line | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3591 | Vegetation | Tree - grew into line | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3592 | Vegetation | Tree - grew into line | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3593 | Vegetation | Tree - grew into line | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3594 | Vegetation | Tree - grew into line | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3595 | Vegetation | Tree - grew into line | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3596 | Vegetation | Tree - grew into line | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3597 | Vegetation | Tree - grew into line | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3598 | Vegetation | Tree - grew into line | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3599 | Vegetation | Tree - grew into line | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3600 | Vegetation | Tree - palm frond fell into line |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3601 | Vegetation | Tree - palm frond fell into line | Bushing | Blown/failed | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3602 | Vegetation | Tree - palm frond fell into line | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
3603 | Vegetation | Tree - palm frond fell into line | Capacitor | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3604 | Vegetation | Tree - palm frond fell into line | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3605 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3606 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3607 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3608 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3609 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3610 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3611 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3612 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3613 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3614 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3615 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3616 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3617 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3618 | Vegetation | Tree - palm frond fell into line | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
3619 | Vegetation | Tree - palm frond fell into line | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3620 | Vegetation | Tree - palm frond fell into line | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3621 | Vegetation | Tree - palm frond fell into line | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3622 | Vegetation | Tree - palm frond fell into line | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3623 | Vegetation | Tree - palm frond fell into line | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3624 | Vegetation | Tree - palm frond fell into line | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3625 | Vegetation | Tree - palm frond fell into line | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3626 | Vegetation | Tree - palm frond fell into line | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3627 | Vegetation | Tree - palm frond fell into line | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3628 | Vegetation | Tree - palm frond fell into line | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3629 | Vegetation | Tree - palm frond fell into line | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3630 | Vegetation | Tree - palm frond fell into line | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3631 | Vegetation | Tree - palm frond fell into line | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3632 | Vegetation | Tree - palm frond fell into line | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3633 | Vegetation | Tree - palm frond fell into line | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
3634 | Vegetation | Tree - palm frond fell into line | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3635 | Vegetation | Tree - palm frond fell into line | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3636 | Vegetation | Tree - palm frond fell into line | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3637 | Vegetation | Tree - palm frond fell into line | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3638 | Vegetation | Tree - palm frond fell into line | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3639 | Vegetation | Tree - palm frond fell into line | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3640 | Vegetation | Tree - palm frond fell into line | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3641 | Vegetation | Tree - palm frond fell into line | Pothead/Riser Termination | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3642 | Vegetation | Tree - palm frond fell into line | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
3643 | Vegetation | Tree - palm frond fell into line | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3644 | Vegetation | Tree - palm frond fell into line | Secondary |  | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3645 | Vegetation | Tree - palm frond fell into line | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3646 | Vegetation | Tree - palm frond fell into line | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3647 | Vegetation | Tree - palm frond fell into line | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3648 | Vegetation | Tree - palm frond fell into line | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3649 | Vegetation | Tree - palm frond fell into line | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3650 | Vegetation | Tree - palm frond fell into line | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3651 | Vegetation | Tree - palm frond fell into line | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3652 | Vegetation | Tree - palm frond fell into line | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3653 | Vegetation | Tree - palm frond fell into line | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3654 | Vegetation | Tree - palm frond fell into line | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3655 | Vegetation | Tree - palm frond fell into line | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3656 | Vegetation | Tree - palm frond fell into line | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3657 | Vegetation | Tree - palm frond fell into line | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3658 | Vegetation | Tree - palm frond fell into line | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3659 | Vegetation | Tree - palm frond fell into line | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3660 | Vegetation | Tree - palm frond fell into line | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3661 | Vegetation | Tree - palm frond fell into line | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3662 | 3rd Party | Aircraft- crop dusting | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3663 | 3rd Party | Aircraft- crop dusting | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3664 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3665 | 3rd Party | Contact with High Voltage- 3rd party | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3666 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3667 | 3rd Party | Contact with High Voltage- 3rd party | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3668 | 3rd Party | Contact with High Voltage- 3rd party | Anchor or Guy | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3669 | 3rd Party | Contact with High Voltage- 3rd party | Pothead/Riser Termination | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3670 | 3rd Party | Contact with High Voltage- 3rd party | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3671 | 3rd Party | Contact with High Voltage- 3rd party | Elbow | Broken | All | Underground facilities = no ignition risk
3672 | 3rd Party | Contact with High Voltage- 3rd party | Transformer | Malfunctioning | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3673 | 3rd Party | Contact with High Voltage- 3rd party | Street Light Equipment | Burned/flashed | Medium | System Hardening will not address Street Lights but will address their transformers.
3674 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
3675 | 3rd Party | Contact with High Voltage- 3rd party | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3676 | 3rd Party | Contact with High Voltage- 3rd party | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
3677 | 3rd Party | Contact with High Voltage- 3rd party | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3678 | 3rd Party | Customer Equipment | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
3679 | 3rd Party | Customer Equipment | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3680 | 3rd Party | Customer Equipment | Customer Equipment | Broken- wire on ground | None | No work is being completed on customer equipment.
3681 | 3rd Party | Customer Equipment | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3682 | 3rd Party | Customer Equipment | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
3683 | 3rd Party | Customer Equipment | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3684 | 3rd Party | Customer Equipment |  | Broken | None | No work is being completed on customer equipment.
3685 | 3rd Party | Customer Equipment | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
3686 | 3rd Party | Customer Equipment | Pole-Wood | Malfunctioning | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3687 | 3rd Party | Customer Equipment | Switch | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3688 | 3rd Party | Customer Equipment | Switch | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3689 | 3rd Party | Customer Equipment | Metering Equipment | Burned Open | None | System Hardening does not address Metering facilities.
3690 | 3rd Party | Customer Equipment | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3691 | 3rd Party | Customer Equipment | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3692 | 3rd Party | Customer Equipment | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
3693 | 3rd Party | Customer Equipment | Splice box | Blown/failed | All | Underground facilities = no ignition risk
3694 | 3rd Party | Customer Equipment | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3695 | 3rd Party | Customer Equipment | Relay | Normal | None | No work is being completed on customer equipment.
3696 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
3697 | 3rd Party | Dig in- 3rd party | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3698 | 3rd Party | Dig in- 3rd party | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3699 | 3rd Party | Dig in- 3rd party | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3700 | 3rd Party | Dig in- 3rd party | Conductor- Underground | On Ground | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3701 | 3rd Party | Dig in- 3rd party | Connector or Splice (UG) | Bent or Twisted | All | Underground facilities = no ignition risk
3702 | 3rd Party | Dig in- 3rd party |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3703 | 3rd Party | Dig in- 3rd party | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3704 | 3rd Party | Fire- house or bldg. | Service conductor | On Ground | None | 3rd party fire impacting PGE equipment
3705 | 3rd Party | Fire- house or bldg. | Service conductor | Deteriorated | None | 3rd party fire impacting PGE equipment
3706 | 3rd Party | Fire- house or bldg. | Connector or Splice (OH) | Broken- wire on ground | None | 3rd party fire impacting PGE equipment
3707 | 3rd Party | Fire- house or bldg. | Transformer | Malfunctioning | None | 3rd party fire impacting PGE equipment
3708 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Burned Open | None | 3rd party fire impacting PGE equipment
3709 | 3rd Party | Fire- house or bldg. | Pole-Wood | Burned Open | None | 3rd party fire impacting PGE equipment
3710 | 3rd Party | Fire- house or bldg. | Interrupter | Normal | None | 3rd party fire impacting PGE equipment
3711 | 3rd Party | Fire- house or bldg. | Customer Equipment | On Ground | None | 3rd party fire impacting PGE equipment
3712 | 3rd Party | Gun Shot | Conductor- Overhead | Malfunctioning | None | Covered wire will not prevent gun shot damage
3713 | 3rd Party | Gun Shot | Transformer | Broken | None | Covered wire will not prevent gun shot damage
3714 | 3rd Party | Gun Shot | Secondary | Deteriorated | None | Covered wire will not prevent gun shot damage
3715 | 3rd Party | Gun Shot | Fuse | Broken | None | Covered wire will not prevent gun shot damage
3716 | 3rd Party | Gun Shot | Cutout- fuse holder | Broken | None | Covered wire will not prevent gun shot damage
3717 | 3rd Party | Gun Shot | Conductor- Overhead | Contaminated | None | Covered wire will not prevent gun shot damage
3718 | 3rd Party | Kite | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3719 | 3rd Party | Kite | Cutout- fuse holder | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3720 | 3rd Party | Kite | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3721 | 3rd Party | Metallic Balloon | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3722 | 3rd Party | Metallic Balloon | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3723 | 3rd Party | Metallic Balloon | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3724 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3725 | 3rd Party | Metallic Balloon | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
3726 | 3rd Party | Metallic Balloon | Cutout- Fused- Distribution | Contaminated | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3727 | 3rd Party | Metallic Balloon | Transformer | Malfunctioning | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3728 | 3rd Party | Metallic Balloon | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3729 | 3rd Party | Metallic Balloon | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3730 | 3rd Party | Metallic Balloon | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3731 | 3rd Party | Metallic Balloon | Pothead/Riser Termination | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3732 | 3rd Party | Metallic Balloon | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3733 | 3rd Party | Other | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3734 | 3rd Party | Other |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3735 | 3rd Party | Thrown Object | Cutout- Fused- Distribution | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3736 | 3rd Party | Thrown Object | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3737 | 3rd Party | Thrown Object | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3738 | 3rd Party | Thrown Object | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3739 | 3rd Party | Thrown Object | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3740 | 3rd Party | Thrown Object | Cutout- Fused- Distribution | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3741 | 3rd Party | Thrown Object | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3742 | 3rd Party | Tree - cutting- 3rd party | Other | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3743 | 3rd Party | Tree - cutting- 3rd party | Service conductor | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3744 | 3rd Party | Tree - cutting- 3rd party | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3745 | 3rd Party | Tree - cutting- 3rd party | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3746 | 3rd Party | Vandalism | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3747 | 3rd Party | Vandalism | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3748 | 3rd Party | Vandalism | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
3749 | 3rd Party | Vandalism | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
3750 | 3rd Party | Vandalism | Switch | Broken | None | System Hardening does not address ….
3751 | 3rd Party | Vandalism | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
3752 | 3rd Party | Vandalism | Switch | Malfunctioning | None | System Hardening does not address ….
3753 | 3rd Party | Vandalism | Conductor- Overhead | Malfunctioning | All | New covered conductor will eliminate these contact type outages.
3754 | 3rd Party | Vandalism | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3755 | 3rd Party | Vandalism | Service conductor | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3756 | 3rd Party | Vandalism | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
3757 | 3rd Party | Vandalism | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3758 | 3rd Party | Vehicle | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3759 | 3rd Party | Vehicle | Jumper | Arcing | High | Larger covered conductor to mostly eliminate cause and risk.
3760 | 3rd Party | Vehicle | Pole-Wood | Malfunctioning | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3761 | 3rd Party | Vehicle | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3762 | 3rd Party | Vehicle | Pole-Wood | Bent or Twisted | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3763 | 3rd Party | Vehicle | Street Light Equipment | On Ground | Medium | System Hardening will not address Street Lights but will address their transformers.
3764 | 3rd Party | Vehicle | Fuse | Bent or Twisted | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3765 | 3rd Party | Vehicle | Crossarm- Wood | Bent or Twisted | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3766 | 3rd Party | Vehicle | Cutout- fuse holder | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3767 | 3rd Party | Vehicle | Transformer | Contaminated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3768 | 3rd Party | Vehicle | Manhole- primary box | Broken | All | Underground facilities = no ignition risk
3769 | 3rd Party | Vehicle |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3770 | 3rd Party | Vehicle | Other | Burned/flashed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3771 | 3rd Party | Vehicle | Cutout- Fused- Distribution | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3772 | 3rd Party | Vehicle | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3773 | 3rd Party | Vehicle | Transformer | Burned Open | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3774 | 3rd Party | Vehicle | Cutout- Fused- Distribution | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3775 | 3rd Party | Vehicle | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3776 | 3rd Party | Vehicle | Customer Equipment | Normal | None | No work is being completed on customer equipment.
3777 | 3rd Party | Vehicle | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3778 | 3rd Party | Vehicle | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3779 | 3rd Party | Vehicle | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
3780 | 3rd Party | Vehicle | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3781 | 3rd Party | Vehicle | Street Light Equipment | Broken | Medium | System Hardening will not address Street Lights but will address their transformers.
3782 | 3rd Party | Vehicle | Customer Equipment | Bent or Twisted | None | No work is being completed on customer equipment.
3783 | 3rd Party | Vehicle | Cutout- Fused- Distribution | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3784 | 3rd Party | Vehicle | Pole-Wood | Together | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3785 | 3rd Party | Vehicle | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3786 | 3rd Party | Vehicle | Street Light Equipment | Together | Medium | System Hardening will not address Street Lights but will address their transformers.
3787 | 3rd Party | Vehicle | Connector or Splice (OH) | Bent or Twisted | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3788 | Animal | Bird found | Cutout- Fused- Distribution | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3789 | Animal | Bird found | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3790 | Animal | Bird found | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3791 | Animal | Bird found | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3792 | Animal | Bird found | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3793 | Animal | Bird found | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3794 | Animal | Bird found | Cutout- fuse holder | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3795 | Animal | Bird found | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3796 | Animal | Bird found | Cutout- Fused- Distribution | Contaminated | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3797 | Animal | Bird found | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
3798 | Animal | Bird found | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3799 | Animal | Bird found | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3800 | Animal | Bird found | Riser | Burned/flashed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
3801 | Animal | Bird found | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3802 | Animal | Bird found | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3803 | Animal | Bird found | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3804 | Animal | Bird found | Connector or Splice (OH) | Together | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3805 | Animal | Bird found | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
3806 | Animal | Bird found | PGs- Kearneys | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3807 | Animal | Bird found | Recloser | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3808 | Animal | Other | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3809 | Animal | Other | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3810 | Animal | Other | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3811 | Animal | Other | Switch | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3812 | Animal | Other | Pothead/Riser Termination | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3813 | Animal | Other | Pothead/Riser Termination | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3814 | Animal | Other | Metering Equipment | Burned Open | None | System Hardening does not address Metering facilities.
3815 | Animal | Other | Jumper | Malfunctioning | High | Larger covered conductor to mostly eliminate cause and risk.
3816 | Animal | Other | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3817 | Animal | Squirrel | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3818 | Animal | Squirrel | Cutout- Fused- Distribution | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3819 | Animal | Squirrel | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3820 | Animal | Squirrel | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
3821 | Animal | Squirrel | Elbow | Normal | All | Underground facilities = no ignition risk
3822 | Animal | Squirrel | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3823 | Animal | Squirrel | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3824 | Animal | Squirrel | Cutout- fuse holder | Together | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3825 | Animal | Squirrel | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3826 | Animal | Squirrel | Cutout- fuse holder | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3827 | Animal | Squirrel | Jumper | Together | High | Larger covered conductor to mostly eliminate cause and risk.
3828 | Animal | Squirrel | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
3829 | Animal | Squirrel | Riser | Blown/failed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
3830 | Animal | Squirrel | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3831 | Animal | Squirrel | Cutout- Fused- Distribution | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3832 | Animal | Squirrel | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3833 | Animal | Squirrel | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
3834 | Animal | Squirrel | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3835 | Animal | Squirrel | Connector or Splice (UG) | Malfunctioning | All | Underground facilities = no ignition risk
3836 | Animal | Squirrel | Pothead/Riser Termination | Malfunctioning | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3837 | Animal | Squirrel | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3838 | Animal | Squirrel | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3839 | Animal | Squirrel | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
3840 | Animal | Squirrel | Footings- Tower or Pole | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3841 | Animal | Squirrel | Cutout- Fused- Distribution | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3842 | Animal | Squirrel | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3843 | Animal | Squirrel | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3844 | Animal | Squirrel | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3845 | Animal | Squirrel | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3846 | Animal | Squirrel | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3847 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
3848 | Company Initiated | Construction Activity/equip- company | Secondary | Deteriorated | None | Company Initiated Outage. Not outage related.
3849 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
3850 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
3851 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
3852 | Company Initiated | Construction Activity/equip- company | Other | Normal | None | Company Initiated Outage. Not outage related.
3853 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
3854 | Company Initiated | Construction Activity/equip- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
3855 | Company Initiated | Construction Activity/equip- company | Jumper | Normal | None | Company Initiated Outage. Not outage related.
3856 | Company Initiated | Construction Activity/equip- company | Transformer | Deteriorated | None | Company Initiated Outage. Not outage related.
3857 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
3858 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3859 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
3860 | Company Initiated | Construction Activity/equip- company | Fuse | Burned Open | None | Company Initiated Outage. Not outage related.
3861 | Company Initiated | Construction Activity/equip- company | Transformer | Normal | None | Company Initiated Outage. Not outage related.
3862 | Company Initiated | Construction Activity/equip- company | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
3863 | Company Initiated | Construction Activity/equip- company | Anchor or Guy | Normal | None | Company Initiated Outage. Not outage related.
3864 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
3865 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3866 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
3867 | Company Initiated | Construction Activity/equip- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
3868 | Company Initiated | Construction Activity/equip- company | Jumper | Burned/flashed | None | Company Initiated Outage. Not outage related.
3869 | Company Initiated | Construction Activity/equip- company | Secondary | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3870 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Malfunctioning | None | Company Initiated Outage. Not outage related.
3871 | Company Initiated | Construction Activity/equip- company | Switch | Normal | None | Company Initiated Outage. Not outage related.
3872 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
3873 | Company Initiated | Construction Activity/equip- company | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
3874 | Company Initiated | Construction Activity/equip- company | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
3875 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
3876 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
3877 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
3878 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
3879 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
3880 | Company Initiated | Construction Activity/equip- company | Pole - Tower- steel | Normal | None | Company Initiated Outage. Not outage related.
3881 | Company Initiated | Construction Activity/equip- company | Secondary | Malfunctioning | None | Company Initiated Outage. Not outage related.
3882 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
3883 | Company Initiated | Construction Activity/equip- company | Footings- Tower or Pole | Normal | None | Company Initiated Outage. Not outage related.
3884 | Company Initiated | Construction Activity/equip- company | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
3885 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | On Ground | None | Company Initiated Outage. Not outage related.
3886 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
3887 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
3888 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
3889 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
3890 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
3891 | Company Initiated | Construction Activity/equip- company | Riser | Blown/failed | None | Company Initiated Outage. Not outage related.
3892 | Company Initiated | Construction Activity/equip- company | Capacitor | Malfunctioning | None | Company Initiated Outage. Not outage related.
3893 | Company Initiated | Construction Activity/equip- company | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
3894 | Company Initiated | Construction Activity/equip- company | Riser | Normal | None | Company Initiated Outage. Not outage related.
3895 | Company Initiated | Construction Activity/equip- company | Secondary | Together | None | Company Initiated Outage. Not outage related.
3896 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
3897 | Company Initiated | Construction Activity/equip- company | Elbow | Normal | None | Company Initiated Outage. Not outage related.
3898 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
3899 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
3900 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
3901 | Company Initiated | Construction Activity/equip- company | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
3902 | Company Initiated | Construction Activity/equip- company | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
3903 | Company Initiated | Construction Activity/equip- company | Jumper | Broken | None | Company Initiated Outage. Not outage related.
3904 | Company Initiated | Construction Activity/equip- company | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
3905 | Company Initiated | Construction Activity/equip- company | Anchor or Guy | Deteriorated | None | Company Initiated Outage. Not outage related.
3906 | Company Initiated | Construction Activity/equip- company | Lightning Arrestor | Normal | None | Company Initiated Outage. Not outage related.
3907 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
3908 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
3909 | Company Initiated | Construction Activity/equip- company | Relay | Malfunctioning | None | Company Initiated Outage. Not outage related.
3910 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Together | None | Company Initiated Outage. Not outage related.
3911 | Company Initiated | Construction Activity/equip- company |  |  | None | Company Initiated Outage. Not outage related.
3912 | Company Initiated | Construction Activity/equip- company | Cutout- Fused- Distribution | Blown/failed | None | Company Initiated Outage. Not outage related.
3913 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Malfunctioning | None | Company Initiated Outage. Not outage related.
3914 | Company Initiated | Construction Activity/equip- company | Transformer | Burned/flashed | None | Company Initiated Outage. Not outage related.
3915 | Company Initiated | Construction Activity/equip- company | Recloser | Normal | None | Company Initiated Outage. Not outage related.
3916 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
3917 | Company Initiated | Construction Activity/equip- company | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
3918 | Company Initiated | Construction Activity/equip- company | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
3919 | Company Initiated | Construction Activity/equip- company | Transformer | Broken | None | Company Initiated Outage. Not outage related.
3920 | Company Initiated | Construction Activity/equip- company | Transformer | Leaking | None | Company Initiated Outage. Not outage related.
3921 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
3922 | Company Initiated | Construction Activity/equip- company | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
3923 | Company Initiated | Construction Activity/equip- company | Regulator | Normal | None | Company Initiated Outage. Not outage related.
3924 | Company Initiated | Construction Activity/equip- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
3925 | Company Initiated | Construction Activity/equip- company | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
3926 | Company Initiated | Construction Activity/equip- company | Secondary | Bent or Twisted | None | Company Initiated Outage. Not outage related.
3927 | Company Initiated | Construction Activity/equip- company | Insulator | Broken- wire on object | None | Company Initiated Outage. Not outage related.
3928 | Company Initiated | Construction Activity/equip- company | Pole-Wood | On Ground | None | Company Initiated Outage. Not outage related.
3929 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken- wire on object | None | Company Initiated Outage. Not outage related.
3930 | Company Initiated | Construction Activity/equip- company | Transformer | Blown/failed | None | Company Initiated Outage. Not outage related.
3931 | Company Initiated | Construction Activity/equip- company | Other | Deteriorated | None | Company Initiated Outage. Not outage related.
3932 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
3933 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Burned Open | None | Company Initiated Outage. Not outage related.
3934 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
3935 | Company Initiated | Construction Activity/equip- company | Switch (OH) | Broken | None | Company Initiated Outage. Not outage related.
3936 | Company Initiated | Construction Activity/equip- company | Secondary | Normal | None | Company Initiated Outage. Not outage related.
3937 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
3938 | Company Initiated | Construction Activity/equip- company |  | Malfunctioning | None | Company Initiated Outage. Not outage related.
3939 | Company Initiated | Construction Activity/equip- company | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
3940 | Company Initiated | Construction Activity/equip- company | Service conductor | Broken | None | Company Initiated Outage. Not outage related.
3941 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
3942 | Company Initiated | Construction Activity/equip- company | Other | Broken | None | Company Initiated Outage. Not outage related.
3943 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
3944 | Company Initiated | Construction Activity/equip- company | Insulator | Broken | None | Company Initiated Outage. Not outage related.
3945 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
3946 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Broken | None | Company Initiated Outage. Not outage related.
3947 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3948 | Company Initiated | Construction Activity/equip- company | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
3949 | Company Initiated | Construction Activity/equip- company | Generator | Malfunctioning | None | Company Initiated Outage. Not outage related.
3950 | Company Initiated | Contact with High Voltage- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
3951 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
3952 | Company Initiated | Contact with High Voltage- company | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
3953 | Company Initiated | Contact with High Voltage- company | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
3954 | Company Initiated | Contact with High Voltage- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
3955 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | On Ground | None | Company Initiated Outage. Not outage related.
3956 | Company Initiated | Contact with High Voltage- company | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
3957 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3958 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
3959 | Company Initiated | Contact with High Voltage- company | Pothead(Riser Termination) | Burned/flashed | None | Company Initiated Outage. Not outage related.
3960 | Company Initiated | Contact with High Voltage- company |  | Blown/failed | None | Company Initiated Outage. Not outage related.
3961 | Company Initiated | Contact with High Voltage- company | Transformer | Normal | None | Company Initiated Outage. Not outage related.
3962 | Company Initiated | Contact with High Voltage- company | Secondary | Burned/flashed | None | Company Initiated Outage. Not outage related.
3963 | Company Initiated | Contact with High Voltage- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
3964 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
3965 | Company Initiated | Contact with High Voltage- company | Elbow | Normal | None | Company Initiated Outage. Not outage related.
3966 | Company Initiated | Contact with High Voltage- company | Other | Arcing | None | Company Initiated Outage. Not outage related.
3967 | Company Initiated | Contact with High Voltage- company | Secondary | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3968 | Company Initiated | Contact with High Voltage- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
3969 | Company Initiated | Coordination failure | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
3970 | Company Initiated | Coordination failure | Fuse | Normal | None | Company Initiated Outage. Not outage related.
3971 | Company Initiated | Coordination failure | Other | Normal | None | Company Initiated Outage. Not outage related.
3972 | Company Initiated | Coordination failure | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
3973 | Company Initiated | Coordination failure | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
3974 | Company Initiated | Coordination failure | Recloser | Normal | None | Company Initiated Outage. Not outage related.
3975 | Company Initiated | Coordination failure | Transformer | Normal | None | Company Initiated Outage. Not outage related.
3976 | Company Initiated | Coordination failure | Crossarm- Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
3977 | Company Initiated | Coordination failure | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
3978 | Company Initiated | Coordination failure | Relay | Malfunctioning | None | Company Initiated Outage. Not outage related.
3979 | Company Initiated | Coordination failure | Insulator | Broken | None | Company Initiated Outage. Not outage related.
3980 | Company Initiated | Coordination failure | Circuit Breaker | Malfunctioning | None | Company Initiated Outage. Not outage related.
3981 | Company Initiated | Coordination failure | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
3982 | Company Initiated | Coordination failure | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
3983 | Company Initiated | Coordination failure |  | Normal | None | Company Initiated Outage. Not outage related.
3984 | Company Initiated | Coordination failure | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
3985 | Company Initiated | Coordination failure | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
3986 | Company Initiated | Coordination failure | SCADA | Malfunctioning | None | Company Initiated Outage. Not outage related.
3987 | Company Initiated | Coordination failure | Stepdown | Normal | None | Company Initiated Outage. Not outage related.
3988 | Company Initiated | Coordination failure | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3989 | Company Initiated | Coordination failure | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
3990 | Company Initiated | Coordination failure | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
3991 | Company Initiated | Coordination failure | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
3992 | Company Initiated | Coordination failure | Transformer |  | None | Company Initiated Outage. Not outage related.
3993 | Company Initiated | Coordination failure | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
3994 | Company Initiated | Dig in- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
3995 | Company Initiated | Dig in- company | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
3996 | Company Initiated | Dig in- company | Transformer | Normal | None | Company Initiated Outage. Not outage related.
3997 | Company Initiated | Dig in- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
3998 | Company Initiated | Dig in- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
3999 | Company Initiated | Dig in- company | Service conductor | Broken | None | Company Initiated Outage. Not outage related.
4000 | Company Initiated | Dig in- company | Conductor- Underground | Malfunctioning | None | Company Initiated Outage. Not outage related.
4001 | Company Initiated | Dig in- company | Conductor- Underground | Blown/failed | None | Company Initiated Outage. Not outage related.
4002 | Company Initiated | Improper Construction | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
4003 | Company Initiated | Improper Construction | Secondary | Malfunctioning | None | Company Initiated Outage. Not outage related.
4004 | Company Initiated | Improper Construction | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
4005 | Company Initiated | Improper Construction | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
4006 | Company Initiated | Improper Construction | Elbow | Normal | None | Company Initiated Outage. Not outage related.
4007 | Company Initiated | Improper Construction | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
4008 | Company Initiated | Improper Construction | Booster | Normal | None | Company Initiated Outage. Not outage related.
4009 | Company Initiated | Improper Construction | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
4010 | Company Initiated | Improper Construction | Conductor- Overhead | Annealed | None | Company Initiated Outage. Not outage related.
4011 | Company Initiated | Improper Construction | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
4012 | Company Initiated | Improper Construction | Connector or Splice (UG) | Broken | None | Company Initiated Outage. Not outage related.
4013 | Company Initiated | Improper Construction | Cutout- Fused- Distribution | Normal | None | Company Initiated Outage. Not outage related.
4014 | Company Initiated | Improper Construction | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
4015 | Company Initiated | Improper Construction | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
4016 | Company Initiated | Improper Construction | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
4017 | Company Initiated | Improper Construction | Switch | Malfunctioning | None | Company Initiated Outage. Not outage related.
4018 | Company Initiated | Improper Construction | Other | Normal | None | Company Initiated Outage. Not outage related.
4019 | Company Initiated | Improper Construction | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
4020 | Company Initiated | Improper Construction | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
4021 | Company Initiated | Improper Construction | Switch | Normal | None | Company Initiated Outage. Not outage related.
4022 | Company Initiated | Improper Construction | Switch (UG) | Burned/flashed | None | Company Initiated Outage. Not outage related.
4023 | Company Initiated | Improper Construction | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
4024 | Company Initiated | Improper Construction | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
4025 | Company Initiated | Improper Construction | Switch (OH) | Arcing | None | Company Initiated Outage. Not outage related.
4026 | Company Initiated | Improper Construction | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
4027 | Company Initiated | Improper Construction | Secondary | Broken | None | Company Initiated Outage. Not outage related.
4028 | Company Initiated | Improper Construction | Anchor or Guy | Broken | None | Company Initiated Outage. Not outage related.
4029 | Company Initiated | Improper Construction | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
4030 | Company Initiated | Improper Construction | Transformer | Normal | None | Company Initiated Outage. Not outage related.
4031 | Company Initiated | Improper Construction | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
4032 | Company Initiated | Improper Construction | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
4033 | Company Initiated | Improper Construction | Regulator | Burned/flashed | None | Company Initiated Outage. Not outage related.
4034 | Company Initiated | Improper Construction | Secondary | Normal | None | Company Initiated Outage. Not outage related.
4035 | Company Initiated | Improper Construction | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
4036 | Company Initiated | Improper Construction | Transformer | Blown/failed | None | Company Initiated Outage. Not outage related.
4037 | Company Initiated | Improper Construction | Fuse | Normal | None | Company Initiated Outage. Not outage related.
4038 | Company Initiated | Improper Construction | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
4039 | Company Initiated | Improper Construction | Customer Equipment | Normal | None | Company Initiated Outage. Not outage related.
4040 | Company Initiated | Improper Construction | Other | Arcing | None | Company Initiated Outage. Not outage related.
4041 | Company Initiated | Improper Construction | Switch (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
4042 | Company Initiated | Improper Construction | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
4043 | Company Initiated | Improper Construction | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
4044 | Company Initiated | Improper Construction | Connector or Splice (OH) | Contaminated | None | Company Initiated Outage. Not outage related.
4045 | Company Initiated | Improper Construction | Connector or Splice (UG) | Together | None | Company Initiated Outage. Not outage related.
4046 | Company Initiated | Improper Construction | Jumper | Normal | None | Company Initiated Outage. Not outage related.
4047 | Company Initiated | Improper Construction | Crossarm- Wood | Contaminated | None | Company Initiated Outage. Not outage related.
4048 | Company Initiated | Improper Construction | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
4049 | Company Initiated | Improper Construction | Recloser | Normal | None | Company Initiated Outage. Not outage related.
4050 | Company Initiated | Improper Construction | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
4051 | Company Initiated | Improper Construction | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
4052 | Company Initiated | Improper Construction | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4053 | Company Initiated | Improper Construction | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
4054 | Company Initiated | Improper Construction | Secondary | Together | None | Company Initiated Outage. Not outage related.
4055 | Company Initiated | Improper Construction | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
4056 | Company Initiated | Improper Construction | Conductor- Overhead | Bent or Twisted | None | Company Initiated Outage. Not outage related.
4057 | Company Initiated | Improper Construction | Connector or Splice (OH) | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4058 | Company Initiated | Improper Construction | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
4059 | Company Initiated | Improper Construction | Transformer |  | None | Company Initiated Outage. Not outage related.
4060 | Company Initiated | Improper Construction | Other | Bent or Twisted | None | Company Initiated Outage. Not outage related.
4061 | Company Initiated | Improper Construction | Conductor- Overhead | Malfunctioning | None | Company Initiated Outage. Not outage related.
4062 | Company Initiated | Improper Construction | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
4063 | Company Initiated | Improper Construction | Conductor- Underground | Together | None | Company Initiated Outage. Not outage related.
4064 | Company Initiated | Improper Construction | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
4065 | Company Initiated | Improper Construction | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
4066 | Company Initiated | Improper Construction | Conductor- Underground | Malfunctioning | None | Company Initiated Outage. Not outage related.
4067 | Company Initiated | Improper Construction | Other | Together | None | Company Initiated Outage. Not outage related.
4068 | Company Initiated | Improper Construction | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
4069 | Company Initiated | Improper Construction | Insulator | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4070 | Company Initiated | Improper Construction | Secondary | Bent or Twisted | None | Company Initiated Outage. Not outage related.
4071 | Company Initiated | Improper Construction | Secondary | Burned Open | None | Company Initiated Outage. Not outage related.
4072 | Company Initiated | Improper Construction | Regulator | Normal | None | Company Initiated Outage. Not outage related.
4073 | Company Initiated | Improper Construction | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
4074 | Company Initiated | Insulator washing | Bushing | Broken | None | Company Initiated Outage. Not outage related.
4075 | Company Initiated | Insulator washing | Circuit Breaker | Burned/flashed | None | Company Initiated Outage. Not outage related.
4076 | Company Initiated | Insulator washing | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
4077 | Company Initiated | Operating error | Recloser | Normal | None | Company Initiated Outage. Not outage related.
4078 | Company Initiated | Operating error | Other | Normal | None | Company Initiated Outage. Not outage related.
4079 | Company Initiated | Operating error | Fuse | Normal | None | Company Initiated Outage. Not outage related.
4080 | Company Initiated | Operating error | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
4081 | Company Initiated | Operating error | SCADA | Normal | None | Company Initiated Outage. Not outage related.
4082 | Company Initiated | Operating error | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
4083 | Company Initiated | Operating error | Regulator | Normal | None | Company Initiated Outage. Not outage related.
4084 | Company Initiated | Operating error | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
4085 | Company Initiated | Operating error | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
4086 | Company Initiated | Operating error | Jumper | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4087 | Company Initiated | Operating error | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
4088 | Company Initiated | Operating error | Jumper | Normal | None | Company Initiated Outage. Not outage related.
4089 | Company Initiated | Operating error | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
4090 | Company Initiated | Operating error | Other | Burned/flashed | None | Company Initiated Outage. Not outage related.
4091 | Company Initiated | Operating error |  |  | None | Company Initiated Outage. Not outage related.
4092 | Company Initiated | Operating error | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
4093 | Company Initiated | Operating error | Capacitor | Blown/failed | None | Company Initiated Outage. Not outage related.
4094 | Company Initiated | Operating error | Cutout- Fused- Distribution | Normal | None | Company Initiated Outage. Not outage related.
4095 | Company Initiated | Operating error | Sectionalizer | Normal | None | Company Initiated Outage. Not outage related.
4096 | Company Initiated | Operating error | Switch | Contaminated | None | Company Initiated Outage. Not outage related.
4097 | Company Initiated | Operating error |  | Normal | None | Company Initiated Outage. Not outage related.
4098 | Company Initiated | Operating error | Transformer (UG) |  | None | Company Initiated Outage. Not outage related.
4099 | Company Initiated | Operating error | Switch |  | None | Company Initiated Outage. Not outage related.
4100 | Company Initiated | Operating error | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
4101 | Company Initiated | Operating error | Switch (OH) | Burned/flashed | None | Company Initiated Outage. Not outage related.
4102 | Company Initiated | Operating error | Relay | Normal | None | Company Initiated Outage. Not outage related.
4103 | Company Initiated | Operating error | Fuse |  | None | Company Initiated Outage. Not outage related.
4104 | Company Initiated | Operating error | Secondary | Arcing | None | Company Initiated Outage. Not outage related.
4105 | Company Initiated | Operating error | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
4106 | Company Initiated | Operating error | Transformer (UG) | Burned/flashed | None | Company Initiated Outage. Not outage related.
4107 | Company Initiated | Operating error | Switch | Normal | None | Company Initiated Outage. Not outage related.
4108 | Company Initiated | Operating error | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
4109 | Company Initiated | Operating error | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4110 | Company Initiated | Operating error | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
4111 | Company Initiated | Operating error | Customer Equipment | Malfunctioning | None | Company Initiated Outage. Not outage related.
4112 | Company Initiated | Operating error | Transformer | Normal | None | Company Initiated Outage. Not outage related.
4113 | Company Initiated | Operating error | Elbow | Normal | None | Company Initiated Outage. Not outage related.
4114 | Company Initiated | Operating error | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
4115 | Company Initiated | Operating error | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
4116 | Company Initiated | Operating error | Recloser | Blown/failed | None | Company Initiated Outage. Not outage related.
4117 | Company Initiated | Operating error | Jumper | Broken | None | Company Initiated Outage. Not outage related.
4118 | Company Initiated | Other Circuits | Pole-Wood | Together | None | Company Initiated Outage. Not outage related.
4119 | Company Initiated | Other Circuits |  |  | None | Company Initiated Outage. Not outage related.
4120 | Company Initiated | Other Circuits | Recloser | Normal | None | Company Initiated Outage. Not outage related.
4121 | Company Initiated | Other Circuits | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
4122 | Company Initiated | Other Circuits | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
4123 | Company Initiated | Other Circuits | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
4124 | Company Initiated | Other Circuits | Booster | Deteriorated | None | Company Initiated Outage. Not outage related.
4125 | Company Initiated | Other Circuits | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
4126 | Company Initiated | Other Circuits | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
4127 | Company Initiated | Other Circuits | Jumper | Malfunctioning | None | Company Initiated Outage. Not outage related.
4128 | Company Initiated | Other Circuits | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
4129 | Company Initiated | Other Circuits | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
4130 | Company Initiated | Other Circuits | Other | Normal | None | Company Initiated Outage. Not outage related.
4131 | Company Initiated | Other Circuits | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
4132 | Company Initiated | Other Circuits | Generator | Malfunctioning | None | Company Initiated Outage. Not outage related.
4133 | Company Initiated | Other Circuits | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
4134 | Company Initiated | Other Circuits | Jumper | Normal | None | Company Initiated Outage. Not outage related.
4135 | Company Initiated | Other Circuits | Fuse | Normal | None | Company Initiated Outage. Not outage related.
4136 | Company Initiated | Other Circuits | Conductor- Overhead | Broken- wire on object | None | Company Initiated Outage. Not outage related.
4137 | Company Initiated | Other Circuits | Other | Broken | None | Company Initiated Outage. Not outage related.
4138 | Company Initiated | Other Circuits | Regulator | Broken | None | Company Initiated Outage. Not outage related.
4139 | Company Initiated | Other Circuits | Secondary | Burned/flashed | None | Company Initiated Outage. Not outage related.
4140 | Company Initiated | Other Circuits | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4141 | Company Initiated | Other Circuits | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
4142 | Company Initiated | Other Circuits | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
4143 | Company Initiated | Other Circuits | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
4144 | Company Initiated | Other Circuits | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
4145 | Company Initiated | Other Circuits | Regulator- LTC substation | Normal | None | Company Initiated Outage. Not outage related.
4146 | Company Initiated | Other Circuits | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
4147 | Company Initiated | Other Circuits | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
4148 | Company Initiated | Other Circuits | Generator | Contaminated | None | Company Initiated Outage. Not outage related.
4149 | Company Initiated | Other Circuits | Footings- Tower or Pole | Bent or Twisted | None | Company Initiated Outage. Not outage related.
4150 | Company Initiated | Other Circuits | Lightning Arrestor | Blown/failed | None | Company Initiated Outage. Not outage related.
4151 | Company Initiated | Other Circuits | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
4152 | Company Initiated | Other Circuits | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
4153 | Company Initiated | Other Circuits | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
4154 | Company Initiated | Other Circuits | Transformer | Deteriorated | None | Company Initiated Outage. Not outage related.
4155 | Company Initiated | Other Circuits | Transformer | Blown/failed | None | Company Initiated Outage. Not outage related.
4156 | Company Initiated | Other Circuits | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
4157 | Company Initiated | Other Circuits | Secondary | Burned Open | None | Company Initiated Outage. Not outage related.
4158 | Company Initiated | Other Circuits | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
4159 | Company Initiated | Other Circuits | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
4160 | Company Initiated | Other Circuits | Transformer | Broken | None | Company Initiated Outage. Not outage related.
4161 | Company Initiated | Other Circuits | Other |  | None | Company Initiated Outage. Not outage related.
4162 | Company Initiated | Other Circuits | Lightning Arrestor | Malfunctioning | None | Company Initiated Outage. Not outage related.
4163 | Company Initiated | Other Circuits | Transformer | Normal | None | Company Initiated Outage. Not outage related.
4164 | Company Initiated | Other Circuits | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
4165 | Company Initiated | Other Circuits | Switch | Malfunctioning | None | Company Initiated Outage. Not outage related.
4166 | Company Initiated | Other Circuits | Fuse | Deteriorated | None | Company Initiated Outage. Not outage related.
4167 | Company Initiated | Personnel- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
4168 | Company Initiated | Personnel- company | Elbow | Broken | None | Company Initiated Outage. Not outage related.
4169 | Company Initiated | Personnel- company | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
4170 | Company Initiated | Personnel- company | Cutout- fuse holder | Arcing | None | Company Initiated Outage. Not outage related.
4171 | Company Initiated | Personnel- company | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
4172 | Company Initiated | Personnel- company | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
4173 | Company Initiated | Personnel- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
4174 | Company Initiated | Personnel- company | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
4175 | Company Initiated | Personnel- company | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
4176 | Company Initiated | Personnel- company | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
4177 | Company Initiated | Personnel- company | Regulator | Broken | None | Company Initiated Outage. Not outage related.
4178 | Company Initiated | Personnel- company | Recloser | Normal | None | Company Initiated Outage. Not outage related.
4179 | Company Initiated | Personnel- company |  |  | None | Company Initiated Outage. Not outage related.
4180 | Company Initiated | Personnel- company | Jumper | Burned/flashed | None | Company Initiated Outage. Not outage related.
4181 | Company Initiated | Personnel- company | Other | Normal | None | Company Initiated Outage. Not outage related.
4182 | Company Initiated | Personnel- company | Service conductor | Together | None | Company Initiated Outage. Not outage related.
4183 | Company Initiated | Personnel- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
4184 | Company Initiated | Personnel- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
4185 | Company Initiated | Personnel- company | Secondary | Normal | None | Company Initiated Outage. Not outage related.
4186 | Company Initiated | Personnel- company | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
4187 | Company Initiated | Personnel- company | Relay | Normal | None | Company Initiated Outage. Not outage related.
4188 | Company Initiated | Personnel- company | Secondary | Together | None | Company Initiated Outage. Not outage related.
4189 | Company Initiated | Personnel- company | Transformer | Normal | None | Company Initiated Outage. Not outage related.
4190 | Company Initiated | Personnel- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
4191 | Company Initiated | Personnel- company | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
4192 | Company Initiated | Personnel- company | Transformer (UG) | Arcing | None | Company Initiated Outage. Not outage related.
4193 | Company Initiated | Personnel- company | Transformer (UG) | Deteriorated | None | Company Initiated Outage. Not outage related.
4194 | Company Initiated | Personnel- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
4195 | Company Initiated | Personnel- company | Switch (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
4196 | Company Initiated | Personnel- company | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
4197 | Company Initiated | Personnel- company | Interrupter | Malfunctioning | None | Company Initiated Outage. Not outage related.
4198 | Company Initiated | Personnel- company | Conductor- Underground | Blown/failed | None | Company Initiated Outage. Not outage related.
4199 | Company Initiated | Personnel- company | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
4200 | Company Initiated | Personnel- company | Transformer (UG) |  | None | Company Initiated Outage. Not outage related.
4201 | Company Initiated | Personnel- company | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
4202 | Company Initiated | Personnel- company | Switch | Normal | None | Company Initiated Outage. Not outage related.
4203 | Company Initiated | Personnel- company | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
4204 | Company Initiated | Personnel- company | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
4205 | Company Initiated | Personnel- company | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
4206 | Company Initiated | Personnel- company | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
4207 | Company Initiated | Personnel- company |  | Broken | None | Company Initiated Outage. Not outage related.
4208 | Company Initiated | Personnel- company | Elbow | Normal | None | Company Initiated Outage. Not outage related.
4209 | Company Initiated | Personnel- company | Transformer (OH) | Contaminated | None | Company Initiated Outage. Not outage related.
4210 | Company Initiated | Personnel- company |  | Blown/failed | None | Company Initiated Outage. Not outage related.
4211 | Company Initiated | Personnel- company | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
4212 | Company Initiated | Personnel- company | SCADA | Normal | None | Company Initiated Outage. Not outage related.
4213 | Company Initiated | Personnel- company | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
4214 | Company Initiated | Personnel- company | Transformer | Leaking | None | Company Initiated Outage. Not outage related.
4215 | Company Initiated | Personnel- company | Jumper | Normal | None | Company Initiated Outage. Not outage related.
4216 | Company Initiated | Personnel- company | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
4217 | Company Initiated | Personnel- company | Sectionalizer | Normal | None | Company Initiated Outage. Not outage related.
4218 | Company Initiated | Personnel- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4219 | Company Initiated | Personnel- company | Capacitor | Malfunctioning | None | Company Initiated Outage. Not outage related.
4220 | Company Initiated | Personnel- company | Conductor- Overhead |  | None | Company Initiated Outage. Not outage related.
4221 | Company Initiated | Personnel- company | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
4222 | Company Initiated | Personnel- company | Secondary | Deteriorated | None | Company Initiated Outage. Not outage related.
4223 | Company Initiated | Personnel- company | Secondary | Burned Open | None | Company Initiated Outage. Not outage related.
4224 | Company Initiated | Personnel- company | Other | Deteriorated | None | Company Initiated Outage. Not outage related.
4225 | Company Initiated | Personnel- company | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
4226 | Company Initiated | Personnel- company | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
4227 | Company Initiated | Personnel- company |  | Normal | None | Company Initiated Outage. Not outage related.
4228 | Company Initiated | Personnel- company | Regulator | Blown/failed | None | Company Initiated Outage. Not outage related.
4229 | Company Initiated | Personnel- company | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
4230 | Company Initiated | Personnel- company | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
4231 | Company Initiated | Personnel- company | Cutout- Fused- Distribution | Arcing | None | Company Initiated Outage. Not outage related.
4232 | Company Initiated | Personnel- company | Crossarm- Steel | Arcing | None | Company Initiated Outage. Not outage related.
4233 | Company Initiated | Personnel- company | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
4234 | Company Initiated | Personnel- company | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
4235 | Company Initiated | Personnel- company | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
4236 | Company Initiated | Personnel- company | Metering Equipment |  | None | Company Initiated Outage. Not outage related.
4237 | Company Initiated | Personnel- company | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
4238 | Company Initiated | Personnel- company | Conductor- Underground | Malfunctioning | None | Company Initiated Outage. Not outage related.
4239 | Company Initiated | Personnel- company | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
4240 | Company Initiated | Personnel- company | Switch | Malfunctioning | None | Company Initiated Outage. Not outage related.
4241 | Company Initiated | Personnel- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
4242 | Company Initiated | Personnel- company | Cutout- Fused- Distribution | Normal | None | Company Initiated Outage. Not outage related.
4243 | Company Initiated | Personnel- company | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
4244 | Company Initiated | Personnel- company | Bus | Normal | None | Company Initiated Outage. Not outage related.
4245 | Company Initiated | Personnel- company | Transformer (OH) | Leaking | None | Company Initiated Outage. Not outage related.
4246 | Company Initiated | Personnel- company | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
4247 | Company Initiated | Personnel- company | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
4248 | Company Initiated | Return Circuit Normal | Stepdown | Normal | None | Company Initiated Outage. Not outage related.
4249 | Company Initiated | Return Circuit Normal | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
4250 | Company Initiated | Return Circuit Normal | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
4251 | Company Initiated | Return Circuit Normal | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
4252 | Company Initiated | Return Circuit Normal | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
4253 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
4254 | Company Initiated | Return Circuit Normal | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
4255 | Company Initiated | Return Circuit Normal | Other | Normal | None | Company Initiated Outage. Not outage related.
4256 | Company Initiated | Return Circuit Normal | Fuse | Normal | None | Company Initiated Outage. Not outage related.
4257 | Company Initiated | Return Circuit Normal | Jumper | Normal | None | Company Initiated Outage. Not outage related.
4258 | Company Initiated | Return Circuit Normal | Recloser | Normal | None | Company Initiated Outage. Not outage related.
4259 | Company Initiated | Return Circuit Normal | Secondary | Broken | None | Company Initiated Outage. Not outage related.
4260 | Company Initiated | Return Circuit Normal | Switch (OH) | Broken | None | Company Initiated Outage. Not outage related.
4261 | Company Initiated | Return Circuit Normal | Insulator | Burned/flashed | None | Company Initiated Outage. Not outage related.
4262 | Company Initiated | Return Circuit Normal | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
4263 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
4264 | Company Initiated | Return Circuit Normal | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
4265 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken- wire on object | None | Company Initiated Outage. Not outage related.
4266 | Company Initiated | Return Circuit Normal | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
4267 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
4268 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
4269 | Company Initiated | Return Circuit Normal | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
4270 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
4271 | Company Initiated | Return Circuit Normal | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
4272 | Company Initiated | Return Circuit Normal | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
4273 | Company Initiated | Return Circuit Normal | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
4274 | Company Initiated | Return Circuit Normal | Recloser | Burned/flashed | None | Company Initiated Outage. Not outage related.
4275 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
4276 | Company Initiated | Return Circuit Normal | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
4277 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
4278 | Company Initiated | Return Circuit Normal | Elbow | Normal | None | Company Initiated Outage. Not outage related.
4279 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
4280 | Company Initiated | Return Circuit Normal | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4281 | Company Initiated | Return Circuit Normal | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
4282 | Company Initiated | Return Circuit Normal | Generator | Normal | None | Company Initiated Outage. Not outage related.
4283 | Company Initiated | Return Circuit Normal | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
4284 | Company Initiated | Return Circuit Normal | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
4285 | Company Initiated | Return Circuit Normal | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
4286 | Company Initiated | Return Circuit Normal | Cable Termination(live front | Blown/failed | None | Company Initiated Outage. Not outage related.
4287 | Company Initiated | Return Circuit Normal | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
4288 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Blown/failed | None | Company Initiated Outage. Not outage related.
4289 | Company Initiated | Return Circuit Normal | Secondary | Normal | None | Company Initiated Outage. Not outage related.
4290 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4291 | Company Initiated | Return Circuit Normal | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
4292 | Company Initiated | Return Circuit Normal | Other | Deteriorated | None | Company Initiated Outage. Not outage related.
4293 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
4294 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
4295 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
4296 | Company Initiated | Return Circuit Normal | Circuit Breaker | Burned/flashed | None | Company Initiated Outage. Not outage related.
4297 | Company Initiated | Return Circuit Normal | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
4298 | Company Initiated | Return Circuit Normal | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
4299 | Company Initiated | Return Circuit Normal | Regulator | Normal | None | Company Initiated Outage. Not outage related.
4300 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
4301 | Company Initiated | Return Circuit Normal | Other | Blown/failed | None | Company Initiated Outage. Not outage related.
4302 | Company Initiated | Return Circuit Normal | Insulator | Normal | None | Company Initiated Outage. Not outage related.
4303 | Company Initiated | Return Circuit Normal | Switch (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
4304 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Arcing | None | Company Initiated Outage. Not outage related.
4305 | Company Initiated | Return Circuit Normal | SCADA | Normal | None | Company Initiated Outage. Not outage related.
4306 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
4307 | Company Initiated | Return Circuit Normal | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
4308 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Arcing | None | Company Initiated Outage. Not outage related.
4309 | Company Initiated | Return Circuit Normal | Lightning Arrestor | Blown/failed | None | Company Initiated Outage. Not outage related.
4310 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
4311 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
4312 | Company Initiated | Return Circuit Normal | Customer Equipment | Normal | None | Company Initiated Outage. Not outage related.
4313 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Broken | None | Company Initiated Outage. Not outage related.
4314 | Company Initiated | Return Circuit Normal | Secondary | Burned/flashed | None | Company Initiated Outage. Not outage related.
4315 | Company Initiated | Return Circuit Normal | Jumper | Broken | None | Company Initiated Outage. Not outage related.
4316 | Company Initiated | Return Circuit Normal | PGs- Kearneys | Normal | None | Company Initiated Outage. Not outage related.
4317 | Company Initiated | Return Circuit Normal | Pole-Wood | On Ground | None | Company Initiated Outage. Not outage related.
4318 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Burned/flashed | None | Company Initiated Outage. Not outage related.
4319 | Company Initiated | Return Circuit Normal | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
4320 | Company Initiated | Return Circuit Normal | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
4321 | Company Initiated | Return Circuit Normal | Insulator | Broken | None | Company Initiated Outage. Not outage related.
4322 | Company Initiated | Return Circuit Normal | Other | Broken | None | Company Initiated Outage. Not outage related.
4323 | Company Initiated | Return Circuit Normal | Transformer (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
4324 | Company Initiated | Return Circuit Normal | Booster | Burned/flashed | None | Company Initiated Outage. Not outage related.
4325 | Company Initiated | Return Circuit Normal | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
4326 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Bent or Twisted | None | Company Initiated Outage. Not outage related.
4327 | Company Initiated | Return Circuit Normal | Insulator | Broken- wire on object | None | Company Initiated Outage. Not outage related.
4328 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
4329 | Company Initiated | Return Circuit Normal | Bushing | Normal | None | Company Initiated Outage. Not outage related.
4330 | Company Initiated | Return Circuit Normal | Switch (OH) | Arcing | None | Company Initiated Outage. Not outage related.
4331 | Company Initiated | Return Circuit Normal | Woodpin | Broken | None | Company Initiated Outage. Not outage related.
4332 | Company Initiated | Return Circuit Normal | Service conductor | Normal | None | Company Initiated Outage. Not outage related.
4333 | Company Initiated | Return Circuit Normal | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
4334 | Company Initiated | Return Circuit Normal | Sectionalizer | Normal | None | Company Initiated Outage. Not outage related.
4335 | Company Initiated | Return Circuit Normal | Elbow | Broken | None | Company Initiated Outage. Not outage related.
4336 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Burned/flashed | None | Company Initiated Outage. Not outage related.
4337 | Company Initiated | Return Circuit Normal | Recloser | Broken | None | Company Initiated Outage. Not outage related.
4338 | Company Initiated | Return Circuit Normal | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
4339 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
4340 | Environmental/External | Earthquake | Other | Deteriorated | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
4341 | Environmental/External | Earthquake | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4342 | Environmental/External | Earthquake | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4343 | Environmental/External | Earthquake | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4344 | Environmental/External | Earthquake | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4345 | Environmental/External | Earthquake | Crossarm- Wood | Burned Open | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
4346 | Environmental/External | Earthquake | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4347 | Environmental/External | Earthquake | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4348 | Environmental/External | Earthquake | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4349 | Environmental/External | Earthquake | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4350 | Environmental/External | Earthquake | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4351 | Environmental/External | Earthquake | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
4352 | Environmental/External | Earthquake | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4353 | Environmental/External | Earthquake | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4354 | Environmental/External | Earthquake | Crossarm- Wood | Broken | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
4355 | Environmental/External | Earthquake | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4356 | Environmental/External | Earthquake | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4357 | Environmental/External | Earthquake | Service conductor | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4358 | Environmental/External | Earthquake | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4359 | Environmental/External | Earthquake | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4360 | Environmental/External | Earthquake | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4361 | Environmental/External | Earthquake | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4362 | Environmental/External | Earthquake | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4363 | Environmental/External | Earthquake | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4364 | Environmental/External | Earthquake | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4365 | Environmental/External | Earthquake | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
4366 | Environmental/External | Earthquake | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4367 | Environmental/External | Earthquake | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4368 | Environmental/External | Earthquake | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4369 | Environmental/External | Earthquake | Elbow | Blown/failed | All | Underground facilities = no ignition risk
4370 | Environmental/External | Earthquake | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4371 | Environmental/External | Earthquake | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
4372 | Environmental/External | Earthquake | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4373 | Environmental/External | Earthquake | Insulator | Broken | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
4374 | Environmental/External | Earthquake | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4375 | Environmental/External | Earthquake | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4376 | Environmental/External | Earthquake | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4377 | Environmental/External | Earthquake | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4378 | Environmental/External | Earthquake | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4379 | Environmental/External | Earthquake | Insulator | Blown/failed | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
4380 | Environmental/External | Earthquake | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4381 | Environmental/External | Earthquake | Recloser | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4382 | Environmental/External | Fire- Forest/Grass | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4383 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4384 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4385 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Burned/flashed | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4386 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4387 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4388 | Environmental/External | Fire- Forest/Grass | Switch (UG) | Normal | All | Underground facilities = no ignition risk
4389 | Environmental/External | Fire- Forest/Grass | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4390 | Environmental/External | Fire- Forest/Grass | Cutout- fuse holder | Normal | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
4391 | Environmental/External | Fire- Forest/Grass | Recloser | Normal | All | Covered conductor will eliminate the line slap/smoke arc and risk associated with this outage.
4392 | Environmental/External | Fire- Forest/Grass | Crossarm- Wood | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4393 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Broken | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4394 | Environmental/External | Fire- Forest/Grass | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk/smoke arc associated with this outage.
4395 | Environmental/External | Fire- Forest/Grass | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4396 | Environmental/External | Fire- Forest/Grass | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4397 | Environmental/External | Fire- Forest/Grass | Other | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4398 | Environmental/External | Fire- Forest/Grass | Other | Burned Open | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4399 | Environmental/External | Fire- Forest/Grass | Other | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4400 | Environmental/External | Fire- Forest/Grass | Pole-Wood | On Ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4401 | Environmental/External | Fire- Forest/Grass | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4402 | Environmental/External | Fire- Forest/Grass | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4403 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Blown/failed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4404 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Broken | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4405 | Environmental/External | Fire- Forest/Grass | Insulator | Broken- wire on object | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4406 | Environmental/External | Fire- Forest/Grass | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
4407 | Environmental/External | Fire- Forest/Grass | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
4408 | Environmental/External | Fire- Forest/Grass | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4409 | Environmental/External | Fire- Forest/Grass | Transformer | Arcing | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4410 | Environmental/External | Fire- Forest/Grass | Transformer | Malfunctioning | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4411 | Environmental/External | Fire- Forest/Grass | Customer Equipment | Burned/flashed | None | System hardening does not address customer equipment
4412 | Environmental/External | Fire- Forest/Grass | Pothead(Riser Termination) | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4413 | Environmental/External | Fire- Forest/Grass | Pothead(Riser Termination) | Deteriorated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4414 | Environmental/External | Fire- Forest/Grass | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
4415 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Deteriorated | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4416 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | On Ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4417 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Deteriorated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4418 | Environmental/External | Fire- Forest/Grass | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4419 | Environmental/External | Fire- Forest/Grass | Transformer | Blown/failed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4420 | Environmental/External | Fire- Forest/Grass |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4421 | Environmental/External | Fire- Forest/Grass | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
4422 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Burned/flashed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4423 | Environmental/External | Fire- Forest/Grass | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4424 | Environmental/External | Fire- Forest/Grass | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4425 | Environmental/External | Fire- Forest/Grass | Crossarm- Wood | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4426 | Environmental/External | Fire- Forest/Grass | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4427 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Normal | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4428 | Environmental/External | Fire- Forest/Grass | Connector or Splice (OH) | Broken- wire on ground | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4429 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Leaking | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4430 | Environmental/External | Fire- Forest/Grass | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4431 | Environmental/External | Fire- Forest/Grass | Insulator | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4432 | Environmental/External | Fire- Forest/Grass | Regulator | Burned/flashed | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
4433 | Environmental/External | Fire- Forest/Grass | Crossarm- Wood | Broken | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4434 | Environmental/External | Fire- Forest/Grass | Insulator | Malfunctioning | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4435 | Environmental/External | Fire- Forest/Grass | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4436 | Environmental/External | Fire- Forest/Grass | Switch (OH) | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4437 | Environmental/External | Fire- Forest/Grass | Cutout- Fused- Distribution | Blown/failed | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
4438 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Normal | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4439 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Contaminated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4440 | Environmental/External | Fire- Forest/Grass | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
4441 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Broken | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4442 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Broken- wire on object | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4443 | Environmental/External | Fire- Forest/Grass | Relay | Normal | All | Covered conductor will eliminate "smoke arcing" and risk associated with this outage.
4444 | Environmental/External | Fire- Forest/Grass | Transformer | Burned/flashed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4445 | Environmental/External | Fire- Forest/Grass | Elbow | Blown/failed | All | Underground facilities = no ignition risk
4446 | Environmental/External | Fire- Forest/Grass | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
4447 | Environmental/External | Fire- Forest/Grass | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4448 | Environmental/External | Fire- Forest/Grass | Footings- Tower or Pole | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4449 | Environmental/External | Fire- Forest/Grass | Jumper | Broken | High | SECONDARY IGNITION RISK - Larger covered conductor to mostly eliminate cause and risk.
4450 | Environmental/External | Fire- Forest/Grass | Switch | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4451 | Environmental/External | Fire- Forest/Grass | Transformer | Broken | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4452 | Environmental/External | Fire- Forest/Grass | Riser | Blown/failed | High | SECONDARY IGNITION RISK - Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
4453 | Environmental/External | Fire- Forest/Grass | Woodpin | Burned Open | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4454 | Environmental/External | Fire- Forest/Grass | Recloser | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4455 | Environmental/External | Fire- Forest/Grass | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4456 | Environmental/External | Fire- Forest/Grass | Cutout- fuse holder | Broken | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
4457 | Environmental/External | Fire- Forest/Grass | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
4458 | Environmental/External | Fire- Forest/Grass | Customer Equipment | Broken | None | System hardening does not address customer equipment
4459 | Environmental/External | Fire- Forest/Grass | Insulator | Contaminated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4460 | Environmental/External | Fire- Forest/Grass | Connector or Splice (OH) | Burned Open | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4461 | Environmental/External | Fire- Forest/Grass | Cutout- fuse holder | Burned Open | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
4462 | Environmental/External | Fire- Forest/Grass | Transformer | Normal | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4463 | Environmental/External | Fire- Forest/Grass | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4464 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Contaminated | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4465 | Environmental/External | Fire- Forest/Grass | Connector or Splice (OH) | On Ground | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4466 | Environmental/External | Fire- Forest/Grass | Jumper | Normal | High | SECONDARY IGNITION RISK - Larger covered conductor to mostly eliminate cause and risk.
4467 | Environmental/External | Fire- Forest/Grass | Regulator | Blown/failed | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
4468 | Environmental/External | Fire- Forest/Grass | Other | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4469 | Environmental/External | Fire- Forest/Grass | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4470 | Environmental/External | Fire- Forest/Grass | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
4471 | Environmental/External | Fire- Forest/Grass | Anchor or Guy | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4472 | Environmental/External | Fire- Forest/Grass | Recloser | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4473 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Burned Open | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4474 | Environmental/External | Fire- Forest/Grass | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4475 | Environmental/External | Fire- Forest/Grass | Connector or Splice (OH) | Burned/flashed | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4476 | Environmental/External | Fire- Forest/Grass | Pole - Tower- steel | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4477 | Environmental/External | Fire- Forest/Grass | Insulator | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4478 | Environmental/External | Fire- Forest/Grass | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4479 | Environmental/External | Fire- Forest/Grass | Customer Equipment | Malfunctioning | None | System hardening does not address customer equipment
4480 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Deteriorated | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4481 | Environmental/External | Fire- Forest/Grass | Switch | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4482 | Environmental/External | Fire- Forest/Grass | Connector or Splice (OH) | Broken- wire on object | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4483 | Environmental/External | Fire- Forest/Grass | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent.
4484 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Annealed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4485 | Environmental/External | Flood/Erosion | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4486 | Environmental/External | Flood/Erosion | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4487 | Environmental/External | Flood/Erosion | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4488 | Environmental/External | Flood/Erosion | Conductor- Overhead | Together | Low | Water and Moisture limit ignition risk
4489 | Environmental/External | Flood/Erosion | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4490 | Environmental/External | Flood/Erosion | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4491 | Environmental/External | Flood/Erosion | Conductor- Overhead | Normal | Low | Water and Moisture limit ignition risk
4492 | Environmental/External | Flood/Erosion | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4493 | Environmental/External | Flood/Erosion | Fuse | Normal | High | Moisture and Water should eliminate Ignition Risk. Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4494 | Environmental/External | Flood/Erosion | Conductor- Overhead | Broken | Low | Water and Moisture limit ignition risk
4495 | Environmental/External | Flood/Erosion | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4496 | Environmental/External | Flood/Erosion | Conductor- Overhead | Bent or Twisted | Low | Water and Moisture limit ignition risk
4497 | Environmental/External | Flood/Erosion | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4498 | Environmental/External | Flood/Erosion | Conductor- Overhead | Arcing | Low | Water and Moisture limit ignition risk
4499 | Environmental/External | Flood/Erosion | Anchor or Guy | Broken | Low | Water and Moisture limit ignition risk
4500 | Environmental/External | Flood/Erosion | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
4501 | Environmental/External | Flood/Erosion | Conductor- Overhead | Deteriorated | Low | Water and Moisture limit ignition risk
4502 | Environmental/External | Flood/Erosion | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4503 | Environmental/External | Flood/Erosion | Switch (UG) | Normal | All | Underground facilities = no ignition risk
4504 | Environmental/External | Flood/Erosion | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4505 | Environmental/External | Flood/Erosion | Insulator | Burned/flashed | Low | Water and Moisture limit ignition risk
4506 | Environmental/External | Flood/Erosion | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
4507 | Environmental/External | Flood/Erosion | Fuse | Blown/failed | High | Moisture and Water should eliminate Ignition Risk. Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4508 | Environmental/External | Flood/Erosion | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4509 | Environmental/External | Flood/Erosion | Crossarm- Wood | Broken | Low | Water and Moisture limit ignition risk
4510 | Environmental/External | Flood/Erosion | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4511 | Environmental/External | Flood/Erosion | Customer Equipment | Normal | None | System hardening does not address customer equipment
4512 | Environmental/External | Flood/Erosion | Connector or Splice (UG) | Deteriorated | All | Underground facilities = no ignition risk
4513 | Environmental/External | Flood/Erosion | Other | Normal | Low | Water and Moisture limit ignition risk
4514 | Environmental/External | Flood/Erosion | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
4515 | Environmental/External | Flood/Erosion | Customer Equipment | Contaminated | None | System hardening does not address customer equipment
4516 | Environmental/External | Flood/Erosion | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
4517 | Environmental/External | Flood/Erosion | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4518 | Environmental/External | Flood/Erosion | Switch (OH) | Normal | Low | Water and Moisture limit ignition risk
4519 | Environmental/External | Flood/Erosion | Other | Arcing | Low | Water and Moisture limit ignition risk
4520 | Environmental/External | Flood/Erosion | Other | Deteriorated | Low | Water and Moisture limit ignition risk
4521 | Environmental/External | Flood/Erosion | Conductor- Overhead | Burned/flashed | Low | Water and Moisture limit ignition risk
4522 | Environmental/External | Flood/Erosion | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4523 | Environmental/External | Flood/Erosion | Crossarm- Wood | Deteriorated | Low | Water and Moisture limit ignition risk
4524 | Environmental/External | Flood/Erosion | Pole - Tower- steel | Deteriorated | Low | Water and Moisture limit ignition risk
4525 | Environmental/External | Flood/Erosion | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4526 | Environmental/External | Flood/Erosion | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
4527 | Environmental/External | Flood/Erosion | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4528 | Environmental/External | Flood/Erosion | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4529 | Environmental/External | Flood/Erosion | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4530 | Environmental/External | Flood/Erosion | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
4531 | Environmental/External | Flood/Erosion | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
4532 | Environmental/External | Flood/Erosion | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
4533 | Environmental/External | Flood/Erosion | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4534 | Environmental/External | Flood/Erosion | Anchor or Guy | Deteriorated | Low | Water and Moisture limit ignition risk
4535 | Environmental/External | Flood/Erosion | Switch | Broken | Low | Water and Moisture limit ignition risk
4536 | Environmental/External | Flood/Erosion | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4537 | Environmental/External | Ice or snow | Conductor- Overhead | Normal | All | Ice and Snow conditions should have no ignition risk.
4538 | Environmental/External | Ice or snow | Service conductor | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4539 | Environmental/External | Ice or snow | Crossarm- Wood | Broken | All | Ice and Snow conditions should have no ignition risk.
4540 | Environmental/External | Ice or snow | Conductor- Overhead | On Ground | All | Ice and Snow conditions should have no ignition risk.
4541 | Environmental/External | Ice or snow | Conductor- Overhead | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4542 | Environmental/External | Ice or snow | Conductor- Overhead | Together | All | Ice and Snow conditions should have no ignition risk.
4543 | Environmental/External | Ice or snow | Recloser | Normal | All | Ice and Snow conditions should have no ignition risk.
4544 | Environmental/External | Ice or snow | Insulator | Broken | All | Ice and Snow conditions should have no ignition risk.
4545 | Environmental/External | Ice or snow | Pole-Wood | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4546 | Environmental/External | Ice or snow | Pole-Wood | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
4547 | Environmental/External | Ice or snow | Fuse | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
4548 | Environmental/External | Ice or snow | Transformer (OH) | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
4549 | Environmental/External | Ice or snow | Conductor- Overhead | Bent or Twisted | All | Ice and Snow conditions should have no ignition risk.
4550 | Environmental/External | Ice or snow | Connector or Splice (OH) | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4551 | Environmental/External | Ice or snow | Insulator | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
4552 | Environmental/External | Ice or snow | Conductor- Overhead | Broken | All | Ice and Snow conditions should have no ignition risk.
4553 | Environmental/External | Ice or snow | Crossarm- Wood | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4554 | Environmental/External | Ice or snow | Fuse | Normal | All | Ice and Snow conditions should have no ignition risk.
4555 | Environmental/External | Ice or snow | Transformer | Broken | All | Ice and Snow conditions should have no ignition risk.
4556 | Environmental/External | Ice or snow | Transformer | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
4557 | Environmental/External | Ice or snow | Connector or Splice (OH) | Broken | All | Ice and Snow conditions should have no ignition risk.
4558 | Environmental/External | Ice or snow | Pole-Wood | Broken | All | Ice and Snow conditions should have no ignition risk.
4559 | Environmental/External | Ice or snow | Conductor- Overhead | Arcing | All | Ice and Snow conditions should have no ignition risk.
4560 | Environmental/External | Ice or snow | Secondary | Deteriorated | All | Ice and Snow conditions should have no ignition risk.
4561 | Environmental/External | Ice or snow | Service conductor | Broken | All | Ice and Snow conditions should have no ignition risk.
4562 | Environmental/External | Ice or snow | Secondary | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4563 | Environmental/External | Ice or snow | Other | Broken | All | Ice and Snow conditions should have no ignition risk.
4564 | Environmental/External | Ice or snow | Conductor- Overhead | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
4565 | Environmental/External | Ice or snow |  |  | All | Ice and Snow conditions should have no ignition risk.
4566 | Environmental/External | Ice or snow | Jumper | Broken | All | Ice and Snow conditions should have no ignition risk.
4567 | Environmental/External | Ice or snow | Conductor- Overhead | Burned/flashed | All | Ice and Snow conditions should have no ignition risk.
4568 | Environmental/External | Ice or snow |  | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
4569 | Environmental/External | Ice or snow | Transformer | Normal | All | Ice and Snow conditions should have no ignition risk.
4570 | Environmental/External | Ice or snow | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
4571 | Environmental/External | Ice or snow | Crossarm- Wood | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
4572 | Environmental/External | Ice or snow | Other | Annealed | All | Ice and Snow conditions should have no ignition risk.
4573 | Environmental/External | Ice or snow | Insulator | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4574 | Environmental/External | Ice or snow | Connector or Splice (OH) | Normal | All | Ice and Snow conditions should have no ignition risk.
4575 | Environmental/External | Ice or snow | Secondary | Broken | All | Ice and Snow conditions should have no ignition risk.
4576 | Environmental/External | Lightning | Recloser | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4577 | Environmental/External | Lightning | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4578 | Environmental/External | Lightning | Circuit Breaker | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
4579 | Environmental/External | Lightning | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent.
4580 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4581 | Environmental/External | Lightning | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4582 | Environmental/External | Lightning | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4583 | Environmental/External | Lightning |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4584 | Environmental/External | Lightning | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4585 | Environmental/External | Lightning | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4586 | Environmental/External | Lightning | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4587 | Environmental/External | Lightning | Switch | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4588 | Environmental/External | Lightning | Conductor- Overhead | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
4589 | Environmental/External | Lightning | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4590 | Environmental/External | Lightning | Other | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4591 | Environmental/External | Lightning | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4592 | Environmental/External | Lightning | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
4593 | Environmental/External | Lightning |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4594 | Environmental/External | Lightning | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4595 | Environmental/External | Lightning | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
4596 | Environmental/External | Lightning | Other | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4597 | Environmental/External | Lightning | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4598 | Environmental/External | Lightning | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4599 | Environmental/External | Lightning | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4600 | Environmental/External | Lightning | Recloser | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
4601 | Environmental/External | Lightning | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4602 | Environmental/External | Lightning | Insulator | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4603 | Environmental/External | Lightning | Conductor- Overhead | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4604 | Environmental/External | Lightning | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4605 | Environmental/External | Lightning | Conductor- Overhead | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4606 | Environmental/External | Lightning | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4607 | Environmental/External | Lightning | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4608 | Environmental/External | Lightning | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent.
4609 | Environmental/External | Lightning | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
4610 | Environmental/External | Lightning | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4611 | Environmental/External | Lightning | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4612 | Environmental/External | Lightning | Capacitor | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4613 | Environmental/External | Lightning | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4614 | Environmental/External | Lightning | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4615 | Environmental/External | Lightning | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4616 | Environmental/External | Lightning | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
4617 | Environmental/External | Lightning | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4618 | Environmental/External | Lightning | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4619 | Environmental/External | Lightning | Crossarm- Wood | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4620 | Environmental/External | Lightning | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4621 | Environmental/External | Lightning | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
4622 | Environmental/External | Lightning | Conductor- Overhead | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4623 | Environmental/External | Lightning | Crossarm- Wood | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4624 | Environmental/External | Lightning | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4625 | Environmental/External | Lightning | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4626 | Environmental/External | Lightning | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
4627 | Environmental/External | Lightning | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk/smoke arc associated with this outage.
4628 | Environmental/External | Lightning | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4629 | Environmental/External | Lightning | Regulator | Burned/flashed | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
4630 | Environmental/External | Lightning | Insulator | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4631 | Environmental/External | Lightning | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4632 | Environmental/External | Lightning | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4633 | Environmental/External | Lightning | Insulator | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4634 | Environmental/External | Lightning | Anchor or Guy | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4635 | Environmental/External | Lightning | Booster | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4636 | Environmental/External | Lightning | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4637 | Environmental/External | Lightning | Regulator | Blown/failed | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
4638 | Environmental/External | Lightning | Recloser | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4639 | Environmental/External | Lightning | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4640 | Environmental/External | Lightning | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4641 | Environmental/External | Lightning |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4642 | Environmental/External | Lightning | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4643 | Environmental/External | Lightning | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4644 | Environmental/External | Lightning | Crossarm- Steel | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4645 | Environmental/External | Lightning | Switch (OH) | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4646 | Environmental/External | Lightning | Switch | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4647 | Environmental/External | Lightning | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4648 | Environmental/External | Lightning | Bushing | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4649 | Environmental/External | Lightning | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4650 | Environmental/External | Lightning | Capacitor | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4651 | Environmental/External | Lightning | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
4652 | Environmental/External | Lightning | Transformer |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4653 | Environmental/External | Lightning | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4654 | Environmental/External | Lightning | Customer Equipment | Burned/flashed | None | System hardening does not address customer equipment
4655 | Environmental/External | Lightning | PGs- Kearneys | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4656 | Environmental/External | Lightning | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4657 | Environmental/External | Lightning | Cutout- fuse holder | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4658 | Environmental/External | Lightning | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4659 | Environmental/External | Lightning |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4660 | Environmental/External | Lightning | Other | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
4661 | Environmental/External | Lightning | Recloser | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
4662 | Environmental/External | Lightning | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4663 | Environmental/External | Lightning |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4664 | Environmental/External | Lightning | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent.
4665 | Environmental/External | Lightning | Customer Equipment | Blown/failed | None | System hardening does not address customer equipment
4666 | Environmental/External | Lightning | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4667 | Environmental/External | Lightning | Bushing | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4668 | Environmental/External | Lightning | Street Light Equipment | Blown/failed | Medium | System Hardening will not address Street Lights but will address their transformers.
4669 | Environmental/External | Lightning | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4670 | Environmental/External | Lightning | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
4671 | Environmental/External | Lightning | Splice box | Burned/flashed | All | Underground facilities = no ignition risk
4672 | Environmental/External | Lightning | Recloser | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4673 | Environmental/External | Lightning | Stepdown | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4674 | Environmental/External | Lightning | Transformer (UG) | Deteriorated | All | Underground facilities = no ignition risk
4675 | Environmental/External | Lightning | Splice box | Malfunctioning | All | Underground facilities = no ignition risk
4676 | Environmental/External | Lightning | Conductor- Overhead | Together | None | System Hardening will not mitigate for Environmental factors for this outage.
4677 | Environmental/External | Lightning | Switch (OH) | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4678 | Environmental/External | Lightning | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4679 | Environmental/External | Lightning | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4680 | Environmental/External | Lightning | Bushing | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4681 | Environmental/External | Lightning | Transformer (OH) |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4682 | Environmental/External | Lightning | Sectionalizer | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4683 | Environmental/External | Lightning | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4684 | Environmental/External | Lightning | Switch (UG) | Blown/failed | All | Underground facilities = no ignition risk
4685 | Environmental/External | Lightning | Other | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4686 | Environmental/External | Lightning | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4687 | Environmental/External | Lightning | Capacitor | Arcing | None | System Hardening will not mitigate for Environmental factors for this outage.
4688 | Environmental/External | Lightning | Conductor- Overhead | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
4689 | Environmental/External | Lightning | Insulator | Arcing | None | System Hardening will not mitigate for Environmental factors for this outage.
4690 | Environmental/External | Lightning | Conductor- Overhead | Burned Open | None | System Hardening will not mitigate for Environmental factors for this outage.
4691 | Environmental/External | Lightning | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4692 | Environmental/External | Lightning | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4693 | Environmental/External | Lightning | Elbow | Blown/failed | All | Underground facilities = no ignition risk
4694 | Environmental/External | Lightning | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4695 | Environmental/External | Lightning | Jumper | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4696 | Environmental/External | Lightning | Fuse | Arcing | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4697 | Environmental/External | Lightning | Crossarm- Steel | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4698 | Environmental/External | Lightning | Conductor- Overhead | Arcing | None | System Hardening will not mitigate for Environmental factors for this outage.
4699 | Environmental/External | Lightning | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
4700 | Environmental/External | Lightning | Other | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
4701 | Environmental/External | Lightning | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4702 | Environmental/External | Lightning | Other | Bent or Twisted | None | System Hardening will not mitigate for Environmental factors for this outage.
4703 | Environmental/External | Lightning | Regulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4704 | Environmental/External | Lightning | Pothead/Riser Termination | Burned Open | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4705 | Environmental/External | Lightning | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4706 | Environmental/External | Lightning | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4707 | Environmental/External | Lightning | Sectionalizer | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
4708 | Environmental/External | Lightning | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4709 | Environmental/External | Lightning | Lightning Arrestor | Arcing | All | We are replacing lightning arrestors with their exempt equivalent.
4710 | Environmental/External | Water | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
4711 | Environmental/External | Water | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4712 | Environmental/External | Water | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
4713 | Environmental/External | Water | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
4714 | Environmental/External | Water | Conductor- Overhead | Normal | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4715 | Environmental/External | Water | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4716 | Environmental/External | Water | Crossarm- Wood | Burned Open | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4717 | Environmental/External | Water | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4718 | Environmental/External | Water | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4719 | Environmental/External | Water | Recloser | Normal | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4720 | Environmental/External | Water | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4721 | Environmental/External | Water | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4722 | Environmental/External | Water | Crossarm- Wood | Burned/flashed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4723 | Environmental/External | Water | Elbow | Blown/failed | All | Underground facilities = no ignition risk
4724 | Environmental/External | Water | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4725 | Environmental/External | Water | Secondary | Burned/flashed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4726 | Environmental/External | Water | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
4727 | Environmental/External | Water | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4728 | Environmental/External | Water | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4729 | Environmental/External | Water | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
4730 | Environmental/External | Water | Connector or Splice (UG) | Contaminated | All | Underground facilities = no ignition risk
4731 | Environmental/External | Water | Conductor- Overhead | Together | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4732 | Environmental/External | Water | Other | Leaking | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4733 | Environmental/External | Water | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
4734 | Environmental/External | Water | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4735 | Environmental/External | Water | Insulator | Blown/failed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4736 | Environmental/External | Water | Insulator | Broken | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4737 | Environmental/External | Water | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4738 | Environmental/External | Water | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
4739 | Environmental/External | Water | Pothead/Riser Termination | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4740 | Environmental/External | Water | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4741 | Environmental/External | Water | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4742 | Environmental/External | Water | Insulator | Arcing | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4743 | Environmental/External | Water | Connector or Splice (UG) | Burned Open | All | Underground facilities = no ignition risk
4744 | Environmental/External | Water | Secondary | Normal | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4745 | Environmental/External | Water | Switch | Blown/failed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4746 | Environmental/External | Water | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4747 | Environmental/External | Water | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4748 | Environmental/External | Water | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4749 | Environmental/External | Water | Conductor- Overhead | Contaminated | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4750 | Environmental/External | Water | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
4751 | Environmental/External | Water | Connector or Splice (OH) | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4752 | Environmental/External | Water | Transformer (UG) | Leaking | All | Underground facilities = no ignition risk
4753 | Environmental/External | Water | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4754 | Environmental/External | Water | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4755 | Environmental/External | Water | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
4756 | Environmental/External | Water | Customer Equipment | Normal | None | System hardening does not address customer equipment
4757 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Burned Open | All | Underground facilities = no ignition risk
4758 | Equipment Failure/Involved | Electrical Overload | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4759 | Equipment Failure/Involved | Electrical Overload | PGs- Kearneys | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4760 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
4761 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Broken | None | No work is being completed on customer equipment.
4762 | Equipment Failure/Involved | Electrical Overload | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4763 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Annealed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4764 | Equipment Failure/Involved | Electrical Overload | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4765 | Equipment Failure/Involved | Electrical Overload | Elbow | Normal | All | Underground facilities = no ignition risk
4766 | Equipment Failure/Involved | Electrical Overload | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4767 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4768 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
4769 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4770 | Equipment Failure/Involved | Electrical Overload | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4771 | Equipment Failure/Involved | Electrical Overload | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4772 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Deteriorated | All | Underground facilities = no ignition risk
4773 | Equipment Failure/Involved | Electrical Overload | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4774 | Equipment Failure/Involved | Electrical Overload | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4775 | Equipment Failure/Involved | Electrical Overload | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
4776 | Equipment Failure/Involved | Electrical Overload | Bus | Burned Open | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4777 | Equipment Failure/Involved | Electrical Overload | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4778 | Equipment Failure/Involved | Electrical Overload | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4779 | Equipment Failure/Involved | Electrical Overload | Controls | Broken | None | System hardening project will not typically address controls.
4780 | Equipment Failure/Involved | Electrical Overload | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4781 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Burned Open | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4782 | Equipment Failure/Involved | Fire- pole | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4783 | Equipment Failure/Involved | Fire- pole | Lightning Arrestor | Arcing | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
4784 | Equipment Failure/Involved | Fire- pole | Fuse | Malfunctioning | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4785 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Together | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4786 | Equipment Failure/Involved | Fire- pole | Transformer | Malfunctioning | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
4787 | Equipment Failure/Involved | Fire- pole | Pole - Tower- steel | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
4788 | Equipment Failure/Involved | Fire- pole | Cutout- fuse holder | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
4789 | Equipment Failure/Involved | Fire- pole | Transformer |  | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
4790 | Equipment Failure/Involved | Fire- pole | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4791 | Equipment Failure/Involved | Fire- pole | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4792 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
4793 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4794 | Equipment Failure/Involved | Other | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4795 | Equipment Failure/Involved | Other | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4796 | Equipment Failure/Involved | Other | Pole-Wood | Together | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4797 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4798 | Equipment Failure/Involved | Other | Switch | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4799 | Equipment Failure/Involved | Other | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4800 | Equipment Failure/Involved | Other | Conductor- Underground | Arcing | All | Underground facilities = no ignition risk
4801 | Equipment Failure/Involved | Other | Sectionalizer | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
4802 | Equipment Failure/Involved | Other | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4803 | Equipment Failure/Involved | Other | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4804 | Equipment Failure/Involved | Other | Riser | Burned Open | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
4805 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Blown/failed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4806 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Contaminated | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4807 | Equipment Failure/Involved | Other | Recloser | Normal | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4808 | Equipment Failure/Involved | Other | Jumper | Together | High | Larger covered conductor to mostly eliminate cause and risk.
4809 | Equipment Failure/Involved | Other | Sectionalizer | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
4810 | Equipment Failure/Involved | Other | Pole-Wood | Malfunctioning | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4811 | Equipment Failure/Involved | Other | Booster | Blown/failed | All | Circuit Hardening replaces boosters with voltage regulators.
4812 | Equipment Failure/Involved | Other | Capacitor | Burned Open | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
4813 | Equipment Failure/Involved | Other | Elbow | Deteriorated | All | Underground facilities = no ignition risk
4814 | Equipment Failure/Involved | Other | Riser | Burned/flashed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
4815 | Equipment Failure/Involved | Other | Other | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4816 | Equipment Failure/Involved | Other | Customer Equipment | Together | None | No work is being completed on customer equipment.
4817 | Equipment Failure/Involved | Other | Switch | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4818 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Annealed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4819 | Equipment Failure/Involved | Other | Anchor or Guy | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4820 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4821 | Equipment Failure/Involved | Other | Bus | Burned Open | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4822 | Equipment Failure/Involved | Other | Conductor- Underground | Annealed | All | Underground facilities = no ignition risk
4823 | Equipment Failure/Involved | Other | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4824 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4825 | Equipment Failure/Involved | Other | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4826 | Equipment Failure/Involved | Other | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4827 | Equipment Failure/Involved | Other | PGs- Kearneys | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4828 | Equipment Failure/Involved | Other | Relay | Malfunctioning | None | Circuit Hardening will not affect substation equipment.
4829 | Equipment Failure/Involved | Other | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4830 | Equipment Failure/Involved | Other | Metering Equipment | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4831 | Equipment Failure/Involved | Other | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
4832 | Equipment Failure/Involved | Other | Fuse | Contaminated | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4833 | Equipment Failure/Involved | Other | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4834 | Equipment Failure/Involved | Other | Booster | Deteriorated | All | Circuit Hardening replaces boosters with voltage regulators.
4835 | Equipment Failure/Involved | Other | Elbow | Normal | All | Underground facilities = no ignition risk
4836 | Equipment Failure/Involved | Other | Anchor or Guy | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4837 | Equipment Failure/Involved | Other | Recloser | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4838 | Equipment Failure/Involved | Other | Relay | Burned/flashed | None | Circuit Hardening will not affect substation equipment.
4839 | Equipment Failure/Involved | Other | Woodpin | Broken- wire on object | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
4840 | Equipment Failure/Involved | Other |  | Arcing | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4841 | Equipment Failure/Involved | Other | Manhole- primary box | Blown/failed | All | Underground facilities = no ignition risk
4842 | Equipment Failure/Involved | Other | Jumper | Leaking | High | Larger covered conductor to mostly eliminate cause and risk.
4843 | Equipment Failure/Involved | Other | Recloser | Broken | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4844 | Equipment Failure/Involved | Other | Sectionalizer | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4845 | Equipment Failure/Involved | Other | Capacitor | Contaminated | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
4846 | Equipment Failure/Involved | Other | Splice box | Blown/failed | All | Underground facilities = no ignition risk
4847 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Together | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4848 | Equipment Failure/Involved | Other | Manhole- primary box | Contaminated | All | Underground facilities = no ignition risk
4849 | Equipment Failure/Involved | Other | Interrupter | Normal | All | Underground facilities = no ignition risk
4850 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Together | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4851 | Equipment Failure/Involved | Other | Regulator- LTC substation | Normal | None | Circuit Hardening will not affect substation equipment.
4852 | Equipment Failure/Involved | Other | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4853 | Equipment Failure/Involved | Other | Regulator | Deteriorated | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
4854 | Equipment Failure/Involved | Other | Crossarm- Wood | Together | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4855 | Equipment Failure/Involved | Other | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4856 | Equipment Failure/Involved | Other | Pole - Tower- steel | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4857 | Equipment Failure/Involved | Other | Crossarm- Wood | Arcing | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4858 | Equipment Failure/Involved | Other | Bushing | Burned Open | None | Significant external force broke the bushing. Ignition risk not mitigated.
4859 | Equipment Failure/Involved | Other | Crossarm- Wood | Bent or Twisted | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4860 | Equipment Failure/Involved | Other | Splice box | Burned/flashed | All | Underground facilities = no ignition risk
4861 | Equipment Failure/Involved | Other | Booster | Arcing | All | Circuit Hardening replaces boosters with voltage regulators.
4862 | Equipment Failure/Involved | Other | Switch | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4863 | Equipment Failure/Involved | Other | Metering Equipment | Broken | None | System Hardening does not address Metering facilities.
4864 | Equipment Failure/Involved | Other | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
4865 | Equipment Failure/Involved | Other | Bushing | Malfunctioning | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
4866 | Equipment Failure/Involved | Other | Bus | Malfunctioning | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4867 | Equipment Failure/Involved | Other | Cutout- fuse holder | Bent or Twisted | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4868 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Contaminated | All | Underground facilities = no ignition risk
4869 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4870 | Equipment Failure/Involved | Other | Regulator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
4871 | Equipment Failure/Involved | Other | Bushing | Arcing | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
4872 | Equipment Failure/Involved | Other | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4873 | Equipment Failure/Involved | Other | Street Light Equipment | Malfunctioning | Medium | System Hardening will not address Street Lights but will address their transformers.
4874 | Equipment Failure/Involved | Other | Riser | Arcing | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
4875 | Equipment Failure/Involved | Other | Splice box | Broken | All | Underground facilities = no ignition risk
4876 | Equipment Failure/Involved | Other | Fuse | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4877 | Equipment Failure/Involved | Other | PGs- Kearneys | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4878 | Equipment Failure/Involved | Other | Bus | Arcing | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4879 | Equipment Failure/Involved | Other | Woodpin | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4880 | Equipment Failure/Involved | Other | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4881 | Equipment Failure/Involved | Other | Splice box | Malfunctioning | All | Underground facilities = no ignition risk
4882 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Broken- wire on ground | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4883 | Equipment Failure/Involved | Other | Crossarm- Steel | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4884 | Equipment Failure/Involved | Other | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4885 | Equipment Failure/Involved | Other | Metering Equipment | Deteriorated | None | System Hardening does not address Metering facilities.
4886 | Equipment Failure/Involved | Other | Pole - Tower- steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4887 | Equipment Failure/Involved | Other | Other | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4888 | Equipment Failure/Involved | Other | Service conductor | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4889 | Equipment Failure/Involved | Other | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4890 | Equipment Failure/Involved | Other | Woodpin | Burned Open | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4891 | Equipment Failure/Involved | Other | Elbow | Bent or Twisted | All | Underground facilities = no ignition risk
4892 | Equipment Failure/Involved | Other | Lightning Arrestor | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4893 | Equipment Failure/Involved | Other | Fuse | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4894 | Equipment Failure/Involved | Other | Sectionalizer | Broken | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
4895 | Equipment Failure/Involved | Other | Fuse | Bent or Twisted | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4896 | Equipment Failure/Involved | Other | Manhole- primary box | Broken | All | Underground facilities = no ignition risk
4897 | Equipment Failure/Involved | Other | Metering Equipment | Arcing | None | System Hardening does not address Metering facilities.
4898 | Equipment Failure/Involved | Other | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
4899 | Equipment Failure/Involved | Other | Regulator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
4900 | Equipment Failure/Involved | Other | Booster | Broken | All | Circuit Hardening replaces boosters with voltage regulators.
4901 | Equipment Failure/Involved | Other | Booster | Leaking | All | Circuit Hardening replaces boosters with voltage regulators.
4902 | Equipment Failure/Involved | Other | Recloser | Burned Open | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4903 | Equipment Failure/Involved | Other | Bus | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4904 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4905 | Unknown Cause | Patrol - found nothing | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4906 | Unknown Cause | Patrol - found nothing | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4907 | Unknown Cause | Patrol - found nothing | Sectionalizer | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
4908 | Unknown Cause | Patrol - found nothing | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
4909 | Unknown Cause | Patrol - found nothing | Connector or Splice (OH) | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4910 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4911 | Unknown Cause | Patrol - found nothing | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4912 | Unknown Cause | Patrol - found nothing | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4913 | Unknown Cause | Patrol - found nothing | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4914 | Unknown Cause | Patrol - found nothing | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
4915 | Unknown Cause | Patrol - found nothing | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
4916 | Unknown Cause | Patrol - found nothing | Other | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4917 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4918 | Unknown Cause | Patrol - found nothing | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4919 | Unknown Cause | Patrol - found nothing | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4920 | Unknown Cause | Patrol - found nothing | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4921 | Unknown Cause | Patrol - not conducted | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
4922 | Unknown Cause | Patrol - not conducted | Elbow | Blown/failed | All | Underground facilities = no ignition risk
4923 | Unknown Cause | Patrol - not conducted | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4924 | Unknown Cause | Patrol - not conducted | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4925 | Unknown Cause | Patrol - not conducted | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4926 | Vegetation | Other ground vegetation | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4927 | Vegetation | Other ground vegetation | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
4928 | Vegetation | Other ground vegetation | Bus | Contaminated | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4929 | Vegetation | Other ground vegetation | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4930 | Vegetation | Other ground vegetation | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4931 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4932 | Vegetation | Tree - bark fell into line | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4933 | Vegetation | Tree - bark fell into line | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4934 | Vegetation | Tree - bark fell into line | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4935 | Vegetation | Tree - bark fell into line | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4936 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4937 | Vegetation | Tree - bark fell into line | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
4938 | Vegetation | Tree - bark fell into line | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4939 | Vegetation | Tree - bark fell into line | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
4940 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4941 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4942 | Vegetation | Tree - branch fell on line | Riser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4943 | Vegetation | Tree - branch fell on line | Crossarm- Steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4944 | Vegetation | Tree - branch fell on line | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4945 | Vegetation | Tree - branch fell on line | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4946 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4947 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Blown/failed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4948 | Vegetation | Tree - branch fell on line | Conductor- Underground | Broken- wire on ground | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4949 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4950 | Vegetation | Tree - branch fell on line | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
4951 | Vegetation | Tree - branch fell on line | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4952 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4953 | Vegetation | Tree - branch fell on line | Crossarm- Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4954 | Vegetation | Tree - branch fell on line | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4955 | Vegetation | Tree - branch fell on line | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4956 | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4957 | Vegetation | Tree - branch fell on line | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
4958 | Vegetation | Tree - branch fell on line | Elbow | Normal | All | Underground facilities = no ignition risk
4959 | Vegetation | Tree - branch fell on line | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4960 | Vegetation | Tree - branch fell on line | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4961 | Vegetation | Tree - branch fell on line | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4962 | Vegetation | Tree - cutting- PG&E contractor | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4963 | Vegetation | Tree - cutting- PG&E contractor | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4964 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4965 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4966 | Vegetation | Tree - cutting- PG&E contractor | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4967 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4968 | Vegetation | Tree - fell into line | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
4969 | Vegetation | Tree - fell into line | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4970 | Vegetation | Tree - fell into line | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4971 | Vegetation | Tree - fell into line | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4972 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4973 | Vegetation | Tree - fell into line | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4974 | Vegetation | Tree - fell into line | Riser | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4975 | Vegetation | Tree - fell into line | Pole-Wood | Bent or Twisted | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4976 | Vegetation | Tree - fell into line | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4977 | Vegetation | Tree - fell into line | Splice box | Malfunctioning | All | Underground facilities = no ignition risk
4978 | Vegetation | Tree - fell into line | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4979 | Vegetation | Tree - fell into line | Crossarm- Steel | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4980 | Vegetation | Tree - fell into line | Fuse | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4981 | Vegetation | Tree - fell into line | Cutout- Fused- Distribution | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4982 | Vegetation | Tree - fell into line | Anchor or Guy | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4983 | Vegetation | Tree - fell into line | Riser | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4984 | Vegetation | Tree - fell into line | Pole-Wood | Malfunctioning | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4985 | Vegetation | Tree - fell into line | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4986 | Vegetation | Tree - grew into line | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4987 | Vegetation | Tree - grew into line | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4988 | Vegetation | Tree - grew into line | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4989 | Vegetation | Tree - grew into line | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4990 | Vegetation | Tree - grew into line | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4991 | Vegetation | Tree - grew into line | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4992 | Vegetation | Tree - grew into line | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4993 | Vegetation | Tree - grew into line | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4994 | Vegetation | Tree - grew into line | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4995 | Vegetation | Tree - grew into line | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4996 | Vegetation | Tree - grew into line | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4997 | Vegetation | Tree - grew into line | Customer Equipment | Broken | None | No work is being completed on customer equipment.
4998 | Vegetation | Tree - grew into line | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4999 | Vegetation | Tree - grew into line | Connector or Splice (OH) |  | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
5000 | Vegetation | Tree - grew into line | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
5001 | Vegetation | Tree - grew into line | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5002 | Vegetation | Tree - palm frond fell into line | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
5003 | Vegetation | Tree - palm frond fell into line | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5004 | Vegetation | Tree - palm frond fell into line | Connector or Splice (OH) | On Ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
5005 | Vegetation | Tree - palm frond fell into line | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5006 | Vegetation | Tree - palm frond fell into line | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
5007 | Vegetation | Tree - palm frond fell into line | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
5008 | Vegetation | Tree - palm frond fell into line | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
5009 | Vegetation | Tree - palm frond fell into line | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
5010 | Vegetation | Tree - palm frond fell into line | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
5011 | Vegetation | Tree - palm frond fell into line | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
5012 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
5013 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
5014 | Vegetation | Tree - palm frond fell into line | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
5015 | Wildfire Mitigation | CWSP - Vegetation Removal |  |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5016 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor- Overhead | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5017 | Wildfire Mitigation | CWSP - Vegetation Removal | Transformer (OH) | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5018 | Wildfire Mitigation | CWSP - Vegetation Removal | Other | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5019 | Wildfire Mitigation | CWSP - Vegetation Removal | Fuse | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5020 | Wildfire Mitigation | CWSP - Vegetation Removal | Pole-Wood | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5021 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor- Overhead | Annealed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5022 | Wildfire Mitigation | CWSP - Vegetation Removal | Secondary | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5023 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5024 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5025 | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm- Wood | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5026 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5027 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5028 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (UG) | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5029 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5030 | Wildfire Mitigation | Public Safety Power Shut-off | Cutout- fuse holder | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5031 | Wildfire Mitigation | Public Safety Power Shut-off | Customer Equipment | Broken | None | No work is being completed on customer equipment.
5032 | Wildfire Mitigation | Public Safety Power Shut-off | Other | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5033 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Deteriorated | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5034 | Wildfire Mitigation | Public Safety Power Shut-off | Anchor or Guy | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5035 | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5036 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5037 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5038 | Wildfire Mitigation | Public Safety Power Shut-off | Insulator | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5039 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Contaminated | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5040 | Wildfire Mitigation | Public Safety Power Shut-off | Circuit Breaker | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5041 | Wildfire Mitigation | Public Safety Power Shut-off | Fuse | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5042 | Wildfire Mitigation | Public Safety Power Shut-off | Recloser | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5043 | Wildfire Mitigation | Public Safety Power Shut-off | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5044 | Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5045 | Wildfire Mitigation | Public Safety Power Shut-off | Sectionalizer | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5046 | Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5047 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Underground | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5048 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (OH) | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5049 | Wildfire Mitigation | Public Safety Power Shut-off | SCADA | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5050 | Wildfire Mitigation | Public Safety Power Shut-off | Generator | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5051 | Wildfire Mitigation | Public Safety Power Shut-off | Fuse |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5052 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Together | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5053 | Wildfire Mitigation | Public Safety Power Shut-off | Other | Malfunctioning | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5054 | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm- Wood | Deteriorated | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5055 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5056 | Wildfire Mitigation | Public Safety Power Shut-off |  | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5057 | Wildfire Mitigation | Public Safety Power Shut-off | Switch (UG) | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5058 | Wildfire Mitigation | Public Safety Power Shut-off |  | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5059 | Wildfire Mitigation | Public Safety Power Shut-off | Connector or Splice (OH) | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5060 | Wildfire Mitigation | Public Safety Power Shut-off | Connector or Splice (OH) | Broken- wire on ground | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5061 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5062 | Wildfire Mitigation | Public Safety Power Shut-off | Jumper | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5063 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5064 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5065 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5066 | Wildfire Mitigation | Public Safety Power Shut-off | Regulator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
5067 | Wildfire Mitigation | Public Safety Power Shut-off | Recloser |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5068 | Wildfire Mitigation | Public Safety Power Shut-off | Woodpin | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5069 | Wildfire Mitigation | Public Safety Power Shut-off | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
5070 | Wildfire Mitigation | Public Safety Power Shut-off | Jumper | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5071 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Bent or Twisted | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5072 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5073 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5074 | Wildfire Mitigation | Public Safety Power Shut-off | Bushing | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5075 | Wildfire Mitigation | Public Safety Power Shut-off | Jumper | Burned Open | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5076 | Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5077 | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm- Wood | Burned/flashed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5078 | Wildfire Mitigation | Public Safety Power Shut-off | Other | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5079 | Wildfire Mitigation | Public Safety Power Shut-off | Relay | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5080 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5081 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (OH) | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5082 | Wildfire Mitigation | Public Safety Power Shut-off | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5083 | Wildfire Mitigation | Public Safety Power Shut-off | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5084 | Wildfire Mitigation | Public Safety Power Shut-off | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5085 | Wildfire Mitigation | Public Safety Power Shut-off | Fuse | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5086 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Burned/flashed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5087 | Wildfire Mitigation | Public Safety Power Shut-off | Customer Equipment | Deteriorated | None | No work is being completed on customer equipment.
5088 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (UG) | Burned/flashed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5089 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5090 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5091 | Wildfire Mitigation | Public Safety Power Shut-off | Cutout- fuse holder | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5092 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Deteriorated | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5093 | Wildfire Mitigation | Public Safety Power Shut-off | Customer Equipment | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5094 | Wildfire Mitigation | Public Safety Power Shut-off | Lightning Arrestor | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5095 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.

## 7.3.3.17.1 (OH)_Effectiveness
|  |  | Source: | 7.3.3.17.1_SME_Input tab
RAMP Driver | RAMP Subdriver | RAMP Eff | GRC driver | GRC subdriver | RAMP subdriver | Eff
3rd Party | 3rd Party - Other | 48.42% | Contact from object | Animal contact | Animal | 58.48%
3rd Party | 3rd Party - Unknown | 40.48% | Contact from object | Balloon contact | Balloons | 75.6%
3rd Party | Balloons | 80.68% | Contact from object | Other contact from object | 3rd Party - Other | 52.87%
3rd Party | Vehicle | 47.73% | Contact from object | Vehicle contact | Vehicle | 46.48%
Animal | Animal | 69.33% | Vegetation Contact | Branch (Not overhanging, > 12ft) | Branch (Not overhanging, > 12ft) | 52.5%
Equip Failure | Capacitor Bank | 7.234% | Vegetation Contact | Branch (Not overhanging, 4-12ft) | Branch (Not overhanging, 4-12ft) | 65%
Equip Failure | Conductor | 50.8% | Vegetation Contact | Branch (Not overhanging, Distance Unknown) | Branch (Not overhanging, Distance Unknown) | 47.97%
Equip Failure | Crossarm | 75.83% | Vegetation Contact | Branch (Not overhanging, within 4ft) | Branch (Not overhanging, within 4ft) | 58.09%
Equip Failure | Equip Failure - Other | 43.51% | Vegetation Contact | Branch (Overhanging) | Branch (Overhanging) | 46.49%
Equip Failure | Equip Failure - Unknown | 71.54% | Vegetation Contact | Dead | Dead | 53.18%
Equip Failure | Fuse | 69.19% | Vegetation Contact | Fell into (Moderate-Severe defect) | Fell into (Moderate-Severe defect) | 46.25%
Equip Failure | Guy/Span Wire | 73.33% | Vegetation Contact | Fell into (No defect) | Fell into (No defect) | 50.75%
Equip Failure | Insulator | 68.8% | Vegetation Contact | Fell into (slight defect) | Fell into (slight defect) | 45.49%
Equip Failure | Lightning Arrestor | 90% | Vegetation Contact | Grow Into | Grow Into | 50%
Equip Failure | Pole | 55.85% | Vegetation Contact | Other/Unknown | Other/Unknown | 48.13%
Equip Failure | Recloser | 61.67% | Contamination | Contamination | Animal | 30%
Equip Failure | Sectionalizer | 40% | Equipment / facility failure | Anchor / guy damage or failure | Guy/Span Wire | 56.67%
Equip Failure | Splice/Clamp/Connector | 70% | Equipment / facility failure | Capacitor bank damage or failure | Capacitor Bank | 25%
Equip Failure | Switch | 77.5% | Equipment / facility failure | Conductor damage or failure | Conductor | 45.36%
Equip Failure | Transformer | 74% | Equipment / facility failure | Connection device damage or failure | Splice/Clamp/Connector | 66.28%
Equip Failure | Voltage Regulator | 34.29% | Equipment / facility failure | Crossarm damage or failure | Crossarm | 68.33%
Unk or Other | Unk or Other - Other | 59.33% | Equipment / facility failure | Fuse damage or failure | Fuse | 62.11%
Unk or Other | Unk or Other - Unknown | 60% | Equipment / facility failure | Insulator and brushing damage or failure | Insulator | 57.2%
Vegetation | Branch (Not overhanging, > 12ft) | 54.29% | Equipment / facility failure | Lightning arrestor damage or failure | Lightning Arrestor | 90%
Vegetation | Branch (Overhanging) | 47.65% | Equipment / facility failure | Other equipment / facility failure | Equip Failure - Other | 46.4%
Vegetation | Dead | 53.5% | Equipment / facility failure | Pole damage or failure | Pole | 44.15%
Vegetation | Fell into (Moderate-Severe defect) | 46.1% | Equipment / facility failure | Recloser damage or failure | Recloser | 45%
Vegetation | Fell into (No defect) | 50.41% | Equipment / facility failure | Sectionalizer damage or failure | Sectionalizer | 40%
Vegetation | Fell into (Slight defect) | 45.23% | Equipment / facility failure | Switch damage or failure | Switch | 83.33%
Vegetation | Grow Into | 50% | Equipment / facility failure | Transformer damage or failure | Transformer | 63.91%
Vegetation | Other/Unknown | 17.96% | Equipment / facility failure | Voltage regulator / booster damage or failure | Voltage Regulator | 14.44%
Vegetation | Branch (Not overhanging, Distance Unknown) | 51.27% | Other | All Other | Unk or Other - Other | 52%
Vegetation | Branch (Not overhanging, 4-12ft) | 65% | Unknown | Unknown | Unk or Other - Unknown | 30.71%
Vegetation | Branch (Not overhanging, within 4ft) | 57.39% | Vandalism / Theft | Vandalism / Theft |  | 44.17%
CC - Seismic Scenario | Seismic Scenario | 50.44% | Utility work / Operation | Utility work / Operation |  | 0%
|  |  | CC - Seismic Scenario | Seismic Scenario | Seismic Scenario | 50.65%

## 7.3.3.17.3_Exposure
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Non Exempt Surge Arrestors | 2A | 2AR | 0 | 0 | 0 | 0 | 14372 | 15477 | 7750 | 4396
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 0 | 0 | 0 | 0 | 3449 | 5065 | 1396.6744 | 0
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 0 | 0 | 0 | 0 | 6824 | 10412 | 3600.3774 | 0
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.9482 | 0
Distribution - HTFD Split | 0% | Tier 1 |  |  | 0 | 0 | 0 | 0 | 4099 | 0 | 2750 | 4396
From GRC 2023 filing:
Miles covered per non-exempt surge arrestor replacement is calculated as follows:
| 1.68 | HFTD miles per Surge Arrestor replacement
| 0.99 | non-HFTD miles per Surge Arrestor replacement

## 7.3.3.17.3_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Non Exempt Surge Arrestors | 2A | 2AR |  |  |  |  | 63497995.35 | 74190939.07 | 33172115.7824 | 17706361.1148

## 7.3.3.17.5_Financials
Source file: | 2022 WMP MASTER financials reach out v2_122821
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
Remote Grid (PO 5052592) |  |  | AB# | AB | 755231.11 | 1382417.529 | 2200468.9 | 1422982.0543 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 210962.3911 | 386157.4339 | 614667.7151 | 397488.5207 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 543823.4 | 995444.9584 | 1584503.6877 | 1024654.4782 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 445.3189 | 815.1367 | 1297.4973 | 839.0554 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 0% | Tier 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 7.3.3.17.5_Effectiveness
90% | Per SME judgement. Remote grid once installed would avoid 100% of ignitions associated with Equipment failure. There is a 1.7% ignition risk possibility on the basis of failure associated to the remote grid itself. To be conservative PG&E uses a 90% effectiveness value.

## M014
WLDFR-M014 (MAT:95F)
Underground Miles | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Total | 25.5 | 37 | 42.7 | 36.5 | 23.9 | 0
08W | 9.69 | 14.06 | 16.226 | 13.87 | 9.082 | 0
95F | 7.14 | 10.36 | 11.956 | 10.22 | 6.692 | 0
95Other | 8.67 | 12.58 | 14.518 | 12.41 | 8.126 | 0
Sum of 95F + 95 Other | 23.64 | 22.94 | 26.474 | 22.63 | 14.818 | 0
Sum of 95F + 95 Other | 15.81 | 22.94 | 26.474 | 22.63 | 14.818 | 0

## 7.3.3.17.6_Exposure
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Butte Rebuild - Undergrounding Total | [6 empty] | 29.3 | 23.6 | 35 | 45
|  | Butte Rebuild - Undergrounding 08W | 8 | 08W |  |  |  |  | 17.6028 |  | 14.1 | 16.2
Distribution - HTFD Split | 75% | Tier 3 | [6 empty] | 13.2021 | 0 | 10.575 | 13
Distribution - HTFD Split | 0% | Tier 2 | [6 empty] | 0 | 0 | 0 | 1.62
Distribution - HTFD Split | 0% | Zone 1 | [6 empty] | 0 | 0 | 0 | 0
Distribution - HTFD Split | 25% | Tier 1 | [6 empty] | 4.4007 | 0 | 3.525 | 1.62
|  | Butte Rebuild - Undergrounding 95 (some is actually done in tier 1 that will count towards mileage goal) | 95, IF | 95F, IFF |  |  |  |  | 4.0972 | 0 | 22.9 | 27.3
Distribution - All tier Split | 75% | Tier 3 | [6 empty] | 3.0729 | 0 | 17.175 | 22
Distribution - All tier Split | 0% | Tier 2 | [6 empty] | 0 | 0 | 0 | 2.65
Distribution - All tier Split | 0% | Zone 1 | [6 empty] | 0 | 0 | 0 | 0
Distribution - All tier Split | 25% | Tier 1 | [6 empty] | 1.0243 | 0 | 5.725 | 2.65

## 7.3.3.17.6_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Butte Rebuild - Undergrounding Total | 08, 95, IF | 08W, 95F, IFF |  |  |  |  | 64587023.09 | 98429015.9 | 138750000 | 142521925

## 7.3.3.17.6_Effectiveness
95% | Per SME judgement. Undergrounding of electric assets eliminated the risk of ignition caused by the failure of these equipment by 100%. To be conservative, program effectiveness of 95% is used

## Match esc definition
Define a Customer Extrapolation Multiplier
match | x_match | matching with other series | y[i, j]= y[i-1, j] * x_match[i]/x_match[i-1]
x_match | Description | Year1 | Year2 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121
case1 |  | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Data & Validation
Lookup tables
No. | A | B | C | Risk/Cross Cutting Factor Name | RISK ID | Program Cost Options
1 | 0% | 10% | 15% | Aviation Incident | AVATN | prorate by Program Exposure
2 | 0% | 10% | 15% | Electric Transmission System-Wide Blackout | BLKOT | % of Total Cost (specify to the right)
3 | 0% | 10% | 15% | Loss of Containment on Gas Customer Connected Equipment | CCEPQ
4 | 0% | 2.5% | 5% | Climate | CLIMT | Program Exposure Options
5 | 0% | 2.5% | 5% | Loss of Containment on CNG Station Equipment | CNGEQ | Exposure unit
6 | 0% | 2.5% | 5% | Contractor Safety Incident | CNTSI | % of tranche exposure
7 | 0% | 2.5% | 5% | Insufficient Capacity to Meet High Demand | CPCTY | Work unit
8 | 0% | 2.5% | 5% | Contract Management | CTMGT
9 | 0% | 2.5% | 5% | Cyber Attack | CYBER | Program Type Options
10 | 0% | 2.5% | 5% | Failure of Electric Distribution Network Assets | DNTWK | Mitigation
11 | 0% | 2.5% | 5% | Failure of Electric Distribution Overhead Assets | DOVHD | Control
12 | 0% | 2.5% | 5% | Data Loss Event | DTALS | Foundational Mitigation
13 | 0% | 2.5% | 5% | Failure of Electric Distribution Underground Assets | DUNGD | Foundational Control
|  |  |  | Business Model - Electric | EMODL
|  |  |  | Employee Safety Incident | EMPSI
|  |  |  | Emergency Preparedness and Response | EPNDR
|  |  |  | Business Model - Gas | GMODL | Consequence Options
|  |  |  | Extended Unplanned Shutdown of a Critical Power Generation Asset | GSHUT | Safety
|  |  |  | Hazardous Material Release | HZMAT | Electric Reliability
|  |  |  | IT Asset Failure | ITAFL | Gas Reliability
|  |  |  | Large Uncontrolled Water Release (Dam Failure) | LGUWR | Financial
|  |  |  | Loss of Containment on LNG/CNG Portable Equipment | LNCNG
|  |  |  | Loss of Containment on Gas Distribution Main or Service | LOCDM | Bow Tie Element
|  |  |  | Loss of Containment on Gas Transmission Pipeline | LOCTR | LOF
|  |  |  | Liquidity Shortage | LQDTY | COF
|  |  |  | Large Overpressure Event Downstream of Gas Measurement and Control Facility | LRGOP | LOF and COF
|  |  |  | Loss of Containment at Gas Measurement and Control or Compression and Processing Facility | MCCPF
|  |  |  | Motor Vehicle Safety Incident | MTRSI
|  |  |  | Nuclear Core Damaging Event | NCORE
|  |  |  | Loss of Containment at Natural Gas Storage Well or Reservoir | NGSWR
|  |  |  | Nuclear Extended Shutdown | NSHUT
|  |  |  | Physical Attack | PHYSA
|  |  |  | Records and Information Management | RECIM
|  |  |  | Real Estate and Facilities Failure | REFFL
|  |  |  | Failure of Substation Assets | SBSTN
|  |  |  | Skilled and Qualified Workforce | SQWKF
|  |  |  | Seismic | SSMIC
|  |  |  | 3rd-Party Safety Incident | TPTSI
|  |  |  | Third-Party Risk | TRDPY
|  |  |  | Failure of Electric Transmission Overhead Assets | TRNHD
|  |  |  | Failure of Electric Transmission Underground Assets | TUNGD
|  |  |  | Wildfire | WLDFR

## BowTie
TableDriverSubdriver |  | TableTranche |  |  |  | TableOutcome
Driver | Subdriver | Tranche | Exposure | Unit | 2021 miles | Outcome
Contact from object | Animal contact | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | 163.6441 | Miles | 184.2524 | Red Flag Warning - Catastrophic Fires
Contact from object | Balloon contact | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | 353.5334 | Miles | 342.1459 | Red Flag Warning - Destructive Fires
Contact from object | Other contact from object | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | 1013.9529 | Miles | 1045.7977 | Red Flag Warning - Large Fires
Contact from object | Vehicle contact | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | 1483.0022 | Miles | 1437.6834 | Red Flag Warning - Small Fires
Vegetation Contact | Branch (Not overhanging, > 12ft) | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | 1601.5759 | Miles | 1615.3706 | Non-Red Flag Warning - Catastrophic Fires
Vegetation Contact | Branch (Not overhanging, 4-12ft) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | 193.7699 | Miles | 179.7119 | Non-Red Flag Warning - Destructive Fires
Vegetation Contact | Branch (Not overhanging, Distance Unknown) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | 543.1039 | Miles | 509.5661 | Non-Red Flag Warning - Large Fires
Vegetation Contact | Branch (Not overhanging, within 4ft) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | 946.5765 | Miles | 950.8276 | Non-Red Flag Warning - Small Fires
Vegetation Contact | Branch (OverHanging) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | 1078.9824 | Miles | 1134.6096 | Seismic - Red Flag Warning - Catastrophic Fires
Vegetation Contact | Dead | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | 1464.9153 | Miles | 1463.3797 | Seismic - Non-Red Flag Warning - Catastrophic Fires
Vegetation Contact | Fell into (Moderate-Severe defect) | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | 489.6273 | Miles | 494.5343
Vegetation Contact | Fell into (No defect) | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | 791.1377 | Miles | 739.0344
Vegetation Contact | Fell into (slight defect) | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | 791.1875 | Miles | 796.2245
Vegetation Contact | Grow Into | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | 741.5879 | Miles | 757.6487
Vegetation Contact | Other/Unknown | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | 715.8465 | Miles | 721.5283
Contamination | Contamination | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | 772.1066 | Miles | 734.0513
Equipment / facility failure | Anchor / guy damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | 522.2177 | Miles | 549.0677
Equipment / facility failure | Capacitor bank damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | 750.2287 | Miles | 758.0137
Equipment / facility failure | Conductor damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | 696.1473 | Miles | 682.1613
Equipment / facility failure | Connection device damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | 470.836 | Miles | 487.3876
Equipment / facility failure | Crossarm damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | 752.6401 | Miles | 714.6389
Equipment / facility failure | Fuse damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | 768.4668 | Miles | 794.6718
Equipment / facility failure | Insulator and brushing damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | 467.0501 | Miles | 439.3061
Equipment / facility failure | Lightning arrestor damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | 347.2658 | Miles | 382.7904
Equipment / facility failure | Other equipment / facility failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | 406.8993 | Miles | 411.898
Equipment / facility failure | Pole damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | 58.7222 | Miles | 68.3395
Equipment / facility failure | Recloser damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | 156.5661 | Miles | 163.8201
Equipment / facility failure | Sectionalizer damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | 56.2394 | Miles | 39.0328
Equipment / facility failure | Switch damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | 111.286 | Miles | 119.909
Equipment / facility failure | Transformer damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | 65.8407 | Miles | 57.0212
Equipment / facility failure | Voltage regulator / booster damage or failure | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | 184.1265 | Miles | 226.4749
Other | All Other | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | 264.4574 | Miles | 311.9586
Unknown | Unknown | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | 279.2931 | Miles | 224.2508
Vandalism / Theft | Vandalism / Theft | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | 108.7427 | Miles | 69.0654
Wire-to-wire contact | Wire-to-wire contact / contamination | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | 22.7224 | Miles | 33.5215
Utility work / Operation | Utility work / Operation | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | 423.2024 | Miles | 449.4697
CC - Seismic Scenario | Seismic Scenario | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | 595.3479 | Miles | 574.4306
|  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | 215.5262 | Miles | 247.7504
|  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | 223.3454 | Miles | 213.7942
|  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | 134.3564 | Miles | 105.542
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | 607.6134 | Miles | 608.7309
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | 572.0063 | Miles | 551.9796
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | 384.7705 | Miles | 400.6021
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | 202.884 | Miles | 213.1612
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | 117.3278 | Miles | 105.5226
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | 1430.0123 | Miles | 1412.9227
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | 527.1275 | Miles | 559.1759
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | 190.7177 | Miles | 189.2879
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | 95.1547 | Miles | 86.1355
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | 97.3625 | Miles | 92.8527
|  | HFTD - Distribution - Zone 1 - 1QU CoRE ¦ 5QU LoRE | 0.18783 | Miles | 0.18783
|  | HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | 0.13442 | Miles | 0.13442
|  | HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | 10.0154 | Miles | 10.0154
|  | HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | 0.27822 | Miles | 0.27822
|  | HFTD - Substation | 1 | Unit | 1
|  | HFTD - Transmission - Tier 2 - 115 kV or Lower | 1299.3 | Miles | 1299.3
|  | HFTD - Transmission - Tier 2 - 230 kV or Higher | 1759.53 | Miles | 1759.53
|  | HFTD - Transmission - Tier 2 - 60/70 kV | 1419.51 | Miles | 1419.51
|  | HFTD - Transmission - Tier 3 - 115 kV or Lower | 446.95 | Miles | 446.95
|  | HFTD - Transmission - Tier 3 - 230 kV or Higher | 557.6 | Miles | 557.6
|  | HFTD - Transmission - Tier 3 - 60/70 kV | 376.43 | Miles | 376.43
|  | HFTD - Transmission - Zone 1 - 115 kV or Lower | 1.27 | Miles | 1.27
|  | HFTD - Transmission - Zone 1 - 230 kV or Higher | 3.1 | Miles | 3.1
|  | HFTD - Transmission - Zone 1 - 60/70 kV | 1.8 | Miles | 1.8
|  | non-HFTD - Distribution | 55300 | Miles | 55300
|  | non-HFTD - Substation | 1 | Unit | 1
|  | non-HFTD - Transmission - 115 kV or Lower | 4431.1 | Miles | 4431.1
|  | non-HFTD - Transmission - 230 kV or Higher | 5106.55 | Miles | 5106.55
|  | non-HFTD - Transmission - 60/70 kV | 3682.86 | Miles | 3682.86
|  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles
|  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles
|  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles
|  | HFTD - Distribution - All | 25461.6694 | Miles
|  | HFTD - Transmission - All | 5865.49 | Miles
|  | HFTD - All | 31327.1594 | Miles
|  | non-HFTD - Transmission - All | 13220.51 | Miles
|  | HFTD - Transmission - Tier 2 - All | 4478.34 | Miles
|  | HFTD - Transmission - Tier 3 - All | 1380.98 | Miles
|  | HFTD - Transmission - Zone 1 - All | 6.17 | Miles

## HFTD Miles
HFTD Line Miles | 25461.6694
| HFTD Tranche % based on WMP BowTie | Line Miles
Zone 1 | 0.06% | 15.277
Tier 3 | 27.93% | 7111.4443
Tier 2 | 72.01% | 18334.9481

## TablePVRR
Asset Group | PVRR Multiplier (no O&M) | Lifetime O&M as % of PVRR
Buildings | 1.4702 | 0
Communications equipment | 1.2527 | 0
Computer hardware | 1.1238 | 0.44918
Computer software | 1.1074 | 0.44918
Electric distribution (<69kV) - Overhead | 1.3891 | 1.1158
Electric distribution (<69kV) - Underground | 1.3891 | 0.38678
Electric transmission (69kV+) | 1.3758 | 0
Electric smart meter | 1.229 | 0
Gas distribution after 2010 | 1.4002 | 1.1518
Gas Meters | 1.3726 | 7.7616
Gas transmission & storage | 1.3686 | 1.7862
Gas (current) held for resale | 1.5881 | 0
Land easement | 1.5197 | 0
Land purchase | 1.448 | 0
Motor vehicles | 1.1661 | 0
Office furniture | 1.241 | 0
Hydro | 1.405 | 0
Hydro additions | 1.3416 | 0
Nuclear | 1.2779 | 0
Nuclear additions | 1.1917 | 0
Fuel cell | 1.1589 | 0
Custom | 0 | 0