## Table 7.2
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 7.2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2022-06-27 | Data from 2015 - 2021 should be actual numbers. 2022 and 2023 should be projected. In future submissions update projected numbers with actuals
| Table 7.2: Key recent and projected drivers of ignitions | [5 empty] | Number of ignitions | [6 empty] | Projected ignitions
| Metric type | # | Ignition driver | Line Type | HFTD tier | Are ignitions tracked for ignition driver? (yes / no) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Unit(s) | Comments
x | 1. Contact from object | 1.a.i | Veg. contact | Distribution | Non-HFTD | Yes | 45 | 45 | 75 | 57 | 75 | 63 | 75 | 60.9 | 60.9 | # ignitions
|  | 1.a.ii | Veg. contact | Distribution | HFTD Zone 1 | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | # ignitions
|  | 1.a.iii | Veg. contact | Distribution | HFTD Tier 2 | Yes | 38 | 40 | 63 | 32 | 46 | 37 | 40 | 32.9 | 24.8 | # ignitions
|  | 1.a.iv | Veg. contact | Distribution | HFTD Tier 3 | Yes | 24 | 23 | 40 | 36 | 16 | 27 | 24 | 14.2 | 9.5 | # ignitions
|  | 1.a.v | Veg. contact | Distribution | System | Yes | 108 | 108 | 178 | 125 | 137 | 127 | 140 | 108 | 95.2 | # ignitions
|  | 1.a.vi | Veg. contact | Transmission | Non-HFTD | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 9.a
|  | 1.a.vii | Veg. contact | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.a.viii | Veg. contact | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0.4 | 0.4 | # ignitions
|  | 1.a.ix | Veg. contact | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.2 | 0.2 | # ignitions
|  | 1.a.x | Veg. contact | Transmission | System | Yes | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 0.6 | 0.6 | # ignitions
|  | 1.b.i | Animal contact | Distribution | Non-HFTD | Yes | 48 | 33 | 51 | 37 | 57 | 36 | 28 | 40.5 | 40.5 | # ignitions
|  | 1.b.ii | Animal contact | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.b.iii | Animal contact | Distribution | HFTD Tier 2 | Yes | 7 | 6 | 10 | 12 | 10 | 9 | 8 | 7.5 | 2.9 | # ignitions
|  | 1.b.iv | Animal contact | Distribution | HFTD Tier 3 | Yes | 2 | 2 | 1 | 5 | 1 | 0 | 1 | 1 | 1.1 | # ignitions
|  | 1.b.v | Animal contact | Distribution | System | Yes | 57 | 41 | 62 | 54 | 68 | 45 | 37 | 49 | 44.5 | # ignitions
|  | 1.b.vi | Animal contact | Transmission | Non-HFTD | Yes | 3 | 5 | 5 | 5 | 7 | 3 | 0 | 3.7 | 3.7 | # ignitions | Previously 9.b
|  | 1.b.vii | Animal contact | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.b.viii | Animal contact | Transmission | HFTD Tier 2 | Yes | 4 | 4 | 4 | 4 | 1 | 3 | 1 | 3 | 3 | # ignitions
|  | 1.b.ix | Animal contact | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 2 | 3 | 0 | 2 | 0 | 1.2 | 1.2 | # ignitions
|  | 1.b.x | Animal contact | Transmission | System | Yes | 7 | 9 | 11 | 12 | 8 | 8 | 1 | 7.8 | 7.8 | # ignitions
|  | 1.c.i | Balloon contact | Distribution | Non-HFTD | Yes | 19 | 11 | 11 | 10 | 15 | 14 | 15 | 13.4 | 13.4 | # ignitions
|  | 1.c.ii | Balloon contact | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.c.iii | Balloon contact | Distribution | HFTD Tier 2 | Yes | 4 | 2 | 0 | 3 | 0 | 0 | 1 | 0.1 | 0.1 | # ignitions
|  | 1.c.iv | Balloon contact | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.1 | # ignitions
|  | 1.c.v | Balloon contact | Distribution | System | Yes | 23 | 13 | 11 | 13 | 15 | 14 | 16 | 14.5 | 13.6 | # ignitions
|  | 1.c.vi | Balloon contact | Transmission | Non-HFTD | Yes | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0.5 | 0.5 | # ignitions | Previously 9.c
|  | 1.c.vii | Balloon contact | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.c.viii | Balloon contact | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.2 | 0.2 | # ignitions
|  | 1.c.ix | Balloon contact | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | # ignitions
|  | 1.c.x | Balloon contact | Transmission | System | Yes | 0 | 1 | 1 | 0 | 1 | 2 | 1 | 0.8 | 0.8 | # ignitions
|  | 1.d.i | Vehicle contact | Distribution | Non-HFTD | Yes | 37 | 23 | 40 | 18 | 31 | 42 | 26 | 31.7 | 31.7 | # ignitions
|  | 1.d.ii | Vehicle contact | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.d.iii | Vehicle contact | Distribution | HFTD Tier 2 | Yes | 9 | 13 | 11 | 8 | 5 | 10 | 7 | 6.3 | 3.8 | # ignitions
|  | 1.d.iv | Vehicle contact | Distribution | HFTD Tier 3 | Yes | 1 | 0 | 4 | 2 | 0 | 3 | 1 | 3.3 | 1.5 | # ignitions
|  | 1.d.v | Vehicle contact | Distribution | System | Yes | 47 | 36 | 55 | 28 | 36 | 55 | 34 | 41.3 | 36.9 | # ignitions
|  | 1.d.vi | Vehicle contact | Transmission | Non-HFTD | Yes | 0 | 1 | 1 | 3 | 4 | 2 | 3 | 1.8 | 1.8 | # ignitions | Previously 9.d
|  | 1.d.vii | Vehicle contact | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.d.viii | Vehicle contact | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.d.ix | Vehicle contact | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.d.x | Vehicle contact | Transmission | System | Yes | 0 | 1 | 1 | 3 | 4 | 2 | 3 | 1.8 | 1.8 | # ignitions
|  | 1.e.i | Other contact from object | Distribution | Non-HFTD | Yes | 7 | 3 | 2 | 32 | 16 | 17 | 14 | 15.3 | 15.3 | # ignitions
|  | 1.e.ii | Other contact from object | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.e.iii | Other contact from object | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 3 | 8 | 5 | 6 | 2 | 2.2 | 1.4 | # ignitions
|  | 1.e.iv | Other contact from object | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 1.5 | 0.5 | # ignitions
|  | 1.e.v | Other contact from object | Distribution | System | Yes | 7 | 3 | 5 | 47 | 21 | 23 | 16 | 19 | 17.3 | # ignitions
|  | 1.e.vi | Other contact from object | Transmission | Non-HFTD | Yes | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1.3 | 1.3 | # ignitions | Previously 9.e
|  | 1.e.vii | Other contact from object | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 1.e.viii | Other contact from object | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0.9 | 0.9 | # ignitions
|  | 1.e.ix | Other contact from object | Transmission | HFTD Tier 3 | Yes | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0.3 | 0.3 | # ignitions
|  | 1.e.x | Other contact from object | Transmission | System | Yes | 0 | 1 | 1 | 3 | 2 | 3 | 0 | 2.5 | 2.5 | # ignitions
| 2. Equipment / facility failure | 2.a.i | Capacitor bank damage or failure | Distribution | Non-HFTD | Yes | 12 | 10 | 11 | 5 | 7 | 7 | 4 | 8.2 | 8.2 | # ignitions
|  | 2.a.ii | Capacitor bank damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.iii | Capacitor bank damage or failure | Distribution | HFTD Tier 2 | Yes | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0.4 | 0.5 | # ignitions
|  | 2.a.iv | Capacitor bank damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 1 | 1 | 2 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions
|  | 2.a.v | Capacitor bank damage or failure | Distribution | System | Yes | 14 | 12 | 13 | 8 | 7 | 7 | 4 | 8.7 | 8.8 | # ignitions
|  | 2.a.vi | Capacitor bank damage or failure | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 10.a
|  | 2.a.vii | Capacitor bank damage or failure | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.viii | Capacitor bank damage or failure | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.ix | Capacitor bank damage or failure | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.a.x | Capacitor bank damage or failure | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.b.i | Conductor damage or failure | Distribution | Non-HFTD | Yes | 36 | 42 | 54 | 27 | 61 | 48 | 52 | 49 | 49 | # ignitions
|  | 2.b.ii | Conductor damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.b.iii | Conductor damage or failure | Distribution | HFTD Tier 2 | Yes | 10 | 8 | 15 | 11 | 10 | 7 | 5 | 2.3 | 2.7 | # ignitions
|  | 2.b.iv | Conductor damage or failure | Distribution | HFTD Tier 3 | Yes | 3 | 6 | 3 | 2 | 3 | 0 | 4 | 1.9 | 1 | # ignitions
|  | 2.b.v | Conductor damage or failure | Distribution | System | Yes | 49 | 56 | 72 | 40 | 74 | 55 | 61 | 53.2 | 52.7 | # ignitions
|  | 2.b.vi | Conductor damage or failure | Transmission | Non-HFTD | Yes | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0.7 | 0.7 | # ignitions | Previously 10.b
|  | 2.b.vii | Conductor damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.b.viii | Conductor damage or failure | Transmission | HFTD Tier 2 | Yes | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0.8 | 0.8 | # ignitions
|  | 2.b.ix | Conductor damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.3 | 0.3 | # ignitions
|  | 2.b.x | Conductor damage or failure | Transmission | System | Yes | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1.8 | 1.8 | # ignitions
|  | 2.c.i | Fuse damage or failure | Distribution | Non-HFTD | Yes | 5 | 7 | 8 | 2 | 5 | 7 | 7 | 5.3 | 5.3 | # ignitions
|  | 2.c.ii | Fuse damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.c.iii | Fuse damage or failure | Distribution | HFTD Tier 2 | Yes | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0.5 | 0.5 | # ignitions
|  | 2.c.iv | Fuse damage or failure | Distribution | HFTD Tier 3 | Yes | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0.2 | 0.2 | # ignitions
|  | 2.c.v | Fuse damage or failure | Distribution | System | Yes | 8 | 7 | 10 | 2 | 5 | 11 | 7 | 6 | 6 | # ignitions
|  | 2.c.vi | Fuse damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 10.c
|  | 2.c.vii | Fuse damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.c.viii | Fuse damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.c.ix | Fuse damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.c.x | Fuse damage or failure | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.i | Lightning arrestor damage or failure | Distribution | Non-HFTD | Yes | 6 | 3 | 6 | 1 | 4 | 1 | 1 | 3.2 | 3 | # ignitions
|  | 2.d.ii | Lightning arrestor damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.iii | Lightning arrestor damage or failure | Distribution | HFTD Tier 2 | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.iv | Lightning arrestor damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.v | Lightning arrestor damage or failure | Distribution | System | Yes | 7 | 3 | 6 | 1 | 4 | 1 | 1 | 3.2 | 3 | # ignitions
|  | 2.d.vi | Lightning arrestor damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 10.d
|  | 2.d.vii | Lightning arrestor damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.viii | Lightning arrestor damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.ix | Lightning arrestor damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.d.x | Lightning arrestor damage or failure | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.i | Switch damage or failure | Distribution | Non-HFTD | Yes | 3 | 3 | 4 | 1 | 1 | 2 | 4 | 2 | 2 | # ignitions
|  | 2.e.ii |  | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.iii | Switch damage or failure | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | # ignitions
|  | 2.e.iv | Switch damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  | 2.e.v | Switch damage or failure | Distribution | System | Yes | 3 | 3 | 4 | 1 | 2 | 3 | 5 | 2 | 2 | # ignitions
|  | 2.e.vi | Switch damage or failure | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 10.e
|  | 2.e.vii | Switch damage or failure | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.viii | Switch damage or failure | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.ix | Switch damage or failure | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.e.x | Switch damage or failure | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.f.i | Pole damage or failure | Distribution | Non-HFTD | Yes | 4 | 5 | 11 | 7 | 6 | 8 | 10 | 6.6 | 6.6 | # ignitions
|  | 2.f.ii | Pole damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.f.iii | Pole damage or failure | Distribution | HFTD Tier 2 | Yes | 1 | 2 | 2 | 4 | 0 | 1 | 2 | 0.7 | 0.8 | # ignitions
|  | 2.f.iv | Pole damage or failure | Distribution | HFTD Tier 3 | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | # ignitions
|  | 2.f.v | Pole damage or failure | Distribution | System | Yes | 6 | 7 | 13 | 11 | 6 | 9 | 12 | 7.6 | 7.7 | # ignitions
|  | 2.f.vi | Pole damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions | Previously 10.f
|  | 2.f.vii | Pole damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.f.viii | Pole damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | # ignitions
|  | 2.f.ix | Pole damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.f.x | Pole damage or failure | Transmission | System | Yes | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.3 | 0.3 | # ignitions
|  | 2.g.i | Insulator and brushing damage or failure | Distribution | Non-HFTD | Yes | 6 | 4 | 8 | 4 | 3 | 4 | 2 | 4.2 | 4.2 | # ignitions
|  | 2.g.ii | Insulator and brushing damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.g.iii | Insulator and brushing damage or failure | Distribution | HFTD Tier 2 | Yes | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0.4 | 0.4 | # ignitions
|  | 2.g.iv | Insulator and brushing damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1.1 | 0.2 | # ignitions
|  | 2.g.v | Insulator and brushing damage or failure | Distribution | System | Yes | 7 | 4 | 9 | 5 | 4 | 6 | 3 | 5.7 | 4.8 | # ignitions
|  | 2.g.vi | Insulator and brushing damage or failure | Transmission | Non-HFTD | Yes | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 0.7 | 0.7 | # ignitions | Previously 10.g
|  | 2.g.vii | Insulator and brushing damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.g.viii | Insulator and brushing damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 1 | 0 | 2 | 1 | 0 | 0.5 | 0.5 | # ignitions
|  | 2.g.ix | Insulator and brushing damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions
|  | 2.g.x | Insulator and brushing damage or failure | Transmission | System | Yes | 1 | 0 | 2 | 1 | 2 | 2 | 0 | 1.3 | 1.3 | # ignitions
|  | 2.h.i | Crossarm damage or failure | Distribution | Non-HFTD | Yes | 5 | 7 | 5 | 1 | 1 | 2 | 4 | 2.8 | 2.8 | # ignitions
|  | 2.h.ii | Crossarm damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.h.iii | Crossarm damage or failure | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 5 | 1 | 1 | 0 | 1 | 0.6 | 0.7 | # ignitions
|  | 2.h.iv | Crossarm damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0.2 | 0.3 | # ignitions
|  | 2.h.v | Crossarm damage or failure | Distribution | System | Yes | 5 | 7 | 13 | 2 | 2 | 2 | 6 | 3.6 | 3.7 | # ignitions
|  | 2.h.vi | Crossarm damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions | Previously 10.h
|  | 2.h.vii | Crossarm damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.h.viii | Crossarm damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.h.ix | Crossarm damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.h.x | Crossarm damage or failure | Transmission | System | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions
|  | 2.i.i | Voltage regulator / booster damage or failure | Distribution | Non-HFTD | Yes | 2 | 0 | 5 | 0 | 1 | 3 | 3 | 1.5 | 1.5 | # ignitions
|  | 2.i.ii | Voltage regulator / booster damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.i.iii | Voltage regulator / booster damage or failure | Distribution | HFTD Tier 2 | Yes | 4 | 1 | 0 | 0 | 1 | 1 | 0 | 0.2 | 0.2 | # ignitions
|  | 2.i.iv | Voltage regulator / booster damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | # ignitions
|  | 2.i.v | Voltage regulator / booster damage or failure | Distribution | System | Yes | 6 | 1 | 5 | 0 | 2 | 4 | 3 | 1.7 | 1.8 | # ignitions
|  | 2.i.vi | Voltage regulator / booster damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 10.i
|  | 2.i.vii | Voltage regulator / booster damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.i.viii | Voltage regulator / booster damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  | 2.i.ix | Voltage regulator / booster damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.i.x | Voltage regulator / booster damage or failure | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  | 2.j.i | Recloser damage or failure | Distribution | Non-HFTD | Yes | 0 | 3 | 3 | 0 | 3 | 0 | 3 | 1.5 | 1.5 | # ignitions
|  | 2.j.ii | Recloser damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.iii | Recloser damage or failure | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  | 2.j.iv | Recloser damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.v | Recloser damage or failure | Distribution | System | Yes | 0 | 3 | 3 | 0 | 3 | 1 | 3 | 1.5 | 1.5 | # ignitions
|  | 2.j.vi | Recloser damage or failure | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 10.j
|  | 2.j.vii | Recloser damage or failure | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.viii | Recloser damage or failure | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.ix | Recloser damage or failure | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.j.x | Recloser damage or failure | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.i | Anchor / guy damage or failure | Distribution | Non-HFTD | Yes | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0.7 | 0.7 | # ignitions
|  | 2.k.ii | Anchor / guy damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.iii | Anchor / guy damage or failure | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | # ignitions
|  | 2.k.iv | Anchor / guy damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.v | Anchor / guy damage or failure | Distribution | System | Yes | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0.8 | 0.8 | # ignitions
|  | 2.k.vi | Anchor / guy damage or failure | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 10.k
|  | 2.k.vii | Anchor / guy damage or failure | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.viii | Anchor / guy damage or failure | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.ix | Anchor / guy damage or failure | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.k.x | Anchor / guy damage or failure | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.i | Sectionalizer damage or failure | Distribution | Non-HFTD | Yes | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions
|  | 2.l.ii | Sectionalizer damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.iii | Sectionalizer damage or failure | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.iv | Sectionalizer damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.v | Sectionalizer damage or failure | Distribution | System | Yes | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions
|  | 2.l.vi | Sectionalizer damage or failure | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 10.l
|  | 2.l.vii | Sectionalizer damage or failure | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.viii | Sectionalizer damage or failure | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.ix | Sectionalizer damage or failure | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.l.x | Sectionalizer damage or failure | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.m.i | Connection device damage or failure | Distribution | Non-HFTD | Yes | 39 | 20 | 29 | 2 | 0 | 28 | 31 | 19 | 19 | # ignitions
|  | 2.m.ii | Connection device damage or failure | Distribution | HFTD Zone 1 | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.m.iii | Connection device damage or failure | Distribution | HFTD Tier 2 | Yes | 2 | 3 | 8 | 2 | 0 | 8 | 9 | 1.8 | 0.9 | # ignitions
|  | 2.m.iv | Connection device damage or failure | Distribution | HFTD Tier 3 | Yes | 2 | 1 | 2 | 0 | 0 | 0 | 1 | 0.3 | 0.4 | # ignitions
|  | 2.m.v | Connection device damage or failure | Distribution | System | Yes | 44 | 24 | 39 | 4 | 0 | 36 | 41 | 21.2 | 20.3 | # ignitions
|  | 2.m.vi | Connection device damage or failure | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | # ignitions | Previously 10.m
|  | 2.m.vii | Connection device damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.m.viii | Connection device damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0.1 | 0.1 | # ignitions
|  | 2.m.ix | Connection device damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.m.x | Connection device damage or failure | Transmission | System | Yes | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0.2 | 0.2 | # ignitions
|  | 2.n.i | Transformer damage or failure | Distribution | Non-HFTD | Yes | 14 | 11 | 18 | 11 | 19 | 15 | 11 | 14 | 14 | # ignitions
|  | 2.n.ii | Transformer damage or failure | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.n.iii | Transformer damage or failure | Distribution | HFTD Tier 2 | Yes | 4 | 2 | 3 | 2 | 1 | 6 | 2 | 1.3 | 1.4 | # ignitions
|  | 2.n.iv | Transformer damage or failure | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 0.5 | 0.6 | # ignitions
|  | 2.n.v | Transformer damage or failure | Distribution | System | Yes | 18 | 13 | 23 | 17 | 20 | 21 | 13 | 15.7 | 16 | # ignitions
|  | 2.n.vi | Transformer damage or failure | Transmission | Non-HFTD | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions | Previously 10.n
|  | 2.n.vii | Transformer damage or failure | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.n.viii | Transformer damage or failure | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.n.ix | Transformer damage or failure | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.n.x | Transformer damage or failure | Transmission | System | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions
|  | 2.o.i | Other | Distribution | Non-HFTD | Yes | 31 | 22 | 23 | 26 | 21 | 20 | 28 | 20.5 | 20.5 | # ignitions
|  | 2.o.ii | Other | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.o.iii | Other | Distribution | HFTD Tier 2 | Yes | 4 | 3 | 4 | 9 | 3 | 2 | 4 | 2 | 2.3 | # ignitions
|  | 2.o.iv | Other | Distribution | HFTD Tier 3 | Yes | 5 | 2 | 3 | 7 | 1 | 0 | 0 | 0.8 | 0.9 | # ignitions
|  | 2.o.v | Other | Distribution | System | Yes | 40 | 27 | 30 | 42 | 25 | 22 | 32 | 23.4 | 23.8 | # ignitions
|  | 2.o.vi | Other | Transmission | Non-HFTD | Yes | 3 | 0 | 1 | 0 | 1 | 1 | 4 | 0.2 | 0.2 | # ignitions | Previously 10.o
|  | 2.o.vii | Other | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 2.o.viii | Other | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 1 | 3 | 1 | 1 | 1 | 0.9 | 0.9 | # ignitions
|  | 2.o.ix | Other | Transmission | HFTD Tier 3 | Yes | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0.3 | 0.3 | # ignitions
|  | 2.o.x | Other | Transmission | System | Yes | 3 | 1 | 3 | 3 | 2 | 3 | 6 | 1.3 | 1.3 | # ignitions
| 3. Wire-to-wire contact | 3.a.i | Wire-to-wire contact / contamination | Distribution | Non-HFTD | Yes | 3 | 4 | 3 | 1 | 10 | 20 | 0 | 1.3 | 1.3 | # ignitions
|  | 3.a.ii | Wire-to-wire contact / contamination | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 3.a.iii | Wire-to-wire contact / contamination | Distribution | HFTD Tier 2 | Yes | 1 | 2 | 0 | 3 | 1 | 7 | 0 | 2.8 | 3.3 | # ignitions
|  | 3.a.iv | Wire-to-wire contact / contamination | Distribution | HFTD Tier 3 | Yes | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1.1 | 1.3 | # ignitions
|  | 3.a.v | Wire-to-wire contact / contamination | Distribution | System | Yes | 5 | 6 | 3 | 5 | 11 | 27 | 0 | 5.3 | 5.9 | # ignitions
|  | 3.a.vi | Wire-to-wire contact / contamination | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 11.a
|  | 3.a.vii | Wire-to-wire contact / contamination | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 3.a.viii | Wire-to-wire contact / contamination | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 3.a.ix | Wire-to-wire contact / contamination | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 3.a.x | Wire-to-wire contact / contamination | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
| 4. Contamination | 4.a.i | Contamination | Distribution | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 1.3 | 1.3 | # ignitions
|  | 4.a.ii | Contamination | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 4.a.iii | Contamination | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 1 | 1 | 0 | 2 | 3 | 0.2 | 0.2 | # ignitions
|  | 4.a.iv | Contamination | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.1 | 0.1 | # ignitions
|  | 4.a.v | Contamination | Distribution | System | Yes | 0 | 0 | 1 | 1 | 0 | 5 | 15 | 1.6 | 1.6 | # ignitions
|  | 4.a.vi | Contamination | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.5 | 0.5 | # ignitions | Previously 12.a
|  | 4.a.vii | Contamination | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 4.a.viii | Contamination | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 4.a.ix | Contamination | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 4.a.x | Contamination | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.5 | 0.5 | # ignitions
| 5. Utility work / Operation | 5.a.i | Utility work / Operation | Distribution | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions
|  | 5.a.ii | Utility work / Operation | Distribution | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 5.a.iii | Utility work / Operation | Distribution | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0.3 | # ignitions
|  | 5.a.iv | Utility work / Operation | Distribution | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.1 | 0.1 | # ignitions
|  | 5.a.v | Utility work / Operation | Distribution | System | No | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2.6 | 0.6 | # ignitions
|  | 5.a.vi | Utility work / Operation | Transmission | Non-HFTD | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 13.a
|  | 5.a.vii | Utility work / Operation | Transmission | HFTD Zone 1 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 5.a.viii | Utility work / Operation | Transmission | HFTD Tier 2 | No | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  | 5.a.ix | Utility work / Operation | Transmission | HFTD Tier 3 | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 5.a.x | Utility work / Operation | Transmission | System | No | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
| 6. Vandalism / Theft | 6.a.i | Vandalism / Theft | Distribution | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 1.8 | 1.8 | # ignitions
|  | 6.a.ii | Vandalism / Theft | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6.a.iii | Vandalism / Theft | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.1 | 0.1 | # ignitions
|  | 6.a.iv | Vandalism / Theft | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6.a.v | Vandalism / Theft | Distribution | System | Yes | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 2 | 2 | # ignitions
|  | 6.a.vi | Vandalism / Theft | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | # ignitions | Previously 14.a
|  | 6.a.vii | Vandalism / Theft | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6.a.viii | Vandalism / Theft | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | # ignitions
|  | 6.a.ix | Vandalism / Theft | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6.a.x | Vandalism / Theft | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | # ignitions
| 7. Other | 7.a.i | All Other | Distribution | Non-HFTD | Yes | 1 | 6 | 1 | 7 | 3 | 3 | 1 | 3.5 | 3.5 | # ignitions
|  | 7.a.ii | All Other | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 7.a.iii | All Other | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 0 | 3 | 1 | 1 | 3 | 1 | 1.2 | # ignitions
|  | 7.a.iv | All Other | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0.4 | 0.4 | # ignitions
|  | 7.a.v | All Other | Distribution | System | Yes | 1 | 6 | 1 | 10 | 5 | 6 | 4 | 4.9 | 5.1 | # ignitions
|  | 7.a.vi | All Other | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions | Previously 15.a
|  | 7.a.vii | All Other | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 7.a.viii | All Other | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.1 | 0.1 | # ignitions
|  | 7.a.ix | All Other | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 7.a.x | All Other | Transmission | System | Yes | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.2 | 0.2 | # ignitions
| 8. Unknown | 8.a.i | Unknown | Distribution | Non-HFTD | Yes | 2 | 1 | 2 | 18 | 12 | 1 | 4 | 10.2 | 10.2 | # ignitions
|  | 8.a.ii | Unknown | Distribution | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 8.a.iii | Unknown | Distribution | HFTD Tier 2 | Yes | 0 | 0 | 2 | 6 | 2 | 0 | 3 | 2 | 2.3 | # ignitions
|  | 8.a.iv | Unknown | Distribution | HFTD Tier 3 | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0.8 | 0.9 | # ignitions
|  | 8.a.v | Unknown | Distribution | System | Yes | 2 | 1 | 4 | 25 | 14 | 1 | 8 | 12.9 | 13.3 | # ignitions
|  | 8.a.vi | Unknown | Transmission | Non-HFTD | Yes | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.7 | 0.7 | # ignitions | Previously 16.a
|  | 8.a.vii | Unknown | Transmission | HFTD Zone 1 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 8.a.viii | Unknown | Transmission | HFTD Tier 2 | Yes | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.4 | 0.4 | # ignitions
|  | 8.a.ix | Unknown | Transmission | HFTD Tier 3 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | # ignitions
|  | 8.a.x | Unknown | Transmission | System | Yes | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 1.2 | 1.2 | # ignitions
Comments for Table 7.2: The fire ignition data provided in this table is based on fire incident reports filed with the CPUC annually in accordance with D.14-02-015. The ignition data provided in these tables was pulled from PG&E’s systems in mid-January 2022 and reflects preliminary data for two reasons: first, PG&E’s final 2021 fire ignition report is due on April 1, 2022 and 2021 data will be further reviewed in advance of that filing. Second, in late 2020 PG&E self-identified a data omission regarding prior year’s fire ignition data in the annual reports submitted and notified the CPUC of this issue on December 23, 2020. More detail is provided in WMP Section 6.7 discussion. PG&E’s Ignition Investigation team is conducting a system of record audit for ignition events. The updated counts in Table 7.2 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. 2022 and 2023 HFTD Distribution: Values show decreases as compared to 2021 HFTD distribution based on preliminary EPSS modeling forecasted against 2018-2020 data.