121587537 | E | LC | ETL.2790.INSL | 40895783 | CONCORD | EAST BAY | 2021-06-22 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40870725 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-09-04 | Glass | Suspension |  |  |  |  | 0.00096923 | 63.3245 | 0.061376
121587537 | E | LC | ETL.2790.INSL | 40895783 | CONCORD | EAST BAY | 2021-06-22 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40870725 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 0.00096923 | 63.3245 | 0.061376
121600875 | E | LC | ETL.5430.POLE.WDPS | 44560749 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40601089 | 1992-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00013978 | 2314.1801 | 0.32347
121609263 | B | LC | ETL.5960.INSL.CERA | 44374375 | PISMOBCH | LOS PADRES | 2021-06-26 | 2021-07-15 | ETL.5960 | DIABLO-GATES #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40581808 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-04-12 | Ceramic | Suspension |  |  |  |  | 2.6756e-08 | 777.0289
121609372 | E | LC | ETL.6760.INSL.NCER | 44997689 | SACTO | SIERRA | 2021-06-18 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44997686 | 2020-11-06 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-11-06 | Glass | Double Dead End |  |  |  |  | 0.026374 | 142.5076 | 3.7584
121653907 | E | LC | ETL.5140.POLE.WDPS | 44558218 | SACTO | SACRAMENTO | 2021-06-30 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44557842 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.1699e-05 | 5241.394 | 0.27098
121664419 | F | LC | ETL.5540.TOWR | 40598061 | TABLEMTN | NORTH VALLEY | 2021-07-05 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40598061 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 9.7491e-05 | 3642.2964 | 0.35509
121678738 | F | LC | ETL.6020.TOWR | 41162689 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.6020 | MALIN-ROUND MTN #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41162689 | 1965-01-01 | LATTICE STEEL TOWER | Unknown | [7 empty] | 1.2217e-08 | 174.1517
121679570 | E | LC | ETL.9240.TOWR | 43249795 | PISMOBCH | LOS PADRES | 2021-07-07 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249795 |  | LATTICE STEEL TOWER | [9 empty] | 950.9399
121717435 | F | LC | ETL.5630.POLE.NWOD | 43249817 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.5630 | ROCK CREEK-POE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 43249817 |  | Lattice Steel Pole | Unknown |  | Ceramic | Dead End |  |  |  |  | 0.00056065 | 5950.4492
121721236 | E | LC | ETL.7140.POLE.WDPS | 45096568 | LAKEVLLE | NORTH BAY | 2021-07-13 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41111803 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.28751 | 680.8114 | 195.7384
121743622 | F | LC | ETL.6230.POLE.NWOD | 44149271 | MOSSLNDG | CENTRAL COAST | 2021-07-13 |  | ETL.6230 | BURNS-LONE STAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44149271 | 2013-10-03 | Light Duty Steel Pole | T-1 - Tri Post | 2013-10-03 | Non Ceramic | Post |  |  |  |  | 0.057071 | 79.1724
121785381 | B | LC | ETL.5934.TOWR | 40805225 | FRESNO | FRESNO | 2021-07-22 | 2021-10-01 | ETL.5934 | TEMPLETON-GATES | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40805225 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.0020904
121786406 | E | LC | ETL.2395.POLE.WOOD | 44948581 | TABLEMTN | NORTH VALLEY | 2021-07-23 |  | ETL.2395 | GRIZZLY TAP | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44948581 |  | Single Wood Pole | DV - Double Vertical |  | Unknown | Dead End |  |  |  |  | 0.091367 | 189.8861 | 17.3493
121790564 | B | LC | ETL.8365.INSL.NCER | 40916341 | EUREKA | HUMBOLDT | 2021-07-24 | 2021-08-19 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906669 | 2011-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.047729
121800591 | E | LC | ETL.6880.POLE.STPS | 45102096 | LAKEVLLE | NORTH BAY | 2021-07-26 |  | ETL.6880 | FULTON-CALISTOGA | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45100498 | 2020-10-06 | 3-Pole Non Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 7.5445e-06 | 680.6089 | 0.0051348
121805192 | B | LC | ETL.6290.POLE.WOOD | 40656457 | TABLEMTN | NORTH VALLEY | 2021-07-27 | 2021-10-27 | ETL.6290 | CARIBOU-PLUMAS JCT | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40656457 | 1962-01-01 | Single Wood Pole | FDDE - Flat Dead End Construction | 2020-02-01 | Glass | Dead End |  |  |  |  | 0.2876 | 63.3304
121805384 | B | LC | ETL.6290.POLE.WOOD | 40589799 | TABLEMTN | NORTH VALLEY | 2021-07-27 | 2021-10-27 | ETL.6290 | CARIBOU-PLUMAS JCT | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40589799 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.34205 | 158.4559
121806512 | E | LC | ETL.7490.POLE.WOOD | 45114358 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45114358 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Dead End | [5 empty] | 20.6453
121815600 | E | LC | ETL.5960.TOWR | 40746854 | FRESNO | FRESNO | 2021-07-29 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40746854 | 1973-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1973-01-01 | Ceramic | Dead End |  |  |  |  | 2.6248e-05
121820768 | E | LC | ETL.6880.POLE.WOOD | 40912471 | LAKEVLLE | NORTH BAY | 2021-07-28 | 2021-08-13 | ETL.6880 | FULTON-CALISTOGA | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40912471 |  | Single Wood Pole | T2N | 2021-04-15 | Polymer | Post |  |  |  |  | 0.01603 | 476.0715
122017740 | E | LC | ETL.7560.POLE.WOOD | 40677915 | SACTO | SACRAMENTO | 2021-09-09 |  | ETL.7560 | WEIMAR #1 | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40677915 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.18104 | 221.5622 | 40.1118
122183944 | B | LC | ETL.1470.POLE.STPS | 44634840 | LAKEVLLE | SONOMA | 2021-10-10 | 2021-10-14 | ETL.1470 | EAGLE ROCK-CORTINA | Non-Routine Patrol | Investigate | [Air Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44634840 | 2018-08-01 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2018-08-01 | Ceramic | Dead End |  |  |  |  | 0.00038752
122183944 | B | LC | ETL.1470.POLE.STPS | 44634840 | LAKEVLLE | SONOMA | 2021-10-10 | 2021-10-14 | ETL.1470 | EAGLE ROCK-CORTINA | Non-Routine Patrol | Investigate | [Air Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44634840 | 2018-08-01 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2018-08-01 | Ceramic | Dead End |  |  |  |  | 0.00038752
122183944 | B | LC | ETL.1470.POLE.STPS | 44634840 | LAKEVLLE | SONOMA | 2021-10-10 | 2021-10-14 | ETL.1470 | EAGLE ROCK-CORTINA | Non-Routine Patrol | Investigate | [Air Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44634840 | 2018-08-01 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2018-08-01 | Ceramic | Dead End |  |  |  |  | 0.00038752
122284007 | B | LC | ETL.8480.POLE.STPS | 45102162 | PISMOBCH | LOS PADRES | 2021-11-01 | 2021-11-17 | ETL.8480 | ATASCADERO-CAYUCOS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 45102111 | 2021-05-27 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 5.1326e-08 | 2199.9841 | 0.00011292
118455797 | E | LC | ETL.4780.INSL.CERA | 40779513 | LAKEVLLE |  | 2020-01-23 | 2020-02-26 | ETL.4780 | GEYSERS #9-LAKEVILLE | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129173 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.0047741 | 2012.3107
118553071 | F | LC | ETL.4393.TOWR | 41196120 | SACTO | SACRAMENTO | 2020-02-20 | 2020-03-23 | ETL.4393 | DRUM-HIGGINS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41196120 |  | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-02-18 | Glass | Dead End |  |  |  |  | 3.4327e-07 | 110.7947
118553758 | E | LC | ETL.6890.POLE.NWOD | 44963401 | LAKEVLLE | SONOMA | 2020-02-20 | 2021-08-14 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44963401 | 2019-11-06 | Light Duty Steel Pole | T-1 - Tri Post | 2019-11-06 | Polymer | Post |  |  |  |  | 9.1816e-07 | 4339.4863
118763175 | F | LC | ETL.5090.TOWR | 40608555 | MOSSLNDG | DE ANZA | 2020-03-31 | 2020-04-22 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40608555 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.010758 | 854.5627
118796470 | E | LC | ETL.7270.POLE.WOOD | 40867097 | TABLEMTN | NORTH VALLEY | 2020-04-08 | 2021-09-12 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP | [12 empty] | 957.2229
118913045 | B | LC | ETL.8210.INSL.CERA | 40918289 | VICTOR | STOCKTON | 2020-04-10 | 2020-07-02 | ETL.8210 | VALLEY SPRINGS #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118926700 | E | LC | ETL.6470.POLE.WOOD | 40672218 | SACTO | SACRAMENTO | 2020-04-16 | 2020-07-15 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118935818 | E | LC | ETL.7590.POLE.WOOD | 40760171 | MOSSLNDG | CENTRAL COAST | 2020-04-20 | 2020-07-30 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118936775 | E | LC | ETL.6330.POLE.WOOD | 40824059 | TABLEMTN | NORTH VALLEY | 2020-04-21 | 2021-10-18 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.0048258 | 1046.0669 | 5.0481
118946512 | F | LC | ETL.5660.TOWR | 40805040 | CONCORD | MISSION | 2020-04-20 | 2021-01-21 | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805040 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.5106e-06 | 2754.8582
118946512 | F | LC | ETL.5660.TOWR | 40805040 | CONCORD | MISSION | 2020-04-20 | 2021-01-21 | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805040 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-29 | Glass | Suspension |  |  |  |  | 6.5106e-06 | 2754.8582
118953798 | A | LC | ETL.1470.INSL.CERA | 40915453 | LAKEVLLE | SONOMA | 2020-04-27 | 2020-05-01 | ETL.1470 | EAGLE ROCK-CORTINA | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40905788 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 5.4391e-05 | 6475.0005
118961051 | F | LC | ETL.4220.POLE.WOOD | 40664914 | TABLEMTN | NORTH VALLEY | 2020-04-29 | 2020-05-29 | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40664914 | 1962-01-01 | Single Wood Pole | WB - Wishbone | 1962-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0084974 | 5019.5959
118966444 | E | LC | ETL.8240.POLE.WOOD | 40758493 | VICTOR | STOCKTON | 2020-04-28 | 2021-08-16 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758493 | 1992-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Glass | [5 empty] | 0.00067733 | 902.8336
118967518 | E | LC | ETL.8240.INSL | 40798969 | VICTOR | STOCKTON | 2020-04-28 | 2021-09-13 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118971739 | E | LC | ETL.7590.POLE.WOOD | 40581859 | MOSSLNDG | SAN JOSE | 2020-05-01 | 2021-03-23 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40581859 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.1763 | 63.351
118976528 | F | LC | ETL.5140.POLE.STPS | 44690706 | SACTO | SIERRA | 2020-04-28 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44141453 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.7859e-09 | 269.0304
118993626 | A | LC | ETL.8410.POLE.WOOD | 40770654 | LAKEVLLE | SONOMA | 2020-05-07 | 2020-05-12 | ETL.8410 | ELK-GUALALA | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770654 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 0.2258 | 950.644
119017125 | F | LC | ETL.1330.TOWR | 40750610 | LAKEVLLE | HUMBOLDT | 2020-04-24 | 2021-04-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750610 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 3.0353e-05 | 4882.0518
119022412 | E | LC | ETL.9090.POLE.WOOD | 40597794 | PISMOBCH | LOS PADRES | 2020-05-04 | 2021-06-02 | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40597794 |  | Single Wood Pole | SS2 - Susp. Steel Double CIR. |  | Ceramic | Other |  |  |  |  | 0.0035792 | 743.4382
119059370 | E | LC | ETL.6760.POLE.WOOD | 40913019 | SACTO | SACRAMENTO | 2020-05-22 | 2021-06-30 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119075704 | B | LC | ETL.1650.INSL.NCER | 44298425 | LAKEVLLE |  | 2020-05-27 | 2020-06-15 | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44298416 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | Suspension |  |  |  |  | 0.00012837 | 2393.1714
119083164 | B | LC | ETL.7560.POLE.WOOD | 40913130 | SACTO | SIERRA | 2020-05-29 | 2020-08-20 | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119083797 | F | LC | ETL.6870.POLE.WOOD | 40603361 | SACTO | SIERRA | 2020-05-28 | 2021-06-01 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40603361 | 1966-01-01 | Single Wood Pole | DV - Double Vertical | 2020-05-15 | Polymer | Dead End |  |  |  |  | 0.030328 | 142.4895
119087084 | E | LC | ETL.6980.POLE.WOOD | 40860968 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-06-17 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860968 | 1968-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2010-01-01 | Polymer | Suspension |  |  |  |  | 0.15052 | 15.8947
119088823 | E | LC | ETL.8410.POLE.WOOD | 40819549 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-01-20 | ETL.8410 | ELK-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119091224 | F | LC | ETL.7780.POLE.WOOD | 40614228 | LAKEVLLE | HUMBOLDT | 2020-05-18 | 2021-02-16 | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40614228 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.0025662 | 5382.875
119103115 | F | LC | ETL.6760.POLE.WOOD | 40654108 | SACTO | SIERRA | 2020-05-28 | 2021-03-11 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40654108 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.075442 | 94.9894
119112209 | E | LC | ETL.6720.POLE.WDPS | 44949082 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2021-09-01 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 42578810 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0015781 | 0.065151
119114900 | E | LC | ETL.1420.TOWR | 40582451 | SACTO | SIERRA | 2020-05-22 | 2021-03-08 | ETL.1420 | DRUM-RIO OSO #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40582451 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-05 | Glass | Suspension |  |  |  |  | 1.2878e-05 | 142.4642
119116994 | E | LC | ETL.8290.POLE.WOOD | 40660881 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-21 | ETL.8290 | VOLTA-DESCHUTES | Guy Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660881 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 8.2102e-05 | 3829.1331
119117550 | F | LC | ETL.7290.POLE.WOOD | 40876540 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40876540 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.011253 | 712.3871
119118139 | F | LC | ETL.7140.POLE.WOOD | 40588056 | LAKEVLLE | NORTH BAY | 2020-05-29 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40588056 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.14837 | 4560.6943
119122238 | F | LC | ETL.7300.POLE.WOOD | 40877900 | TABLEMTN |  | 2020-06-03 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40877900 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00054044 | 1878.7069
119125662 | E | LC | ETL.6690.POLE.WOOD | 40654873 | SACTO | SIERRA | 2020-05-28 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40654873 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Non Ceramic | [5 empty] | 0.099543 | 158.2976 | 15.7574
119125770 | E | LC | ETL.7290.POLE.WOOD | 40816384 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-03-15 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119152840 | E | LC | ETL.6470.POLE.WOOD | 40874830 | SACTO | SIERRA | 2020-06-11 | 2020-07-02 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40874830 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.26824 | 300.6841
119165857 | F | LC | ETL.6760.POLE.NWOD | 40816309 | SACTO | SIERRA | 2020-06-09 | 2021-05-11 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40816309 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.012437 | 110.7947
119168423 | B | LC | ETL.8170.INSL.CERA | 40915994 | EUREKA | HUMBOLDT | 2020-06-15 | 2020-09-17 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906325 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.015308
119168423 | B | LC | ETL.8170.INSL.CERA | 40915994 | EUREKA | HUMBOLDT | 2020-06-15 | 2020-09-17 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906325 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.015308
119168423 | B | LC | ETL.8170.INSL.CERA | 40915994 | EUREKA | HUMBOLDT | 2020-06-15 | 2020-09-17 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906325 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.015308
119179992 | F | LC | ETL.2720.TOWR | 40659393 | CONCORD | EAST BAY | 2020-06-15 | 2021-03-02 | ETL.2720 | MORAGA-OAKLAND #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40659393 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 2.896e-05 | 0.065158
119180962 | F | LC | ETL.7300.POLE.WOOD | 44744778 | TABLEMTN | NORTH VALLEY | 2020-06-16 |  | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44744778 |  | Single Wood Pole | T-1 - Tri Post | 2019-04-12 | Polymer | Post |  |  |  |  | 7.9206e-08 | 3914.5493
119181022 | F | LC | ETL.6280.POLE.WOOD | 40861853 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-08-03 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40861853 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 3.0662e-05 | 1739.9091
119184452 | F | LC | ETL.6280.POLE.WOOD | 40666832 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-09-10 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40666832 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 9.6347e-05 | 5934.9365
119189747 | E | LC | ETL.1440.POLE.WOOD | 40756799 | SACTO | SACRAMENTO | 2020-06-19 | 2020-07-21 | ETL.1440 | DRUM-SUMMIT #1 | Damper-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119194364 | F | LC | ETL.8210.POLE.WOOD | 40904195 | VICTOR | STOCKTON | 2020-06-18 |  | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40904195 | 1964-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0065084 | 4666.4149
119198551 | E | LC | ETL.6470.POLE.WOOD | 40598570 | SACTO | SIERRA | 2020-06-22 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40598570 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.091787 | 221.5931
119198881 | E | LC | ETL.6470.INSL.NCER | 40688243 | SACTO | SACRAMENTO | 2020-06-23 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119198960 | F | LC | ETL.6480.POLE.WOOD | 40655133 | SACTO | SIERRA | 2020-06-22 | 2021-02-11 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40655133 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.14969 | 1139.0737
119200741 | F | LC | ETL.6470.POLE.WOOD | 40590449 | SACTO | SIERRA | 2020-06-23 | 2021-07-06 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40590449 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.21037 | 142.4516
119213813 | F | LC | ETL.7270.POLE.WOOD | 40909453 | TABLEMTN | NORTH VALLEY | 2020-06-25 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40909453 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0039457 | 1443.1068
119232078 | E | LC | ETL.1110.POLE.WDPS | 44424119 | EUREKA | HUMBOLDT | 2020-06-29 | 2021-07-17 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44424117 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0037771 | 268.9929
119236383 | E | LC | ETL.7270.POLE.NWOD | 44649358 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2021-10-19 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44649358 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.0003991 | 0.065152 | 2.6002e-05
119290607 | E | LC | ETL.7180.POLE.WOOD | 40658533 | LAKEVLLE | SONOMA | 2020-07-01 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40658533 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 3.4171e-06 | 407.8042 | 0.0013935
119292259 | F | LC | ETL.7180.POLE.WOOD | 40825705 | LAKEVLLE | SONOMA | 2020-07-01 | 2020-11-10 | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40825705 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 4.9099e-05 | 411.2508
119301791 | F | LC | ETL.4393.POLE.WDPS | 44172231 | SACTO | SACRAMENTO | 2020-07-01 |  | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44172230 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0078246 | 49.1321
119308835 | E | LC | ETL.1350.POLE.WDPS | 44549898 | TABLEMTN |  | 2020-07-02 | 2021-07-28 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549436 |  | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.012073 | 411.4229
119309295 | E | LC | ETL.6900.POLE.WOOD | 40616449 | LAKEVLLE | SONOMA | 2020-06-30 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40616449 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 3.0106e-05 | 0.065158 | 1.9616e-06
119309701 | F | LC | ETL.8060.POLE.WOOD | 40660203 | SACTO | SIERRA | 2020-07-02 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660203 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0088062 | 31.7066
119314266 | F | LC | ETL.5960.TOWR | 40741755 | PISMOBCH | LOS PADRES | 2020-07-06 | 2021-07-30 | ETL.5960 | DIABLO-GATES #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40741755 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 1.0213e-07 | 838.9597
119315307 | F | LC | ETL.8170.POLE.WDPS | 44420688 | EUREKA | HUMBOLDT | 2020-07-06 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44420686 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0089752 | 0.065148
119330083 | E | LC | ETL.6710.POLE.WOOD | 40768322 | MOSSLNDG | CENTRAL COAST | 2020-07-08 | 2021-03-11 | ETL.6710 | DEL MONTE-VIEJO | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40768322 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.14798 | 0.066432
119331943 | F | LC | ETL.6880.POLE.NWOD | 40588859 | LAKEVLLE | SONOMA | 2020-07-08 |  | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40588859 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0019215 | 63.3804
119341103 | F | LC | ETL.7030.POLE.WOOD | 40667955 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40667955 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.011353 | 698.4329
119341394 | E | LC | ETL.1430.TOWR | 40822812 | SACTO | SACRAMENTO | 2020-07-09 | 2020-12-03 | ETL.1430 | DRUM-RIO OSO #2 | Vegetation-Tower | Overgrown | [Cage Clearing, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40822812 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2016-11-14 | Ceramic | Suspension |  |  |  |  | 0.00024134 | 15.9216
119341435 | F | LC | ETL.7180.POLE.WOOD | 40750710 | LAKEVLLE | SONOMA | 2020-07-09 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40750710 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 2020-06-27 | Polymer | Post |  |  |  |  | 0.00070709 | 126.5965
119355085 | E | LC | ETL.6861.POLE.WOOD | 40585190 | LAKEVLLE | SONOMA | 2020-07-10 | 2020-07-27 | ETL.6861 | KONOCTI-EAGLE ROCK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40585190 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2018-11-06 | Ceramic | Dead End |  |  |  |  | 0.0045196 | 4672.6953
119364826 | E | LC | ETL.6380.POLE.WOOD | 40768972 | LAKEVLLE | SONOMA | 2020-07-13 | 2021-03-09 | ETL.6380 | KONOCTI-MIDDLETOWN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768972 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 2.6419e-05 | 2260.7849
119368729 | F | LC | ETL.7260.POLE.WOOD | 40759219 | TABLEMTN | NORTH VALLEY | 2020-07-14 |  | ETL.7260 | KESWICK-CASCADE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40759219 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 1.9865e-05 | 2124.5115
119371044 | E | LC | ETL.6290.POLE.WOOD | 40758737 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-07-09 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758737 | 1962-01-01 | Single Wood Pole | T2N | 2020-06-02 | Polymer | Post |  |  |  |  | 0.087698 | 4919.2388
119371701 | F | LC | ETL.6280.POLE.WOOD | 40649945 | TABLEMTN | NORTH VALLEY | 2020-07-14 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40649945 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Other |  |  |  |  | 2.8423e-05 | 4223.3467
119373423 | E | LC | ETL.6220.POLE.WOOD | 44896383 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44896383 | 2019-06-28 | Single Wood Pole | T2N | 2019-06-28 | Polymer | Post |  |  |  |  | 0.016747 | 332.2834 | 5.5647
119379523 | F | LC | ETL.7030.POLE.WOOD | 40676350 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-07-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676350 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0079846 | 6610.0464
119381616 | F | LC | ETL.8960.POLE.WOOD | 40765923 | FRESNO | FRESNO | 2020-07-16 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40765923 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 1.2832e-05
119381756 | F | LC | ETL.6222.POLE.WOOD | 40656606 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6222 | FORT SEWARD TAP | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40656606 | 1952-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0046716
119466164 | F | LC | ETL.6280.POLE.WOOD | 40875408 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40875408 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Pin |  |  |  |  | 4.8412e-06 | 537.8195
119466747 | E | LC | ETL.7560.POLE.WOOD | 44263355 | SACTO | SACRAMENTO | 2020-07-17 | 2021-04-06 | ETL.7560 | WEIMAR #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44263355 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2019-09-10 | Glass | Suspension |  |  |  |  | 0.057454 | 15.8837
119475817 | F | LC | ETL.7160.POLE.WOOD | 44871196 | LAKEVLLE | NORTH BAY | 2020-07-20 |  | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871196 | 2019-09-19 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2019-09-19 | Polymer | Dead End |  |  |  |  | 0.21707 | 205.9363
119482109 | E | LC | ETL.9200.POLE.WOOD | 40654826 | MIDWAY | KERN | 2020-07-20 |  | ETL.9200 | TAFT-CUYAMA #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40654826 | 1962-01-01 | Single Wood Pole | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.0033203
119489930 | E | LC | ETL.6280.POLE.WOOD | 40769590 | TABLEMTN | NORTH VALLEY | 2020-07-22 | 2021-10-11 | ETL.6280 | CARIBOU #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40769590 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Other |  |  |  |  | 1.1163e-05 | 126.5956
119496011 | F | LC | ETL.6440.POLE.NWOD | 44927790 | TABLEMTN | NORTH VALLEY | 2020-07-23 | 2020-08-25 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44927790 | 2020-05-14 | Light Duty Steel Pole | T-1 - Tri Post | 2020-05-14 | Polymer | Post |  |  |  |  | 0.002549 | 4800.9653
119517564 | E | LC | ETL.2060.POLE.WOOD | 40586954 | LAKEVLLE | SONOMA | 2020-07-27 | 2020-10-19 | ETL.2060 | FORT BRAGG-ELK | Other | Customer Issue | [Access Issue] | Tier2 | Tier 2 | Within Both | COMP | 40586954 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.32375 | 31.6963
119519033 | E | LC | ETL.5450.TOWR | 40587051 | TABLEMTN | NORTH VALLEY | 2020-07-28 |  | ETL.5450 | PIT #3-CARBERRY SW STA | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587051 | 1924-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2021-01-14 | Glass | Dead End |  |  |  |  | 2.0246e-06 | 4825.6079 | 0.0097699
119555797 | F | LC | ETL.7490.POLE.WOOD | 40877970 | EUREKA | HUMBOLDT | 2020-08-04 | 2021-08-05 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40877970 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 0.0028939 | 221.4934
119569470 | F | LC | ETL.6980.POLE.WOOD | 40648469 | LAKEVLLE | SONOMA | 2020-08-06 |  | ETL.6980 | FORT ROSS-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40648469 | 2007-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Other |  |  |  |  | 0.42502 | 1174.0449
119571403 | E | LC | ETL.6300.POLE.WOOD | 40824715 | TABLEMTN |  | 2020-08-06 | 2021-08-16 | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119577519 | F | LC | ETL.8365.POLE.WOOD | 40750497 | EUREKA | HUMBOLDT | 2020-08-07 | 2021-05-03 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40750497 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-04-28 | Glass | Dead End |  |  |  |  | 0.050769 | 1046.2505
119590924 | E | LC | ETL.7180.POLE.WOOD | 40861081 | LAKEVLLE | NORTH BAY | 2020-08-07 | 2021-04-21 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861081 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 4.4021e-06 | 71.6461
119594623 | E | LC | ETL.8210.POLE.WOOD | 40908569 | VICTOR | STOCKTON | 2020-08-10 | 2021-08-26 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0088599 | 4670.8359
119604396 | E | LC | ETL.9330.TOWR | 40820717 | FRESNO | FRESNO | 2020-08-12 |  | ETL.9330 | WISHON-COPPERMINE | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40820717 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2014-12-31 | Glass | Suspension |  |  |  |  | 0.00056361
119621844 | E | LC | ETL.1420.POLE.STPS | 44337047 | SACTO | SACRAMENTO | 2020-08-15 |  | ETL.1420 | DRUM-RIO OSO #1 | Crossarm-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 3 | Within Both | PEND | 44337046 | 2016-08-08 | 2-Pole Non Wood | 2P DDE-A - 2 Pole Double Dead End Angle | [7 empty] | 2.3237e-05 | 870.2298 | 0.020222
119624970 | E | LC | ETL.4960.INSL | 40635473 | CONCORD | DIABLO | 2020-08-16 | 2021-08-10 | ETL.4960 | LAKEVILLE-SOBRANTE #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602306 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.00081071 | 930.4564
119632931 | E | LC | ETL.6710.POLE.WOOD | 40809358 | MOSSLNDG | CENTRAL COAST | 2020-08-18 | 2021-08-17 | ETL.6710 | DEL MONTE-VIEJO | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809358 |  | Single Wood Pole | T-1 - Tri Post | 2019-08-18 | Polymer | Post |  |  |  |  | 0.10708 | 0.065148
119658776 | A | LC | ETL.6240.POLE.WOOD | 40812278 | MOSSLNDG | CENTRAL COAST | 2020-08-22 | 2020-09-19 | ETL.6240 | BURNS-LONE STAR #2 | Emergency-Wood | Other | [Replace, Completed] | Tier3 |  |  | COMP
119659285 | E | LC | ETL.3500.TOWR | 40804243 | VICTOR | STOCKTON | 2020-08-23 | 2021-06-23 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40804243 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 7.0162e-05 | 5974.9344
119682047 | E | LC | ETL.1110.POLE.WDPS | 44561125 | TABLEMTN | HUMBOLDT | 2020-08-25 | 2021-04-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 44515914 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014769 | 5050.3735
119687017 | E | LC | ETL.8410.POLE.WOOD | 40660601 | LAKEVLLE | SONOMA | 2020-08-28 | 2021-06-07 | ETL.8410 | ELK-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119701350 | E | LC | ETL.8650.TOWR | 40806670 | FRESNO | FRESNO | 2020-09-01 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40806670 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1929-01-01 | Polymer | Double Dead End - Suspension |  |  |  |  | 0.038887 | 15.88
119701351 | F | LC | ETL.8060.POLE.WOOD | 40862170 | SACTO | SIERRA | 2020-08-28 | 2021-06-09 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0070958 | 0.065152
119721890 | A | LC | ETL.7590.POLE.WOOD | 40576677 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-10-21 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119752514 | E | LC | ETL.9460.POLE.WOOD | 44207030 | VICTOR | STOCKTON | 2020-08-13 | 2021-09-01 | ETL.9460 | VALLEY SPRINGS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44207030 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Dead End |  |  |  |  | 0.0025769 | 2773.5339
119754509 | B | LC | ETL.6950.POLE.WOOD | 40666247 | SACTO | SIERRA | 2020-09-11 | 2020-10-06 | ETL.6950 | GOLD HILL #1 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40666247 |  | Single Wood Pole | DCPOST - Double Circuit Post |  | Porcelain | [5 empty] | 0.00058057 | 5756.2148
119763822 | F | LC | ETL.2395.POLE.WDPS | 44551359 | TABLEMTN | NORTH VALLEY | 2020-09-08 |  | ETL.2395 | GRIZZLY TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
119765190 | F | LC | ETL.6690.POLE.NWOD | 44919750 | SACTO | SIERRA | 2020-09-08 |  | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44919750 | 2019-09-13 | Light Duty Steel Pole | T2N | 2019-09-13 | Polymer | Post |  |  |  |  | 0.021186 | 1234.2582
119775098 | F | LC | ETL.7390.POLE.NWOD | 44966221 | LAKEVLLE | SONOMA | 2020-09-16 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44966221 | 2020-08-26 | Light Duty Steel Pole | T2N | 2020-08-26 | Polymer | Post |  |  |  |  | 0.00084868
119775153 | E | LC | ETL.6480.POLE.NWOD | 44695518 | SACTO | NORTH VALLEY | 2020-09-08 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44695518 | 2018-12-10 | Light Duty Steel Pole | T2N | 2018-12-10 | Polymer | Post |  |  |  |  | 0.040548 | 284.7983 | 11.5479
119776734 | B | LC | ETL.6220.POLE.WOOD | 40591049 | EUREKA | HUMBOLDT | 2020-09-16 | 2020-09-22 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40591049 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2020-10-04 | Polymer | Post |  |  |  |  | 0.0059758 | 405.3814
119809924 | F | LC | ETL.4050.POLE.WOOD | 40750651 | LAKEVLLE | SONOMA | 2020-08-17 | 2021-09-27 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40750651 |  | Light Duty Steel Pole | T-1 - Tri Post | 1970-01-01 | Ceramic | Post |  |  |  |  | 3.4872e-07 | 1030.8367
119816381 | F | LC | ETL.8650.POLE.NWOD | 44420174 | FRESNO | YOSEMITE | 2020-08-29 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44420174 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0021672 | 3305.365
119818282 | F | LC | ETL.7300.POLE.WOOD | 40867876 | TABLEMTN |  | 2020-09-11 |  | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40867876 | 1998-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0059625 | 110.8046
119819509 | F | LC | ETL.7490.POLE.NWOD | 44969782 | EUREKA | HUMBOLDT | 2020-09-02 |  | ETL.7490 | MAPLE CREEK-HOOPA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44969782 | 2020-07-10 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-07-10 | Glass | Dead End |  |  |  |  | 0.0068604 | 722.8942
119819986 | F | LC | ETL.6280.POLE.WOOD | 40591751 | TABLEMTN | NORTH VALLEY | 2020-08-31 | 2021-09-10 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40591751 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 5.968e-06 | 6157.4399
119839765 | F | LC | ETL.6760.POLE.WOOD | 40693415 | SACTO | SIERRA | 2020-09-08 | 2021-02-12 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40693415 |  | Single Wood Pole | T2N | 2021-06-30 | Polymer | Post |  |  |  |  | 0.0099412 | 363.8909
119898482 | F | LC | ETL.6770.POLE.NWOD | 44396921 | SACTO | SIERRA | 2020-10-07 | 2021-04-19 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44396921 | 2018-09-06 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | [7 empty] | 3.0326e-06 | 949.3081
119936628 | F | LC | ETL.1730.POLE.NWOD | 44601339 | MOSSLNDG | CENTRAL COAST | 2020-10-22 | 2020-11-07 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44601339 | 2017-09-25 | Light Duty Steel Pole | SVDE - Single Vertical Dead End | 2017-09-25 | Polymer | Dead End - Suspension |  |  |  |  | 7.286e-09 | 15.88
119960043 | E | LC | ETL.6240.POLE.WOOD | 40593140 | MOSSLNDG | CENTRAL COAST | 2020-10-28 | 2021-08-09 | ETL.6240 | BURNS-LONE STAR #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593140 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.55457 | 110.8153
120007386 | E | LC | ETL.3750.TOWR | 40804878 | CONCORD | EAST BAY | 2020-11-10 | 2021-03-24 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | HFRA Removal | DLFL | 40804878 | 1932-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 1.2388e-06 | 15.88
120085010 | B | LC | ETL.6280.INSL.NCER | 44217565 | TABLEMTN | NORTH VALLEY | 2020-11-20 | 2021-03-02 | ETL.6280 | CARIBOU #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
120110315 | E | LC | ETL.1260.TOWR | 40669433 | CONCORD | DIABLO | 2020-11-17 |  | ETL.1260 | CHRISTIE-SOBRANTE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40669433 | 1941-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | 2021-05-10 | Glass Silicone Coated | Dead End |  |  |  |  | 1.2729e-07 | 857.9032 | 0.0001092
120160565 | F | LC | ETL.8650.TOWR | 40606165 | FRESNO | FRESNO | 2020-12-09 | 2021-08-30 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40606165 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0051682 | 4649.6255
120444950 | A | LC | ETL.6220.POLE.WOOD | 40752633 | EUREKA | HUMBOLDT | 2021-01-19 | 2021-01-19 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Emergency-Wood | Other | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40752633 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2020-01-19 | Glass | Double Dead End |  |  |  |  | 0.11297
120663373 | E | LC | ETL.4316.INSL.CERA | 40691000 | TABLEMTN | NORTH VALLEY | 2021-03-19 | 2021-07-29 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120665671 | E | LC | ETL.6950.POLE.WOOD | 40697242 | SACTO | SIERRA | 2021-03-19 | 2021-10-14 | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.010462 | 6282.2275 | 65.7277
120696065 | E | LC | ETL.5430.POLE.WDPS | 44562778 | TABLEMTN | NORTH VALLEY | 2021-03-26 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44562329 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0033958 | 590.2179 | 2.0043
120705812 | B | LC | ETL.7140.POLE.WOOD | 40809036 | LAKEVLLE | SONOMA | 2021-03-25 | 2021-06-23 | ETL.7140 | IGNACIO-BOLINAS #1 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809036 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | [5 empty] | 0.22845 | 276.9274
120707042 | B | LC | ETL.1350.INSL.CERA | 40771672 | TABLEMTN |  | 2021-03-29 | 2021-05-19 | ETL.1350 | CRAG VIEW-CASCADE | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44512268 |  | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.052408
120707042 | B | LC | ETL.1350.INSL.CERA | 40771672 | TABLEMTN |  | 2021-03-29 | 2021-05-19 | ETL.1350 | CRAG VIEW-CASCADE | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44512268 |  | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.052408
120719424 | F | LC | ETL.7390.POLE.NWOD | 45041702 | LAKEVLLE | SONOMA | 2021-03-31 |  | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45041702 | 2020-07-28 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2020-07-28 | Glass | Dead End |  |  |  |  | 0.0027664 | 632.8561
120727680 | F | LC | ETL.2900.TOWR | 40811074 | MOSSLNDG | CENTRAL COAST | 2021-04-01 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40811074 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1963-01-01 | Porcelain | Dead End |  |  |  |  | 0.0054858 | 743.9189 | 4.081
120737185 | E | LC | ETL.7590.POLE.WDPS | 45041304 | MOSSLNDG | CENTRAL COAST | 2021-04-02 |  | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45041262 | 2020-09-17 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.39236 | 15.8866 | 6.2332
120751466 | F | LC | ETL.5300.TOWR | 40662275 | PISMOBCH | LOS PADRES | 2021-04-02 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40662275 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 4.2617e-07 | 2753.9968 | 0.0011737
120755486 | E | LC | ETL.8480.POLE.WOOD | 40606006 | PISMOBCH | LOS PADRES | 2021-03-30 |  | ETL.8480 | ATASCADERO-CAYUCOS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40606006 | 1954-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1954-01-01 | Polymer | Dead End |  |  |  |  | 0.0012458 | 3527.3293 | 4.3944
120758522 | E | LC | ETL.1350.POLE.STPS | 44273548 | TABLEMTN | NORTH VALLEY | 2021-04-07 |  | ETL.1350 | CRAG VIEW-CASCADE | Vegetation | Overgrown | [Trim] | Tier2 | Tier 2 | Within Both | PEND | 44273547 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 6.234e-05 | 15.8866 | 0.00099037
120769035 | B | LC | ETL.3190.TOWR | 40910321 | TABLEMTN | NORTH VALLEY | 2021-04-08 | 2021-06-24 | ETL.3190 | CARIBOU-PALERMO | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910321 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 0.0052396 | 5252.52
120787033 | E | LC | ETL.6030.TOWR | 40749859 | MIDWAY | KERN | 2021-04-10 |  | ETL.6030 | MIDWAY-WHIRLWIND | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40749859 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-01-28 | Glass | Suspension |  |  |  |  | 9.1821e-05 | 6906.6963 | 0.63418
120788467 | F | LC | ETL.8250.POLE.WOOD | 40908843 | VICTOR | STOCKTON | 2021-04-10 | 2021-07-02 | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40908843 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0057599 | 1727.0282
120796043 | E | LC | ETL.4040.POLE.STPS | 44648004 | TABLEMTN | NORTH VALLEY | 2021-04-12 | 2021-10-11 | ETL.4040 | TRINITY-COTTONWOOD | Hardware-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44647967 | 2018-06-30 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 1.9532e-06 | 2708.5825 | 0.0052905
120798140 | E | LC | ETL.2720.INSL | 40851155 | CONCORD | DIABLO | 2021-04-07 | 2021-05-05 | ETL.2720 | MORAGA-OAKLAND #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40822215 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 0.00016476 | 0.065158
120826855 | B | LC | ETL.6880.POLE.NWOD | 45071348 | LAKEVLLE | SONOMA | 2021-04-16 | 2021-05-04 | ETL.6880 | FULTON-CALISTOGA | Other | Customer Issue | [Access Issue] | Tier3 | Tier 3 | Within Both | COMP | 45071348 | 2020-03-05 | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 2020-03-05 | Glass | Suspension |  |  |  |  | 6.0341e-05 | 110.894
120828875 | F | LC | ETL.1073.POLE.NWOD | 44384836 | VICTOR | STOCKTON | 2021-04-16 | 2021-07-12 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44384836 | 2017-08-17 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 1.4819e-05 | 31.7081
120831517 | F | LC | ETL.5090.TOWR | 40753101 | MOSSLNDG | CENTRAL COAST | 2021-04-16 |  | ETL.5090 | MONTA VISTA-COYOTE SW STA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40753101 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.060979 | 474.7087 | 28.9472
120840989 | E | LC | ETL.8340.POLE.WOOD | 40810008 | SACTO | SIERRA | 2021-04-19 |  | ETL.8340 | WEIMAR-HALSEY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810008 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 9.2906e-05 | 15.8837 | 0.0014757
120844731 | B | LC | ETL.2740.INSL.NCER | 40775600 | CONCORD | DIABLO | 2021-04-19 | 2021-04-27 | ETL.2740 | MORAGA-OAKLAND #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
120850197 | E | LC | ETL.5300.TOWR | 40871163 | PISMOBCH | LOS PADRES | 2021-04-12 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40871163 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.6399e-05 | 539.2498 | 0.030413
120867099 | E | LC | ETL.3840.INSL.NCER | 44363318 | VICTOR | STOCKTON | 2021-04-22 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40649521 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-08-13 | Polymer | Post |  |  |  |  | 3.4147e-06 | 5823.2505 | 0.019885
120867099 | E | LC | ETL.3840.INSL.NCER | 44363318 | VICTOR | STOCKTON | 2021-04-22 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40649521 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 3.4147e-06 | 5823.2505 | 0.019885
120868593 | E | LC | ETL.6040.TOWR | 40858416 | MOSSLNDG | CENTRAL COAST | 2021-04-14 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Vegetation-Tower | Overgrown | [Cage Clearing] |  | Non-HFTD | HFRA Addition | PEND | 40858416 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2011-11-16 | Ceramic | Suspension |  |  |  |  | 1.6168e-08
120878214 | E | LC | ETL.5490.TOWR | 40805062 | CONCORD | DIABLO | 2021-04-23 |  | ETL.5490 | PITTSBURG-SAN RAMON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40805062 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.00029011 | 5078.5112 | 1.4733
120878462 | E | LC | ETL.5300.TOWR | 40689436 | PISMOBCH | LOS PADRES | 2021-04-20 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40689436 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00017362 | 3451.7769 | 0.5993
120883077 | E | LC | ETL.7550.POLE.WOOD | 40809266 | LAKEVLLE | SONOMA | 2021-04-26 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40809266 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00011308 | 3342.5151 | 0.37796
120890318 | E | LC | ETL.1430.INSL.CERA | 40636382 | SACTO | SACRAMENTO | 2021-04-26 | 2021-09-28 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40604309 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.0018919 | 3865.0645
120890318 | E | LC | ETL.1430.INSL.CERA | 40636382 | SACTO | SACRAMENTO | 2021-04-26 | 2021-09-28 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40604309 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-09-08 | Glass | Suspension |  |  |  |  | 0.0018919 | 3865.0645
120893430 | E | LC | ETL.3700.INSL.CERA | 40722670 | PISMOBCH | LOS PADRES | 2021-04-27 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40678407 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Porcelain | Dead End |  |  |  |  | 0.0035982 | 3183.8059 | 11.4559
120909015 | E | LC | ETL.1450.POLE.WDPS | 44559070 | SACTO | SACRAMENTO | 2021-04-30 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44558487 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00031064 | 15.8859 | 0.0049347
120937373 | F | LC | ETL.1600.TOWR | 40872212 | LAKEVLLE | SONOMA | 2021-05-05 |  | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40872212 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1997-01-01 | Polymer | Dead End |  |  |  |  | 7.4147e-08 | 142.5961 | 1.0573e-05
120938341 | F | LC | ETL.1890.TOWR | 40859518 | FRESNO | FRESNO | 2021-04-16 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40859518 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 1.5564e-05 | 5540.6968 | 0.086237
120938584 | E | LC | ETL.7060.POLE.WDPS | 44732844 | METCALF | SAN JOSE | 2021-05-05 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42564698 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0077985 | 0.066432 | 0.00051807
120942250 | B | LC | ETL.5934.TOWR | 40680917 | PISMOBCH | LOS PADRES | 2021-05-04 | 2021-06-28 | ETL.5934 | TEMPLETON-GATES | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40680917 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 2.5679e-09 | 4734.0898
120991747 | E | LC | ETL.8350.INSL.NCER | 40895551 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40870546 | 2017-01-08 | Single Wood Pole | T-1 - Tri Post | 2017-01-08 | Polymer | Post |  |  |  |  | 0.00089561 | 2581.9299 | 2.3124
121191550 | E | LC | ETL.5310.INSL | 40620901 | PISMOBCH | LOS PADRES | 2021-04-20 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40594719 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 2.7409e-05 | 1603.2282 | 0.043942
121326113 | E | LC | ETL.4316.INSL.NCER | 41176879 | TABLEMTN | NORTH VALLEY | 2021-05-05 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41127255 | 2002-01-01 | Tubular Steel Pole | DCPOST - Double Circuit Post | 2021-04-16 | Polymer | Post |  |  |  |  | 0.0012288 | 2615.1708 | 3.2135
121326113 | E | LC | ETL.4316.INSL.NCER | 41176879 | TABLEMTN | NORTH VALLEY | 2021-05-05 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41127255 | 2002-01-01 | Tubular Steel Pole | DCPOST - Double Circuit Post | 2002-01-01 | Polymer | Post |  |  |  |  | 0.0012288 | 2615.1708 | 3.2135
121328784 | E | LC | ETL.4950.TOWR | 40593056 | LAKEVLLE | SONOMA | 2021-04-13 |  | ETL.4950 | FULTON-LAKEVILLE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40593056 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010214 | 1350.1429 | 1.3791
121328784 | E | LC | ETL.4950.TOWR | 40593056 | LAKEVLLE | SONOMA | 2021-04-13 |  | ETL.4950 | FULTON-LAKEVILLE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40593056 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0010214 | 1350.1429 | 1.3791
121329010 | F | LC | ETL.4850.TOWR | 40858146 | FRESNO | FRESNO | 2021-04-21 |  | ETL.4850 | HAAS-MCCALL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40858146 | 1957-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1957-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.6002e-07 | 6331.1787 | 0.0016462
121336890 | E | LC | ETL.1820.POLE.WDPS | 44560653 | EUREKA | HUMBOLDT | 2021-05-14 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560131 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.22446 | 822.5129 | 184.6172
121339283 | E | LC | ETL.3750.INSL.CERA | 42582048 | CONCORD | EAST BAY | 2021-04-24 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44188840 | 2008-01-01 | LATTICE STEEL TOWER | Unknown |  | Ceramic | Unknown |  |  |  |  | 4.3016e-07 | 855.4896 | 0.000368
121347533 | E | LC | ETL.6100.TOWR | 40664397 | VICTOR | YOSEMITE | 2021-05-17 |  | ETL.6100 | TESLA-LOS BANOS #1 | Raptor Guard-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40664397 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Glass | Suspension |  |  |  |  | 3.0296e-06 | 748.5006 | 0.0022676
121363052 | E | LC | ETL.6720.INSL.NCER | 44324234 | TABLEMTN | NORTH VALLEY | 2021-05-19 |  | ETL.6720 | DESABLA-CENTERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44324212 | 2015-11-03 | Fiberglass | T-1 - Tri Post | 2015-11-03 | Polymer | Post |  |  |  |  | 0.0010535 | 79.2789 | 0.083522
121363493 | F | LC | ETL.1250.POLE.WOOD | 40604441 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40604441 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 5.1919e-05 | 4323.0181
121364066 | E | LC | ETL.6950.POLE.WOOD | 40600055 | SACTO | SIERRA | 2021-05-01 | 2021-06-23 | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40600055 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00041499 | 1123.8499
121365158 | E | LC | ETL.6870.POLE.WOOD | 40822842 | SACTO | SIERRA | 2021-05-19 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40822842 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.092822 | 0.065152 | 0.0060475
121375327 | F | LC | ETL.9250.POLE.WOOD | 40607632 | MIDWAY | KERN | 2021-05-05 |  | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40607632 |  | Single Wood Pole | SV-PJ - Single Vertical Post Jumper |  | Ceramic | [5 empty] | 0.066711 | 3692.9529
121377789 | E | LC | ETL.5280.INSL.CERA | 44358910 | PISMOBCH | LOS PADRES | 2021-05-04 |  | ETL.5280 | MORRO BAY-CALIFORNIA FLATS SW STA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40862965 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-08-27 | Ceramic | Suspension |  |  |  |  | 1.2556e-06 | 4813.2778 | 0.0060437
121379450 | E | LC | ETL.1600.INSL | 40837930 | LAKEVLLE | SONOMA | 2021-05-07 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810958 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 4.1393e-06 | 3143.4478 | 0.013012
121380455 | F | LC | ETL.6320.POLE.WOOD | 40591727 | TABLEMTN | NORTH VALLEY | 2021-05-08 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40591727 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0023311 | 1539.3938
121381954 | F | LC | ETL.8250.POLE.WOOD | 40904158 | VICTOR | STOCKTON | 2021-05-11 | 2021-06-24 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40904158 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00049991 | 2471.0422
121388400 | E | LC | ETL.6220.POLE.WOOD | 40661815 | EUREKA | HUMBOLDT | 2021-05-24 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40661815 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.33751 | 419.5236 | 141.5924
121389697 | E | LC | ETL.7550.INSL.CERA | 40802387 | LAKEVLLE |  | 2021-05-15 | 2021-11-02 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40771413 |  | Single Wood Pole | SV-PJ - Single Vertical Post Jumper |  | Porcelain | [5 empty] | 6.1737e-06 | 854.2646
121391748 | E | LC | ETL.6760.POLE.WOOD | 40693553 | SACTO | SIERRA | 2021-05-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40693553 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.020183 | 205.7564 | 4.1528
121405388 | E | LC | ETL.7000.INSL.NCER | 44426922 | TABLEMTN |  | 2021-05-22 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44426921 | 2018-05-27 | Light Duty Steel Pole | T-1 - Tri Post | 2018-05-27 | Polymer | Post |  |  |  |  | 0.00051509 | 47.5141 | 0.024474
121420159 | F | LC | ETL.1401.POLE.STPS | 44161090 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1401 | BEARDSLEY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44161089 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.9365e-06 | 253.2337
121422860 | E | LC | ETL.6220.POLE.WOOD | 40698435 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40698435 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.065273 | 570.0973 | 37.2119
121430933 | F | LC | ETL.1402.POLE.STPS | 44915907 | VICTOR | YOSEMITE | 2021-05-25 | 2021-06-25 | ETL.1402 | SPRING GAP TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44915845 | 2019-11-18 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.2541e-05 | 174.1264
121435351 | B | LC | ETL.2141.INSL.NCER | 40802116 | MIDWAY | KERN | 2021-05-28 | 2021-07-06 | ETL.2141 | VEDDER TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771158 |  | Single Wood Pole | SV-PJ-90 - Single Vertical Post Jumper 90 |  | Polymer | [5 empty] | 0.0035244 | 6774.418
121466787 | B | LC | ETL.8365.POLE.WOOD | 40912640 | EUREKA | HUMBOLDT | 2021-06-03 | 2021-06-17 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912640 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.21507
121466787 | B | LC | ETL.8365.POLE.WOOD | 40912640 | EUREKA | HUMBOLDT | 2021-06-03 | 2021-06-17 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912640 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.21507
121467756 | E | LC | ETL.8365.POLE.WOOD | 40912513 | EUREKA | HUMBOLDT | 2021-06-03 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40912513 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.081425
121475565 | E | LC | ETL.1350.POLE.WDPS | 44512139 | TABLEMTN |  | 2021-05-28 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40821469 | 1943-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.040322 | 2995.4678 | 120.7842
121482113 | E | LC | ETL.1400.INSL.CERA | 44384862 | VICTOR | YOSEMITE | 2021-06-04 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44384821 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 0.0001363
121482113 | E | LC | ETL.1400.INSL.CERA | 44384862 | VICTOR | YOSEMITE | 2021-06-04 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44384821 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 0.0001363
121485787 | F | LC | ETL.4392.TOWR | 41129357 | LAKEVLLE | SONOMA | 2021-06-01 | 2021-09-30 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41129357 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 1.8675e-05 | 3897.7966
121485787 | F | LC | ETL.4392.TOWR | 41129357 | LAKEVLLE | SONOMA | 2021-06-01 | 2021-09-30 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41129357 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 1.8675e-05 | 3897.7966
121494819 | E | LC | ETL.2770.TOWR | 40609137 | CONCORD | EAST BAY | 2021-06-03 |  | ETL.2770 | MORAGA-SAN LEANDRO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40609137 | 1925-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Dead End |  |  |  |  | 1.1606e-05 | 0.065147 | 7.5609e-07
121494819 | E | LC | ETL.2770.TOWR | 40609137 | CONCORD | EAST BAY | 2021-06-03 |  | ETL.2770 | MORAGA-SAN LEANDRO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40609137 | 1925-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.1606e-05 | 0.065147 | 7.5609e-07
121496301 | E | LC | ETL.8060.INSL.CERA | 40801507 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40770670 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | [5 empty] | 0.072811 | 0.065152 | 0.0047438
121500301 | E | LC | ETL.8365.POLE.WOOD | 40587735 | EUREKA | HUMBOLDT | 2021-06-03 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40587735 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0034804
121513167 | B | LC | ETL.6880.INSL.CERA | 44286180 | LAKEVLLE |  | 2021-06-09 | 2021-07-08 | ETL.6880 | FULTON-CALISTOGA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40912488 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.005358 | 6398.8071
121514811 | F | LC | ETL.5100.TOWR | 40753008 | MOSSLNDG | SAN JOSE | 2021-06-03 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40753008 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2005-01-01 | Non Ceramic | Suspension |  |  |  |  | 9.1477e-05 | 490.5807 | 0.044877
121521775 | B | LC | ETL.5720.TOWR | 40810880 | CONCORD | MISSION | 2021-06-11 | 2021-07-12 | ETL.5720 | TESLA-NEWARK #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810880 | 1971-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-04-12 | Glass | Suspension |  |  |  |  | 1.7849e-09 | 6658.5884
121521775 | B | LC | ETL.5720.TOWR | 40810880 | CONCORD | MISSION | 2021-06-11 | 2021-07-12 | ETL.5720 | TESLA-NEWARK #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810880 | 1971-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 1.7849e-09 | 6658.5884
121522894 | E | LC | ETL.8170.POLE.WOOD | 40906462 | EUREKA | HUMBOLDT | 2021-06-11 |  | ETL.8170 | TRINITY-MAPLE CREEK | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40906462 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.24189 | 0.065152 | 0.01576
121526722 | E | LC | ETL.1350.POLE.WDPS | 44552254 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44551563 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.002136 | 0.066431 | 0.0001419
121526843 | F | LC | ETL.1820.POLE.WDPS | 44565436 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564219 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.21802 | 95.0515
121530919 | E | LC | ETL.1110.POLE.WDPS | 44424397 | TABLEMTN | HUMBOLDT | 2021-06-08 | 2021-07-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424396 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012557 | 5069.9922
121532893 | E | LC | ETL.6470.POLE.WOOD | 40760412 | SACTO | SIERRA | 2021-06-14 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40760412 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.034137 | 1408.1655 | 48.0705
121536578 | F | LC | ETL.6500.POLE.WOOD | 40664509 | SACTO | SIERRA | 2021-06-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40664509 |  | Single Wood Pole | T2N | 2018-06-29 | Polymer | Post |  |  |  |  | 0.00079978 | 96.5581
121542592 | E | LC | ETL.8290.INSL.NCER | 45078188 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.8290 | VOLTA-DESCHUTES | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45078159 | 2021-04-20 | Light Duty Steel Pole | T2N | 2021-04-20 | Polymer | Post |  |  |  |  | 0.0002783 | 609.2106 | 0.16954
121543112 | F | LC | ETL.1440.POLE.WOOD | 40814122 | SACTO | SIERRA | 2021-06-12 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40814122 | 1956-01-01 | Single Wood Pole | 3P DV - 3 Pole Double Vertical | 1956-01-01 | Ceramic | Dead End |  |  |  |  | 0.021336 | 1260.556 | 26.8949
121565161 | F | LC | ETL.1450.POLE.NWOD | 44965308 | SACTO | SIERRA | 2021-06-15 |  | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44965308 | 2020-08-28 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2020-08-28 | Glass | Dead End |  |  |  |  | 1.8633e-06 | 363.9416
121567908 | E | LC | ETL.2395.INSL.NCER | 40736774 | TABLEMTN | NORTH VALLEY | 2021-06-15 | 2021-09-15 | ETL.2395 | GRIZZLY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44550851 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.032409
121567908 | E | LC | ETL.2395.INSL.NCER | 40736774 | TABLEMTN | NORTH VALLEY | 2021-06-15 | 2021-09-15 | ETL.2395 | GRIZZLY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44550851 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.032409
121572821 | F | LC | ETL.5510.TOWR | 40586624 | CONCORD | DIABLO | 2021-06-16 | 2021-10-04 | ETL.5510 | PITTSBURG-TESLA #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586624 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 7.4019e-09 | 5019.1978
121578852 | E | LC | ETL.6720.POLE.WDPS | 44926546 | TABLEMTN | NORTH VALLEY | 2021-06-17 | 2021-09-02 | ETL.6720 | DESABLA-CENTERVILLE | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 42578821 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 6.5736e-05 | 949.264
121586857 | E | LC | ETL.1372.INSL.CERA | 42573715 | PISMOBCH | LOS PADRES | 2021-06-23 |  | ETL.1372 | MANVILLE TAP | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44283696 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 0.00081932
121586857 | E | LC | ETL.1372.INSL.CERA | 42573715 | PISMOBCH | LOS PADRES | 2021-06-23 |  | ETL.1372 | MANVILLE TAP | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44283696 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 0.00081932
121586857 | E | LC | ETL.1372.INSL.CERA | 42573715 | PISMOBCH | LOS PADRES | 2021-06-23 |  | ETL.1372 | MANVILLE TAP | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44283696 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 0.00081932
121606815 | F | LC | ETL.7550.POLE.WOOD | 40698025 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40698025 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 6.216e-05 | 110.7947 | 0.006887
121607941 | E | LC | ETL.2900.TOWR | 40680589 | MOSSLNDG | CENTRAL COAST | 2021-06-18 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40680589 | 1929-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1970-01-01 | Porcelain | Dead End |  |  |  |  | 0.0014915 | 555.1911
121609550 | F | LC | ETL.1070.POLE.WOOD | 40681772 | VICTOR | STOCKTON | 2021-06-22 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40681772 | 1998-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1998-01-01 | Polymer | Post |  |  |  |  | 1.114e-05 | 2504.1895 | 0.027897
121643657 | E | LC | ETL.1440.POLE.WDPS | 45096559 | SACTO | SACRAMENTO | 2021-06-25 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40603748 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.013989 | 3243.312 | 45.3699
121649398 | E | LC | ETL.1440.POLE.WOOD | 42572724 | SACTO | SIERRA | 2021-06-28 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42572724 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.045425 | 0.066431 | 0.0030176
121657914 | B | LC | ETL.1440.POLE.WOOD | 40597485 | SACTO | SACRAMENTO | 2021-07-02 | 2021-07-06 | ETL.1440 | DRUM-SUMMIT #1 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.022792 | 0.065152
121662796 | F | LC | ETL.5430.POLE.WDPS | 44561501 | TABLEMTN | NORTH VALLEY | 2021-07-01 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44560781 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0022472 | 665.1749
121662885 | E | LC | ETL.6910.POLE.WOOD | 40876011 | LAKEVLLE | SONOMA | 2021-07-01 |  | ETL.6910 | FULTON-MOLINO-COTATI | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40876011 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 5.0526e-05 | 317.1074 | 0.016022
121674269 | E | LC | ETL.1350.POLE.WDPS | 44513777 | TABLEMTN |  | 2021-07-07 | 2021-07-19 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44512267 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.030806 | 205.744
121677989 | E | LC | ETL.6020.TOWR | 40605579 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40605579 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.3177e-05 | 791.1504 | 0.010425
121685774 | F | LC | ETL.1400.POLE.NWOD | 44797077 | VICTOR | YOSEMITE | 2021-06-12 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44797077 | 2019-06-21 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2019-06-21 | Glass | Suspension |  |  |  |  | 0.00017622 | 63.3763
121692683 | F | LC | ETL.4393.POLE.NWOD | 44947391 | SACTO | SIERRA | 2021-06-12 |  | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44947391 | 2019-04-29 | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2019-04-29 | Glass | Dead End |  |  |  |  | 4.9745e-05 | 664.5352
121719769 | F | LC | ETL.6650.POLE.WDPS | 44561231 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44559155 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0020712 | 1426.2432
121725277 | E | LC | ETL.1820.INSL.CERA | 44560439 | EUREKA | HUMBOLDT | 2021-07-01 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44559957 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.024233 | 15.8866 | 0.38498
121731888 | E | LC | ETL.3780.INSL.NCER | 44396596 | CONCORD | EAST BAY | 2021-07-07 |  | ETL.3780 | SOBRANTE-R #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40804942 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-08-29 | Glass | Double Dead End |  |  |  |  | 2.1438e-05 | 443.3865 | 0.0095053
121734348 | E | LC | ETL.4040.POLE.WDPS | 44557563 | TABLEMTN | NORTH VALLEY | 2021-03-19 | 2021-11-18 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [12 empty] | 2441.9417
121780169 | E | LC | ETL.7060.POLE.WDPS | 45099512 | METCALF | PENINSULA | 2021-07-14 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42564720 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 2.4935e-05 | 728.5342 | 0.018166
121781810 | E | LC | ETL.2390.POLE.WDPS | 44391048 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391046 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.001057 | 3292.7512 | 3.4803
121783047 | E | LC | ETL.9240.TOWR | 43249510 | PISMOBCH | LOS PADRES | 2021-07-22 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249510 |  | LATTICE STEEL TOWER | [9 empty] | 2470.1736
121788074 | B | LC | ETL.6280.POLE.WOOD | 40659831 | TABLEMTN | NORTH VALLEY | 2021-07-23 |  | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 |  |  | PEND | [11 empty] | 1.8713e-05 | 680.1661 | 0.012728
121788083 | B | LC | ETL.6280.POLE.WOOD | 40593020 | TABLEMTN | NORTH VALLEY | 2021-07-23 |  | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 |  |  | PEND | [11 empty] | 1.605e-07 | 711.7988 | 0.00011424
121794802 | E | LC | ETL.6130.TOWR | 40753765 | VICTOR | STOCKTON | 2021-07-26 |  | ETL.6130 | TRACY-LOS BANOS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40753765 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Glass | Suspension |  |  |  |  | 1.436e-09 | 751.3264 | 1.0789e-06
121806255 | B | LC | ETL.8365.POLE.WOOD | 40861085 | EUREKA | HUMBOLDT | 2021-07-26 | 2021-08-19 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861085 | 2010-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0026206 | 587.0327
121812377 | E | LC | ETL.6020.TOWR | 41162772 | TABLEMTN | NORTH VALLEY | 2021-07-27 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41162772 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | [7 empty] | 0.00086126 | 427.2444 | 0.36797
121816468 | E | LC | ETL.8365.INSL.CERA | 40922517 | EUREKA | HUMBOLDT | 2021-07-27 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40912708 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.016678 | 2151.1467 | 35.8769
121830538 | B | LC | ETL.6280.POLE.WOOD | 40591748 | TABLEMTN | NORTH VALLEY | 2021-08-01 | 2021-10-06 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40591748 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 6.0205e-06 | 1739.9091
121860188 | B | LC | ETL.6300.POLE.WDPS | 44976218 | TABLEMTN | NORTH VALLEY | 2021-08-07 | 2021-09-14 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 63.3304
121946522 | F | LC | ETL.9100.POLE.WOOD | 44191890 | PISMOBCH | LOS PADRES | 2021-08-24 | 2021-08-31 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.00020437 | 2704.2016
121947055 | B | LC | ETL.6650.POLE.WDPS | 44386784 | TABLEMTN | NORTH VALLEY | 2021-08-14 | 2021-11-16 | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | Rotten | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44386783 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0091541 | 269.1427 | 2.4638
121974215 | B | LC | ETL.6220.POLE.NWOD | 45019166 | EUREKA | HUMBOLDT | 2021-08-30 | 2021-09-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45019166 | 2020-08-23 | Light Duty Steel Pole | T2N | 2020-08-23 | Polymer | Post |  |  |  |  | 0.018113 | 332.2581
122019302 | F | LC | ETL.4440.POLE.NWOD | 40816409 | TABLEMTN | NORTH VALLEY | 2021-09-03 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40816409 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle | 1968-01-01 | Porcelain | Dead End |  |  |  |  | 4.6465e-05 | 1804.4395
118537816 | E | LC | ETL.1110.POLE.WDPS | 44512064 | EUREKA | HUMBOLDT | 2020-02-14 | 2021-07-12 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118575990 | E | LC | ETL.5930.INSL.NCER | 44768968 | CONCORD |  | 2020-02-25 | 2021-03-10 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862755 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-26 | Glass Silicone Coated | Suspension |  |  |  |  | 1.3065e-08 | 556.4825
118575990 | E | LC | ETL.5930.INSL.NCER | 44768968 | CONCORD |  | 2020-02-25 | 2021-03-10 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862755 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.3065e-08 | 556.4825
118781829 | F | LC | ETL.8210.POLE.WOOD | 40905507 | VICTOR | STOCKTON | 2020-04-06 | 2020-04-08 | ETL.8210 | VALLEY SPRINGS #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL | [12 empty] | 950.9167
118909625 | F | LC | ETL.4441.POLE.NWOD | 43198032 | TABLEMTN | NORTH VALLEY | 2020-04-10 | 2021-04-26 | ETL.4441 | BELDEN TAP | Structure-Tower | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
118937891 | E | LC | ETL.6220.POLE.WOOD | 40810335 | EUREKA | HUMBOLDT | 2020-04-21 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40810335 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.21462 | 1028.302 | 220.6988
118949767 | E | LC | ETL.4392.TOWR | 41129316 | LAKEVLLE | SONOMA | 2020-04-26 | 2021-03-23 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129316 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.0022368 | 2615.8572
118949767 | E | LC | ETL.4392.TOWR | 41129316 | LAKEVLLE | SONOMA | 2020-04-26 | 2021-03-23 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129316 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.0022368 | 2615.8572
118964371 | B | LC | ETL.1650.POLE.NWOD | 44398442 | LAKEVLLE | SONOMA | 2020-04-24 | 2020-06-16 | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44398442 | 2018-08-23 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2018-08-22 | Polymer | Suspension |  |  |  |  | 4.2447e-09 | 4970.959
118966639 | E | LC | ETL.7590.POLE.WOOD | 41124293 | MOSSLNDG | CENTRAL COAST | 2020-05-01 | 2020-12-16 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118971996 | F | LC | ETL.4392.TOWR | 41129313 | LAKEVLLE | SONOMA | 2020-04-30 | 2021-07-19 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41129313 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.0062586 | 2758.967
118971996 | F | LC | ETL.4392.TOWR | 41129313 | LAKEVLLE | SONOMA | 2020-04-30 | 2021-07-19 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41129313 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.0062586 | 2758.967
118975986 | E | LC | ETL.6980.POLE.WOOD | 40661457 | LAKEVLLE | SONOMA | 2020-04-24 | 2021-03-12 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40661457 | 1953-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1953-01-01 | Polymer | Suspension |  |  |  |  | 0.63364 | 47.5317
119013685 | F | LC | ETL.4680.TOWR | 40592327 | LAKEVLLE | SONOMA | 2020-05-06 | 2021-03-02 | ETL.4680 | FULTON-IGNACIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40592327 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Ceramic | Suspension |  |  |  |  | 4.2814e-07 | 1790.5603
119017476 | E | LC | ETL.8650.INSL.CERA | 40847984 | FRESNO | FRESNO | 2020-05-01 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44420159 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0031915 | 1249.5254
119027099 | F | LC | ETL.7510.POLE.WDPS | 44218388 | LAKEVLLE |  | 2020-05-11 | 2020-07-08 | ETL.7510 | MENDOCINO-HARTLEY | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 44218387 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00015326 | 4355.1782
119027630 | F | LC | ETL.1420.POLE.STPS | 44415581 | SACTO | SACRAMENTO | 2020-05-11 | 2021-10-19 | ETL.1420 | DRUM-RIO OSO #1 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Tier 3 | Within Both | DLFL | 44415579 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.9931e-06 | 142.4516
119070232 | E | LC | ETL.8405.POLE.WOOD | 42569707 | SACTO | SIERRA | 2020-05-11 | 2021-10-14 | ETL.8405 | MIDDLE FORK #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42569707 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.21518 | 585.5076
119078535 | E | LC | ETL.7510.POLE.WOOD | 40862974 | LAKEVLLE | HUMBOLDT | 2020-05-26 | 2020-07-03 | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862974 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 3.1384e-05 | 1327.7733
119083602 | E | LC | ETL.6760.INSL.CERA | 40853610 | SACTO | SACRAMENTO | 2020-05-27 | 2021-03-18 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119096489 | E | LC | ETL.1430.INSL | 40578817 | SACTO | SACRAMENTO | 2020-05-19 | 2021-03-30 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119096826 | F | LC | ETL.1650.POLE.WOOD | 40657192 | LAKEVLLE | SONOMA | 2020-05-27 | 2021-02-14 | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40657192 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 0.00023871 | 4151.2271
119111374 | E | LC | ETL.2540.POLE.WDPS | 44401550 | MOSSLNDG | CENTRAL COAST | 2020-05-20 | 2021-01-27 | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44401549 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.002431 | 474.5354
119114756 | F | LC | ETL.5290.TOWR | 40662879 | PISMOBCH | LOS PADRES | 2020-05-26 | 2021-05-19 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662879 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2016-01-26 | Ceramic | Other |  |  |  |  | 2.9094e-08 | 1885.8511
119116953 | E | LC | ETL.4316.POLE.NWOD | 44712215 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-06-14 | ETL.4316 | PARADISE-TABLE MTN | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44712215 |  | Light Duty Steel Pole | T-1 - Tri Post | 2019-02-13 | Polymer | Post |  |  |  |  | 0.0021133 | 1125.879
119118018 | E | LC | ETL.5140.TOWR | 40820687 | SACTO | SIERRA | 2020-06-01 | 2021-11-17 | ETL.5140 | MIDDLE FORK-GOLD HILL | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40820687 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Dead End |  |  |  |  | 3.6598e-09 | 6807.7681 | 2.4915e-05
119118522 | E | LC | ETL.6330.POLE.WOOD | 40610776 | TABLEMTN | NORTH VALLEY | 2020-06-02 | 2021-03-12 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Insulator Bond Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40610776 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00202 | 4985.4875
119119140 | E | LC | ETL.6950.POLE.WOOD | 40666255 | SACTO | SIERRA | 2020-06-02 | 2021-08-05 | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40666255 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0013334 | 1224.7897
119119330 | E | LC | ETL.8170.POLE.WOOD | 40906467 | EUREKA | HUMBOLDT | 2020-06-03 | 2021-09-01 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906467 |  | Single Wood Pole | 3P DDE - 3 Pole Double Dead End |  | Ceramic | [5 empty] | 0.044429 | 31.7081
119119903 | E | LC | ETL.7270.POLE.WOOD | 40771192 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-08-25 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | DLFL | 40771192 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.058807 | 3233.4868
119128391 | F | LC | ETL.7780.POLE.WOOD | 40876332 | LAKEVLLE | SONOMA | 2020-06-09 | 2020-11-10 | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40876332 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Ceramic | [5 empty] | 0.00024451 | 79.143
119132596 | E | LC | ETL.5463.INSL | 40724040 | CONCORD | EAST BAY | 2020-06-04 | 2021-06-09 | ETL.5463 | PITTSBURG-SAN MATEO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119146305 | F | LC | ETL.6220.POLE.WOOD | 40591948 | EUREKA | HUMBOLDT | 2020-06-02 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40591948 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.0027322 | 253.1893
119150441 | F | LC | ETL.6490.POLE.NWOD | 44642271 | SACTO | SIERRA | 2020-06-03 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44642271 | 2018-08-19 | Light Duty Steel Pole | T-1 - Tri Post | 2018-08-19 | Polymer | Post |  |  |  |  | 0.0025033 | 2175.1291
119163229 | F | LC | ETL.1350.POLE.NWOD | 44993096 | TABLEMTN | NORTH VALLEY | 2020-06-13 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 44993096 | 2020-06-04 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-04 | Glass | Dead End |  |  |  |  | 0.00035248 | 15.8866 | 0.0055998
119166705 | B | LC | ETL.6750.INSL | 41115165 | TABLEMTN |  | 2020-06-08 | 2020-06-16 | ETL.6750 | DELTA-MTN GATE JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40650383 | 1944-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0094278 | 0.066431
119179256 | F | LC | ETL.7300.POLE.WOOD | 40827912 | TABLEMTN |  | 2020-06-16 | 2021-07-07 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827912 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00022295 | 5356.6348
119183865 | E | LC | ETL.4223.POLE.WDPS | 44313778 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2020-08-17 | ETL.4223 | KANAKA TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119184798 | F | LC | ETL.6280.POLE.NWOD | 45115727 | TABLEMTN | NORTH VALLEY | 2020-06-16 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45115727 | 2020-03-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-03-03 | Polymer | Dead End | [5 empty] | 6187.9214
119195271 | F | LC | ETL.6470.POLE.WOOD | 40767227 | SACTO | SIERRA | 2020-06-19 | 2021-06-08 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40767227 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.088003 | 221.5931
119201082 | E | LC | ETL.9340.POLE.WOOD | 44267617 | FRESNO | FRESNO | 2020-06-23 | 2020-09-09 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44267617 | 2016-02-11 | Light Duty Steel Pole | TPA - Tri Pin Arm | 2016-02-11 | Polymer | Dead End |  |  |  |  | 0.00021072 | 5192.4033
119210790 | E | LC | ETL.6070.TOWR | 40595194 | TABLEMTN | NORTH VALLEY | 2020-06-25 | 2021-05-28 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40595194 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.5734e-07 | 1776.1339
119230569 | E | LC | ETL.7270.POLE.NWOD | 44649258 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2021-11-08 | ETL.7270 | KESWICK-TRINITY | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44649258 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.0011808 | 79.1977 | 0.093513
119231136 | F | LC | ETL.4050.POLE.WOOD | 40761341 | LAKEVLLE | SONOMA | 2020-06-29 | 2021-02-16 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40761341 | 1990-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1970-01-01 | Ceramic | Post |  |  |  |  | 1.9402e-05 | 2628.4556
119235118 | E | LC | ETL.8060.POLE.WOOD | 40577368 | SACTO | SIERRA | 2020-06-29 | 2020-11-12 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [11 empty] | 0.073196 | 31.7066
119289794 | F | LC | ETL.6690.POLE.WOOD | 40866660 | SACTO | SACRAMENTO | 2020-06-30 | 2021-07-15 | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40866660 |  | Single Wood Pole | T2N | 2021-07-09 | Polymer | Post |  |  |  |  | 0.037867 | 82.3455
119312606 | F | LC | ETL.8180.POLE.WOOD | 40602363 | LAKEVLLE | NORTH BAY | 2020-07-01 |  | ETL.8180 | TULUCAY-NAPA #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40602363 |  | Single Wood Pole | WB - Wishbone |  | Porcelain | [5 empty] | 0.014417 | 5746.8428
119329296 | E | LC | ETL.1110.POLE.STPS | 44424630 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-04-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Anchor-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424629 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 9.452e-06 | 3453.0132
119335092 | F | LC | ETL.7030.POLE.WOOD | 40668036 | TABLEMTN | NORTH VALLEY | 2020-07-08 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40668036 |  | Single Wood Pole | T2N | 2015-02-10 | Polymer | Post |  |  |  |  | 0.00023489 | 619.0493
119338502 | F | LC | ETL.1440.POLE.WOOD | 40597045 | SACTO | SIERRA | 2020-07-08 | 2021-06-24 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119339285 | E | LC | ETL.5980.TOWR | 40820151 | PISMOBCH | LOS PADRES | 2020-07-09 | 2020-11-12 | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40820151 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-10-13 | Glass | Suspension |  |  |  |  | 8.1366e-10 | 1552.8336
119340808 | E | LC | ETL.5934.TOWR | 40647367 | PISMOBCH | LOS PADRES | 2020-07-09 | 2021-03-02 | ETL.5934 | TEMPLETON-GATES | Vegetation | Overgrown | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40647367 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00025376 | 4115.4043
119341090 | F | LC | ETL.7030.POLE.WOOD | 40676366 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40676366 |  | Single Wood Pole | T2N | 2018-12-02 | Polymer | Post |  |  |  |  | 0.014808 | 698.4329
119341759 | B | LC | ETL.6280.POLE.WOOD | 40826371 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2020-10-27 | ETL.6280 | CARIBOU #2 | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826371 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 3.0662e-05 | 490.3705
119357056 | F | LC | ETL.7030.POLE.WOOD | 40827491 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40827491 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.011289 | 808.4792
119357444 | F | LC | ETL.6280.POLE.WOOD | 40668314 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40668314 |  | Single Wood Pole | T2N | 2018-11-24 | Polymer | Post |  |  |  |  | 2.4837e-05 | 5520.0938
119357985 | E | LC | ETL.1450.POLE.STPS | 44989178 | SACTO | SIERRA | 2020-07-10 | 2020-11-12 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [12 empty] | 253.1966
119360150 | F | LC | ETL.1350.POLE.STPS | 44996564 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44996546 | 2020-06-15 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.8841e-05 | 318.0763
119379151 | E | LC | ETL.8405.POLE.WOOD | 40809620 | SACTO | SACRAMENTO | 2020-07-15 | 2021-10-14 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.29867 | 142.4895 | 42.558
119381198 | E | LC | ETL.2060.POLE.WOOD | 40860673 | LAKEVLLE | SONOMA | 2020-07-16 |  | ETL.2060 | FORT BRAGG-ELK | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40860673 | 1961-01-01 | Single Wood Pole | SVDE - Single Vertical Dead End | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.31079 | 284.7454 | 88.4956
119469061 | E | LC | ETL.8410.POLE.NWOD | 44946529 | LAKEVLLE | HUMBOLDT | 2020-07-17 | 2021-03-02 | ETL.8410 | ELK-GUALALA | Guy Pole-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44946529 | 2020-07-07 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2020-07-07 | Glass | Suspension |  |  |  |  | 0.054812 | 219.9952
119469935 | E | LC | ETL.7030.POLE.WOOD | 40825620 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-06-30 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40825620 |  | Single Wood Pole | T2N | 2021-06-07 | Polymer | Post |  |  |  |  | 0.0047442
119470096 | F | LC | ETL.6290.POLE.NWOD | 44883383 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44883383 | 2020-02-03 | Light Duty Steel Pole | T2N | 2020-02-03 | Polymer | Post |  |  |  |  | 0.1643 | 63.4948
119481671 | F | LC | ETL.7030.POLE.WOOD | 40600137 | TABLEMTN | NORTH VALLEY | 2020-07-21 | 2021-02-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40600137 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 2018-12-04 | Polymer | Post |  |  |  |  | 0.05201 | 6221.1479
119484059 | F | LC | ETL.6280.POLE.WOOD | 40656539 | TABLEMTN | NORTH VALLEY | 2020-07-21 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40656539 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Pin |  |  |  |  | 0.00011361 | 1739.9091
119489214 | E | LC | ETL.4680.TOWR | 40651565 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-03-04 | ETL.4680 | FULTON-IGNACIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40651565 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 3.2458e-05 | 665.4853
119489214 | E | LC | ETL.4680.TOWR | 40651565 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-03-04 | ETL.4680 | FULTON-IGNACIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40651565 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.2458e-05 | 665.4853
119490874 | F | LC | ETL.6720.POLE.WOOD | 40649880 | TABLEMTN | NORTH VALLEY | 2020-07-22 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40649880 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 7.874e-05 | 0.065151
119535398 | F | LC | ETL.1470.POLE.WOOD | 41176318 | LAKEVLLE | HUMBOLDT | 2020-07-31 |  | ETL.1470 | EAGLE ROCK-CORTINA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41176318 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Porcelain | Post |  |  |  |  | 0.0057666 | 0.065149
119591231 | E | LC | ETL.7590.POLE.WOOD | 40694958 | MOSSLNDG | CENTRAL COAST | 2020-08-10 | 2021-01-12 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119599318 | E | LC | ETL.4392.INSL.CERA | 44387076 | LAKEVLLE |  | 2020-08-11 | 2021-08-04 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40814648 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-03-09 | Porcelain | Dead End |  |  |  |  | 1.7661e-07 | 5180.0576
119599318 | E | LC | ETL.4392.INSL.CERA | 44387076 | LAKEVLLE |  | 2020-08-11 | 2021-08-04 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40814648 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-05-12 | Porcelain | Dead End |  |  |  |  | 1.7661e-07 | 5180.0576
119609631 | F | LC | ETL.5934.TOWR | 40858101 | FRESNO | FRESNO | 2020-08-12 | 2021-04-07 | ETL.5934 | TEMPLETON-GATES | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40858101 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00015184
119618877 | F | LC | ETL.2700.TOWR | 40644180 | CONCORD | DIABLO | 2020-08-14 | 2020-11-02 | ETL.2700 | MORAGA-CLAREMONT #1 | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40644180 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | [5 empty] | 1.0376e-07 | 593.9911
119619235 | A | LC | ETL.4040.INSL.NCER | 44784194 | TABLEMTN | NORTH VALLEY | 2020-08-14 | 2020-08-21 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44554053 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 2019-07-14 | Glass | Suspension |  |  |  |  | 0.013498
119619235 | A | LC | ETL.4040.INSL.NCER | 44784194 | TABLEMTN | NORTH VALLEY | 2020-08-14 | 2020-08-21 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44554053 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 2019-07-14 | Glass | Suspension |  |  |  |  | 0.013498
119632737 | F | LC | ETL.9200.POLE.WOOD | 40749618 | MIDWAY | KERN | 2020-08-18 |  | ETL.9200 | TAFT-CUYAMA #1 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40749618 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Ceramic | Pin |  |  |  |  | 0.0025621
119658048 | E | LC | ETL.1420.INSL.CERA | 40786130 | SACTO | SACRAMENTO | 2020-08-22 | 2021-02-25 | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119679369 | B | LC | ETL.1440.INSL | 40786933 | SACTO | SIERRA | 2020-08-25 | 2021-06-23 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119692396 | A | LC | ETL.7590.POLE.WOOD | 40805890 | MOSSLNDG | CENTRAL COAST | 2020-08-30 | 2020-09-19 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119693009 | E | LC | ETL.1440.POLE.WDPS | 44837677 | SACTO | SACRAMENTO | 2020-08-25 | 2021-05-23 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40819191 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.011379 | 31.7066
119707318 | E | LC | ETL.6290.POLE.WOOD | 40591663 | TABLEMTN | NORTH VALLEY | 2020-08-31 | 2021-11-16 | ETL.6290 | CARIBOU-PLUMAS JCT | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591663 | 1962-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.34785 | 1376.0835
119723696 | F | LC | ETL.6440.POLE.WOOD | 40576699 | TABLEMTN | NORTH VALLEY | 2020-08-04 |  | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40576699 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 0.0045207 | 4284.2378
119765503 | E | LC | ETL.6470.POLE.WOOD | 40760719 | SACTO | SIERRA | 2020-09-08 | 2021-08-23 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [12 empty] | 544.4154
119766821 | E | LC | ETL.4221.POLE.WOOD | 42564535 | TABLEMTN | NORTH VALLEY | 2020-09-09 | 2021-04-19 | ETL.4221 | SLY CREEK TAP | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42564535 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2019-05-21 | Glass | Suspension |  |  |  |  | 0.00040476 | 94.963
119771719 | E | LC | ETL.7820.POLE.WOOD | 40750475 | LAKEVLLE | HUMBOLDT | 2020-08-20 | 2021-03-11 | ETL.7820 | POTTER VALLEY-WILLITS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750475 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 5.583e-05 | 917.5893
119775552 | F | LC | ETL.6760.POLE.WOOD | 40822684 | SACTO | SIERRA | 2020-09-09 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
119778810 | E | LC | ETL.1110.POLE.WDPS | 44423306 | TABLEMTN | HUMBOLDT | 2020-09-08 | 2021-04-13 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423305 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0010383 | 3499.2989
119788828 | E | LC | ETL.6470.POLE.WOOD | 40590441 | SACTO | SIERRA | 2020-09-17 | 2021-07-20 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.070269 | 139.314
119790598 | B | LC | ETL.8365.POLE.WOOD | 40906654 | EUREKA | HUMBOLDT | 2020-09-17 | 2020-11-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906654 |  | Single Wood Pole | T2N | 2021-04-25 | Polymer | Post |  |  |  |  | 0.018253
119812526 | F | LC | ETL.8170.POLE.WOOD | 44947094 | EUREKA | HUMBOLDT | 2020-09-17 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | DLFL
119816329 | F | LC | ETL.1650.POLE.STPS | 44298400 | LAKEVLLE |  | 2020-08-29 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44298398 |  | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 1.7146e-08 | 3278.8411
119819841 | E | LC | ETL.8580.TOWR | 40597827 | FRESNO | FRESNO | 2020-09-25 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40597827 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Glass | [5 empty] | 1.3537e-05
119897309 | F | LC | ETL.6810.POLE.WOOD | 40585287 | EUREKA | HUMBOLDT | 2020-10-08 | 2021-08-27 | ETL.6810 | ESSEX JCT-ORICK | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Zone 1 | HFRA Removal | DLFL | 40585287 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.015714
119907622 | E | LC | ETL.6720.POLE.NWOD | 44324208 | TABLEMTN | NORTH VALLEY | 2020-10-07 | 2021-02-22 | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44324208 | 2015-11-03 | Fiberglass | TPD - Tri Post Dead End Construction | 2015-11-03 | Ceramic | Suspension |  |  |  |  | 0.00055987 | 63.3704
119916364 | E | LC | ETL.8170.POLE.WOOD | 40810494 | EUREKA | HUMBOLDT | 2020-10-16 | 2021-06-08 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810494 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2020-06-23 | Glass | Dead End |  |  |  |  | 0.0068724 | 2360.6118
119995946 | F | LC | ETL.6880.POLE.WOOD | 40905738 | LAKEVLLE | HUMBOLDT | 2020-10-06 | 2021-04-15 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
120126760 | F | LC | ETL.3800.TOWR | 40580996 | CONCORD | EAST BAY | 2020-10-09 |  | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40580996 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-16 | Polymer | Suspension |  |  |  |  | 1.2356e-07 | 0.090453 | 1.1176e-08
120126760 | F | LC | ETL.3800.TOWR | 40580996 | CONCORD | EAST BAY | 2020-10-09 |  | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40580996 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 1.2356e-07 | 0.090453 | 1.1176e-08
120127962 | F | LC | ETL.1110.POLE.STPS | 44891842 | TABLEMTN | NORTH VALLEY | 2020-10-09 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44891788 | 2019-09-16 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.5887e-06 | 4229.4111
120136420 | F | LC | ETL.7590.POLE.STPS | 44945893 | MOSSLNDG | DE ANZA | 2020-12-01 | 2021-08-03 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | DLFL | 44935264 | 2020-07-20 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [8 empty] | 522.1984
120150288 | F | LC | ETL.6280.POLE.NWOD | 45121216 | TABLEMTN | NORTH VALLEY | 2020-11-04 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45121216 | 2020-02-20 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-02-20 | Polymer | Dead End | [5 empty] | 5602.6106
120161862 | F | LC | ETL.6280.POLE.WOOD | 40675435 | TABLEMTN | NORTH VALLEY | 2020-11-04 | 2021-02-10 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40675435 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 5.0586e-06 | 15.8815
120210244 | F | LC | ETL.4040.POLE.NWOD | 44874426 | TABLEMTN | NORTH VALLEY | 2020-11-06 | 2021-11-18 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44874426 | 2020-01-18 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2020-01-18 | Polymer | Dead End |  |  |  |  | 6.4224e-05 | 253.2084
120229566 | F | LC | ETL.6280.POLE.NWOD | 40768761 | TABLEMTN | NORTH VALLEY | 2020-11-20 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40768761 |  | Light Duty Steel Pole | TP - Tri Pin |  | Non Ceramic | Pin |  |  |  |  | 4.4859e-06 | 0.065148
120230032 | B | LC | ETL.7780.INSL | 40637121 | LAKEVLLE | HUMBOLDT | 2020-12-22 | 2021-02-04 | ETL.7780 | PHILO JCT-ELK | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40605869 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 3.2468e-05 | 158.2502
120232458 | F | LC | ETL.5440.POLE.NWOD | 44931480 | TABLEMTN | NORTH VALLEY | 2020-11-30 |  | ETL.5440 | PIT #6 JCT-ROUND MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44931480 | 2020-05-20 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2020-05-20 | Glass | Dead End |  |  |  |  | 0.00015723 | 952.427
120236689 | F | LC | ETL.3020.TOWR | 40580877 | CONCORD | MISSION | 2020-11-25 | 2021-03-16 | ETL.3020 | NEWARK-JARVIS #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40580877 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.6871e-07
120236689 | F | LC | ETL.3020.TOWR | 40580877 | CONCORD | MISSION | 2020-11-25 | 2021-03-16 | ETL.3020 | NEWARK-JARVIS #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40580877 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-11-03 | Ceramic | Dead End |  |  |  |  | 1.6871e-07
120255829 | E | LC | ETL.7590.POLE.WOOD | 40612273 | MOSSLNDG | CENTRAL COAST | 2021-01-04 |  | ETL.7590 | MONTA VISTA-BURNS | Switch-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40612273 |  | Light Duty Steel Pole | FSS - Field Switch Structure | [7 empty] | 0.18334 | 63.351 | 11.6148
120663949 | E | LC | ETL.7630.POLE.WOOD | 40825469 | LAKEVLLE | SONOMA | 2021-03-17 | 2021-06-25 | ETL.7630 | MONTE RIO-FULTON | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40825469 | 1952-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2021-06-23 | Glass | Suspension |  |  |  |  | 0.020803 | 15.8851
120673281 | F | LC | ETL.4920.TOWR | 40871695 | LAKEVLLE | SONOMA | 2021-03-22 |  | ETL.4920 | IGNACIO-SOBRANTE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40871695 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 7.4398e-05 | 1427.1888 | 0.10618
120677271 | E | LC | ETL.3700.POLE.WOOD | 40760205 | PISMOBCH | LOS PADRES | 2021-03-22 | 2021-11-22 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760205 | 1989-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1989-01-01 | Porcelain | Suspension |  |  |  |  | 0.0015336 | 5447.0627 | 8.3535
120679216 | E | LC | ETL.4920.INSL.CERA | 40618891 | LAKEVLLE | EAST BAY | 2021-03-23 |  | ETL.4920 | IGNACIO-SOBRANTE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40593169 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.0063267 | 16.3243 | 0.10328
120683877 | E | LC | ETL.4316.POLE.STPS | 44674931 | TABLEMTN | NORTH VALLEY | 2021-03-24 | 2021-08-13 | ETL.4316 | PARADISE-TABLE MTN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44674853 | 2018-11-17 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00022684 | 2757.4497
120685129 | F | LC | ETL.6720.POLE.WDPS | 44949076 | TABLEMTN | NORTH VALLEY | 2021-03-24 | 2021-06-11 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 42578833 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0004205 | 2104.1226
120695871 | F | LC | ETL.5390.TOWR | 40651397 | TABLEMTN | NORTH VALLEY | 2021-03-26 |  | ETL.5390 | PIT #1-COTTONWOOD | Guy Wire Mark /Indic-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40651397 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 4.1413e-08 | 4183.5889
120696851 | E | LC | ETL.6760.POLE.WOOD | 40756940 | SACTO | SACRAMENTO | 2021-03-26 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40756940 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0025497 | 854.4165 | 2.1785
120706524 | A | LC | ETL.6880.POLE.NWOD | 40828833 | LAKEVLLE | SONOMA | 2021-03-29 | 2021-04-05 | ETL.6880 | FULTON-CALISTOGA | Emergency | Storm Related | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40828833 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 1.1107e-07 | 332.3002
120711526 | B | LC | ETL.1890.INSL.CERA | 43599507 | FRESNO | FRESNO | 2021-03-29 | 2021-05-03 | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40584879 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1986-01-01 | Ceramic | Dead End |  |  |  |  | 5.055e-05 | 5461.6226
120711526 | B | LC | ETL.1890.INSL.CERA | 43599507 | FRESNO | FRESNO | 2021-03-29 | 2021-05-03 | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40584879 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1986-01-01 | Porcelain | Dead End |  |  |  |  | 5.055e-05 | 5461.6226
120719426 | E | LC | ETL.7390.POLE.WOOD | 40860893 | LAKEVLLE | SONOMA | 2021-03-31 | 2021-06-25 | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860893 |  | Single Wood Pole | T2N | 2021-06-22 | Polymer | Post |  |  |  |  | 0.013557 | 696.1808
120736276 | E | LC | ETL.1720.POLE.WDPS | 44401004 | MOSSLNDG | CENTRAL COAST | 2021-04-01 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44401003 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00012692 | 31.7081 | 0.0040242
120737748 | E | LC | ETL.1820.POLE.WDPS | 44560096 | EUREKA | HUMBOLDT | 2021-04-02 | 2021-04-06 | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
120749329 | E | LC | ETL.1530.TOWR | 40804971 | SACTO | SIERRA | 2021-03-25 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40804971 | 1980-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1980-01-01 | Ceramic | Dead End |  |  |  |  | 2.196e-06 | 0.06515 | 1.4307e-07
120755672 | F | LC | ETL.1530.TOWR | 40810219 | SACTO | SIERRA | 2021-03-25 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810219 | 1980-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 2.0886e-06 | 0.066432 | 1.3875e-07
120759252 | E | LC | ETL.7590.POLE.WOOD | 44209069 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44209069 | 2014-06-26 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2014-06-26 | Polymer | Dead End |  |  |  |  | 0.0297 | 31.7081 | 0.94173
120761776 | E | LC | ETL.7140.POLE.WOOD | 41111791 | LAKEVLLE | SONOMA | 2021-04-07 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41111791 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.090128 | 4560.6943 | 411.0465
120763175 | E | LC | ETL.1810.POLE.WDPS | 44322362 | EUREKA | HUMBOLDT | 2021-04-08 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44322360 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0048898
120769032 | B | LC | ETL.3190.TOWR | 40910319 | TABLEMTN | NORTH VALLEY | 2021-04-08 | 2021-06-24 | ETL.3190 | CARIBOU-PALERMO | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910319 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.030544 | 3875.0593
120770668 | B | LC | ETL.7140.INSL.NCER | 41111800 | LAKEVLLE | NORTH BAY | 2021-04-08 | 2021-07-06 | ETL.7140 | IGNACIO-BOLINAS #1 | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111799 |  | 3-Pole Wood | DV-DE - Double Vertical Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.0093056
120770668 | B | LC | ETL.7140.INSL.NCER | 41111800 | LAKEVLLE | NORTH BAY | 2021-04-08 | 2021-07-06 | ETL.7140 | IGNACIO-BOLINAS #1 | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111799 |  | 3-Pole Wood | DV-DE - Double Vertical Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.0093056
120770668 | B | LC | ETL.7140.INSL.NCER | 41111800 | LAKEVLLE | NORTH BAY | 2021-04-08 | 2021-07-06 | ETL.7140 | IGNACIO-BOLINAS #1 | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111799 |  | 3-Pole Wood | DV-DE - Double Vertical Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.0093056
120771281 | E | LC | ETL.8250.POLE.WOOD | 40812116 | VICTOR | STOCKTON | 2021-04-09 | 2021-04-13 | ETL.8250 | CLAY-MARTEL | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40812116 | 1957-01-01 | Single Wood Pole | SV-DE-90 - Single Vertical Dead End 90 |  | Porcelain | [5 empty] | 8.8823e-05 | 1665.905
120794416 | E | LC | ETL.1430.INSL.CERA | 40786150 | SACTO | SACRAMENTO | 2021-04-12 | 2021-10-04 | ETL.1430 | DRUM-RIO OSO #2 | Splice-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756312 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.00037906 | 4956.6104 | 1.8788
120797733 | E | LC | ETL.2720.INSL | 40851155 | CONCORD | DIABLO | 2021-04-07 |  | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40822215 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 0.00016476 | 0.065158 | 1.0735e-05
120801942 | F | LC | ETL.5540.TOWR | 40757647 | TABLEMTN | NORTH VALLEY | 2021-04-06 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40757647 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 2.8021e-07 | 4102.1982 | 0.0011495
120813230 | E | LC | ETL.5300.INSL | 40714491 | PISMOBCH | LOS PADRES | 2021-04-14 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40663372 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 6.2926e-06 | 652.484 | 0.0041058
120814922 | B | LC | ETL.8365.INSL.NCER | 40733602 | EUREKA | HUMBOLDT | 2021-04-14 | 2021-06-17 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40698315 | 2016-06-11 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End | 2016-06-11 | Polymer | Post |  |  |  |  | 0.00052655
120819697 | F | LC | ETL.6690.POLE.NWOD | 44919745 | SACTO | SACRAMENTO | 2021-04-15 |  | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44919745 | 2019-06-28 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-06-28 | Glass | Dead End |  |  |  |  | 0.010089 | 120.3152
120819718 | E | LC | ETL.5390.TOWR | 40821475 | TABLEMTN | NORTH VALLEY | 2021-04-15 |  | ETL.5390 | PIT #1-COTTONWOOD | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40821475 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.1257e-06 | 1966.7024 | 0.0041806
120827138 | E | LC | ETL.9250.POLE.WOOD | 40749372 | MIDWAY | KERN | 2021-04-16 | 2021-09-09 | ETL.9250 | TEJON-LEBEC | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40749372 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.034846 | 4279.1353
120827544 | E | LC | ETL.6470.POLE.WOOD | 40693481 | SACTO | SACRAMENTO | 2021-04-16 | 2021-08-17 | ETL.6470 | COLGATE-ALLEGHANY | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40693481 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0087958 | 5778.439
120831864 | B | LC | ETL.5540.INSL.CERA | 40616288 | TABLEMTN | NORTH VALLEY | 2021-04-15 | 2021-06-22 | ETL.5540 | POE-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
120849998 | E | LC | ETL.8423.POLE.NWOD | 40614058 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.8423 | SALINAS-FORT ORD #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40614058 |  | Lattice Steel Pole | DCPOST - Double Circuit Post |  | Porcelain | [5 empty] | 8.0509e-06 | 583.6659 | 0.004699
120851579 | E | LC | ETL.8060.POLE.WOOD | 40862184 | SACTO | SACRAMENTO | 2021-04-20 | 2021-09-14 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862184 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Polymer | [5 empty] | 0.30024 | 1123.6396
120873183 | B | LC | ETL.4880.INSL | 40898653 | FRESNO | FRESNO | 2021-04-20 | 2021-06-17 | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873017 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.0417e-06 | 6774.1143
120878647 | E | LC | ETL.3730.INSL.CERA | 40705242 | CONCORD | DIABLO | 2021-04-24 |  | ETL.3730 | SOBRANTE-G #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | HFRA Removal | PEND | 44359228 |  | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 2.164e-06 | 0.065147 | 1.4098e-07
120889592 | E | LC | ETL.3960.TOWR | 40662698 | PISMOBCH | LOS PADRES | 2021-04-27 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40662698 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 6.2296e-09 | 2883.6785 | 1.7964e-05
120889592 | E | LC | ETL.3960.TOWR | 40662698 | PISMOBCH | LOS PADRES | 2021-04-27 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40662698 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 6.2296e-09 | 2883.6785 | 1.7964e-05
120895159 | E | LC | ETL.6470.POLE.WOOD | 40824369 | SACTO | SACRAMENTO | 2021-04-28 | 2021-08-12 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824369 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.013293 | 3118.1978
120899004 | B | LC | ETL.4620.TOWR | 40651062 | PISMOBCH | LOS PADRES | 2021-04-28 | 2021-05-24 | ETL.4620 | DIABLO-MESA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40651062 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1969-01-01 | Ceramic | Dead End |  |  |  |  | 9.8159e-07 | 79.1393
120899004 | B | LC | ETL.4620.TOWR | 40651062 | PISMOBCH | LOS PADRES | 2021-04-28 | 2021-05-24 | ETL.4620 | DIABLO-MESA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40651062 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2017-11-30 | Ceramic | Double Dead End |  |  |  |  | 9.8159e-07 | 79.1393
120919908 | B | LC | ETL.1481.POLE.WOOD | 44201581 | LAKEVLLE | SONOMA | 2021-04-29 | 2021-07-06 | ETL.1481 | LOWER LAKE-HOMESTAKE | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44201581 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.00070063 | 2155.9131
120928571 | E | LC | ETL.3830.TOWR | 40642817 | VICTOR | STOCKTON | 2021-05-04 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40642817 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 0.0002199 | 4559.6204 | 1.0027
120931396 | E | LC | ETL.7550.POLE.WOOD | 40826149 | LAKEVLLE | SONOMA | 2021-05-04 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | PEND | 40826149 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 4.7456e-05 | 79.143 | 0.0037558
120935612 | E | LC | ETL.7490.POLE.NWOD | 40650887 | EUREKA | HUMBOLDT | 2021-05-05 |  | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40650887 | 2011-01-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Ceramic | [5 empty] | 0.00018177 | 189.8608 | 0.034511
120940933 | E | LC | ETL.6280.POLE.NWOD | 44414596 | TABLEMTN | NORTH VALLEY | 2021-05-05 | 2021-08-05 | ETL.6280 | CARIBOU #2 | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44414596 | 2014-08-27 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2014-08-27 | Polymer | Suspension |  |  |  |  | 2.7637e-05 | 5950.0312
120944118 | F | LC | ETL.1810.POLE.WDPS | 44322735 | EUREKA | HUMBOLDT | 2021-05-05 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44322734 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.7501e-05 | 0.065148
120944252 | F | LC | ETL.7212.POLE.STPS | 45102170 | METCALF | PENINSULA | 2021-05-06 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45102123 | 2021-05-02 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.16598 | 602.2181
120950078 | E | LC | ETL.2750.INSL.NCER | 44696491 | CONCORD | EAST BAY | 2021-04-19 |  | ETL.2750 | MORAGA-OAKLAND #4 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40745871 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-01-29 | Polymer | Suspension |  |  |  |  | 9.9567e-06 | 1362.2408 | 0.013563
120950078 | E | LC | ETL.2750.INSL.NCER | 44696491 | CONCORD | EAST BAY | 2021-04-19 |  | ETL.2750 | MORAGA-OAKLAND #4 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40745871 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-07-24 | Ceramic | Suspension |  |  |  |  | 9.9567e-06 | 1362.2408 | 0.013563
120953654 | E | LC | ETL.7550.POLE.WOOD | 40861439 | LAKEVLLE | SONOMA | 2021-05-08 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40861439 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | [5 empty] | 0.0012326 | 0.066432 | 8.1885e-05
121326337 | E | LC | ETL.5390.TOWR | 40593953 | TABLEMTN | NORTH VALLEY | 2021-05-13 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40593953 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.12e-06 | 1064.7484 | 0.0011926
121327260 | F | LC | ETL.1600.TOWR | 40682365 | LAKEVLLE | SONOMA | 2021-05-13 | 2021-10-18 | ETL.1600 | FULTON-PUEBLO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40682365 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1997-01-01 | Polymer | Dead End |  |  |  |  | 0.00019555 | 886.3674
121327260 | F | LC | ETL.1600.TOWR | 40682365 | LAKEVLLE | SONOMA | 2021-05-13 | 2021-10-18 | ETL.1600 | FULTON-PUEBLO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40682365 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2019-06-20 | Glass | Dead End |  |  |  |  | 0.00019555 | 886.3674
121354253 | F | LC | ETL.1600.POLE.WOOD | 40809222 | LAKEVLLE | SONOMA | 2021-05-17 |  | ETL.1600 | FULTON-PUEBLO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40809222 | 1977-01-01 | Single Wood Pole | T-1 - Tri Post | 1977-01-01 | Porcelain | Post |  |  |  |  | 4.6498e-06 | 820.0981 | 0.0038133
121363638 | B | LC | ETL.3750.INSL.CERA | 42582070 | CONCORD | EAST BAY | 2021-05-19 | 2021-06-17 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP | [5 empty] | Ceramic
121372857 | F | LC | ETL.9331.POLE.NWOD | 40859578 | FRESNO | FRESNO | 2021-05-05 |  | ETL.9331 | AUBERRY TAP | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40859578 |  | Light Duty Steel Pole | T-1 - Tri Post | 1964-01-01 | Non Ceramic | Post |  |  |  |  | 7.9832e-05 | 6473.7969 | 0.51681
121377430 | F | LC | ETL.5140.POLE.NWOD | 44141444 | SACTO | SIERRA | 2021-05-06 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44141444 | 2017-10-29 | Light Duty Steel Pole | 1VP - 1 Vertical | 2017-10-29 | Glass | Suspension |  |  |  |  | 3.3009e-09 | 2963.3518
121379230 | E | LC | ETL.6760.POLE.WOOD | 40758341 | SACTO | SIERRA | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758341 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.042968 | 901.7202 | 38.7449
121385625 | E | LC | ETL.1430.INSL | 40786549 | SACTO | SACRAMENTO | 2021-05-13 |  | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40757315 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.00061366 | 1328.8579 | 0.81547
121387345 | B | LC | ETL.3830.TOWR | 40589676 | VICTOR | STOCKTON | 2021-05-21 | 2021-08-11 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40589676 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.5403e-07 | 1976.5953
121391327 | E | LC | ETL.1430.TOWR | 40597539 | SACTO | SIERRA | 2021-05-15 |  | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40597539 | 1913-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1913-01-01 | Ceramic | Dead End |  |  |  |  | 0.0029035 | 1993.4753 | 5.788
121392215 | F | LC | ETL.6760.POLE.WOOD | 40867118 | SACTO | SIERRA | 2021-05-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40867118 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.022161 | 126.6638
121402200 | F | LC | ETL.6760.POLE.NWOD | 40656071 | SACTO | SIERRA | 2021-05-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40656071 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0026 | 110.7947
121404537 | E | LC | ETL.4040.SWIT | 42682159 | TABLEMTN | NORTH VALLEY | 2021-05-26 |  | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | PEND | [10 empty] | Manual
121405321 | E | LC | ETL.6640.POLE.WOOD | 40827038 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40827038 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0015757 | 933.8852 | 1.4715
121406846 | B | LC | ETL.4220.POLE.STPS | 44558318 | TABLEMTN |  | 2021-05-25 | 2021-06-21 | ETL.4220 | WOODLEAF-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44557885 | 2019-07-27 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0011981 | 174.0849
121418287 | E | LC | ETL.6640.POLE.WOOD | 40586301 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | PEND | 40586301 |  | Single Wood Pole | T-1 - Tri Post | 2016-11-15 | Polymer | Post |  |  |  |  | 0.00076967 | 1653.7387 | 1.2728
121418340 | E | LC | ETL.6640.POLE.WOOD | 40678699 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | PEND | 40678699 |  | Single Wood Pole | TPA - Tri Pin Arm | 2013-02-26 | Ceramic | Pin |  |  |  |  | 0.0042248 | 1473.9127 | 6.227
121421455 | E | LC | ETL.7040.INSL.CERA | 40841016 | TABLEMTN | NORTH VALLEY | 2021-05-24 | 2021-06-11 | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40815236 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.17058 | 1428.0112
121428214 | F | LC | ETL.1402.POLE.STPS | 44161082 | VICTOR | YOSEMITE | 2021-05-26 | 2021-07-12 | ETL.1402 | SPRING GAP TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44161082 | 2016-11-15 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2016-11-15 | Porcelain | Suspension |  |  |  |  | 3.9457e-06
121428214 | F | LC | ETL.1402.POLE.STPS | 44161082 | VICTOR | YOSEMITE | 2021-05-26 | 2021-07-12 | ETL.1402 | SPRING GAP TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44161082 | 2016-11-15 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2016-11-15 | Porcelain | Suspension |  |  |  |  | 3.9457e-06
121445379 | E | LC | ETL.1600.INSL.NCER | 40792010 | LAKEVLLE | SONOMA | 2021-06-01 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761989 | 1955-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1946-01-01 | Polymer | Suspension |  |  |  |  | 1.7861e-05 | 313.8482 | 0.0056057
121471189 | E | LC | ETL.1350.POLE.WDPS | 44552496 | TABLEMTN |  | 2021-05-28 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44551516 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.010852 | 3880.9729 | 42.1158
121475156 | F | LC | ETL.6750.POLE.WDPS | 44562143 | TABLEMTN | NORTH VALLEY | 2021-06-05 | 2021-07-26 | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44561573 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.012151 | 490.5302
121481890 | E | LC | ETL.6770.INSL.NCER | 40801834 | SACTO | SIERRA | 2021-06-05 | 2021-11-29 | ETL.6770 | DRUM-SPAULDING | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40770265 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 0.067484 | 1329.6379
121481890 | E | LC | ETL.6770.INSL.NCER | 40801834 | SACTO | SIERRA | 2021-06-05 | 2021-11-29 | ETL.6770 | DRUM-SPAULDING | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40770265 |  | Single Wood Pole | DDE - Double Dead End | 2017-08-02 | Polymer | Dead End |  |  |  |  | 0.067484 | 1329.6379
121492777 | E | LC | ETL.2770.TOWR | 40745900 | CONCORD | EAST BAY | 2021-06-02 |  | ETL.2770 | MORAGA-SAN LEANDRO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40745900 | 1925-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 2.9874e-06 | 0.065147 | 1.9462e-07
121492777 | E | LC | ETL.2770.TOWR | 40745900 | CONCORD | EAST BAY | 2021-06-02 |  | ETL.2770 | MORAGA-SAN LEANDRO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40745900 | 1925-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1991-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.9874e-06 | 0.065147 | 1.9462e-07
121496260 | B | LC | ETL.1820.INSL.CERA | 40781159 | EUREKA | HUMBOLDT | 2021-06-08 | 2021-06-17 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562437 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.015903
121496260 | B | LC | ETL.1820.INSL.CERA | 40781159 | EUREKA | HUMBOLDT | 2021-06-08 | 2021-06-17 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562437 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.015903
121500456 | F | LC | ETL.4450.TOWR | 40589822 | CONCORD | MISSION | 2021-06-04 |  | ETL.4450 | CASTRO VALLEY-NEWARK | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40589822 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.794e-05 | 2960.0791 | 0.053104
121516316 | F | LC | ETL.1820.POLE.WDPS | 40662029 | EUREKA | HUMBOLDT | 2021-06-04 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40662029 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 0.07189
121516316 | F | LC | ETL.1820.POLE.WDPS | 40662029 | EUREKA | HUMBOLDT | 2021-06-04 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40662029 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 0.07189
121516316 | F | LC | ETL.1820.POLE.WDPS | 40662029 | EUREKA | HUMBOLDT | 2021-06-04 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40662029 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 0.07189
121518985 | B | LC | ETL.4550.TOWR | 40762893 | TABLEMTN | NORTH VALLEY | 2021-06-10 | 2021-07-27 | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40762893 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.8811e-07 | 3391.7021
121519236 | F | LC | ETL.5390.TOWR | 40592462 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40592462 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.685e-06 | 700.0411 | 0.0018796
121521753 | E | LC | ETL.4680.TOWR | 40811144 | LAKEVLLE | SONOMA | 2021-06-07 |  | ETL.4680 | FULTON-IGNACIO #1 | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40811144 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.2793e-05 | 205.8647 | 0.010868
121521753 | E | LC | ETL.4680.TOWR | 40811144 | LAKEVLLE | SONOMA | 2021-06-07 |  | ETL.4680 | FULTON-IGNACIO #1 | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40811144 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 5.2793e-05 | 205.8647 | 0.010868
121523285 | F | LC | ETL.1670.POLE.WOOD | 40869694 | LAKEVLLE | SONOMA | 2021-06-07 |  | ETL.1670 | GEYSERS #5-GEYSERS #3 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40869694 | 1991-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Post |  |  |  |  | 0.00072884 | 5607.6411
121523465 | E | LC | ETL.1350.POLE.WDPS | 44201742 | TABLEMTN | NORTH VALLEY | 2021-06-09 | 2021-07-02 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44201741 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.14209 | 490.5302
121525100 | F | LC | ETL.5420.POLE.STPS | 44399964 | TABLEMTN | NORTH VALLEY | 2021-06-12 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44399962 | 2017-11-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.8075e-06 | 386.1275
121531640 | E | LC | ETL.4040.POLE.WDPS | 44561396 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44552630 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.057558 | 3987.1216 | 229.4904
121536153 | E | LC | ETL.1600.INSL | 40713505 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40661937 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.7005e-07 | 2203.4587 | 0.0003747
121542136 | E | LC | ETL.4560.INSL | 40635102 | TABLEMTN | NORTH VALLEY | 2021-06-12 |  | ETL.4560 | COTTONWOOD-GLENN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40601405 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Porcelain | Suspension |  |  |  |  | 3.7635e-08 | 2741.812 | 0.00010319
121542136 | E | LC | ETL.4560.INSL | 40635102 | TABLEMTN | NORTH VALLEY | 2021-06-12 |  | ETL.4560 | COTTONWOOD-GLENN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40601405 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 3.7635e-08 | 2741.812 | 0.00010319
121543819 | E | LC | ETL.5630.TOWR | 40598058 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5630 | ROCK CREEK-POE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40598058 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.111e-06 | 6742.9468 | 0.0074912
121544946 | F | LC | ETL.5420.POLE.WDPS | 44562904 | TABLEMTN | NORTH VALLEY | 2021-06-14 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44562414 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.012154 | 1028.4974
121557489 | B | LC | ETL.1110.TOWR | 40759376 | TABLEMTN | HUMBOLDT | 2021-06-15 | 2021-07-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759376 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-01-31 | Glass | Suspension |  |  |  |  | 4.3549e-05 | 221.5655
121565756 | F | LC | ETL.1421.POLE.NWOD | 44911772 | SACTO | SIERRA | 2021-06-15 |  | ETL.1421 | DUTCH FLAT #2 TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44911772 | 2020-03-04 | Light Duty Steel Pole | DDE - Double Dead End | 2020-03-04 | Glass | Dead End |  |  |  |  | 5.3377e-07 | 269.0173
121569263 | E | LC | ETL.6720.POLE.WDPS | 44949083 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.6720 | DESABLA-CENTERVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42578810 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0015781 | 0.065151 | 0.00010282
121572600 | E | LC | ETL.5630.TOWR | 40758239 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.5630 | ROCK CREEK-POE | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758239 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 0.00014889 | 1835.0725 | 0.27322
121582197 | E | LC | ETL.6070.INSL | 40892389 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6070 | ROUND MTN-TABLE MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40869172 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.2362e-05 | 793.5187 | 0.0098097
121589343 | B | LC | ETL.7270.INSL.NCER | 44649459 | TABLEMTN |  | 2021-06-22 | 2021-07-15 | ETL.7270 | KESWICK-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44649318 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.012506 | 126.6494
121599130 | E | LC | ETL.6040.INSL | 40887877 | MOSSLNDG | CENTRAL COAST | 2021-06-25 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40863883 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 0.0008022 | 348.0674 | 0.27922
121604340 | B | LC | ETL.6020.INSL.CERA | 40891277 | TABLEMTN | NORTH VALLEY | 2021-06-24 | 2021-07-20 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40868287 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.0006077 | 791.1378
121623776 | E | LC | ETL.5960.TOWR | 40740529 | PISMOBCH | LOS PADRES | 2021-06-26 | 2021-09-14 | ETL.5960 | DIABLO-GATES #1 | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40740529 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-04-12 | Ceramic | Dead End |  |  |  |  | 4.2106e-07 | 807.0518
121651686 | F | LC | ETL.1450.POLE.WDPS | 44558973 | SACTO | SACRAMENTO | 2021-06-23 |  | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44558457 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0023818 | 31.7066
121687477 | E | LC | ETL.1110.POLE.STPS | 45082501 | EUREKA | HUMBOLDT | 2021-07-06 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45082460 | 2020-06-20 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 6.9577e-07 | 221.5566 | 0.00015415
121705388 | B | LC | ETL.4880.INSL | 40672485 | FRESNO | FRESNO | 2021-07-09 | 2021-10-06 | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40644945 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.5001e-06
121712975 | F | LC | ETL.5630.POLE.NWOD | 43249835 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.5630 | ROCK CREEK-POE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 43249835 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Ceramic | Dead End |  |  |  |  | 0.00025593 | 5950.4492
121713128 | E | LC | ETL.7030.POLE.WOOD | 40759043 | TABLEMTN | NORTH VALLEY | 2021-07-12 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40759043 |  | Single Wood Pole | T2N | 2021-06-18 | Polymer | Post |  |  |  |  | 0.0003028 | 904.5289 | 0.27389
121714778 | E | LC | ETL.1110.TOWR | 40586445 | TABLEMTN | NORTH VALLEY | 2021-07-12 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40586445 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.323e-05 | 0.065152 | 2.165e-06
121724763 | B | LC | ETL.6650.INSL.NCER | 40855386 | TABLEMTN | NORTH VALLEY | 2021-07-13 | 2021-08-02 | ETL.6650 | COTTONWOOD-BENTON #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44386913 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.047624
121724763 | B | LC | ETL.6650.INSL.NCER | 40855386 | TABLEMTN | NORTH VALLEY | 2021-07-13 | 2021-08-02 | ETL.6650 | COTTONWOOD-BENTON #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44386913 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.047624
121732101 | E | LC | ETL.1480.POLE.WDPS | 44298226 | LAKEVLLE |  | 2021-07-09 |  | ETL.1480 | EAGLE ROCK-REDBUD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44298225 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0023078 | 6142.7134 | 14.1764
121743491 | F | LC | ETL.1820.POLE.NWOD | 45065230 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45065230 | 2021-03-16 | Light Duty Steel Pole | 3P DDE - 3 Pole Double Dead End | 2021-03-16 | Glass | Dead End |  |  |  |  | 0.00056509 | 5065.561
121752841 | E | LC | ETL.5520.INSL.CERA | 44313264 | CONCORD | EAST BAY | 2021-07-17 |  | ETL.5520 | PITTSBURG-TESLA #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40682744 | 1953-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1953-01-01 | Ceramic | Dead End |  |  |  |  | 3.9539e-07 | 5497.5933 | 0.0021737
121768096 | E | LC | ETL.6040.TOWR | 40858416 | MOSSLNDG | YOSEMITE | 2021-07-19 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40858416 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2011-11-16 | Ceramic | Suspension |  |  |  |  | 1.6168e-08
121770086 | E | LC | ETL.2390.INSL.NCER | 40773480 | VICTOR | STOCKTON | 2021-07-19 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391160 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 3.9251e-06
121770086 | E | LC | ETL.2390.INSL.NCER | 40773480 | VICTOR | STOCKTON | 2021-07-19 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391160 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 3.9251e-06
121781540 | F | LC | ETL.6510.POLE.STPS | 44399437 | SACTO | SACRAMENTO | 2021-07-20 | 2021-10-25 | ETL.6510 | COLGATE-SMARTVILLE #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44399436 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 2.6164e-06 | 2025.0242
121797927 | E | LC | ETL.6650.INSL.CERA | 44154552 | TABLEMTN | NORTH VALLEY | 2021-07-26 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44154533 | 2015-03-16 | 2-Pole Non Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0014617
121797927 | E | LC | ETL.6650.INSL.CERA | 44154552 | TABLEMTN | NORTH VALLEY | 2021-07-26 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44154533 | 2015-03-16 | 2-Pole Non Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0014617
121809923 | F | LC | ETL.8365.POLE.WOOD | 40906611 | EUREKA | HUMBOLDT | 2021-07-28 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40906611 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.029848
121814596 | E | LC | ETL.5660.INSL | 40615158 | CONCORD | EAST BAY | 2021-07-29 | 2021-08-17 | ETL.5660 | SAN RAMON-MORAGA | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121816411 | F | LC | ETL.7390.POLE.WOOD | 44412207 | LAKEVLLE | HUMBOLDT | 2021-07-27 | 2021-08-16 | ETL.7390 | LAYTONVILLE-COVELO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 44412207 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.080209
121816627 | E | LC | ETL.4870.INSL | 40578723 | FRESNO | FRESNO | 2021-07-28 |  | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576737 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.5567e-06 | 94.963 | 0.00043272
121882759 | B | LC | ETL.6300.POLE.WDPS | 44976226 | TABLEMTN | NORTH VALLEY | 2021-08-10 | 2021-09-23 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 174.1204
121900744 | E | LC | ETL.1820.POLE.WDPS | 44563016 | EUREKA | HUMBOLDT | 2021-08-13 | 2021-10-11 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562387 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.070289 | 6332.6187
121964585 | E | LC | ETL.6470.POLE.WOOD | 40611122 | SACTO | SACRAMENTO | 2021-08-27 | 2021-11-01 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40611122 |  | Single Wood Pole | T2N | 2021-08-04 | Polymer | Post |  |  |  |  | 0.12859 | 814.7879
122063628 | B | LC | ETL.8405.SWIT | 40744202 | SACTO | SACRAMENTO | 2021-09-17 | 2021-10-20 | ETL.8405 | MIDDLE FORK #1 | Switch | Out of Adjustment | [Repair, Completed] | Tier3 |  |  | COMP | [8 empty] | KPF | ARCHING HORNS ONLY | Manual
122266533 | B | LC | ETL.1600.SWIT | 40743260 | LAKEVLLE | SONOMA | 2021-10-26 | 2021-11-04 | ETL.1600 | FULTON-PUEBLO | Switch | Out of Adjustment | [Repair, Completed] | Tier3 |  |  | COMP | [8 empty] | Other | NO ATTACHMENTS | Manual
122284137 | B | LC | ETL.8480.POLE.STPS | 45102163 | PISMOBCH | LOS PADRES | 2021-11-01 | 2021-11-04 | ETL.8480 | ATASCADERO-CAYUCOS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 45102111 | 2021-05-27 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 5.1326e-08 | 2199.9841 | 0.00011292
122372641 | E | LC | ETL.5140.INSL.CERA | 40621579 | SACTO | SIERRA | 2021-11-13 | 2021-11-30 | ETL.5140 | MIDDLE FORK-GOLD HILL | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44551593 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 0.010976
122372641 | E | LC | ETL.5140.INSL.CERA | 40621579 | SACTO | SIERRA | 2021-11-13 | 2021-11-30 | ETL.5140 | MIDDLE FORK-GOLD HILL | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44551593 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 0.010976
122372641 | E | LC | ETL.5140.INSL.CERA | 40621579 | SACTO | SIERRA | 2021-11-13 | 2021-11-30 | ETL.5140 | MIDDLE FORK-GOLD HILL | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44551593 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 0.010976
118390693 | E | LC | ETL.6500.POLE.WOOD | 40577115 | SACTO | SACRAMENTO | 2020-01-02 | 2020-09-30 | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118522384 | E | LC | ETL.4100.TOWR | 40650935 | SACTO | SACRAMENTO | 2020-02-10 | 2020-09-21 | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650935 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-05-28 | Glass | Suspension |  |  |  |  | 7.9261e-07 | 5842.7749
118522384 | E | LC | ETL.4100.TOWR | 40650935 | SACTO | SACRAMENTO | 2020-02-10 | 2020-09-21 | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650935 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-08-26 | Glass | Dead End - Suspension |  |  |  |  | 7.9261e-07 | 5842.7749
118684311 | E | LC | ETL.6280.POLE.NWOD | 40591842 | TABLEMTN | NORTH VALLEY | 2020-03-12 | 2020-06-15 | ETL.6280 | CARIBOU #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591842 | 2006-01-01 | Tubular Steel Pole | FSS - Field Switch Structure |  | Ceramic | [5 empty] | 5.3352e-10 | 1914.1288
118796899 | E | LC | ETL.7270.POLE.WOOD | 40668374 | TABLEMTN | NORTH VALLEY | 2020-04-08 | 2021-09-09 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [12 empty] | 3233.4868
118933491 | F | LC | ETL.5960.TOWR | 40741756 | PISMOBCH | LOS PADRES | 2020-04-20 | 2021-02-22 | ETL.5960 | DIABLO-GATES #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40741756 |  | LATTICE STEEL TOWER | DDE - Double Dead End | 2013-04-12 | Ceramic | Dead End |  |  |  |  | 8.3652e-07 | 821.6836
118940041 | E | LC | ETL.7510.POLE.WDPS | 44218389 | LAKEVLLE | SONOMA | 2020-04-22 | 2020-07-03 | ETL.7510 | MENDOCINO-HARTLEY | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44218387 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00015326 | 4355.1782
118948119 | B | LC | ETL.2810.INSL | 40611535 | PISMOBCH | LOS PADRES | 2020-04-23 | 2021-08-18 | ETL.2810 | MORRO BAY-SAN LUIS OBISPO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118956677 | E | LC | ETL.6690.POLE.WOOD | 40818994 | SACTO | SACRAMENTO | 2020-04-28 | 2020-05-08 | ETL.6690 | DEER CREEK-DRUM | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
118993326 | E | LC | ETL.2660.TOWR | 40913117 | SACTO | SIERRA | 2020-04-29 | 2021-03-15 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40913117 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Ceramic | Suspension |  |  |  |  | 1.7368e-08 | 2627.5825
118993326 | E | LC | ETL.2660.TOWR | 40913117 | SACTO | SIERRA | 2020-04-29 | 2021-03-15 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40913117 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-03-15 | Glass | Suspension |  |  |  |  | 1.7368e-08 | 2627.5825
119004745 | E | LC | ETL.4220.POLE.WOOD | 40591079 | TABLEMTN | NORTH VALLEY | 2020-05-06 | 2020-07-28 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119017087 | E | LC | ETL.1330.TOWR | 40808937 | LAKEVLLE | HUMBOLDT | 2020-04-24 | 2021-05-11 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40808937 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 9.6128e-06 | 6906.559
119039521 | F | LC | ETL.5960.TOWR | 40812113 | PISMOBCH | LOS PADRES | 2020-05-18 | 2021-06-11 | ETL.5960 | DIABLO-GATES #1 | Road | Encroachment | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40812113 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 2.6735e-09 | 180.4428
119070714 | E | LC | ETL.1430.TOWR | 40581250 | SACTO | SIERRA | 2020-05-19 | 2021-01-28 | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581250 | 1913-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-08-13 | Ceramic | Dead End |  |  |  |  | 0.0029035 | 1993.4753
119082162 | F | LC | ETL.1050.TOWR | 40870873 | FRESNO | FRESNO | 2020-05-27 |  | ETL.1050 | BALCH-SANGER | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40870873 | 1927-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1927-01-01 | Porcelain | Dead End |  |  |  |  | 0.03204 | 5762.1968
119082897 | F | LC | ETL.3960.TOWR | 40659176 | PISMOBCH | LOS PADRES | 2020-05-15 | 2021-01-11 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40659176 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 4.9419e-09 | 2045.5404
119082970 | E | LC | ETL.4590.INSL | 40919908 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2021-01-11 | ETL.4590 | CRESTA-RIO OSO | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40910169 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.5777e-06 | 111.7982
119083477 | E | LC | ETL.7290.POLE.WOOD | 40600840 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-03-01 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40600840 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.078901 | 968.9049
119097573 | E | LC | ETL.1430.TOWR | 40597545 | SACTO | SIERRA | 2020-05-19 | 2021-03-08 | ETL.1430 | DRUM-RIO OSO #2 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40597545 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.0074693 | 3797.0496
119102140 | E | LC | ETL.1450.POLE.WDPS | 44549890 | SACTO | SACRAMENTO | 2020-06-03 | 2020-11-12 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119102700 | F | LC | ETL.6950.POLE.WOOD | 40824207 | SACTO | SIERRA | 2020-05-28 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40824207 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0020755 | 5444.5808
119108078 | E | LC | ETL.1420.TOWR | 40588543 | SACTO | SIERRA | 2020-05-20 | 2021-03-08 | ETL.1420 | DRUM-RIO OSO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40588543 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm | 1913-01-01 | Polymer | Suspension |  |  |  |  | 7.811e-08 | 316.4733
119109571 | F | LC | ETL.4393.POLE.WOOD | 44202749 | SACTO | SIERRA | 2020-06-01 | 2021-01-20 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44202749 | 2015-03-27 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 2015-03-27 | Ceramic | Suspension |  |  |  |  | 0.00057013 | 664.5352
119111922 | F | LC | ETL.5140.POLE.WDPS | 44558231 | SACTO | SACRAMENTO | 2020-05-21 | 2020-11-12 | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119112659 | E | LC | ETL.7140.POLE.WOOD | 40657320 | LAKEVLLE | NORTH BAY | 2020-05-27 | 2021-05-13 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119114892 | E | LC | ETL.1430.TOWR | 40683652 | SACTO | SIERRA | 2020-05-19 | 2021-04-05 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40683652 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.0033687 | 3797.0496
119117505 | F | LC | ETL.6760.POLE.NWOD | 40867115 | SACTO | SIERRA | 2020-05-27 | 2020-11-12 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40867115 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.041566 | 95.0268
119117958 | F | LC | ETL.4393.POLE.WOOD | 42550227 | SACTO | SIERRA | 2020-05-29 | 2021-04-06 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42550227 |  | Single Wood Pole | DE - Dead End | [7 empty] | 0.00030655 | 822.7424
119118268 | F | LC | ETL.6490.POLE.WOOD | 40760393 | SACTO | SIERRA | 2020-06-02 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40760393 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0045556 | 3258.7539
119120240 | F | LC | ETL.6490.POLE.WOOD | 40817281 | SACTO | SIERRA | 2020-06-03 |  | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40817281 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Post |  |  |  |  | 0.0082871 | 1218.0903
119127304 | F | LC | ETL.7300.POLE.WOOD | 40617724 | TABLEMTN |  | 2020-06-03 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40617724 |  | Single Wood Pole | T-1 - Tri Post | 2018-06-03 | Polymer | Post |  |  |  |  | 0.012862 | 554.6501
119132074 | F | LC | ETL.6770.POLE.WOOD | 40667536 | SACTO | SIERRA | 2020-06-04 | 2021-04-20 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119179079 | E | LC | ETL.6280.POLE.WOOD | 40809572 | TABLEMTN | NORTH VALLEY | 2020-06-16 | 2021-09-14 | ETL.6280 | CARIBOU #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809572 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Other |  |  |  |  | 0.00015128 | 5520.0054
119199041 | F | LC | ETL.6480.POLE.WOOD | 40611021 | SACTO | SIERRA | 2020-06-22 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40611021 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.18722 | 316.5113
119200007 | E | LC | ETL.6310.POLE.WOOD | 40759421 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2021-08-12 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759421 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 5.1459e-05 | 0.066431
119200660 | E | LC | ETL.6310.POLE.WOOD | 40816316 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2021-09-01 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816316 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 2.8526e-06 | 4546.0571
119202532 | B | LC | ETL.4220.POLE.WDPS | 44766450 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-10-15 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue, No Action Taken] |  | Tier 2 | Within Both | CNCL | 44766392 | 2019-05-21 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.5501e-05 | 174.0849
119205581 | E | LC | ETL.3530.TOWR | 40585573 | PISMOBCH | LOS PADRES | 2020-06-23 | 2021-02-08 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585573 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1952-01-01 | Porcelain | Suspension |  |  |  |  | 1.9052e-07 | 2503.7683
119208043 | E | LC | ETL.6890.INSL | 40609155 | LAKEVLLE | SONOMA | 2020-06-24 | 2021-03-22 | ETL.6890 | FULTON-HOPLAND | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119233711 | F | LC | ETL.8490.POLE.NWOD | 42700019 | PISMOBCH | LOS PADRES | 2020-06-29 | 2021-03-01 | ETL.8490 | ATASCADERO-SAN LUIS OBISPO | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42700019 | 2013-03-11 | Light Duty Steel Pole | T-1 - Tri Post | 2013-03-11 | Non Ceramic | Post |  |  |  |  | 1.943e-06 | 967.313
119302200 | E | LC | ETL.1450.POLE.WDPS | 44549474 | SACTO | SIERRA | 2020-06-30 | 2020-08-28 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119307984 | B | LC | ETL.7140.POLE.WOOD | 40809046 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809046 |  | Single Wood Pole | FIG4DDE - Figure 4 Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.017728 | 728.338
119312555 | F | LC | ETL.4393.POLE.WDPS | 44172196 | SACTO | SACRAMENTO | 2020-07-01 |  | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44172195 | 2016-01-12 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00017148 | 712.0227
119325948 | F | LC | ETL.8060.POLE.WOOD | 40590059 | SACTO | SIERRA | 2020-07-06 | 2021-05-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40590059 | 1996-01-01 | Single Wood Pole | T2N | 2021-05-08 | Polymer | Post |  |  |  |  | 0.0066781 | 33.2887
119334960 | E | LC | ETL.7300.POLE.WOOD | 40617691 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-10-25 | ETL.7300 | KILARC-DESCHUTES | Vegetation | Overgrown | [Trim, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40617691 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00017812 | 1379.2567 | 0.24567
119335111 | E | LC | ETL.7030.POLE.WOOD | 40591884 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-06-21 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591884 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.010627 | 31.7022
119338978 | E | LC | ETL.8060.POLE.WOOD | 40668661 | SACTO | SACRAMENTO | 2020-07-09 | 2021-04-03 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40668661 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.003398 | 95.1488
119341815 | F | LC | ETL.2700.TOWR | 44188777 | CONCORD | DIABLO | 2020-07-08 | 2021-03-01 | ETL.2700 | MORAGA-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44188777 | 2008-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 2.9651e-07 | 398.0443
119351057 | E | LC | ETL.7180.POLE.WOOD | 44660763 | LAKEVLLE | SONOMA | 2020-07-10 | 2021-04-12 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44660763 | 2017-08-08 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2017-08-08 | Porcelain | Dead End - Suspension |  |  |  |  | 3.2156e-11 | 3027.2869
119359492 | F | LC | ETL.7030.POLE.WOOD | 40676187 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40676187 |  | Single Wood Pole | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Pin |  |  |  |  | 0.03853 | 3705.9004
119364631 | E | LC | ETL.6280.POLE.WOOD | 40768815 | TABLEMTN | NORTH VALLEY | 2020-07-13 |  | ETL.6280 | CARIBOU #2 | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40768815 |  | Single Wood Pole | TAP - Tri Arm Post | 2017-07-19 | Polymer | Post |  |  |  |  | 6.228e-06 | 1043.9664 | 0.0065018
119461803 | F | LC | ETL.6280.POLE.WOOD | 44259132 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-08-11 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL | [11 empty] | 3.2921e-05 | 1611.7464
119468789 | F | LC | ETL.7030.POLE.NWOD | 44144265 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Non-HFTD | HFRA Addition | PEND | 44144265 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 0.0014859
119476625 | F | LC | ETL.8960.POLE.WOOD | 40688134 | FRESNO | FRESNO | 2020-07-20 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40688134 |  | Single Wood Pole | SUSP - Suspension (TWR) | 1974-01-01 | Porcelain | Suspension |  |  |  |  | 0.00037053
119481098 | B | LC | ETL.4870.INSL | 40775189 | FRESNO | FRESNO | 2020-07-21 | 2020-09-15 | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40746665 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 7.8912e-09
119481921 | F | LC | ETL.7540.POLE.WOOD | 40768576 | LAKEVLLE | SONOMA | 2020-07-21 |  | ETL.7540 | MENDOCINO-WILLITS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40768576 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 6.0999e-05 | 468.3588
119482584 | F | LC | ETL.1110.TOWR | 40759209 | EUREKA | HUMBOLDT | 2020-07-21 | 2021-01-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759209 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-08-29 | Ceramic | Suspension |  |  |  |  | 0.00066022 | 459.2314
119482584 | F | LC | ETL.1110.TOWR | 40759209 | EUREKA | HUMBOLDT | 2020-07-21 | 2021-01-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759209 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-07-20 | Porcelain | Suspension |  |  |  |  | 0.00066022 | 459.2314
119486575 | F | LC | ETL.9200.POLE.WOOD | 40808054 | MIDWAY | KERN | 2020-07-21 |  | ETL.9200 | TAFT-CUYAMA #1 | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40808054 | 1962-01-01 | Single Wood Pole | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.0040909
119510432 | B | LC | ETL.6880.POLE.WOOD | 40751148 | LAKEVLLE | NORTH BAY | 2020-07-23 | 2020-08-07 | ETL.6880 | FULTON-CALISTOGA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119639923 | B | LC | ETL.8650.POLE.NWOD | 44420207 | FRESNO | FRESNO | 2020-08-19 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420207 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0073358 | 5840.8999
119639935 | B | LC | ETL.1112.TOWR | 40859254 | FRESNO | FRESNO | 2020-08-19 | 2020-12-14 | ETL.1112 | INDIAN FLAT-YOSEMITE | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40859254 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.00016863 | 5471.0873
119658268 | E | LC | ETL.1420.INSL.CERA | 44337136 | SACTO | SACRAMENTO | 2020-08-22 | 2021-02-18 | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119672023 | F | LC | ETL.3020.TOWR | 40646193 | CONCORD | DIABLO | 2020-08-25 |  | ETL.3020 | NEWARK-JARVIS #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40646193 | 1966-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1966-01-01 | Porcelain | Dead End |  |  |  |  | 2.6461e-08
119672023 | F | LC | ETL.3020.TOWR | 40646193 | CONCORD | DIABLO | 2020-08-25 |  | ETL.3020 | NEWARK-JARVIS #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40646193 | 1966-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2015-11-03 | Ceramic | Suspension |  |  |  |  | 2.6461e-08
119681792 | E | LC | ETL.7780.POLE.WOOD | 40600299 | LAKEVLLE | HUMBOLDT | 2020-08-25 | 2021-04-05 | ETL.7780 | PHILO JCT-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600299 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | [5 empty] | 0.00042985 | 142.4053
119682130 | E | LC | ETL.1730.INSL.NCER | 40853655 | MOSSLNDG | CENTRAL COAST | 2020-08-25 | 2020-11-16 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119682616 | E | LC | ETL.1110.INSL.NCER | 40636959 | TABLEMTN | HUMBOLDT | 2020-08-25 | 2021-05-11 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119687014 | E | LC | ETL.1110.INSL | 40610992 | TABLEMTN | HUMBOLDT | 2020-08-25 | 2021-04-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119687014 | E | LC | ETL.1110.INSL | 40610992 | TABLEMTN | HUMBOLDT | 2020-08-25 | 2021-04-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119698843 | F | LC | ETL.6380.POLE.WOOD | 40750188 | LAKEVLLE | HUMBOLDT | 2020-08-31 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40750188 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-09-29 | Ceramic | Suspension |  |  |  |  | 6.8003e-05 | 4829.3574
119707058 | E | LC | ETL.7290.POLE.WOOD | 40600826 | TABLEMTN | NORTH VALLEY | 2020-08-29 | 2021-08-19 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40600826 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.016166 | 205.8514
119707904 | F | LC | ETL.6280.POLE.NWOD | 44259029 | TABLEMTN | NORTH VALLEY | 2020-08-31 | 2021-08-19 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44259029 | 2020-07-16 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2020-07-16 | Polymer | Post |  |  |  |  | 2.8312e-08 | 158.2282
119710807 | A | LC | ETL.6240.POLE.WOOD | 40599247 | MOSSLNDG | CENTRAL COAST | 2020-09-03 | 2020-10-01 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.5743 | 11.1402
119721512 | E | LC | ETL.1330.TOWR | 40584915 | LAKEVLLE | HUMBOLDT | 2020-07-29 | 2021-04-06 | ETL.1330 | CORTINA-MENDOCINO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40584915 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 4.1625e-06 | 5715.6968
119721512 | E | LC | ETL.1330.TOWR | 40584915 | LAKEVLLE | HUMBOLDT | 2020-07-29 | 2021-04-06 | ETL.1330 | CORTINA-MENDOCINO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40584915 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 4.1625e-06 | 5715.6968
119723741 | E | LC | ETL.6440.POLE.WOOD | 40657903 | TABLEMTN | NORTH VALLEY | 2020-08-04 | 2021-08-19 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40657903 |  | Single Wood Pole | T-1 - Tri Post | 2019-05-22 | Polymer | Post |  |  |  |  | 0.00060835 | 4284.2378
119777267 | E | LC | ETL.8650.TOWR | 40764434 | FRESNO | YOSEMITE | 2020-07-29 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
119786388 | E | LC | ETL.6880.POLE.WOOD | 40585426 | LAKEVLLE | NORTH BAY | 2020-09-15 | 2021-08-04 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119787626 | F | LC | ETL.4393.TOWR | 40586119 | SACTO | SIERRA | 2020-09-16 |  | ETL.4393 | DRUM-HIGGINS | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40586119 |  | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | [7 empty] | 0.00030317 | 822.7424
119794607 | E | LC | ETL.5140.INSL.CERA | 40615858 | SACTO | SIERRA | 2020-09-18 | 2021-11-08 | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119810032 | F | LC | ETL.6280.POLE.NWOD | 44259066 | TABLEMTN | NORTH VALLEY | 2020-08-25 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44259066 | 2018-11-01 | Light Duty Steel Pole | T2N | 2018-11-01 | Polymer | Post |  |  |  |  | 1.8031e-10 | 300.5749
119816937 | F | LC | ETL.7270.POLE.NWOD | 44649350 | TABLEMTN | NORTH VALLEY | 2020-08-29 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44649350 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 1.5228e-07 | 166.1904
119817888 | F | LC | ETL.6280.POLE.WOOD | 40758679 | TABLEMTN | NORTH VALLEY | 2020-08-31 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758679 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 6.1964e-06 | 6187.9214
119819435 | F | LC | ETL.6280.POLE.NWOD | 44259172 | TABLEMTN | NORTH VALLEY | 2020-06-16 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44259172 | 2018-11-07 | Light Duty Steel Pole | T2N | 2018-11-07 | Polymer | Post |  |  |  |  | 1.0489e-07 | 1746.1951
119846107 | E | LC | ETL.1450.POLE.WDPS | 44553546 | SACTO | SACRAMENTO | 2020-10-02 | 2021-12-02 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553154 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0024646 | 221.5552
119874682 | B | LC | ETL.6880.INSL.CERA | 44247815 | LAKEVLLE |  | 2020-10-08 | 2020-11-16 | ETL.6880 | FULTON-CALISTOGA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119895649 | E | LC | ETL.5980.TOWR | 40664648 | PISMOBCH | LOS PADRES | 2020-10-13 | 2021-05-17 | ETL.5980 | DIABLO-MIDWAY #3 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664648 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 5.284e-09 | 47.5096
119909708 | E | LC | ETL.7490.POLE.NWOD | 44145872 | EUREKA | HUMBOLDT | 2020-10-07 | 2021-08-11 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44145872 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-07 | Polymer | Suspension |  |  |  |  | 0.0001571 | 221.4934
119963094 | E | LC | ETL.8580.POLE.WOOD | 40609725 | FRESNO | FRESNO | 2020-10-29 | 2021-03-17 | ETL.8580 | COALINGA #1-SAN MIGUEL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40609725 |  | Single Wood Pole | T-1 - Tri Post | 2016-10-04 | Polymer | Post |  |  |  |  | 8.0534e-05
119995899 | F | LC | ETL.6880.POLE.WOOD | 44250238 | LAKEVLLE | NORTH BAY | 2020-10-07 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44250238 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Porcelain | Dead End |  |  |  |  | 0.03347 | 938.7179
120042947 | E | LC | ETL.8580.INSL.CERA | 40618187 | PISMOBCH | LOS PADRES | 2020-11-16 | 2020-12-30 | ETL.8580 | COALINGA #1-SAN MIGUEL | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120125891 | F | LC | ETL.6720.POLE.STPS | 44922939 | TABLEMTN | NORTH VALLEY | 2020-12-01 | 2021-02-10 | ETL.6720 | DESABLA-CENTERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44922939 | 2020-06-06 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2020-06-06 | Glass | Double Dead End - Suspension |  |  |  |  | 1.949e-07
120125891 | F | LC | ETL.6720.POLE.STPS | 44922939 | TABLEMTN | NORTH VALLEY | 2020-12-01 | 2021-02-10 | ETL.6720 | DESABLA-CENTERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44922939 | 2020-06-06 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2020-06-06 | Glass | Double Dead End - Suspension |  |  |  |  | 1.949e-07
120125891 | F | LC | ETL.6720.POLE.STPS | 44922939 | TABLEMTN | NORTH VALLEY | 2020-12-01 | 2021-02-10 | ETL.6720 | DESABLA-CENTERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44922939 | 2020-06-06 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2020-06-06 | Glass | Double Dead End - Suspension |  |  |  |  | 1.949e-07
120126498 | F | LC | ETL.8365.POLE.NWOD | 40912497 | EUREKA | HUMBOLDT | 2020-10-12 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40912497 | 2010-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.033694
120130309 | F | LC | ETL.6980.POLE.WOOD | 40877385 | LAKEVLLE | HUMBOLDT | 2020-10-20 |  | ETL.6980 | FORT ROSS-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40877385 | 1953-01-01 | Single Wood Pole | T-1 - Tri Post | 2010-01-01 | Polymer | Post |  |  |  |  | 0.12568 | 907.2245
120190808 | B | LC | ETL.1110.TOWR | 40759374 | TABLEMTN | HUMBOLDT | 2020-12-11 | 2021-01-12 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759374 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 0.00020886 | 379.78
120607848 | E | LC | ETL.6070.TOWR | 40592702 | TABLEMTN | NORTH VALLEY | 2021-03-05 | 2021-04-19 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40592702 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-05-27 | Ceramic | Suspension |  |  |  |  | 3.57e-06 | 142.5209
120612704 | F | LC | ETL.9341.POLE.WOOD | 40763380 | FRESNO | YOSEMITE | 2021-03-02 | 2021-06-09 | ETL.9341 | YANKE (NORTH FORK) TAP | Structure-Wood | Idle | [Remove, Completed] | Tier3 |  |  | COMP
120634940 | B | LC | ETL.1350.TOWR | 40803388 | TABLEMTN | NORTH VALLEY | 2021-03-11 | 2021-04-05 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803388 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Dead End |  |  |  |  | 0.0001627 | 142.6993
120658901 | F | LC | ETL.4316.POLE.NWOD | 40771739 | TABLEMTN | NORTH VALLEY | 2021-03-17 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40771739 |  | Light Duty Steel Pole | T-1 - Tri Post | 1949-01-01 | Polymer | Unknown |  |  |  |  | 0.00069101 | 2045.7959
120663769 | F | LC | ETL.4920.TOWR | 40817209 | LAKEVLLE | SONOMA | 2021-03-18 |  | ETL.4920 | IGNACIO-SOBRANTE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40817209 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 6.3406e-05 | 952.3076 | 0.060382
120679682 | E | LC | ETL.5932.TOWR | 40690253 | METCALF | SAN JOSE | 2021-03-22 |  | ETL.5932 | VASONA-METCALF | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40690253 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1957-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.4478e-07 | 1744.1501 | 0.00042693
120687047 | B | LC | ETL.6330.POLE.NWOD | 40598453 | TABLEMTN | NORTH VALLEY | 2021-03-24 | 2021-06-15 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40598453 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 1.5237e-06 | 1091.8842
120709216 | E | LC | ETL.5980.INSL | 40726395 | PISMOBCH | LOS PADRES | 2021-03-29 |  | ETL.5980 | DIABLO-MIDWAY #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40684304 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.0042e-07 | 1962.3188 | 0.00019706
120734358 | F | LC | ETL.3820.TOWR | 40750235 | VICTOR | STOCKTON | 2021-04-01 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40750235 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 3.6464e-07 | 189.8937 | 6.9243e-05
120740228 | E | LC | ETL.1110.TOWR | 40762811 | EUREKA | NORTH VALLEY | 2021-04-03 | 2021-08-04 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40762811 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.422e-05 | 221.4934
120742219 | E | LC | ETL.4000.POLE.WOOD | 40912755 | VICTOR | YOSEMITE | 2021-03-31 | 2021-09-30 | ETL.4000 | TESLA-SALADO-MANTECA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40912755 | 2013-04-22 | Single Wood Pole | DDE - Double Dead End | 2013-04-22 | Porcelain | Dead End |  |  |  |  | 0.00097953 | 1840.5094 | 1.8028
120751883 | E | LC | ETL.6300.INSL | 40634424 | TABLEMTN |  | 2021-04-06 | 2021-05-26 | ETL.6300 | CARIBOU-WESTWOOD | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
120772084 | E | LC | ETL.9250.POLE.WOOD | 40807997 | MIDWAY | KERN | 2021-04-09 | 2021-08-14 | ETL.9250 | TEJON-LEBEC | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40807997 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | [5 empty] | 0.004918 | 4334.67
120795416 | B | LC | ETL.3830.INSL.NCER | 44942010 | VICTOR | STOCKTON | 2021-04-06 | 2021-06-14 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818416 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-12 | Glass | Suspension |  |  |  |  | 1.8518e-07 | 4716.1616
120806791 | E | LC | ETL.4316.POLE.STPS | 44383212 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44383211 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.004223 | 316.5913 | 1.337
120830319 | E | LC | ETL.4770.INSL.CERA | 40839418 | LAKEVLLE | SONOMA | 2021-04-16 |  | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40813808 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-03-08 | Porcelain | Dead End |  |  |  |  | 1.0839e-07 | 5116.498 | 0.0005546
120830319 | E | LC | ETL.4770.INSL.CERA | 40839418 | LAKEVLLE | SONOMA | 2021-04-16 |  | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40813808 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 1.0839e-07 | 5116.498 | 0.0005546
120842562 | B | LC | ETL.6880.POLE.WOOD | 40649312 | LAKEVLLE | SONOMA | 2021-04-19 | 2021-05-06 | ETL.6880 | FULTON-CALISTOGA | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40649312 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 0.028818 | 522.4158
120844981 | E | LC | ETL.4870.TOWR | 40858331 | FRESNO | FRESNO | 2021-04-19 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40858331 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.8357e-08 | 5240.2021 | 9.6195e-05
120854549 | E | LC | ETL.4316.TOWR | 40871564 | TABLEMTN | NORTH VALLEY | 2021-04-12 | 2021-06-17 | ETL.4316 | PARADISE-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871564 | 1921-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-23 | Glass | Suspension |  |  |  |  | 0.00065624 | 2092.6382
120858334 | E | LC | ETL.7890.INSL.CERA | 40886660 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.7890 | SALINAS-FORT ORD #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40864192 |  | Lattice Steel Pole | DCPOST - Double Circuit Post |  | Porcelain | [5 empty] | 6.4205e-07 | 0.065148 | 4.1828e-08
120862481 | E | LC | ETL.1820.POLE.WOOD | 45092597 | EUREKA | HUMBOLDT | 2021-04-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 45092597 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Ceramic | Suspension |  |  |  |  | 0.17674 | 79.143 | 13.9878
120872203 | B | LC | ETL.1250.INSL | 40831084 | FRESNO | FRESNO | 2021-04-22 | 2021-05-26 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40806771 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | [5 empty] | 2.8648e-05 | 6932.1865
120880567 | F | LC | ETL.5790.TOWR | 40863677 | VICTOR | STOCKTON | 2021-04-24 |  | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40863677 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 7.8084e-06 | 33.284
120881818 | E | LC | ETL.2730.INSL | 40773208 | CONCORD | DIABLO | 2021-04-21 |  | ETL.2730 | MORAGA-OAKLAND #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40745886 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0014271 | 0.065147 | 9.2972e-05
120890579 | E | LC | ETL.3960.TOWR | 40751436 | PISMOBCH | LOS PADRES | 2021-04-27 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40751436 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 9.7184e-07 | 871.475 | 0.00084693
120892182 | E | LC | ETL.7550.POLE.WOOD | 40600415 | LAKEVLLE | SONOMA | 2021-04-27 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40600415 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 4.5726e-05 | 5324.1685 | 0.24345
120899657 | E | LC | ETL.5300.INSL | 40847593 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40819267 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 9.0072e-07 | 4876.6128 | 0.0043925
120906605 | B | LC | ETL.5933.TOWR | 40863323 | PISMOBCH | LOS PADRES | 2021-04-29 | 2021-07-28 | ETL.5933 | MORRO BAY-TEMPLETON | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40863323 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2016-08-27 | Ceramic | Suspension |  |  |  |  | 1.4488e-08 | 2882.8154
120910671 | F | LC | ETL.6890.POLE.NWOD | 44712982 | LAKEVLLE | SONOMA | 2021-04-30 |  | ETL.6890 | FULTON-HOPLAND | Guy Wire-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44712982 | 2019-02-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-02-16 | Ceramic | Suspension |  |  |  |  | 9.2319e-08 | 3594.7428 | 0.00033186
120910984 | B | LC | ETL.5970.INSL | 40688679 | PISMOBCH | LOS PADRES | 2021-04-30 | 2021-05-19 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40658675 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 5.6535e-11 | 2137.2815
120912675 | E | LC | ETL.3830.TOWR | 40579595 | VICTOR | STOCKTON | 2021-05-01 | 2021-08-09 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40579595 | 1927-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post | 1999-01-01 | Polymer | Suspension |  |  |  |  | 5.9224e-07 | 2044.7079
120913492 | E | LC | ETL.5920.INSL | 40792098 | CONCORD | EAST BAY | 2021-04-29 |  | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40762046 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-03-22 | Glass Silicone Coated | Suspension |  |  |  |  | 0.0022858 | 2709.8901 | 6.1942
120913492 | E | LC | ETL.5920.INSL | 40792098 | CONCORD | EAST BAY | 2021-04-29 |  | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40762046 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0022858 | 2709.8901 | 6.1942
120918164 | E | LC | ETL.1422.TOWR | 40650072 | SACTO | SACRAMENTO | 2021-04-26 | 2021-10-11 | ETL.1422 | BRUNSWICK #1 TAP | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40650072 | 1975-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-03-16 | Glass Silicone Coated | Suspension |  |  |  |  | 1.5779e-07 | 1471.1865
120918164 | E | LC | ETL.1422.TOWR | 40650072 | SACTO | SACRAMENTO | 2021-04-26 | 2021-10-11 | ETL.1422 | BRUNSWICK #1 TAP | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40650072 | 1975-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-05-05 | Glass | Dead End |  |  |  |  | 1.5779e-07 | 1471.1865
120946278 | E | LC | ETL.5220.TOWR | 40869050 | METCALF | SAN JOSE | 2021-05-06 |  | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40869050 | 1963-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1963-01-01 | Ceramic | Suspension |  |  |  |  | 0.19054 | 1170.8525 | 223.0994
120946278 | E | LC | ETL.5220.TOWR | 40869050 | METCALF | SAN JOSE | 2021-05-06 |  | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40869050 | 1963-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1963-01-01 | Ceramic | Dead End |  |  |  |  | 0.19054 | 1170.8525 | 223.0994
120950843 | F | LC | ETL.3500.TOWR | 40857311 | VICTOR | STOCKTON | 2021-04-16 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40857311 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-01-30 | Glass | Dead End |  |  |  |  | 3.4095e-05 | 822.7424 | 0.028051
121325187 | B | LC | ETL.7380.INSL | 40853156 | MOSSLNDG | CENTRAL COAST | 2021-05-12 | 2021-07-13 | ETL.7380 | LAURELES-OTTER | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40825851 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.39632 | 0.065148
121328100 | E | LC | ETL.1820.POLE.WDPS | 44562933 | EUREKA | HUMBOLDT | 2021-05-13 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44562357 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.076645 | 727.8519 | 55.7863
121335598 | E | LC | ETL.8480.POLE.WOOD | 40760295 | PISMOBCH | LOS PADRES | 2021-04-23 |  | ETL.8480 | ATASCADERO-CAYUCOS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40760295 | 1954-01-01 | Single Wood Pole | T-1 - Tri Post | 2019-07-12 | Polymer | Post |  |  |  |  | 0.0017059 | 4444.0327 | 7.5811
121341080 | E | LC | ETL.8405.INSL.NCER | 40629628 | SACTO | SACRAMENTO | 2021-05-15 |  | ETL.8405 | MIDDLE FORK #1 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40602856 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Polymer | [5 empty] | 0.057815 | 6774.7476 | 391.6841
121350019 | B | LC | ETL.5390.INSL.CERA | 40687124 | TABLEMTN | NORTH VALLEY | 2021-05-17 | 2021-05-20 | ETL.5390 | PIT #1-COTTONWOOD | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
121369476 | F | LC | ETL.1820.POLE.WDPS | 44557695 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
121370517 | F | LC | ETL.1250.POLE.NWOD | 40748529 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40748529 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.3974e-06 | 4148.9409
121381296 | E | LC | ETL.5250.TOWR | 40756483 | CONCORD | MISSION | 2021-04-29 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40756483 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.9686e-08 | 333.6693 | 6.5686e-06
121381812 | F | LC | ETL.8250.POLE.WOOD | 40607061 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40607061 | 1995-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 2.3318e-05 | 2923.5044
121382255 | E | LC | ETL.6500.POLE.WOOD | 40597477 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40597477 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.016992 | 158.2502 | 2.6889
121382846 | F | LC | ETL.6470.POLE.WOOD | 40760408 | SACTO | SIERRA | 2021-05-11 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40760408 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.019283 | 2183.0701
121384054 | F | LC | ETL.8250.POLE.WOOD | 40908880 | VICTOR | STOCKTON | 2021-05-11 | 2021-06-24 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 0.0010183 | 2614.054
121384921 | F | LC | ETL.6760.POLE.WOOD | 40766694 | SACTO | SIERRA | 2021-05-13 | 2021-07-12 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40766694 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.037884 | 205.7564
121401380 | E | LC | ETL.6050.TOWR | 40592715 | MOSSLNDG | SAN JOSE | 2021-05-19 |  | ETL.6050 | MOSS LANDING-METCALF | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40592715 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 1.169e-08 | 918.304 | 1.0735e-05
121401854 | F | LC | ETL.1073.POLE.NWOD | 44384837 | VICTOR | YOSEMITE | 2021-05-19 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44384837 | 2017-08-17 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 1.4819e-05 | 31.7081
121428169 | F | LC | ETL.2141.POLE.NWOD | 44257859 | MIDWAY | KERN | 2021-05-27 |  | ETL.2141 | VEDDER TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44257859 |  | Light Duty Steel Pole | 3HP - 3 Horizontal Post |  | Polymer | Post |  |  |  |  | 4.7753e-07 | 6774.418
121438275 | E | LC | ETL.2540.POLE.WDPS | 44401491 | METCALF | CENTRAL COAST | 2021-05-26 |  | ETL.2540 | METCALF-GREEN VALLEY | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44401490 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.1456 | 158.2797 | 23.0449
121446834 | E | LC | ETL.1350.INSL.CERA | 40621371 | TABLEMTN |  | 2021-05-28 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44512296 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 0.008643
121446834 | E | LC | ETL.1350.INSL.CERA | 40621371 | TABLEMTN |  | 2021-05-28 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44512296 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 0.008643
121446834 | E | LC | ETL.1350.INSL.CERA | 40621371 | TABLEMTN |  | 2021-05-28 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44512296 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 0.008643
121455865 | E | LC | ETL.6290.POLE.WOOD | 40826460 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40826460 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.03969 | 4223.3467 | 167.6241
121486005 | E | LC | ETL.4750.INSL.CERA | 40844708 | LAKEVLLE | SONOMA | 2021-05-29 |  | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40818368 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 7.8025e-08 | 2501.0085 | 0.00019514
121491761 | E | LC | ETL.5650.INSL | 40714005 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40662733 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 0.00052571 | 1333.3085 | 0.70093
121493509 | F | LC | ETL.4220.POLE.STPS | 44388367 | TABLEMTN |  | 2021-05-28 |  | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44388365 | 2016-11-28 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00088262 | 205.7375
121518392 | F | LC | ETL.7040.POLE.WOOD | 40674212 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40674212 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | [5 empty] | 0.06457 | 0.35615
121523986 | F | LC | ETL.1450.POLE.WDPS | 44553569 | SACTO | SACRAMENTO | 2021-06-08 | 2021-07-06 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44553152 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0026947 | 31.7066
121524071 | E | LC | ETL.6852.POLE.WOOD | 40667004 | LAKEVLLE | HUMBOLDT | 2021-06-09 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40667004 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.041537 | 6378.4995 | 264.9437
121524237 | E | LC | ETL.4040.POLE.WDPS | 44553657 | TABLEMTN |  | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44553119 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.039476 | 4481.9893 | 176.9323
121524438 | E | LC | ETL.1350.POLE.WDPS | 44549876 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44549445 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 0.037047 | 94.9939 | 3.5193
121543647 | F | LC | ETL.1820.POLE.NWOD | 44324170 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44324170 | 2015-12-01 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2015-12-01 | Ceramic | Suspension |  |  |  |  | 0.0085686 | 94.9939
121543811 | E | LC | ETL.7550.POLE.WOOD | 40768537 | LAKEVLLE | HUMBOLDT | 2021-06-12 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40768537 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00073721 | 15.8837 | 0.01171
121545020 | F | LC | ETL.5390.TOWR | 40816148 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40816148 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 4.9891e-07 | 978.0653 | 0.00048796
121561580 | E | LC | ETL.6110.TOWR | 40863781 | METCALF | SAN JOSE | 2021-06-16 | 2021-09-13 | ETL.6110 | TESLA-METCALF | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863781 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.0618e-08 | 3423.8503
121568126 | E | LC | ETL.6760.POLE.NWOD | 45072094 | SACTO | SIERRA | 2021-06-15 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45072094 | 2020-04-25 | Light Duty Steel Pole | T2N | 2020-04-24 | Polymer | Post |  |  |  |  | 0.0056397 | 1503.0458 | 8.4767
121568398 | F | LC | ETL.1450.POLE.WDPS | 44552257 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44551603 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00028114 | 450.9556 | 0.12678
121574604 | F | LC | ETL.4040.POLE.STPS | 44647136 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44646845 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00021796 | 129.5341
121587399 | E | LC | ETL.1372.POLE.WDPS | 44726498 | PISMOBCH | LOS PADRES | 2021-06-23 |  | ETL.1372 | MANVILLE TAP | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44283672 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00032699 | 4036.8325 | 1.32
121587791 | E | LC | ETL.5640.TOWR | 40816239 | TABLEMTN | NORTH VALLEY | 2021-06-22 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40816239 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 1.2941e-06 | 2599.3877 | 0.0033639
121601405 | F | LC | ETL.1184.TOWR | 45098594 | LAKEVLLE | SONOMA | 2021-06-25 | 2021-08-03 | ETL.1184 | SMUD TAP | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45098594 |  | LATTICE STEEL TOWER | FSS - Field Switch Structure | [8 empty] | 1038.0233
121608243 | F | LC | ETL.6981.POLE.WDPS | 44565340 | LAKEVLLE | SONOMA | 2021-06-26 |  | ETL.6981 | SALMON CREEK TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | HFRA Removal | PEND | 44564242 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.20095 | 1219.1483
121623638 | E | LC | ETL.3820.TOWR | 40579606 | VICTOR | STOCKTON | 2021-06-22 | 2021-10-04 | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40579606 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 1.3533e-06 | 7492.2583 | 0.010139
121633990 | E | LC | ETL.2395.INSL.NCER | 40803210 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.2395 | GRIZZLY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550853 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.0065526
121633990 | E | LC | ETL.2395.INSL.NCER | 40803210 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.2395 | GRIZZLY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550853 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.0065526
121641033 | F | LC | ETL.8365.POLE.WOOD | 40826234 | EUREKA | HUMBOLDT | 2021-06-23 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40826234 | 2010-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.014952 | 616.987
121642257 | F | LC | ETL.4040.POLE.STPS | 44552425 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44551568 | 2018-01-01 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00024423 | 854.4995
121642309 | E | LC | ETL.1440.POLE.WDPS | 44768912 | SACTO | SACRAMENTO | 2021-06-18 |  | ETL.1440 | DRUM-SUMMIT #1 | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40755595 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.02801 | 617.0731 | 17.284
121662997 | F | LC | ETL.7550.POLE.WOOD | 40588485 | LAKEVLLE | HUMBOLDT | 2021-07-01 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40588485 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 4.1861e-06 | 0.065148
121730118 | E | LC | ETL.7640.INSL.CERA | 44296773 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.7640 | MTN GATE JCT-CASCADE | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44564244 |  | 2-Pole Wood | DDE - Double Dead End | 2015-05-05 | Ceramic | Double Dead End |  |  |  |  | 4.3612e-06
121730118 | E | LC | ETL.7640.INSL.CERA | 44296773 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.7640 | MTN GATE JCT-CASCADE | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44564244 |  | 2-Pole Wood | DDE - Double Dead End | 2015-05-05 | Ceramic | Double Dead End |  |  |  |  | 4.3612e-06
121732114 | E | LC | ETL.6380.INSL.NCER | 44433446 | LAKEVLLE |  | 2021-07-08 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44235466 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-09-29 | Polymer | Post |  |  |  |  | 1.4144e-05
121732114 | E | LC | ETL.6380.INSL.NCER | 44433446 | LAKEVLLE |  | 2021-07-08 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44235466 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-09-29 | Polymer | Post |  |  |  |  | 1.4144e-05
121732114 | E | LC | ETL.6380.INSL.NCER | 44433446 | LAKEVLLE |  | 2021-07-08 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44235466 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-09-29 | Polymer | Post |  |  |  |  | 1.4144e-05
121733800 | B | LC | ETL.2540.POLE.WDPS | 44551461 | MOSSLNDG | CENTRAL COAST | 2021-07-14 | 2021-08-27 | ETL.2540 | METCALF-GREEN VALLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [12 empty] | 1190.7595
121735966 | F | LC | ETL.1820.POLE.WDPS | 44557507 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44554046 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.46162 | 47.5118
121738942 | E | LC | ETL.1820.INSL.CERA | 40637020 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560110 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.012986 | 5288.2002 | 68.6707
121748126 | F | LC | ETL.1820.POLE.WOOD | 44562389 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44562389 |  | Single Wood Pole | 3P DV - 3 Pole Double Vertical |  | Ceramic | Suspension |  |  |  |  | 0.17259 | 31.7207
121748733 | F | LC | ETL.1820.POLE.WOOD | 45089723 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45089723 | 2020-03-12 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2020-03-12 | Glass | Dead End |  |  |  |  | 0.025163 | 2753.0989
121750067 | F | LC | ETL.1420.TOWR | 40588546 | SACTO | SIERRA | 2021-07-17 | 2021-07-26 | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40588546 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 4.3744e-06 | 1360.4569
121770910 | E | LC | ETL.2390.POLE.WDPS | 44391184 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391182 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0001952 | 2751.947 | 0.53717
121783410 | E | LC | ETL.2390.POLE.WDPS | 44391090 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391089 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.51e-05 | 727.9523 | 0.04011
121831367 | E | LC | ETL.7270.POLE.WOOD | 42621522 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-11-02 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42621522 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.032124 | 724.7053 | 23.2802
122108915 | E | LC | ETL.3720.POLE.NWOD | 44359225 | CONCORD | DIABLO | 2021-09-27 |  | ETL.3720 | SOBRANTE-G #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | HFRA Removal | PEND | 44359225 |  | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 1.1309e-05 | 47.5096 | 0.00053731
122274996 | E | LC | ETL.7550.INSL | 40899632 | LAKEVLLE | HUMBOLDT | 2021-10-14 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40875186 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 6.1574e-05 | 110.7947 | 0.0068221
118585758 | E | LC | ETL.6070.TOWR | 40820562 | TABLEMTN | NORTH VALLEY | 2020-02-13 | 2021-04-19 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40820562 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1996-01-01 | Ceramic | Suspension |  |  |  |  | 4.4008e-09 | 1426.6595
118736564 | E | LC | ETL.8351.SWIT | 40744194 | VICTOR | STOCKTON | 2020-03-23 | 2021-07-01 | ETL.8351 | PINE GROVE TAP | Switch-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | DLFL
118736653 | E | LC | ETL.8250.SWIT | 40744157 | VICTOR | STOCKTON | 2020-03-24 | 2021-08-10 | ETL.8250 | CLAY-MARTEL | Switch-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
118757998 | F | LC | ETL.8350.POLE.WOOD | 40579953 | VICTOR | STOCKTON | 2020-03-31 | 2021-10-14 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40579953 |  | Single Wood Pole | TPSRD - Tri Post & Susp Dead End |  | Glass | [5 empty] | 6.6727e-05 | 1075.7617
118770952 | E | LC | ETL.4450.INSL.CERA | 44394311 | CONCORD | EAST BAY | 2020-04-02 | 2021-06-10 | ETL.4450 | CASTRO VALLEY-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587524 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 3.5129e-05 | 1739.0215
118770952 | E | LC | ETL.4450.INSL.CERA | 44394311 | CONCORD | EAST BAY | 2020-04-02 | 2021-06-10 | ETL.4450 | CASTRO VALLEY-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587524 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-17 | Glass | Suspension |  |  |  |  | 3.5129e-05 | 1739.0215
118795568 | E | LC | ETL.5920.INSL | 40791096 | CONCORD | EAST BAY | 2020-04-07 | 2021-08-30 | ETL.5920 | TASSAJARA-NEWARK | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761290 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Dead End |  |  |  |  | 1.7587e-07 | 3704.949
118795568 | E | LC | ETL.5920.INSL | 40791096 | CONCORD | EAST BAY | 2020-04-07 | 2021-08-30 | ETL.5920 | TASSAJARA-NEWARK | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761290 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.7587e-07 | 3704.949
118923337 | F | LC | ETL.4680.TOWR | 40811146 | LAKEVLLE | SONOMA | 2020-04-14 | 2021-03-08 | ETL.4680 | FULTON-IGNACIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40811146 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 0.00033581 | 1633.6974
118924523 | F | LC | ETL.6880.POLE.NWOD | 40679497 | LAKEVLLE | NORTH BAY | 2020-04-15 | 2021-01-11 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install, Completed] | Tier3 |  |  | COMP
118943309 | E | LC | ETL.5850.TOWR | 40660123 | SACTO | SACRAMENTO | 2020-04-23 | 2021-02-25 | ETL.5850 | VACA-PARKWAY | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660123 | 1946-01-01 | LATTICE STEEL TOWER | Unknown | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 6.4459e-11 | 9843.8711
118943309 | E | LC | ETL.5850.TOWR | 40660123 | SACTO | SACRAMENTO | 2020-04-23 | 2021-02-25 | ETL.5850 | VACA-PARKWAY | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660123 | 1946-01-01 | LATTICE STEEL TOWER | Unknown | 2019-09-10 | Glass | Suspension |  |  |  |  | 6.4459e-11 | 9843.8711
118949766 | F | LC | ETL.4392.TOWR | 41129318 | LAKEVLLE | SONOMA | 2020-04-26 | 2020-05-07 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129318 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-08-18 | Glass | Double Dead End |  |  |  |  | 4.657e-05 | 3054.8015
118949766 | F | LC | ETL.4392.TOWR | 41129318 | LAKEVLLE | SONOMA | 2020-04-26 | 2020-05-07 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129318 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 4.657e-05 | 3054.8015
118960189 | B | LC | ETL.4770.TOWR | 40756502 | LAKEVLLE | SONOMA | 2020-04-24 | 2020-06-29 | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756502 | 1982-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 4.2071e-07 | 807.3989
118960189 | B | LC | ETL.4770.TOWR | 40756502 | LAKEVLLE | SONOMA | 2020-04-24 | 2020-06-29 | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756502 | 1982-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 4.2071e-07 | 807.3989
118966655 | F | LC | ETL.5780.TOWR | 40680949 | VICTOR | STOCKTON | 2020-04-30 | 2020-05-18 | ETL.5780 | TIGER CREEK-ELECTRA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40680949 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.0194e-06 | 126.8157
118967656 | E | LC | ETL.7590.POLE.WOOD | 42565750 | MOSSLNDG | CENTRAL COAST | 2020-05-01 | 2020-07-28 | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
118980331 | F | LC | ETL.1073.POLE.WOOD | 40803728 | VICTOR | YOSEMITE | 2020-04-27 | 2021-09-27 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40803728 | 1991-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1956-01-01 | Non Ceramic | Other |  |  |  |  | 0.00027917 | 31.7081
119019080 | F | LC | ETL.7510.POLE.WOOD | 40862669 | LAKEVLLE | SONOMA | 2020-05-12 | 2020-06-04 | ETL.7510 | MENDOCINO-HARTLEY | Marker (i.e. signs)-Steel | Missing | [Install, Completed] | Tier2 |  |  | COMP
119036217 | E | LC | ETL.1600.TOWR | 40805568 | LAKEVLLE | NORTH BAY | 2020-05-12 | 2021-01-19 | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805568 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 3.949e-07 | 4878.917
119036217 | E | LC | ETL.1600.TOWR | 40805568 | LAKEVLLE | NORTH BAY | 2020-05-12 | 2021-01-19 | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805568 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-06-10 | Glass | Suspension |  |  |  |  | 3.949e-07 | 4878.917
119039139 | E | LC | ETL.5940.TOWR | 40679198 | PISMOBCH | LOS PADRES | 2020-04-29 | 2020-10-21 | ETL.5940 | DIABLO UNIT #1 | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40679198 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00047846 | 1061
119040276 | E | LC | ETL.6979.POLE.WOOD | 40750316 | LAKEVLLE | SONOMA | 2020-05-18 | 2021-06-09 | ETL.6979 | MONTE RIO-FORT ROSS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750316 | 1985-01-01 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2010-01-01 | Non Ceramic | Other |  |  |  |  | 0.0009442 | 15.8851
119046631 | E | LC | ETL.6880.POLE.WOOD | 44140231 | LAKEVLLE | NORTH BAY | 2020-05-12 | 2021-08-17 | ETL.6880 | FULTON-CALISTOGA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44140231 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Polymer | Suspension |  |  |  |  | 0.00064304 | 110.8668
119082167 | E | LC | ETL.9100.POLE.WOOD | 44191865 | PISMOBCH | LOS PADRES | 2020-05-22 | 2021-10-07 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0007444 | 2503.7137
119084574 | F | LC | ETL.6760.POLE.WOOD | 40814280 | SACTO | SIERRA | 2020-05-28 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40814280 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.093331 | 63.348
119096923 | E | LC | ETL.1650.POLE.WOOD | 40657192 | LAKEVLLE | SONOMA | 2020-05-27 | 2021-04-22 | ETL.1650 | GEYSERS #3-CLOVERDALE | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40657192 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 0.00023871 | 4151.2271
119096927 | E | LC | ETL.7790.POLE.NWOD | 44639190 | TABLEMTN | NORTH VALLEY | 2020-06-02 | 2020-08-17 | ETL.7790 | PIT #1-MCARTHUR | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44639190 | 2018-06-26 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2018-06-26 | Polymer | Post |  |  |  |  | 7.5132e-05 | 2598.873
119097093 | E | LC | ETL.8170.POLE.WOOD | 40906381 | EUREKA | HUMBOLDT | 2020-06-02 | 2021-06-03 | ETL.8170 | TRINITY-MAPLE CREEK | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906381 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.0173 | 15.8866
119103243 | E | LC | ETL.1450.POLE.WOOD | 40755366 | SACTO | SIERRA | 2020-06-01 | 2020-08-11 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119105003 | F | LC | ETL.1430.TOWR | 40814517 | SACTO | SIERRA | 2020-05-19 | 2020-11-12 | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40814517 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.00095228 | 775.2101
119106232 | B | LC | ETL.7930.POLE.WOOD | 42564787 | MOSSLNDG | CENTRAL COAST | 2020-06-03 | 2020-10-14 | ETL.7930 | SALINAS-LAURELES | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42564787 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 0.004676 | 0.066432
119106543 | E | LC | ETL.8170.POLE.WOOD | 40590531 | EUREKA | HUMBOLDT | 2020-06-03 | 2021-09-27 | ETL.8170 | TRINITY-MAPLE CREEK | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40590531 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.0074166 | 727.8646
119110332 | F | LC | ETL.1710.POLE.WDPS | 44513698 | MOSSLNDG | CENTRAL COAST | 2020-05-21 | 2021-07-08 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44512275 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0038027 | 16.6744
119112457 | B | LC | ETL.1050.TOWR | 40751518 | FRESNO | FRESNO | 2020-06-05 | 2020-12-08 | ETL.1050 | BALCH-SANGER | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751518 | 1923-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1923-01-01 | Porcelain | Dead End |  |  |  |  | 0.0015008 | 7774.5303
119115185 | F | LC | ETL.8650.POLE.NWOD | 44420203 | FRESNO | YOSEMITE | 2020-06-02 | 2021-04-27 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44420203 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.01114 | 5066.0874
119127508 | F | LC | ETL.7380.POLE.WOOD | 40877756 | MOSSLNDG | CENTRAL COAST | 2020-05-29 |  | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40877756 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.94964 | 47.5141
119141812 | F | LC | ETL.1810.TOWR | 44321417 | EUREKA | HUMBOLDT | 2020-06-05 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44321417 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | [5 empty] | 4.6325e-07
119162892 | F | LC | ETL.1400.POLE.WDPS | 44800119 | VICTOR | STOCKTON | 2020-06-12 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40744831 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.0033999 | 4145.3232
119164325 | E | LC | ETL.6770.POLE.WOOD | 40650015 | SACTO | SACRAMENTO | 2020-06-14 | 2020-07-07 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119167128 | F | LC | ETL.6760.POLE.NWOD | 44922916 | SACTO | SIERRA | 2020-06-15 | 2021-07-08 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44922916 | 2020-04-14 | Light Duty Steel Pole | T-1 - Tri Post | 2020-04-14 | Polymer | Post |  |  |  |  | 1.8275e-05 | 90.2307
119171150 | E | LC | ETL.7850.POLE.WDPS | 44403581 | EUREKA | HUMBOLDT | 2020-06-15 | 2020-09-09 | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44403578 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 9.1656e-06 | 641.5788
119182231 | F | LC | ETL.6280.POLE.WOOD | 40614795 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-08-02 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40614795 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 3.0662e-05 | 490.3705
119213020 | E | LC | ETL.7390.INSL.NCER | 45041739 | LAKEVLLE | HUMBOLDT | 2020-06-25 |  | ETL.7390 | LAYTONVILLE-COVELO | Damper-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 45041709 | 2020-06-20 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-06-20 | Polymer | Dead End |  |  |  |  | 0.035178
119222169 | E | LC | ETL.7290.POLE.WOOD | 40701755 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2021-03-15 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119237853 | E | LC | ETL.7490.POLE.WDPS | 44743797 | EUREKA | HUMBOLDT | 2020-06-30 | 2021-09-23 | ETL.7490 | MAPLE CREEK-HOOPA | Conductor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL | [12 empty] | 0.065148
119293431 | E | LC | ETL.8170.INSL | 40735639 | EUREKA | HUMBOLDT | 2020-07-01 |  | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40701804 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.05248 | 15.8815 | 0.83346
119295050 | F | LC | ETL.7270.POLE.WOOD | 40906494 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906494 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0031996 | 996.8419
119295253 | E | LC | ETL.6950.POLE.WOOD | 44437419 | SACTO | SACRAMENTO | 2020-07-01 | 2020-12-16 | ETL.6950 | GOLD HILL #1 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44437419 |  | Single Wood Pole | T1-1A |  | Polymer | Pin |  |  |  |  | 0.0011875 | 1593.2229
119303298 | F | LC | ETL.7180.POLE.NWOD | 40770104 | LAKEVLLE | SONOMA | 2020-07-02 | 2021-02-01 | ETL.7180 | IGNACIO-BOLINAS #2 | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40770104 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 8.4796e-07 | 253.482
119308316 | F | LC | ETL.8060.POLE.WOOD | 40809675 | SACTO | SIERRA | 2020-07-02 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809675 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0052244 | 291.1663
119312513 | F | LC | ETL.7980.POLE.NWOD | 40818287 | SACTO | SIERRA | 2020-07-02 |  | ETL.7980 | SMARTVILLE-MARYSVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40818287 | 2011-01-01 | Light Duty Steel Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 1.3307e-06 | 1440.1678
119323908 | E | LC | ETL.6890.POLE.WOOD | 40601288 | LAKEVLLE | SONOMA | 2020-07-07 | 2021-01-13 | ETL.6890 | FULTON-HOPLAND | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40601288 | 1990-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.00045448 | 2138.6487
119325697 | E | LC | ETL.1810.TOWR | 44321412 | EUREKA | HUMBOLDT | 2020-07-07 | 2021-01-25 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44321412 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 1.4686e-06
119325730 | E | LC | ETL.6290.POLE.WOOD | 40666908 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-07-09 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40666908 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.10876 | 4919.2388
119337418 | E | LC | ETL.6861.POLE.WOOD | 40769680 | LAKEVLLE | SONOMA | 2020-07-09 | 2021-08-12 | ETL.6861 | KONOCTI-EAGLE ROCK | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40769680 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-11-06 | Polymer | Dead End |  |  |  |  | 0.00012019 | 2358.8699
119339987 | F | LC | ETL.6900.POLE.WOOD | 40804806 | LAKEVLLE | SONOMA | 2020-07-09 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40804806 | 1932-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 8.9495e-06 | 1613.9003
119340558 | F | LC | ETL.1450.POLE.WDPS | 44420819 | SACTO | SACRAMENTO | 2020-07-07 | 2021-08-09 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420818 |  | 2-Pole Wood | THDE - Tri Post Dead End 60 | [7 empty] | 0.0024883 | 3765.6233
119341654 | B | LC | ETL.6280.POLE.WOOD | 40768800 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2020-10-27 | ETL.6280 | CARIBOU #2 | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768800 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Pin |  |  |  |  | 5.6473e-06 | 1739.9091
119341715 | F | LC | ETL.1450.POLE.WOOD | 42572849 | SACTO | SIERRA | 2020-07-01 | 2021-01-25 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 42572849 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 0.02878 | 1260.556
119354117 | E | LC | ETL.8580.TOWR | 40582580 | FRESNO | FRESNO | 2020-07-10 | 2021-05-19 | ETL.8580 | COALINGA #1-SAN MIGUEL | Damper-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40582580 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-07-07 | Porcelain | Suspension |  |  |  |  | 0.00010625
119356251 | E | LC | ETL.6980.POLE.WOOD | 40587392 | LAKEVLLE | SONOMA | 2020-07-10 | 2021-06-17 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587392 | 1953-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.21886 | 47.5538
119357901 | F | LC | ETL.1110.POLE.WDPS | 44423233 | TABLEMTN | HUMBOLDT | 2020-07-09 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44423232 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017842 | 3344.6018
119359540 | E | LC | ETL.7030.POLE.WOOD | 40827479 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-06-30 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827479 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.014304 | 94.9762
119363874 | E | LC | ETL.6900.POLE.WOOD | 40768049 | LAKEVLLE | SONOMA | 2020-07-13 | 2021-08-11 | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Vegetation | Overgrown | [Trim, Completed] |  | Tier 2 | HFRA Removal | COMP | 40768049 | 1974-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 2.662e-06 | 15.8932
119367393 | E | LC | ETL.1440.POLE.WDPS | 44837632 | SACTO | SACRAMENTO | 2020-07-13 | 2021-06-14 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 31.7066
119371188 | F | LC | ETL.2395.POLE.WDPS | 44550057 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-07-19 | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40753481 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.038536 | 47.5394
119378154 | E | LC | ETL.6290.POLE.WOOD | 40826460 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-08-15 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40826460 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.03969 | 4223.3467
119378268 | E | LC | ETL.6280.POLE.WOOD | 44259125 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-03-14 | ETL.6280 | CARIBOU #2 | Anchor-Wood | Missing | [Install] | Tier2 |  |  | DLFL | [11 empty] | 4.1639e-06 | 695.9825
119462304 | E | LC | ETL.2060.POLE.WOOD | 40584446 | LAKEVLLE | SONOMA | 2020-07-16 | 2021-06-24 | ETL.2060 | FORT BRAGG-ELK | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40584446 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.23653 | 190.0291
119480292 | F | LC | ETL.6760.POLE.WOOD | 40693560 | SACTO | SIERRA | 2020-07-20 | 2021-03-22 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693560 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.025793 | 110.8102
119481143 | E | LC | ETL.8340.POLE.WOOD | 40664772 | SACTO | SACRAMENTO | 2020-07-21 | 2021-06-30 | ETL.8340 | WEIMAR-HALSEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119482209 | F | LC | ETL.7820.POLE.WOOD | 40577247 | LAKEVLLE | HUMBOLDT | 2020-07-21 | 2020-07-31 | ETL.7820 | POTTER VALLEY-WILLITS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119497510 | F | LC | ETL.4040.POLE.STPS | 44328549 | TABLEMTN | NORTH VALLEY | 2020-07-23 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44328548 | 2015-12-10 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 3.1333e-06 | 3563.1055
119511835 | F | LC | ETL.6280.POLE.NWOD | 44259618 | TABLEMTN | NORTH VALLEY | 2020-07-23 | 2020-11-06 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44259618 | 2020-07-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-07-16 | Polymer | Dead End |  |  |  |  | 1.6591e-05 | 57.0038
119515325 | F | LC | ETL.1890.TOWR | 40584885 | FRESNO | FRESNO | 2020-07-23 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40584885 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2015-12-01 | Ceramic | Suspension |  |  |  |  | 2.2442e-08 | 7513.1909
119516160 | E | LC | ETL.1110.POLE.NWOD | 42603424 | TABLEMTN | HUMBOLDT | 2020-07-22 | 2021-07-26 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42603424 |  | Lattice Steel Pole | 3P DV - 3 Pole Double Vertical | 2021-05-28 | Ceramic | Dead End |  |  |  |  | 7.492e-05 | 221.5655
119535643 | E | LC | ETL.6310.POLE.WOOD | 40592300 | TABLEMTN | NORTH VALLEY | 2020-07-30 | 2021-10-21 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592300 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 1.5358e-06 | 5020.748 | 0.007711
119537080 | E | LC | ETL.8182.POLE.STPS | 44820896 | SACTO | SACRAMENTO | 2020-07-31 |  | ETL.8182 | CORDELIA #1 TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44813257 | 2019-05-22 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.6692e-07 | 2396.849 | 0.00087944
119567814 | F | LC | ETL.6880.POLE.WOOD | 44247809 | LAKEVLLE | HUMBOLDT | 2020-08-06 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44247809 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00060684 | 3328.4412
119575164 | E | LC | ETL.6220.POLE.WOOD | 40768681 | EUREKA | HUMBOLDT | 2020-08-06 | 2021-01-20 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40768681 |  | Single Wood Pole | T1-1A | 2021-01-18 | Polymer | Post |  |  |  |  | 0.077685
119594565 | E | LC | ETL.6890.POLE.WOOD | 40601387 | LAKEVLLE | SONOMA | 2020-08-10 | 2021-06-01 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119689562 | F | LC | ETL.1110.POLE.STPS | 44425587 | EUREKA | NORTH VALLEY | 2020-08-29 | 2021-03-24 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] |  | Tier 2 | Within Both | COMP | 44425586 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.7977e-05 | 264.248
119721694 | E | LC | ETL.1240.POLE.STPS | 44197156 | TABLEMTN |  | 2020-07-31 |  | ETL.1240 | CASCADE-COTTONWOOD | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44197155 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.0859e-07 | 4588.5854 | 0.00049829
119722522 | E | LC | ETL.4620.TOWR | 40681119 | PISMOBCH | LOS PADRES | 2020-08-04 | 2021-02-11 | ETL.4620 | DIABLO-MESA | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40681119 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-08-19 | Porcelain | Dead End |  |  |  |  | 1.3959e-05 | 838.9597
119722522 | E | LC | ETL.4620.TOWR | 40681119 | PISMOBCH | LOS PADRES | 2020-08-04 | 2021-02-11 | ETL.4620 | DIABLO-MESA | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40681119 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2011-08-19 | Ceramic | Dead End |  |  |  |  | 1.3959e-05 | 838.9597
119722932 | F | LC | ETL.1440.POLE.WOOD | 40590098 | SACTO | SIERRA | 2020-08-06 | 2021-05-11 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40590098 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00037523
119722932 | F | LC | ETL.1440.POLE.WOOD | 40590098 | SACTO | SIERRA | 2020-08-06 | 2021-05-11 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40590098 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00037523
119756193 | E | LC | ETL.1330.TOWR | 40815438 | SACTO | HUMBOLDT | 2020-08-18 | 2021-01-21 | ETL.1330 | CORTINA-MENDOCINO #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40815438 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Polymer | Suspension |  |  |  |  | 0.00035393 | 6302.062
119756193 | E | LC | ETL.1330.TOWR | 40815438 | SACTO | HUMBOLDT | 2020-08-18 | 2021-01-21 | ETL.1330 | CORTINA-MENDOCINO #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40815438 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.00035393 | 6302.062
119767526 | F | LC | ETL.6520.POLE.WOOD | 40826812 | SACTO | SIERRA | 2020-09-09 |  | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40826812 |  | Single Wood Pole | T-1 - Tri Post | 2019-09-18 | Polymer | Post |  |  |  |  | 0.013518 | 1158.8236
119769397 | E | LC | ETL.1110.TOWR | 40595080 | TABLEMTN | HUMBOLDT | 2020-07-15 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40595080 | 1952-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-04-02 | Glass | Suspension |  |  |  |  | 0.00037452 | 1249.9598
119773721 | F | LC | ETL.8210.POLE.WOOD | 40908237 | VICTOR | STOCKTON | 2020-06-19 |  | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908237 | 1953-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0043462 | 1186.8293
119780777 | F | LC | ETL.8240.POLE.WOOD | 40695143 | VICTOR | STOCKTON | 2020-09-12 |  | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40695143 |  | Single Wood Pole | T-1 - Tri Post | 2020-04-21 | Polymer | Post |  |  |  |  | 0.0050747 | 3815.678
119784102 | F | LC | ETL.8490.TOWR | 40594469 | PISMOBCH | LOS PADRES | 2020-09-14 | 2021-01-04 | ETL.8490 | ATASCADERO-SAN LUIS OBISPO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594469 | 1932-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0012442 | 142.4119
119789073 | E | LC | ETL.6300.POLE.WOOD | 44191074 | TABLEMTN | NORTH VALLEY | 2020-09-18 | 2021-09-01 | ETL.6300 | CARIBOU-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191074 |  | Single Wood Pole | T-1 - Tri Post | [7 empty] | 1.2874e-05 | 221.7338
119790353 | F | LC | ETL.1402.POLE.WDPS | 44550791 | VICTOR | STOCKTON | 2020-07-30 |  | ETL.1402 | SPRING GAP TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44550074 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.011331 | 174.1264
119800376 | E | LC | ETL.6810.INSL.NCER | 40677190 | EUREKA | HUMBOLDT | 2020-09-21 |  | ETL.6810 | ESSEX JCT-ORICK | Insulator-Wood | No Good/Out of Stdrd | [Replace] |  | Zone 1 | HFRA Removal | PEND | 40649183 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.02896
119803610 | E | LC | ETL.1110.POLE.WDPS | 44424055 | TABLEMTN | HUMBOLDT | 2020-09-23 | 2021-04-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424054 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00090359 | 4183.4624
119809840 | F | LC | ETL.7270.POLE.WOOD | 40909527 | TABLEMTN | NORTH VALLEY | 2020-08-13 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40909527 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0026293 | 5300.8838
119809951 | F | LC | ETL.6470.POLE.WOOD | 40824389 | SACTO | SIERRA | 2020-08-18 | 2021-07-06 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40824389 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.088003 | 221.5931
119812697 | F | LC | ETL.7170.POLE.WOOD | 44871203 | LAKEVLLE | NORTH BAY | 2020-08-27 |  | ETL.7170 | IGNACIO-ALTO-SAUSALITO #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871203 | 2019-09-19 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2019-09-19 | Glass | Suspension |  |  |  |  | 0.16488 | 727.8384
119856417 | F | LC | ETL.7030.POLE.WOOD | 40759192 | TABLEMTN | NORTH VALLEY | 2020-10-05 | 2021-02-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40759192 |  | Single Wood Pole | T2N | 2021-05-18 | Polymer | Post |  |  |  |  | 0.04126 | 31.7022
119899366 | E | LC | ETL.6980.POLE.WOOD | 40871400 | LAKEVLLE | SONOMA | 2020-10-07 | 2021-06-23 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871400 | 1985-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1985-01-01 | Polymer | Dead End |  |  |  |  | 0.15593 | 729.3502
119906072 | E | LC | ETL.1110.TOWR | 40596845 | TABLEMTN | HUMBOLDT | 2020-10-14 | 2021-04-06 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40596845 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-10-12 | Glass | Suspension |  |  |  |  | 1.1492e-06 | 284.8513
119944540 | E | LC | ETL.5980.TOWR | 40863927 | PISMOBCH | LOS PADRES | 2020-10-24 | 2021-06-03 | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40863927 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 5.0275e-10 | 3930.6758
119951360 | E | LC | ETL.7540.POLE.WOOD | 40824396 | LAKEVLLE | HUMBOLDT | 2020-10-27 | 2021-05-04 | ETL.7540 | MENDOCINO-WILLITS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119964967 | F | LC | ETL.8960.POLE.WDPS | 44236930 | FRESNO | FRESNO | 2020-10-27 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44236929 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 8.1722e-06
119967658 | B | LC | ETL.1110.POLE.WDPS | 44423986 | TABLEMTN | HUMBOLDT | 2020-08-26 | 2020-12-21 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423984 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00078428 | 3961.8772
119993356 | E | LC | ETL.8960.POLE.WOOD | 40662884 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Conductor-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40662884 | 1979-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1979-01-01 | Polymer | Post |  |  |  |  | 0.0020082
120012431 | E | LC | ETL.6070.TOWR | 40760720 | TABLEMTN | NORTH VALLEY | 2020-11-11 | 2021-06-17 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760720 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 0.0076551 | 190.8412
120012484 | E | LC | ETL.8060.POLE.WOOD | 40618174 | SACTO | SACRAMENTO | 2020-11-11 | 2021-05-20 | ETL.8060 | SPAULDING-SUMMIT | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
120128554 | E | LC | ETL.7590.POLE.STPS | 44984471 | MOSSLNDG | CENTRAL COAST | 2020-11-30 | 2021-03-08 | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44984442 | 2020-09-19 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.11208 | 158.2797
120135722 | E | LC | ETL.8650.INSL.NCER | 40691578 | FRESNO | FRESNO | 2020-12-04 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40660813 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1929-01-01 | Ceramic | Double Dead End - Suspension |  |  |  |  | 0.00625 | 6847.8872
120165122 | E | LC | ETL.3180.INSL | 40880334 | CONCORD | EAST BAY | 2020-12-08 | 2021-07-22 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
120634407 | B | LC | ETL.6750.POLE.WDPS | 44374914 | TABLEMTN | NORTH VALLEY | 2021-03-11 | 2021-03-11 | ETL.6750 | DELTA-MTN GATE JCT | Non-Routine Patrol | Investigate | [Air Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44374914 | 2012-08-04 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 2.5737e-05
120634407 | B | LC | ETL.6750.POLE.WDPS | 44374914 | TABLEMTN | NORTH VALLEY | 2021-03-11 | 2021-03-11 | ETL.6750 | DELTA-MTN GATE JCT | Non-Routine Patrol | Investigate | [Air Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44374914 | 2012-08-04 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 2.5737e-05
120634407 | B | LC | ETL.6750.POLE.WDPS | 44374914 | TABLEMTN | NORTH VALLEY | 2021-03-11 | 2021-03-11 | ETL.6750 | DELTA-MTN GATE JCT | Non-Routine Patrol | Investigate | [Air Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44374914 | 2012-08-04 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 2.5737e-05
120648165 | E | LC | ETL.1350.POLE.STPS | 45021995 | TABLEMTN | NORTH VALLEY | 2021-03-16 | 2021-06-30 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45021968 | 2020-06-02 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 6.5122e-05 | 3564.7319
120690111 | E | LC | ETL.1680.POLE.WDPS | 44298673 | LAKEVLLE | SONOMA | 2021-03-25 | 2021-03-29 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44298670 |  | 3-Pole Wood | FSS - Field Switch Structure | [7 empty] | 0.0013052 | 4639.9287
120696365 | E | LC | ETL.1350.TOWR | 40818768 | TABLEMTN | NORTH VALLEY | 2021-03-26 | 2021-08-09 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Steel | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818768 | 1943-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Dead End |  |  |  |  | 0.0041011 | 253.2084
120706808 | E | LC | ETL.1810.POLE.WDPS | 44322687 | EUREKA | HUMBOLDT | 2021-03-29 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44322684 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0035136 | 79.143 | 0.27808
120714058 | E | LC | ETL.7390.POLE.WDPS | 44412015 | LAKEVLLE | SONOMA | 2021-03-30 | 2021-06-28 | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120717559 | F | LC | ETL.1730.POLE.WOOD | 40876807 | MOSSLNDG | CENTRAL COAST | 2021-03-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40876807 | 1972-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1972-01-01 | Porcelain | Suspension |  |  |  |  | 0.0053267 | 0.065147
120717733 | F | LC | ETL.6880.POLE.WOOD | 40588917 | LAKEVLLE | SONOMA | 2021-03-31 | 2021-07-16 | ETL.6880 | FULTON-CALISTOGA | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40588917 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.0014233 | 4321.8276
120736904 | F | LC | ETL.4440.TOWR | 40871745 | TABLEMTN | NORTH VALLEY | 2021-03-23 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40871745 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 2.2227e-06 | 206.0033 | 0.00045788
120740381 | E | LC | ETL.8350.POLE.WOOD | 40768176 | VICTOR | STOCKTON | 2021-04-03 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40768176 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0038349 | 537.8945 | 2.0628
120745753 | F | LC | ETL.6890.POLE.WOOD | 40592661 | LAKEVLLE | SONOMA | 2021-04-05 | 2021-06-23 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40592661 | 1990-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.0012336 | 2488.3916
120747726 | B | LC | ETL.3830.TOWR | 40803327 | VICTOR | STOCKTON | 2021-04-05 | 2021-05-26 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803327 | 1989-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.2378e-07 | 569.3991
120752086 | B | LC | ETL.3830.TOWR | 40744432 | VICTOR | STOCKTON | 2021-04-06 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40744432 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 0.00034817 | 3195.5342
120754715 | E | LC | ETL.1890.TOWR | 40652053 | FRESNO | FRESNO | 2021-03-29 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40652053 | 1982-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1982-01-01 | Porcelain | Suspension |  |  |  |  | 1.4502e-06 | 5271.8569 | 0.0076454
120771267 | E | LC | ETL.8250.POLE.WOOD | 40812116 | VICTOR | STOCKTON | 2021-04-09 | 2021-04-13 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40812116 | 1957-01-01 | Single Wood Pole | SV-DE-90 - Single Vertical Dead End 90 |  | Porcelain | [5 empty] | 8.8823e-05 | 1665.905
120794312 | B | LC | ETL.3830.INSL | 40844772 | VICTOR | STOCKTON | 2021-04-09 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818418 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 0.00018831 | 428.7104
120803502 | E | LC | ETL.7140.POLE.WOOD | 40617122 | LAKEVLLE | SONOMA | 2021-04-12 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40617122 |  | Single Wood Pole | FIG4W - Wood X Arm |  | Ceramic | [5 empty] | 0.084628 | 63.3833 | 5.364
120806954 | F | LC | ETL.4316.POLE.STPS | 44383212 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44383211 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.004223 | 316.5913
120808950 | F | LC | ETL.8365.POLE.WOOD | 40912604 | EUREKA | HUMBOLDT | 2021-04-13 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Road | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40912604 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-04-22 | Glass | Double Dead End |  |  |  |  | 0.19011
120831366 | F | LC | ETL.5100.TOWR | 40587035 | MOSSLNDG | CENTRAL COAST | 2021-04-16 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40587035 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2005-01-01 | Non Ceramic | Dead End |  |  |  |  | 6.5744e-06 | 3558.4023 | 0.023394
120850290 | E | LC | ETL.8060.POLE.WOOD | 40771558 | SACTO | SACRAMENTO | 2021-04-20 | 2021-09-13 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771558 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Polymer | [5 empty] | 0.073691 | 221.5552
120858236 | F | LC | ETL.1820.POLE.STPS | 44674552 | EUREKA | HUMBOLDT | 2021-04-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44674475 | 2017-09-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0016997 | 63.3274
120859156 | F | LC | ETL.6690.POLE.NWOD | 44916821 | SACTO | SACRAMENTO | 2021-04-21 |  | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44916821 | 2020-05-06 | Light Duty Steel Pole | T2N | 2020-05-06 | Polymer | Post |  |  |  |  | 0.031281 | 142.4769
120878205 | F | LC | ETL.5463.TOWR | 40764878 | CONCORD | DIABLO | 2021-04-23 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40764878 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Non Ceramic | Dead End |  |  |  |  | 5.1509e-08 | 5196.8096 | 0.00026768
120878205 | F | LC | ETL.5463.TOWR | 40764878 | CONCORD | DIABLO | 2021-04-23 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40764878 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 5.1509e-08 | 5196.8096 | 0.00026768
120879311 | E | LC | ETL.1810.POLE.STPS | 44994664 | EUREKA | HUMBOLDT | 2021-04-22 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44994623 | 2020-04-20 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.8524e-06
120895875 | F | LC | ETL.5540.TOWR | 40590789 | TABLEMTN | NORTH VALLEY | 2021-04-14 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40590789 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 3.5652e-07 | 4276.2046 | 0.0015245
120900704 | F | LC | ETL.4440.TOWR | 40758436 | TABLEMTN | NORTH VALLEY | 2021-04-14 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40758436 | 1958-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 3.1714e-06 | 4463.6655
120907138 | B | LC | ETL.5920.INSL | 40792098 | CONCORD | EAST BAY | 2021-04-29 | 2021-06-29 | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762046 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-03-22 | Glass Silicone Coated | Suspension |  |  |  |  | 0.0022858 | 2709.8901
120907138 | B | LC | ETL.5920.INSL | 40792098 | CONCORD | EAST BAY | 2021-04-29 | 2021-06-29 | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762046 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0022858 | 2709.8901
120919613 | E | LC | ETL.5250.TOWR | 40866249 | CONCORD | DIABLO | 2021-05-01 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40866249 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 4.7025e-08 | 379.7729 | 1.7859e-05
120940129 | E | LC | ETL.2720.INSL | 40577582 | CONCORD | DIABLO | 2021-05-05 |  | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40575700 | 1959-01-01 | Lattice Steel Pole | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 0.00046777 | 0.065158 | 3.0479e-05
120940129 | E | LC | ETL.2720.INSL | 40577582 | CONCORD | DIABLO | 2021-05-05 |  | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40575700 | 1959-01-01 | Lattice Steel Pole | SUSP - Suspension (TWR) | 2021-06-03 | Glass | Suspension |  |  |  |  | 0.00046777 | 0.065158 | 3.0479e-05
120990466 | E | LC | ETL.6020.TOWR | 40819382 | TABLEMTN | NORTH VALLEY | 2021-05-06 | 2021-07-12 | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40819382 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.0015356 | 269.0298
121047511 | E | LC | ETL.1820.POLE.WDPS | 44557692 | EUREKA | HUMBOLDT | 2021-05-10 |  | ETL.1820 | HUMBOLDT-TRINITY | Crossarm-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44553902 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.23778 | 4462.79 | 1061.1595
121323131 | F | LC | ETL.5330.TOWR | 40762036 | MOSSLNDG | CENTRAL COAST | 2021-04-22 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762036 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 9.58e-07 | 348.953 | 0.0003343
121323131 | F | LC | ETL.5330.TOWR | 40762036 | MOSSLNDG | CENTRAL COAST | 2021-04-22 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762036 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 9.58e-07 | 348.953 | 0.0003343
121336710 | E | LC | ETL.5452.TOWR | 40604247 | CONCORD | DIABLO | 2021-04-23 |  | ETL.5452 | CONTRA COSTA-MORAGA #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40604247 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-01-01 | Ceramic | Suspension |  |  |  |  | 7.418e-07 | 15.8815 | 1.1781e-05
121338245 | E | LC | ETL.3500.TOWR | 40872938 | VICTOR | STOCKTON | 2021-04-26 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40872938 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 0.00068769 | 284.8886 | 0.19592
121346931 | E | LC | ETL.4450.TOWR | 40656762 | CONCORD | MISSION | 2021-04-29 | 2021-09-29 | ETL.4450 | CASTRO VALLEY-NEWARK | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40656762 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Dead End |  |  |  |  | 2.352e-05 | 4660.7414
121346931 | E | LC | ETL.4450.TOWR | 40656762 | CONCORD | MISSION | 2021-04-29 | 2021-09-29 | ETL.4450 | CASTRO VALLEY-NEWARK | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40656762 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.352e-05 | 4660.7414
121348629 | E | LC | ETL.5660.TOWR | 40746287 | CONCORD | MISSION | 2021-04-29 | 2021-08-24 | ETL.5660 | SAN RAMON-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746287 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Dead End |  |  |  |  | 1.5384e-07 | 442.8804
121348629 | E | LC | ETL.5660.TOWR | 40746287 | CONCORD | MISSION | 2021-04-29 | 2021-08-24 | ETL.5660 | SAN RAMON-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746287 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 1.5384e-07 | 442.8804
121348629 | E | LC | ETL.5660.TOWR | 40746287 | CONCORD | MISSION | 2021-04-29 | 2021-08-24 | ETL.5660 | SAN RAMON-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746287 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.5384e-07 | 442.8804
121351094 | E | LC | ETL.5290.TOWR | 40753095 | PISMOBCH | LOS PADRES | 2021-04-27 |  | ETL.5290 | MORRO BAY-MESA | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40753095 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-19 | Glass | Suspension |  |  |  |  | 4.4226e-09 | 5397.4297 | 2.3871e-05
121351094 | E | LC | ETL.5290.TOWR | 40753095 | PISMOBCH | LOS PADRES | 2021-04-27 |  | ETL.5290 | MORRO BAY-MESA | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40753095 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-07-18 | Ceramic | Suspension |  |  |  |  | 4.4226e-09 | 5397.4297 | 2.3871e-05
121370262 | F | LC | ETL.6950.POLE.WOOD | 40666285 | SACTO | SIERRA | 2021-05-03 |  | ETL.6950 | GOLD HILL #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40666285 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.0014042 | 5506.1968 | 7.732
121379840 | F | LC | ETL.8350.POLE.NWOD | 44918819 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44918819 | 2020-03-03 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-03 | Polymer | Post |  |  |  |  | 1.226e-05 | 2376.6802 | 0.029138
121380875 | A | LC | ETL.6040.TOWR | 40812059 | MOSSLNDG | CENTRAL COAST | 2021-05-21 | 2021-05-26 | ETL.6040 | MOSS LANDING-LOS BANOS | Emergency-Steel | Other | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40812059 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-05-24 | Porcelain | Double Dead End |  |  |  |  | 1.4148e-05 | 431.2029
121385390 | F | LC | ETL.4393.TOWR | 40586122 | SACTO | SIERRA | 2021-05-12 | 2021-10-11 | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40586122 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 1.1469e-05 | 269.0937
121397047 | E | LC | ETL.8250.POLE.WOOD | 45096581 | VICTOR | STOCKTON | 2021-05-25 | 2021-08-17 | ETL.8250 | CLAY-MARTEL | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45096581 | 2021-04-30 | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 3.6678e-06 | 4766.7061
121397760 | F | LC | ETL.8060.POLE.WOOD | 40771544 | SACTO | SIERRA | 2021-05-18 | 2021-05-28 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40771544 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.019525 | 3274.9534
121404095 | F | LC | ETL.6660.POLE.NWOD | 45084724 | TABLEMTN | NORTH VALLEY | 2021-05-18 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45084724 | 2021-03-04 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-04 | Polymer | Post |  |  |  |  | 1.3197e-10 | 3697.6668
121407768 | B | LC | ETL.6880.INSL.NCER | 40609812 | LAKEVLLE | SONOMA | 2021-05-26 | 2021-08-15 | ETL.6880 | FULTON-CALISTOGA | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
121419927 | B | LC | ETL.6470.INSL.CERA | 40731110 | SACTO | SACRAMENTO | 2021-05-27 | 2021-07-27 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693263 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.11625 | 300.6841
121425028 | F | LC | ETL.1420.TOWR | 40814350 | SACTO | SIERRA | 2021-05-27 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40814350 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm | 2016-08-08 | Polymer | Post |  |  |  |  | 6.3303e-05 | 63.348 | 0.0040101
121431168 | E | LC | ETL.2141.POLE.WOOD | 40588649 | MIDWAY | KERN | 2021-05-28 |  | ETL.2141 | VEDDER TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40588649 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.0013938 | 6774.418 | 9.4423
121473362 | F | LC | ETL.1440.POLE.WDPS | 44761206 | SACTO | SACRAMENTO | 2021-06-04 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40683594 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00058853 | 47.5526 | 0.027986
121485299 | E | LC | ETL.5140.POLE.WDPS | 44557766 | SACTO | SACRAMENTO | 2021-05-28 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44554023 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.3193e-05 | 63.3518 | 0.0033699
121487619 | E | LC | ETL.4316.POLE.STPS | 44838823 | TABLEMTN |  | 2021-05-29 |  | ETL.4316 | PARADISE-TABLE MTN | Crossarm-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44838788 | 2018-12-10 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0021193 | 4386.7925 | 9.297
121496102 | F | LC | ETL.8060.POLE.WOOD | 40593597 | SACTO | SIERRA | 2021-06-08 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40593597 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Polymer | [5 empty] | 0.098351 | 0.24228
121510618 | B | LC | ETL.4770.INSL.CERA | 44783717 | LAKEVLLE | SONOMA | 2021-06-09 | 2021-08-30 | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40683484 | 1971-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-05-30 | Ceramic | Double Dead End |  |  |  |  | 5.2322e-06 | 4623.6465
121510618 | B | LC | ETL.4770.INSL.CERA | 44783717 | LAKEVLLE | SONOMA | 2021-06-09 | 2021-08-30 | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40683484 | 1971-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.2322e-06 | 4623.6465
121513786 | A | LC | ETL.1600.TOWR | 40591172 | LAKEVLLE | SONOMA | 2021-06-10 | 2021-06-11 | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591172 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2019-12-16 | Glass | Dead End |  |  |  |  | 1.7267e-07 | 6535.0591
121513786 | A | LC | ETL.1600.TOWR | 40591172 | LAKEVLLE | SONOMA | 2021-06-10 | 2021-06-11 | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591172 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2021-06-10 | Porcelain | Dead End |  |  |  |  | 1.7267e-07 | 6535.0591
121516762 | F | LC | ETL.6770.POLE.WOOD | 40650023 | SACTO | SIERRA | 2021-06-05 | 2021-06-28 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40650023 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 0.0060358 | 1329.6379
121519780 | E | LC | ETL.7000.POLE.WOOD | 40877544 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40877544 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0022973 | 95.1115 | 0.2185
121523811 | F | LC | ETL.1440.POLE.STPS | 44338149 | SACTO | SIERRA | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44338148 | 2018-09-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.4643e-06 | 31.7066
121524159 | E | LC | ETL.6030.INSL | 40608469 | MIDWAY | KERN | 2021-06-05 |  | ETL.6030 | MIDWAY-WHIRLWIND | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40584224 | 1973-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 4.9065e-06 | 7017.4551 | 0.034431
121530970 | E | LC | ETL.1110.POLE.WDPS | 44424398 | TABLEMTN | HUMBOLDT | 2021-06-08 | 2021-07-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424396 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012557 | 5069.9922
121536357 | F | LC | ETL.1440.POLE.WDPS | 44765209 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40876963 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0020261 | 731.1277
121542073 | E | LC | ETL.5650.INSL.NCER | 45051163 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40604759 | 1942-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-02-15 | Glass | Dead End |  |  |  |  | 1.3147e-06 | 3105.6272 | 0.0040831
121542415 | F | LC | ETL.1350.POLE.STPS | 44994608 | TABLEMTN | NORTH VALLEY | 2021-06-15 | 2021-06-28 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44993924 | 2020-06-16 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 5.1506e-05 | 411.4229
121543785 | F | LC | ETL.1820.POLE.STPS | 44395495 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395494 | 2020-03-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0016102 | 2469.0088
121556314 | E | LC | ETL.7020.POLE.WDPS | 44417292 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.7020 | HAT CREEK #1-PIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44417290 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.5462 | 2345.6099 | 1281.1819
121557742 | E | LC | ETL.1820.POLE.NWOD | 44395265 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395265 | 2018-09-14 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2018-09-14 | Glass | Suspension |  |  |  |  | 0.00034824 | 110.7793 | 0.038578
121562045 | E | LC | ETL.5970.TOWR | 40753893 | PISMOBCH | LOS PADRES | 2021-06-16 |  | ETL.5970 | DIABLO-MIDWAY #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40753893 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-09-26 | Glass | Suspension |  |  |  |  | 7.0968e-08 | 948.955 | 6.7345e-05
121645246 | E | LC | ETL.5441.POLE.WDPS | 44553594 | TABLEMTN |  | 2021-06-19 |  | ETL.5441 | PIT #6 TAP | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553179 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0053309 | 300.6727 | 1.6029
121657969 | F | LC | ETL.3830.POLE.NWOD | 45050995 | VICTOR | STOCKTON | 2021-06-25 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45050995 |  | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 3.1897e-08 | 6204.2363
121660556 | E | LC | ETL.4410.INSL.NCER | 44815093 | CONCORD | EAST BAY | 2021-06-28 | 2021-09-14 | ETL.4410 | BRENTWOOD-KELSO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810712 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-26 | Glass | Suspension |  |  |  |  | 1.015e-07 | 4097.0996
121660556 | E | LC | ETL.4410.INSL.NCER | 44815093 | CONCORD | EAST BAY | 2021-06-28 | 2021-09-14 | ETL.4410 | BRENTWOOD-KELSO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810712 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-31 | Glass | Suspension |  |  |  |  | 1.015e-07 | 4097.0996
121662142 | E | LC | ETL.1450.INSL.NCER | 42573086 | SACTO | SIERRA | 2021-06-28 |  | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 42572871 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 0.0094183 | 15.8859 | 0.14962
121677406 | E | LC | ETL.1730.POLE.WDPS | 44413273 | MOSSLNDG | CENTRAL COAST | 2021-06-29 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44413272 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0008868 | 0.065147 | 5.7772e-05
121725251 | E | LC | ETL.6750.POLE.STPS | 45142312 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.6750 | DELTA-MTN GATE JCT | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45142257 | 2020-02-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP
121738692 | F | LC | ETL.6470.POLE.WOOD | 40672197 | SACTO | SIERRA | 2021-07-09 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40672197 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.017824 | 316.9161
121745753 | E | LC | ETL.2390.INSL.NCER | 40829968 | VICTOR | STOCKTON | 2021-07-13 | 2021-07-28 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44391215 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 2.0898e-05
121745753 | E | LC | ETL.2390.INSL.NCER | 40829968 | VICTOR | STOCKTON | 2021-07-13 | 2021-07-28 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44391215 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 2.0898e-05
121748116 | F | LC | ETL.1820.POLE.WOOD | 44562434 | EUREKA | HUMBOLDT | 2021-07-15 | 2021-09-30 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44562434 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Non Ceramic | Suspension |  |  |  |  | 0.056826 | 4084.9047
121748368 | E | LC | ETL.6650.POLE.WDPS | 44386861 | TABLEMTN | NORTH VALLEY | 2021-07-13 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44386859 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.015427 | 300.8844 | 4.6419
121760769 | F | LC | ETL.6020.TOWR | 40576226 | TABLEMTN | NORTH VALLEY | 2021-07-19 |  | ETL.6020 | MALIN-ROUND MTN #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40576226 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 6.7738e-07 | 237.3869
121781527 | B | LC | ETL.1402.INSL.NCER | 44929940 | VICTOR | YOSEMITE | 2021-07-21 | 2021-09-28 | ETL.1402 | SPRING GAP TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44928852 | 2019-11-18 | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2019-11-18 | Glass | Dead End |  |  |  |  | 0.00071813 | 1329.0924
121787066 | E | LC | ETL.9240.TOWR | 43249561 | PISMOBCH | LOS PADRES | 2021-07-22 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249561 |  | LATTICE STEEL TOWER | [9 empty] | 192.31
121787520 | F | LC | ETL.9240.TOWR | 43249512 | PISMOBCH | LOS PADRES | 2021-07-22 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 43249512 |  | LATTICE STEEL TOWER | [9 empty] | 158.4262
121788077 | B | LC | ETL.6280.POLE.WOOD | 40768847 | TABLEMTN | NORTH VALLEY | 2021-07-23 | 2021-09-23 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768847 |  | Single Wood Pole | T2N | 2020-04-10 | Polymer | Post |  |  |  |  | 1.4163e-05 | 711.7988
121803809 | B | LC | ETL.5260.INSL.CERA | 44377876 | PISMOBCH | LOS PADRES | 2021-07-26 | 2021-09-23 | ETL.5260 | MORRO BAY-DIABLO | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40810600 | 1969-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 2011-08-19 | Ceramic | Dead End |  |  |  |  | 2.2789e-06 | 618.0835
121808499 | F | LC | ETL.6220.POLE.WOOD | 40698355 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40698355 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.47029
121810993 | E | LC | ETL.7990.POLE.NWOD | 44837860 | SACTO | SIERRA | 2021-07-28 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44837860 | 2019-08-29 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End | 2019-08-29 | Polymer | Post |  |  |  |  | 1.2164e-07 | 1807.9032 | 0.0002199
121882662 | B | LC | ETL.6300.POLE.WDPS | 44976238 | TABLEMTN | NORTH VALLEY | 2021-08-10 | 2021-09-09 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 15.9194
121921048 | E | LC | ETL.8060.POLE.WOOD | 40586098 | SACTO | SIERRA | 2021-08-12 | 2021-10-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586098 |  | Single Wood Pole | T2N | 2020-11-15 | Polymer | Post |  |  |  |  | 0.003613 | 205.7345
122044120 | E | LC | ETL.6470.POLE.WOOD | 44398864 | SACTO | SIERRA | 2021-09-10 |  | ETL.6470 | COLGATE-ALLEGHANY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44398864 | 2017-04-26 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2017-04-26 | Ceramic | Suspension |  |  |  |  | 0.047263 | 680.6153 | 32.1682
118499210 | F | LC | ETL.7970.POLE.WOOD | 40598840 | SACTO | SIERRA | 2020-02-05 |  | ETL.7970 | SMARTVILLE-CAMP FAR WEST | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40598840 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00014886 | 2125.1653
118502644 | E | LC | ETL.2900.TOWR | 40650909 | MOSSLNDG | CENTRAL COAST | 2020-02-06 | 2020-06-01 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650909 | 1938-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1991-01-01 | Porcelain | Dead End |  |  |  |  | 0.0083905 | 570.9174
118502644 | E | LC | ETL.2900.TOWR | 40650909 | MOSSLNDG | CENTRAL COAST | 2020-02-06 | 2020-06-01 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650909 | 1938-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2020-11-25 | Glass | Dead End |  |  |  |  | 0.0083905 | 570.9174
118572491 | E | LC | ETL.7510.POLE.WOOD | 40862664 | LAKEVLLE | HUMBOLDT | 2020-02-10 | 2020-04-07 | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118591345 | B | LC | ETL.3180.INSL | 40880111 | CONCORD | EAST BAY | 2020-02-28 | 2020-07-20 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118595929 | B | LC | ETL.2270.INSL.CERA | 44737527 | CONCORD | EAST BAY | 2020-03-02 | 2020-06-29 | ETL.2270 | MARTINEZ-SOBRANTE | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118744622 | E | LC | ETL.5630.TOWR | 40762419 | TABLEMTN | NORTH VALLEY | 2020-03-25 | 2021-08-31 | ETL.5630 | ROCK CREEK-POE | Connector | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762419 | 1950-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2019-06-13 | Glass | Dead End |  |  |  |  | 2.0295e-06 | 254.0199
118914996 | E | LC | ETL.4510.TOWR | 40862553 | CONCORD | DIABLO | 2020-04-10 | 2021-10-04 | ETL.4510 | CONTRA COSTA-LAS POSITAS | Animal Guard-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862553 | 1939-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2009-01-01 | Ceramic | Suspension |  |  |  |  | 2.5101e-07 | 5098.2539
118962860 | B | LC | ETL.8351.POLE.WOOD | 40665504 | VICTOR | STOCKTON | 2020-04-27 | 2020-05-14 | ETL.8351 | PINE GROVE TAP | Switch | Out of Adjustment | [Repair, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.00036933 | 300.6168
118967511 | E | LC | ETL.8351.POLE.WOOD | 40874901 | VICTOR | STOCKTON | 2020-04-30 | 2021-06-28 | ETL.8351 | PINE GROVE TAP | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40874901 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Glass | [5 empty] | 0.00011999 | 31.7022
118993545 | F | LC | ETL.1402.POLE.WDPS | 44550730 | VICTOR | STOCKTON | 2020-05-04 |  | ETL.1402 | SPRING GAP TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44550069 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.006849 | 1329.0924
119016680 | E | LC | ETL.6980.INSL.NCER | 40637492 | LAKEVLLE |  | 2020-05-07 | 2021-06-21 | ETL.6980 | FORT ROSS-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119021237 | E | LC | ETL.1400.POLE.WOOD | 40856835 | VICTOR | YOSEMITE | 2020-05-04 | 2020-06-18 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40856835 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010247
119021237 | E | LC | ETL.1400.POLE.WOOD | 40856835 | VICTOR | YOSEMITE | 2020-05-04 | 2020-06-18 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40856835 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010247
119028745 | E | LC | ETL.4610.TOWR | 40647430 | PISMOBCH | LOS PADRES | 2020-05-07 | 2021-06-16 | ETL.4610 | DIABLO PP STANDBY SUPPLY | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119076281 | E | LC | ETL.8650.TOWR | 40584398 | FRESNO | YOSEMITE | 2020-05-26 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
119087623 | E | LC | ETL.7300.POLE.WOOD | 40676461 | TABLEMTN |  | 2020-05-29 | 2021-03-26 | ETL.7300 | KILARC-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40676461 |  | Single Wood Pole | T2N | 2021-03-12 | Polymer | Post |  |  |  |  | 0.0055467 | 1439.4246
119088379 | F | LC | ETL.6880.POLE.NWOD | 40809009 | LAKEVLLE | NORTH BAY | 2020-05-18 | 2020-11-10 | ETL.6880 | FULTON-CALISTOGA | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40809009 |  | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 7.0551e-06 | 537.9695
119102972 | F | LC | ETL.6300.POLE.NWOD | 44948626 | TABLEMTN | NORTH VALLEY | 2020-06-02 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44948626 | 2020-07-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-07-18 | Glass | Dead End |  |  |  |  | 0.0064352 | 47.5141
119107783 | F | LC | ETL.3740.TOWR | 40746108 | CONCORD | EAST BAY | 2020-05-11 | 2021-04-14 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746108 | 1922-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1991-01-01 | Porcelain | Suspension |  |  |  |  | 0.12178 | 15.88
119116651 | F | LC | ETL.6760.POLE.WOOD | 42549841 | SACTO | SIERRA | 2020-05-28 | 2021-06-17 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | DLFL
119117494 | F | LC | ETL.6470.POLE.WOOD | 40679439 | SACTO | SIERRA | 2020-05-29 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40679439 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0053709 | 205.7058
119118684 | E | LC | ETL.6280.POLE.WOOD | 40815719 | TABLEMTN | NORTH VALLEY | 2020-06-03 |  | ETL.6280 | CARIBOU #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40815719 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00060399 | 110.7793 | 0.06691
119118869 | F | LC | ETL.5930.TOWR | 40576197 | CONCORD | EAST BAY | 2020-05-27 | 2021-02-18 | ETL.5930 | PARKWAY-MORAGA | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40576197 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-26 | Glass | Suspension |  |  |  |  | 3.6999e-08 | 88.2694
119118900 | E | LC | ETL.7300.POLE.WOOD | 40602054 | TABLEMTN |  | 2020-06-03 | 2021-09-02 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602054 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.010514 | 79.1904
119128729 | E | LC | ETL.7260.POLE.WOOD | 40877806 | TABLEMTN | NORTH VALLEY | 2020-06-09 |  | ETL.7260 | KESWICK-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40877806 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.00053863 | 3848.5608 | 2.0729
119144856 | F | LC | ETL.7590.POLE.WOOD | 40581878 | MOSSLNDG | CENTRAL COAST | 2020-06-10 | 2020-07-28 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119148337 | E | LC | ETL.1730.POLE.WDPS | 44413437 | MOSSLNDG | CENTRAL COAST | 2020-06-11 | 2020-08-18 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44413434 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.9788e-05 | 0.066432
119149604 | B | LC | ETL.7290.INSL | 40699822 | TABLEMTN | NORTH VALLEY | 2020-06-11 | 2020-07-02 | ETL.7290 | KILARC-CEDAR CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40668408 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.13634 | 189.9176
119150537 | F | LC | ETL.9340.POLE.NWOD | 44180721 | FRESNO | YOSEMITE | 2020-06-02 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44180721 | 2015-06-18 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2015-06-18 | Non Ceramic | Suspension |  |  |  |  | 0.01192 | 5524.4275
119156187 | F | LC | ETL.3740.TOWR | 40746110 | CONCORD | DIABLO | 2020-06-08 | 2021-01-23 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746110 | 1958-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-03-16 | Glass | Dead End |  |  |  |  | 0.016333 | 0.065153
119156187 | F | LC | ETL.3740.TOWR | 40746110 | CONCORD | DIABLO | 2020-06-08 | 2021-01-23 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746110 | 1958-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.016333 | 0.065153
119166566 | E | LC | ETL.5980.TOWR | 40871223 | PISMOBCH | LOS PADRES | 2020-06-15 | 2020-09-01 | ETL.5980 | DIABLO-MIDWAY #3 | Vegetation-Tower | Overgrown | [Cage Clearing, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40871223 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-17 | Glass Silicone Coated | Suspension |  |  |  |  | 7.3716e-09 | 1629.5242
119166881 | F | LC | ETL.6280.POLE.WOOD | 40768896 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND | [11 empty] | 1.5039e-05 | 31.7041
119172196 | E | LC | ETL.1710.POLE.WDPS | 45058601 | MOSSLNDG | CENTRAL COAST | 2020-06-15 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40602325 | 1950-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00011989 | 31.6948 | 0.0037999
119196565 | F | LC | ETL.6470.POLE.WOOD | 40766731 | SACTO | SIERRA | 2020-06-22 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40766731 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.066008 | 269.0426
119205237 | E | LC | ETL.9340.POLE.WOOD | 44274112 | FRESNO | FRESNO | 2020-06-24 | 2020-09-09 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44274112 | 2015-06-20 | Single Wood Pole | T-1 - Tri Post | 2015-06-20 | Non Ceramic | Post |  |  |  |  | 0.0075446 | 5445.5674
119207008 | E | LC | ETL.6900.POLE.WOOD | 40580912 | LAKEVLLE | SONOMA | 2020-06-24 | 2020-12-07 | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40580912 | 1986-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 2.5154e-06 | 285.7849
119238174 | E | LC | ETL.8170.POLE.WOOD | 40602112 | EUREKA | HUMBOLDT | 2020-06-30 | 2021-06-08 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602112 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Ceramic | [5 empty] | 0.01029 | 63.3304
119302134 | F | LC | ETL.1110.POLE.WDPS | 44424401 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-02-11 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44424399 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00083679 | 3706.9577
119309112 | F | LC | ETL.4393.POLE.WDPS | 44172290 | SACTO | SACRAMENTO | 2020-07-02 |  | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44172289 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.5573e-05 | 1977.4294
119317515 | E | LC | ETL.7300.POLE.WOOD | 40877874 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-03-09 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877874 |  | Single Wood Pole | T-1 - Tri Post | 2018-06-03 | Polymer | Post |  |  |  |  | 0.00030097 | 4088.6799
119325028 | E | LC | ETL.6300.POLE.WOOD | 40698983 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-08-26 | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119325733 | E | LC | ETL.6290.POLE.WOOD | 40769607 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40769607 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.12463 | 4811.106 | 599.6189
119341198 | E | LC | ETL.8170.POLE.WOOD | 40803410 | EUREKA | HUMBOLDT | 2020-07-09 | 2021-06-25 | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803410 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.018707 | 300.6727
119354399 | A | LC | ETL.7180.POLE.WOOD | 40861610 | LAKEVLLE | SONOMA | 2020-07-10 | 2020-08-06 | ETL.7180 | IGNACIO-BOLINAS #2 | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40861610 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper |  | Porcelain | [5 empty] | 7.3513e-06 | 1504.5828
119355104 | E | LC | ETL.4220.INSL.CERA | 44388494 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2020-07-17 | ETL.4220 | WOODLEAF-PALERMO | Damper-Wood | Missing | [Install] | Tier2 |  |  | DLFL
119357380 | F | LC | ETL.7030.POLE.WOOD | 40616850 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40616850 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.046434 | 66.5607
119359644 | E | LC | ETL.7030.POLE.WOOD | 40868426 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-05-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
119363587 | F | LC | ETL.4220.POLE.STPS | 44558318 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2020-09-03 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44557885 | 2019-07-27 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0011981 | 174.0849
119370288 | E | LC | ETL.6380.POLE.WOOD | 40876728 | LAKEVLLE | SONOMA | 2020-07-14 | 2021-04-26 | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119466693 | E | LC | ETL.7030.POLE.WOOD | 40815888 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2020-11-06 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119467795 | F | LC | ETL.6290.POLE.WOOD | 40614991 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-11-18 | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40614991 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.50926 | 0.0778
119475055 | E | LC | ETL.1450.POLE.WDPS | 44558985 | SACTO | SACRAMENTO | 2020-07-16 | 2020-08-17 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 47.5273
119487030 | F | LC | ETL.5300.TOWR | 40587294 | PISMOBCH | LOS PADRES | 2020-07-22 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40587294 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 1.1162e-06 | 3768.9041
119487030 | F | LC | ETL.5300.TOWR | 40587294 | PISMOBCH | LOS PADRES | 2020-07-22 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40587294 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.1162e-06 | 3768.9041
119496199 | F | LC | ETL.4393.TOWR | 40814103 | SACTO | SIERRA | 2020-07-23 | 2021-03-18 | ETL.4393 | DRUM-HIGGINS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40814103 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.00013891 | 364.0427
119547492 | E | LC | ETL.1470.POLE.WOOD | 41176386 | LAKEVLLE | HUMBOLDT | 2020-07-31 | 2021-03-08 | ETL.1470 | EAGLE ROCK-CORTINA | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119554802 | E | LC | ETL.6861.POLE.WOOD | 40698967 | LAKEVLLE | HUMBOLDT | 2020-08-04 | 2021-09-13 | ETL.6861 | KONOCTI-EAGLE ROCK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.00014503 | 6364.124
119560948 | E | LC | ETL.7180.POLE.WOOD | 40657346 | LAKEVLLE | NORTH BAY | 2020-08-04 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40657346 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 3.3225e-06 | 117.5681 | 0.00039062
119569135 | F | LC | ETL.6220.POLE.WOOD | 40586749 | EUREKA | HUMBOLDT | 2020-08-06 | 2021-06-22 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40586749 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.41295
119608796 | E | LC | ETL.7490.POLE.NWOD | 44735741 | EUREKA | HUMBOLDT | 2020-08-13 | 2021-08-04 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44735741 | 2019-04-02 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-04-02 | Polymer | Dead End |  |  |  |  | 0.00037191 | 95.0009
119609137 | B | LC | ETL.8365.POLE.WOOD | 40912623 | EUREKA | HUMBOLDT | 2020-08-13 | 2020-11-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912623 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | Dead End |  |  |  |  | 0.80228
119619188 | B | LC | ETL.8650.POLE.NWOD | 44420184 | FRESNO | FRESNO | 2020-08-14 | 2020-12-11 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420184 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0039923 | 6847.8872
119628531 | E | LC | ETL.6870.POLE.WOOD | 42574902 | SACTO | SIERRA | 2020-08-17 | 2021-06-07 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119631862 | F | LC | ETL.6870.POLE.NWOD | 40589913 | SACTO | SIERRA | 2020-08-17 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40589913 |  | Light Duty Steel Pole | T-1 - Tri Post | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.0021792 | 0.065152
119643309 | B | LC | ETL.8650.POLE.NWOD | 44420154 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44420154 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0042008 | 4117.0835
119643313 | B | LC | ETL.8650.POLE.NWOD | 44420193 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420193 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0049846 | 3843.0691
119652843 | F | LC | ETL.4770.TOWR | 40587523 | LAKEVLLE | SONOMA | 2020-08-21 | 2021-04-20 | ETL.4770 | GEYSERS #17-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587523 | 1982-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-05-30 | Glass | Dead End |  |  |  |  | 0.00079051 | 1472.3439
119652843 | F | LC | ETL.4770.TOWR | 40587523 | LAKEVLLE | SONOMA | 2020-08-21 | 2021-04-20 | ETL.4770 | GEYSERS #17-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587523 | 1982-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00079051 | 1472.3439
119695151 | E | LC | ETL.1650.POLE.WOOD | 40818244 | LAKEVLLE | SONOMA | 2020-08-31 | 2021-03-23 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119713494 | F | LC | ETL.6490.POLE.WOOD | 40599636 | SACTO | SIERRA | 2020-08-31 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40599636 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Post |  |  |  |  | 0.072145 | 189.8873
119716113 | E | LC | ETL.8170.POLE.WOOD | 40751121 | EUREKA | HUMBOLDT | 2020-09-02 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40751121 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.34157 | 253.2652 | 86.5079
119763267 | B | LC | ETL.6470.POLE.WOOD | 40874698 | SACTO | SIERRA | 2020-09-08 | 2020-10-07 | ETL.6470 | COLGATE-ALLEGHANY | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40874698 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Post |  |  |  |  | 0.0029667 | 237.3428
119766825 | F | LC | ETL.6760.POLE.WOOD | 40693406 | SACTO | SIERRA | 2020-09-09 | 2021-02-12 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40693406 |  | Single Wood Pole | T2N | 2021-03-29 | Polymer | Post |  |  |  |  | 0.0091168 | 63.3392
119775880 | F | LC | ETL.9090.POLE.WOOD | 40756587 | PISMOBCH | LOS PADRES | 2020-09-10 | 2021-03-11 | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756587 |  | Single Wood Pole | SS2 - Susp. Steel Double CIR. | 2018-09-15 | Glass | Suspension |  |  |  |  | 0.0056696 | 537.8833
119778811 | F | LC | ETL.1110.POLE.WDPS | 44423307 | TABLEMTN | HUMBOLDT | 2020-09-08 | 2021-02-10 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44423305 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0010383 | 3499.2989
119783654 | E | LC | ETL.6220.POLE.WOOD | 40586721 | EUREKA | HUMBOLDT | 2020-09-14 | 2021-04-21 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40586721 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.050761 | 633.9066
119804163 | F | LC | ETL.6280.POLE.NWOD | 44677442 | TABLEMTN | NORTH VALLEY | 2020-08-07 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44677442 | 2018-11-18 | Light Duty Steel Pole | T1-1A | 2018-11-18 | Polymer | Post |  |  |  |  | 3.4472e-07 | 15.8815
119817964 | F | LC | ETL.8350.POLE.WOOD | 40579951 | VICTOR | STOCKTON | 2020-09-11 | 2021-01-20 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40579951 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0014061 | 1556.7621
119844648 | A | LC | ETL.1110.INSL.NCER | 44772145 | TABLEMTN | HUMBOLDT | 2020-10-02 | 2020-10-21 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Emergency | Storm Related | [Repair, Completed, Completed] | Tier2 |  |  | COMP
119850831 | F | LC | ETL.8365.POLE.NWOD | 40906689 | EUREKA | HUMBOLDT | 2020-09-17 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40906689 | 2010-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.024625
119887446 | E | LC | ETL.7030.POLE.WOOD | 40616871 | TABLEMTN | NORTH VALLEY | 2020-10-05 | 2021-05-20 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40616871 |  | Single Wood Pole | T2N | 2021-05-17 | Polymer | Post |  |  |  |  | 0.0086942 | 0.065151
119892260 | E | LC | ETL.6650.POLE.NWOD | 44917356 | TABLEMTN | NORTH VALLEY | 2020-10-12 | 2021-05-11 | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44917356 | 2020-04-08 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2020-04-08 | Glass | Dead End |  |  |  |  | 0.00016494 | 363.0611
119912097 | E | LC | ETL.8365.POLE.WOOD | 43603136 | EUREKA | HUMBOLDT | 2020-10-09 | 2021-05-03 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 43603136 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Other |  |  |  |  | 0.0083219
119917427 | F | LC | ETL.7380.POLE.WDPS | 44562892 | MOSSLNDG | CENTRAL COAST | 2020-09-21 | 2021-04-05 | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44562359 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.57242 | 0.065148
119975211 | F | LC | ETL.8270.POLE.WOOD | 40649680 | MOSSLNDG | CENTRAL COAST | 2020-09-28 |  | ETL.8270 | VIEJO-MONTEREY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40649680 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.099705 | 0.065148
120016099 | E | LC | ETL.2911.INSL.NCER | 44271758 | MOSSLNDG | CENTRAL COAST | 2020-11-10 |  | ETL.2911 | LLAGAS-HOLLISTER | Insulator-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44271757 |  | Single Wood Pole | 3HP-T - 3 Horizontal Post Tap |  | Polymer | Dead End |  |  |  |  | 8.7878e-06
120076229 | E | LC | ETL.6500.POLE.WOOD | 40757201 | TABLEMTN | NORTH VALLEY | 2020-06-22 | 2020-11-20 | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40757201 |  | Single Wood Pole | T-1 - Tri Post | 2019-09-10 | Polymer | Post |  |  |  |  | 0.0010171 | 3374.0149
120084873 | E | LC | ETL.8365.INSL.NCER | 40922458 | EUREKA | HUMBOLDT | 2020-11-20 | 2021-05-07 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912649 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.075972
120131232 | E | LC | ETL.8650.INSL.CERA | 40673983 | FRESNO | FRESNO | 2020-12-04 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40646342 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1929-01-01 | Porcelain | Suspension |  |  |  |  | 0.0032518 | 50.078
120204642 | E | LC | ETL.6020.TOWR | 40684090 | TABLEMTN | NORTH VALLEY | 2020-12-15 | 2021-06-15 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40684090 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00042658 | 316.4942
120228628 | B | LC | ETL.6240.POLE.WOOD | 40665090 | MOSSLNDG | CENTRAL COAST | 2020-12-22 | 2021-02-01 | ETL.6240 | BURNS-LONE STAR #2 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40665090 |  | Single Wood Pole | T-1 - Tri Post | 2020-04-14 | Polymer | Post |  |  |  |  | 0.95988 | 15.8866
120237448 | F | LC | ETL.7590.POLE.STPS | 44984469 | MOSSLNDG | CENTRAL COAST | 2020-11-30 | 2021-02-09 | ETL.7590 | MONTA VISTA-BURNS | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44984442 | 2020-09-19 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.11208 | 158.2797
120642697 | B | LC | ETL.4620.INSL.NCER | 44775196 | PISMOBCH | LOS PADRES | 2021-03-12 | 2021-03-24 | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40869590 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-19 | Glass | Suspension |  |  |  |  | 2.6192e-09 | 1585.3566
120642697 | B | LC | ETL.4620.INSL.NCER | 44775196 | PISMOBCH | LOS PADRES | 2021-03-12 | 2021-03-24 | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40869590 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.6192e-09 | 1585.3566
120667003 | E | LC | ETL.8290.POLE.WOOD | 40601157 | TABLEMTN | NORTH VALLEY | 2021-03-20 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40601157 |  | Single Wood Pole | T-1 - Tri Post | 2019-06-07 | Polymer | Post |  |  |  |  | 0.00019671 | 3955.5208 | 0.77809
120678258 | F | LC | ETL.4950.TOWR | 40869836 | LAKEVLLE | SONOMA | 2021-03-23 |  | ETL.4950 | FULTON-LAKEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40869836 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-07-05 | Ceramic | Suspension |  |  |  |  | 0.0014053 | 665.4853 | 0.93522
120683456 | E | LC | ETL.4440.INSL.CERA | 40634243 | TABLEMTN | NORTH VALLEY | 2021-03-23 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40599058 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.00018848 | 205.7502 | 0.03878
120690378 | E | LC | ETL.8290.POLE.WOOD | 40601143 | TABLEMTN | NORTH VALLEY | 2021-03-25 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40601143 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.007942 | 762.0938 | 6.0525
120705120 | E | LC | ETL.3840.INSL.CERA | 40883238 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40861464 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 6.1868e-06 | 1962.8882 | 0.012144
120705845 | F | LC | ETL.4870.TOWR | 40596799 | FRESNO | FRESNO | 2021-03-25 | 2021-08-19 | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40596799 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.8751e-08 | 6378.9966
120707342 | F | LC | ETL.1070.POLE.NWOD | 44727550 | VICTOR | YOSEMITE | 2021-03-26 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44727550 | 2019-03-25 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-03-25 | Polymer | Post |  |  |  |  | 4.3712e-09 | 2364.1092
120712833 | E | LC | ETL.1530.INSL | 40834426 | SACTO | SACRAMENTO | 2021-03-30 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40809714 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 7.6538e-05 | 158.2629 | 0.012113
120724952 | E | LC | ETL.7390.POLE.NWOD | 44965315 | LAKEVLLE | SONOMA | 2021-04-01 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44965315 | 2020-08-28 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-08-28 | Glass | Suspension |  |  |  |  | 0.0044222
120735861 | E | LC | ETL.4000.POLE.WOOD | 40903940 | VICTOR | YOSEMITE | 2021-03-31 | 2021-10-14 | ETL.4000 | TESLA-SALADO-MANTECA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40903940 | 2013-04-22 | Single Wood Pole | DDE - Double Dead End | 2013-04-22 | Porcelain | Dead End |  |  |  |  | 0.00054346 | 1998.7472 | 1.0862
120748961 | F | LC | ETL.7140.POLE.NWOD | 45017302 | LAKEVLLE | SONOMA | 2021-04-06 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45017302 | 2020-11-16 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2020-11-16 | Glass | Suspension |  |  |  |  | 0.00051204 | 720.4106
120756874 | F | LC | ETL.4393.POLE.WDPS | 44172142 | SACTO | SACRAMENTO | 2021-04-07 | 2021-06-11 | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL
120763643 | E | LC | ETL.7040.POLE.WOOD | 40758090 | TABLEMTN | NORTH VALLEY | 2021-04-08 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758090 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.036321 | 1981.5565 | 71.9722
120808149 | F | LC | ETL.5660.TOWR | 40582067 | CONCORD | DIABLO | 2021-04-13 |  | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40582067 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 2.5381e-07 | 2094.0012 | 0.00053147
120808149 | F | LC | ETL.5660.TOWR | 40582067 | CONCORD | DIABLO | 2021-04-13 |  | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40582067 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Double Dead End |  |  |  |  | 2.5381e-07 | 2094.0012 | 0.00053147
120810921 | F | LC | ETL.9100.POLE.WOOD | 44191223 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191223 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 6.194e-06 | 2878.6064
120812403 | F | LC | ETL.9100.POLE.WOOD | 44191870 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier3 | Non-HFTD | Non-HFRA | DLFL | 44191870 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 2.0841e-06 | 1411.7097
120816207 | E | LC | ETL.3500.INSL | 40603347 | VICTOR | STOCKTON | 2021-04-14 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40579801 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 2.9032e-05 | 1423.9296 | 0.04134
120818896 | B | LC | ETL.5091.INSL | 41122543 | MOSSLNDG | CENTRAL COAST | 2021-04-14 | 2021-05-20 | ETL.5091 | METCALF-MONTA VISTA #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40662908 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0092224 | 15.8866
120820039 | E | LC | ETL.4050.POLE.WOOD | 40861038 | LAKEVLLE | SONOMA | 2021-04-15 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40861038 | 1987-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1970-01-01 | Ceramic | Post |  |  |  |  | 2.0451e-05 | 2369.2024 | 0.048453
120826198 | E | LC | ETL.6500.POLE.WOOD | 40766446 | TABLEMTN | SACRAMENTO | 2021-04-15 |  | ETL.6500 | COLGATE-PALERMO | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40766446 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.00053882 | 3247.3733 | 1.7498
120835377 | F | LC | ETL.8365.POLE.NWOD | 44356200 | EUREKA | HUMBOLDT | 2021-04-17 | 2021-08-02 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44356200 | 2016-06-21 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2016-06-21 | Polymer | Post |  |  |  |  | 0.0026111
120846898 | E | LC | ETL.3500.INSL | 40877690 | VICTOR | STOCKTON | 2021-04-19 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40856710 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 0.00010999 | 95.0148 | 0.01045
120850795 | F | LC | ETL.1820.POLE.NWOD | 45070079 | EUREKA | HUMBOLDT | 2021-04-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45070079 | 2021-03-19 | Light Duty Steel Pole | 3P SV - 3 Pole Single Vertical | 2021-03-19 | Glass | Suspension |  |  |  |  | 0.0016062 | 0.065148
120861641 | F | LC | ETL.5780.TOWR | 40811157 | VICTOR | STOCKTON | 2021-04-21 |  | ETL.5780 | TIGER CREEK-ELECTRA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40811157 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 1.183e-05 | 1939.4662 | 0.022943
120871983 | E | LC | ETL.3500.INSL | 40669941 | VICTOR | STOCKTON | 2021-04-22 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40643017 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 0.0013941 | 6523.0078 | 9.0937
120880249 | E | LC | ETL.1810.POLE.STPS | 44996084 | EUREKA | HUMBOLDT | 2021-04-24 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Ground Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44996004 | 2020-04-15 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.8831e-08
120884457 | E | LC | ETL.7270.POLE.NWOD | 44649333 | TABLEMTN | NORTH VALLEY | 2021-04-26 |  | ETL.7270 | KESWICK-TRINITY | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44649333 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.0019805 | 1347.3177 | 2.6683
120901265 | F | LC | ETL.7100.POLE.WOOD | 40861000 | EUREKA | HUMBOLDT | 2021-04-29 | 2021-10-26 | ETL.7100 | HUMBOLDT BAY-RIO DELL JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40861000 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.17613 | 300.5609
120908642 | E | LC | ETL.7000.POLE.WOOD | 40770052 | TABLEMTN | NORTH VALLEY | 2021-04-30 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40770052 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0061942 | 458.7379 | 2.8415
120910401 | E | LC | ETL.6890.POLE.WOOD | 40808470 | LAKEVLLE | SONOMA | 2021-04-30 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40808470 | 1993-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Other |  |  |  |  | 6.3379e-05 | 2757.8179 | 0.17479
120939354 | E | LC | ETL.4870.TOWR | 40576599 | FRESNO | FRESNO | 2021-05-05 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576599 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 4.7439e-05 | 0.066432 | 3.1515e-06
120940067 | E | LC | ETL.2720.INSL | 40828517 | CONCORD | DIABLO | 2021-05-05 |  | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40804633 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.00017387 | 0.065147 | 1.1327e-05
121340593 | E | LC | ETL.4440.POLE.NWOD | 40674608 | TABLEMTN | NORTH VALLEY | 2021-05-15 |  | ETL.4440 | CARIBOU-TABLE MTN | Anchor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40674608 |  | Lattice Steel Pole | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 2.2347e-05 | 6474.1455 | 0.14468
121361887 | E | LC | ETL.5920.INSL | 40718527 | CONCORD | EAST BAY | 2021-04-29 |  | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40670684 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 6.1872e-07 | 284.7321 | 0.00017617
121361887 | E | LC | ETL.5920.INSL | 40718527 | CONCORD | EAST BAY | 2021-04-29 |  | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40670684 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.1872e-07 | 284.7321 | 0.00017617
121367795 | E | LC | ETL.5660.TOWR | 40805039 | CONCORD | MISSION | 2021-04-29 | 2021-08-24 | ETL.5660 | SAN RAMON-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805039 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.8579e-08 | 3043.1921
121367795 | E | LC | ETL.5660.TOWR | 40805039 | CONCORD | MISSION | 2021-04-29 | 2021-08-24 | ETL.5660 | SAN RAMON-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805039 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 5.8579e-08 | 3043.1921
121369008 | F | LC | ETL.1820.POLE.NWOD | 45014023 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45014023 | 2020-11-08 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-11-08 | Glass | Suspension |  |  |  |  | 0.0038844 | 31.7081
121373656 | F | LC | ETL.4550.TOWR | 40765238 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40765238 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.2232e-07 | 3559.869 | 0.00043546
121379781 | B | LC | ETL.4440.POLE.NWOD | 40873458 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-29 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873458 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.00075924 | 4683.9302
121384205 | F | LC | ETL.8350.POLE.NWOD | 44885874 | VICTOR | STOCKTON | 2021-05-08 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44885874 | 2019-10-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-10-03 | Polymer | Dead End |  |  |  |  | 1.2826e-06 | 1506.0547 | 0.0019317
121384336 | E | LC | ETL.1651.POLE.NWOD | 44144180 | LAKEVLLE | SONOMA | 2021-05-12 |  | ETL.1651 | MISSION POWER TAP | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44144180 |  | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper |  | Polymer | Dead End |  |  |  |  | 9.5582e-07 | 4673.4668 | 0.004467
121384863 | E | LC | ETL.1650.INSL.CERA | 40620028 | LAKEVLLE | SONOMA | 2021-05-12 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40594051 | 1993-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1966-01-01 | Porcelain | Dead End |  |  |  |  | 0.00012446 | 3263.3687 | 0.40617
121385107 | F | LC | ETL.6500.POLE.WOOD | 40874627 | SACTO | SIERRA | 2021-05-10 | 2021-06-30 | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40874627 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.0032953 | 2074.7698
121385399 | E | LC | ETL.5930.TOWR | 40762532 | CONCORD | DIABLO | 2021-05-13 |  | ETL.5930 | PARKWAY-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40762532 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-04 | Glass | Suspension |  |  |  |  | 3.4737e-07 | 426.2318 | 0.00014806
121385399 | E | LC | ETL.5930.TOWR | 40762532 | CONCORD | DIABLO | 2021-05-13 |  | ETL.5930 | PARKWAY-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40762532 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-07-30 | Glass | Suspension |  |  |  |  | 3.4737e-07 | 426.2318 | 0.00014806
121391778 | E | LC | ETL.8450.POLE.NWOD | 44666420 | MIDWAY | KERN | 2021-05-17 |  | ETL.8450 | ARCO-POLONIO PASS PP | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44666420 | 2018-10-02 | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 1.2576e-05 | 7441.7637 | 0.09359
121396130 | E | LC | ETL.6760.POLE.WOOD | 40669956 | SACTO | SIERRA | 2021-05-13 | 2021-06-23 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40669956 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.076665 | 332.3255
121396616 | F | LC | ETL.6660.POLE.NWOD | 45058610 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45058610 | 2020-05-08 | Light Duty Steel Pole | T-1 - Tri Post | 2020-05-08 | Polymer | Post |  |  |  |  | 1.0361e-10 | 4357.7954
121397445 | F | LC | ETL.6890.POLE.NWOD | 44861133 | LAKEVLLE | HUMBOLDT | 2021-05-18 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44861133 | 2019-11-05 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-11-05 | Polymer | Post |  |  |  |  | 9.1548e-07 | 3485.2612
121401786 | E | LC | ETL.6290.POLE.WOOD | 40870646 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40870646 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.019473 | 3179.5974 | 61.9157
121406849 | E | LC | ETL.4220.POLE.STPS | 44558365 | TABLEMTN |  | 2021-05-25 | 2021-06-17 | ETL.4220 | WOODLEAF-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44557885 | 2019-07-27 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0011981 | 174.0849
121416474 | F | LC | ETL.1820.POLE.WDPS | 44560458 | EUREKA | HUMBOLDT | 2021-05-27 | 2021-07-15 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL
121417473 | E | LC | ETL.6870.POLE.WOOD | 40873859 | SACTO | SIERRA | 2021-05-21 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40873859 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.068715 | 0.065152 | 0.0044769
121451356 | E | LC | ETL.7561.POLE.WOOD | 40673578 | SACTO | SIERRA | 2021-06-01 |  | ETL.7561 | OXBOW TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40673578 |  | Single Wood Pole | 3P DDE-A - 3 Pole Double Dead End Angle |  | Ceramic | Pin |  |  |  |  | 0.0021516 | 6059.3994 | 13.0375
121453530 | F | LC | ETL.8365.POLE.WOOD | 40750489 | EUREKA | HUMBOLDT | 2021-05-27 | 2021-07-12 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40750489 | 2010-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0087131 | 300.6168
121471464 | E | LC | ETL.8290.POLE.WOOD | 40875814 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40875814 |  | Single Wood Pole | T2N | 2019-06-14 | Polymer | Post |  |  |  |  | 0.0070072 | 766.1852 | 5.3688
121471697 | E | LC | ETL.5452.TOWR | 40804947 | CONCORD | DIABLO | 2021-05-28 | 2021-12-02 | ETL.5452 | CONTRA COSTA-MORAGA #1 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40804947 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-01-01 | Ceramic | Suspension |  |  |  |  | 2.076e-07 | 31.7066
121481353 | B | LC | ETL.1350.POLE.STPS | 44409296 | TABLEMTN |  | 2021-06-04 | 2021-06-21 | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44409293 | 2017-10-28 | 3-Pole Non Wood | 3HP - 3 Horizontal Post | [7 empty] | 0.00088822 | 316.4942
121492307 | F | LC | ETL.7780.POLE.WOOD | 40824299 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7780 | PHILO JCT-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40824299 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.00011954 | 411.3464 | 0.049174
121492993 | E | LC | ETL.6890.POLE.WOOD | 40759956 | LAKEVLLE | SONOMA | 2021-06-02 | 2021-06-24 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40759956 | 1990-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.0031481 | 2314.6917
121493121 | F | LC | ETL.4770.TOWR | 40819566 | LAKEVLLE | SONOMA | 2021-06-01 |  | ETL.4770 | GEYSERS #17-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40819566 | 1987-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 5.8993e-07 | 2550.4885 | 0.0015046
121493617 | E | LC | ETL.8250.POLE.WDPS | 44254767 | VICTOR | STOCKTON | 2021-06-01 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44254766 |  | 3-Pole Wood | 1VP - 1 Vertical | [7 empty] | 0.00068987 | 3548.5354 | 2.448
121499782 | E | LC | ETL.6020.TOWR | 40821488 | TABLEMTN | NORTH VALLEY | 2021-06-03 |  | ETL.6020 | MALIN-ROUND MTN #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40821488 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.4075e-07 | 570.017 | 8.0231e-05
121516209 | E | LC | ETL.6500.POLE.WOOD | 43690666 | SACTO | NORTH VALLEY | 2021-06-09 | 2021-07-19 | ETL.6500 | COLGATE-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 43690666 | 2015-08-20 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2015-08-20 | Porcelain | Dead End |  |  |  |  | 0.01652 | 4948.6592
121516938 | F | LC | ETL.5100.TOWR | 40811255 | MOSSLNDG | SAN JOSE | 2021-06-03 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40811255 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2005-01-01 | Non Ceramic | Suspension |  |  |  |  | 2.3217e-05 | 3053.9343 | 0.070903
121518848 | E | LC | ETL.5650.INSL | 40891148 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40868134 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 7.1709e-07 | 4295.9818 | 0.0030806
121524158 | E | LC | ETL.1350.POLE.WDPS | 44552460 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44551650 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.035591 | 95.0065 | 3.3814
121524743 | E | LC | ETL.1350.POLE.WDPS | 44552506 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44551646 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.088707 | 250.5059 | 22.2215
121525467 | F | LC | ETL.4040.POLE.STPS | 44647142 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44646862 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.7486e-05 | 2.8233
121526016 | F | LC | ETL.1350.POLE.WDPS | 44551497 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40871617 | 1943-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.089476 | 253.4679
121530618 | B | LC | ETL.4040.INSL.NCER | 44874424 | TABLEMTN | NORTH VALLEY | 2021-06-12 | 2021-07-26 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44874419 | 2020-01-18 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2020-01-18 | Polymer | Dead End |  |  |  |  | 0.00027576 | 253.2084
121532096 | E | LC | ETL.8060.POLE.WOOD | 40603910 | SACTO | SIERRA | 2021-06-08 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40603910 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | [5 empty] | 0.0087579 | 541.3708 | 4.7412
121536159 | E | LC | ETL.1610.INSL | 40713508 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1610 | SILVERADO-FULTON JCT | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40661937 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.7005e-07 | 2203.4587 | 0.0003747
121537502 | E | LC | ETL.6880.INSL.CERA | 44286171 | LAKEVLLE |  | 2021-06-14 |  | ETL.6880 | FULTON-CALISTOGA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40912478 | 2009-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Porcelain | [5 empty] | 0.00053269 | 696.472 | 0.371
121550072 | E | LC | ETL.5630.TOWR | 40820423 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5630 | ROCK CREEK-POE | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40820423 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1950-01-01 | Ceramic | Dead End |  |  |  |  | 4.8566e-05 | 2296.8577 | 0.11155
121554583 | B | LC | ETL.3830.TOWR | 40860791 | VICTOR | STOCKTON | 2021-06-17 | 2021-06-29 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Other | Customer Issue | [Customer Refusal, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860791 | 1927-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1999-01-01 | Polymer | Dead End |  |  |  |  | 7.7118e-07 | 10386.085
121557656 | F | LC | ETL.4440.POLE.NWOD | 44190877 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44190877 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 1.5719e-07 | 443.3138
121561553 | E | LC | ETL.6750.POLE.WDPS | 44374929 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44374927 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00026446 | 221.5655 | 0.058595
121561563 | E | LC | ETL.1350.POLE.WDPS | 44513814 | TABLEMTN |  | 2021-06-04 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44512267 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.030806 | 205.744 | 6.3381
121567667 | E | LC | ETL.1110.TOWR | 40909292 | EUREKA | HUMBOLDT | 2021-06-14 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40909292 | 1952-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 1.51e-05 | 300.6761 | 0.0045401
121572712 | E | LC | ETL.7550.POLE.WOOD | 44337833 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44337833 | 2012-06-28 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2016-06-12 | Polymer | Dead End |  |  |  |  | 6.7922e-06 | 15.8807 | 0.00010786
121596133 | E | LC | ETL.5960.INSL | 40631777 | PISMOBCH | LOS PADRES | 2021-06-24 |  | ETL.5960 | DIABLO-GATES #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40592889 | 1973-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 2.4525e-06 | 1170.3627 | 0.0028703
121609371 | F | LC | ETL.6760.POLE.NWOD | 44997686 | SACTO | SIERRA | 2021-06-18 | 2021-07-19 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44997686 | 2020-11-06 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-11-06 | Glass | Double Dead End |  |  |  |  | 0.026374 | 142.5076
121636050 | E | LC | ETL.6760.POLE.WOOD | 40767356 | SACTO | SIERRA | 2021-06-23 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40767356 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.029697 | 15.8837 | 0.4717
121649542 | E | LC | ETL.6470.POLE.WOOD | 40874813 | SACTO | SIERRA | 2021-06-18 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40874813 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 0.21774 | 110.8481 | 24.1357
121655310 | E | LC | ETL.8310.INSL.CERA | 40628900 | MOSSLNDG | CENTRAL COAST | 2021-06-28 | 2021-10-04 | ETL.8310 | WATSONVILLE-SALINAS | Insulator | Contaminated | [Ground Wash, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564328 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.091089
121655310 | E | LC | ETL.8310.INSL.CERA | 40628900 | MOSSLNDG | CENTRAL COAST | 2021-06-28 | 2021-10-04 | ETL.8310 | WATSONVILLE-SALINAS | Insulator | Contaminated | [Ground Wash, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564328 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.091089
121659501 | F | LC | ETL.5300.TOWR | 40593894 | PISMOBCH | LOS PADRES | 2021-06-25 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40593894 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 2.8871e-07 | 1333.1163 | 0.00038489
121669960 | B | LC | ETL.5140.POLE.WDPS | 44558399 | SACTO | SACRAMENTO | 2021-07-05 | 2021-08-12 | ETL.5140 | MIDDLE FORK-GOLD HILL | Hardware-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44557937 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00048801 | 3374.4685
121676005 | E | LC | ETL.1372.POLE.WDPS | 44283687 | PISMOBCH | LOS PADRES | 2021-07-06 |  | ETL.1372 | MANVILLE TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44283684 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00019582 | 1442.1754 | 0.28241
121678734 | E | LC | ETL.6020.TOWR | 40601184 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.6020 | MALIN-ROUND MTN #2 | Hardware-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40601184 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.2217e-08 | 174.1517 | 2.1276e-06
121682594 | B | LC | ETL.5980.TOWR | 40587709 | PISMOBCH | LOS PADRES | 2021-07-07 | 2021-07-23 | ETL.5980 | DIABLO-MIDWAY #3 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587709 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-10-16 | Glass Silicone Coated | Suspension |  |  |  |  | 1.4905e-06 | 777.7842
121683227 | E | LC | ETL.1250.POLE.WOOD | 40748527 | FRESNO | YOSEMITE | 2021-07-07 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40748527 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0025209 | 6458.0835 | 16.2801
121707782 | F | LC | ETL.1680.POLE.WOOD | 40576804 | LAKEVLLE | SONOMA | 2021-06-12 | 2021-09-10 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40576804 | 1972-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1972-01-01 | Porcelain | Dead End |  |  |  |  | 0.0017821 | 2708.3875
121725122 | F | LC | ETL.1400.POLE.STPS | 44382678 | VICTOR | YOSEMITE | 2021-07-07 | 2021-08-02 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44382678 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 0.00018556
121725122 | F | LC | ETL.1400.POLE.STPS | 44382678 | VICTOR | YOSEMITE | 2021-07-07 | 2021-08-02 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44382678 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 0.00018556
121746665 | E | LC | ETL.1810.INSL.CERA | 40685210 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44322392 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.00022993
121746665 | E | LC | ETL.1810.INSL.CERA | 40685210 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44322392 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.00022993
121748905 | F | LC | ETL.1350.POLE.NWOD | 44771115 | TABLEMTN | NORTH VALLEY | 2021-07-15 |  | ETL.1350 | CRAG VIEW-CASCADE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44771115 | 2019-05-02 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2019-05-02 | Polymer | Dead End |  |  |  |  | 6.2217e-05 | 79.1724
121749605 | F | LC | ETL.5430.POLE.STPS | 44659615 | TABLEMTN |  | 2021-07-14 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44148944 | 2016-12-07 | 2-Pole Non Wood | SS1 - Susp. Steel Single. CIR | [7 empty] | 1.3576e-06 | 364.0218
121769941 | B | LC | ETL.6280.POLE.WOOD | 40876579 | TABLEMTN | NORTH VALLEY | 2021-07-21 | 2021-10-13 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40876579 |  | Single Wood Pole | T-1 - Tri Post | 2018-10-30 | Polymer | Post |  |  |  |  | 1.1768e-05 | 6616.2266
121776572 | E | LC | ETL.6981.POLE.WDPS | 44565339 | LAKEVLLE | SONOMA | 2021-07-20 | 2021-07-28 | ETL.6981 | SALMON CREEK TAP | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | HFRA Removal | DLFL | 44564242 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.20095 | 1219.1483
121803879 | E | LC | ETL.6770.POLE.WOOD | 40769520 | SACTO | SIERRA | 2021-07-26 |  | ETL.6770 | DRUM-SPAULDING | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40769520 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.028767 | 3069.2839 | 88.2949
121810131 | B | LC | ETL.2420.INSL.CERA | 40578161 | LAKEVLLE |  | 2021-07-27 | 2021-08-16 | ETL.2420 | MENDOCINO-UKIAH | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44218012 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0008782
121810131 | B | LC | ETL.2420.INSL.CERA | 40578161 | LAKEVLLE |  | 2021-07-27 | 2021-08-16 | ETL.2420 | MENDOCINO-UKIAH | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44218012 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0008782
121810685 | F | LC | ETL.7390.POLE.NWOD | 45041707 | LAKEVLLE | HUMBOLDT | 2021-07-27 | 2021-08-26 | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 45041707 | 2020-04-01 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-04-01 | Polymer | Suspension |  |  |  |  | 0.031433
121810953 | F | LC | ETL.8365.POLE.WOOD | 40912600 | EUREKA | HUMBOLDT | 2021-07-27 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40912600 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2021-05-03 | Glass | Suspension |  |  |  |  | 0.071312
121816495 | F | LC | ETL.6690.POLE.WOOD | 40756928 | SACTO | SIERRA | 2021-07-29 | 2021-10-05 | ETL.6690 | DEER CREEK-DRUM | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756928 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 0.23604 | 63.3607
121816508 | E | LC | ETL.8405.POLE.WOOD | 40874900 | SACTO | SIERRA | 2021-07-27 |  | ETL.8405 | MIDDLE FORK #1 | Crossarm-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40874900 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0031317 | 2610.7236 | 8.1759
121860123 | B | LC | ETL.6300.POLE.WOOD | 40861869 | TABLEMTN | NORTH VALLEY | 2021-08-07 | 2021-09-09 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.3555e-05 | 15.8815
121889170 | E | LC | ETL.8170.POLE.WOOD | 40604691 | EUREKA | HUMBOLDT | 2021-08-12 | 2021-10-14 | ETL.8170 | TRINITY-MAPLE CREEK | Emergency | Fire | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40604691 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.051003 | 6475.8594
121889184 | B | LC | ETL.1820.POLE.WDPS | 44562950 | EUREKA | HUMBOLDT | 2021-08-11 | 2021-09-29 | ETL.1820 | HUMBOLDT-TRINITY | Emergency | Fire | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [12 empty] | 79.1724
121889639 | E | LC | ETL.4040.POLE.STPS | 44923036 | TABLEMTN | NORTH VALLEY | 2020-06-13 | 2021-08-23 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44922941 | 2020-03-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.4403e-05 | 2077.158
121896288 | B | LC | ETL.8170.POLE.WOOD | 40752254 | EUREKA | HUMBOLDT | 2021-08-13 | 2021-09-27 | ETL.8170 | TRINITY-MAPLE CREEK | Emergency | Fire | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.01334 | 3307.0649
121954204 | E | LC | ETL.7550.POLE.WOOD | 40826072 | LAKEVLLE | SONOMA | 2021-08-25 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40826072 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00014761 | 0.065148 | 9.6162e-06
122322909 | E | LC | ETL.7390.POLE.WOOD | 40876447 | LAKEVLLE | HUMBOLDT | 2021-10-27 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40876447 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.023807 | 3282.1799 | 78.1395
122332381 | F | LC | ETL.1400.POLE.STPS | 44379630 | VICTOR | STOCKTON | 2021-11-07 |  | ETL.1400 | DONNELLS-MI-WUK | Anchor-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44379628 | 2017-08-17 | 3-Pole Non Wood | DV-DE - Double Vertical Dead End | [7 empty] | 0.002514 | 79.1977 | 0.1991
118559611 | F | LC | ETL.8360.POLE.NWOD | 40648661 | LAKEVLLE | SONOMA | 2020-02-21 | 2020-05-27 | ETL.8360 | LAYTONVILLE-WILLITS | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648661 | 2010-01-01 | Light Duty Steel Pole | TPSRD - Tri Post & Susp Dead End |  | Polymer | [5 empty] | 7.662e-06 | 2786.9674
118600451 | E | LC | ETL.2730.INSL | 40828515 | CONCORD | EAST BAY | 2020-03-03 | 2021-06-14 | ETL.2730 | MORAGA-OAKLAND #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118771904 | F | LC | ETL.3720.TOWR | 40644467 | CONCORD | DIABLO | 2020-04-02 | 2021-01-27 | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40644467 | 1968-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | [5 empty] | 3.2831e-07 | 110.7919
118926760 | E | LC | ETL.7270.POLE.NWOD | 44649366 | TABLEMTN | NORTH VALLEY | 2020-04-16 | 2020-08-06 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44649366 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.0020244 | 840.0571
118940440 | F | LC | ETL.7510.POLE.WOOD | 40615234 | LAKEVLLE | SONOMA | 2020-04-22 | 2020-06-09 | ETL.7510 | MENDOCINO-HARTLEY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40615234 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.9133e-05 | 5613.8252
118957452 | F | LC | ETL.6890.POLE.WOOD | 40601400 | LAKEVLLE | SONOMA | 2020-04-27 | 2021-08-05 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601400 | 1990-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.00076221 | 2282.1562
118963867 | E | LC | ETL.2390.POLE.WOOD | 40745372 | VICTOR | STOCKTON | 2020-04-30 | 2021-02-11 | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40745372 | 1978-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1954-01-01 | Polymer | Dead End |  |  |  |  | 4.9905e-06 | 6710.7031
118988981 | E | LC | ETL.7550.POLE.WOOD | 40875210 | LAKEVLLE | HUMBOLDT | 2020-05-04 | 2021-04-27 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40875210 |  | Single Wood Pole | SV-1B - Single Vertical Light Angle BR |  | Porcelain | [5 empty] | 0.0031111 | 1238.8812
119000020 | E | LC | ETL.5430.INSL | 40834747 | TABLEMTN |  | 2020-05-08 | 2020-07-13 | ETL.5430 | PIT #5-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119013886 | E | LC | ETL.7510.POLE.WOOD | 40810505 | LAKEVLLE | SONOMA | 2020-05-11 | 2020-07-09 | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119014465 | E | LC | ETL.1330.TOWR | 40861157 | LAKEVLLE | HUMBOLDT | 2020-04-24 | 2021-04-01 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861157 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.0031831 | 5545.9073
119044736 | F | LC | ETL.5780.TOWR | 40819485 | VICTOR | STOCKTON | 2020-05-11 | 2021-03-17 | ETL.5780 | TIGER CREEK-ELECTRA | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40819485 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 1.5744e-05 | 63.3392
119051129 | E | LC | ETL.4220.POLE.WOOD | 40861995 | TABLEMTN | NORTH VALLEY | 2020-05-11 | 2020-07-31 | ETL.4220 | WOODLEAF-PALERMO | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861995 | 1962-01-01 | Single Wood Pole | 3P DV - 3 Pole Double Vertical | 1962-01-01 | Ceramic | Other |  |  |  |  | 0.010066 | 1791.7156
119084505 | F | LC | ETL.1400.POLE.WOOD | 40763958 | VICTOR | YOSEMITE | 2020-05-27 | 2021-02-09 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40763958 | 1956-01-01 | 3-Pole Wood | SUSP - Suspension (TWR) | 2021-05-04 | Polymer | Double Dead End |  |  |  |  | 0.0093923
119084505 | F | LC | ETL.1400.POLE.WOOD | 40763958 | VICTOR | YOSEMITE | 2020-05-27 | 2021-02-09 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40763958 | 1956-01-01 | 3-Pole Wood | SUSP - Suspension (TWR) | 2021-05-04 | Polymer | Double Dead End |  |  |  |  | 0.0093923
119084505 | F | LC | ETL.1400.POLE.WOOD | 40763958 | VICTOR | YOSEMITE | 2020-05-27 | 2021-02-09 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40763958 | 1956-01-01 | 3-Pole Wood | SUSP - Suspension (TWR) | 2021-05-04 | Polymer | Double Dead End |  |  |  |  | 0.0093923
119088563 | F | LC | ETL.3960.TOWR | 40751462 | PISMOBCH | LOS PADRES | 2020-05-15 | 2021-01-12 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751462 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Porcelain | Dead End |  |  |  |  | 5.8047e-09 | 3863.8943
119109516 | F | LC | ETL.6470.POLE.WOOD | 40766718 | SACTO | SIERRA | 2020-06-01 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40766718 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.01721 | 569.5315
119114374 | E | LC | ETL.1431.TOWR | 40586107 | SACTO | SIERRA | 2020-05-28 |  | ETL.1431 | BRUNSWICK #2 TAP | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40586107 | 1975-01-01 | LATTICE STEEL TOWER | Unknown |  | Ceramic | Dead End |  |  |  |  | 6.8638e-09 | 1471.1865 | 1.0098e-05
119115585 | F | LC | ETL.6470.POLE.WOOD | 40767194 | SACTO | SIERRA | 2020-06-01 | 2021-07-21 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119116174 | F | LC | ETL.1650.POLE.WOOD | 40808559 | LAKEVLLE | SONOMA | 2020-05-27 | 2021-03-16 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808559 | 1966-01-01 | Single Wood Pole | WB - Wishbone | 1966-01-01 | Porcelain | Suspension |  |  |  |  | 4.9935e-05 | 4151.2271
119117535 | F | LC | ETL.6470.POLE.WOOD | 40693511 | SACTO | SIERRA | 2020-05-29 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40693511 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.013288 | 870.1591
119125552 | E | LC | ETL.6950.POLE.WOOD | 40821299 | SACTO | SIERRA | 2020-05-28 | 2021-10-19 | ETL.6950 | GOLD HILL #1 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40821299 | 2014-08-18 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Post |  |  |  |  | 0.0034695 | 1504.152 | 5.2187
119125787 | F | LC | ETL.7930.POLE.WOOD | 42564782 | MOSSLNDG | CENTRAL COAST | 2020-06-03 | 2020-11-12 | ETL.7930 | SALINAS-LAURELES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 42564782 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 0.003065 | 237.3476
119126148 | F | LC | ETL.6490.POLE.WOOD | 40818454 | SACTO | SIERRA | 2020-06-02 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40818454 |  | Single Wood Pole | T-1 - Tri Post | 2019-12-03 | Polymer | Post |  |  |  |  | 0.0061028 | 479.409
119160508 | E | LC | ETL.7260.INSL | 40686948 | TABLEMTN | NORTH VALLEY | 2020-06-09 |  | ETL.7260 | KESWICK-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40657210 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 2.3785e-05 | 459.0366 | 0.010918
119163866 | F | LC | ETL.1810.POLE.WDPS | 44322554 | EUREKA | HUMBOLDT | 2020-06-12 | 2021-05-11 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322553 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00041891
119165537 | E | LC | ETL.7260.POLE.WOOD | 40827857 | TABLEMTN | NORTH VALLEY | 2020-06-09 |  | ETL.7260 | KESWICK-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40827857 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 2.6339e-05 | 648.9557 | 0.017093
119172163 | F | LC | ETL.8170.POLE.WDPS | 44779042 | EUREKA | HUMBOLDT | 2020-06-12 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906458 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.029743 | 664.5661
119183868 | E | LC | ETL.4223.POLE.WDPS | 44313779 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2020-08-17 | ETL.4223 | KANAKA TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119185706 | F | LC | ETL.8210.POLE.WOOD | 40907079 | VICTOR | STOCKTON | 2020-04-10 | 2021-10-11 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40907079 | 1985-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0087093 | 4654.7056
119198756 | F | LC | ETL.6470.POLE.WOOD | 40602534 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40602534 |  | Single Wood Pole | T2N | 2021-07-16 | Polymer | Post |  |  |  |  | 0.25227 | 158.2723
119209695 | E | LC | ETL.4220.POLE.WOOD | 40758035 | TABLEMTN | NORTH VALLEY | 2020-06-24 | 2020-07-29 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758035 | 1962-01-01 | Single Wood Pole | T-1 - Tri Post | 1962-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0217 | 1832.0189
119219547 | E | LC | ETL.8290.POLE.WOOD | 40816171 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2020-09-25 | ETL.8290 | VOLTA-DESCHUTES | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40816171 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0011275 | 554.7007
119222595 | E | LC | ETL.5440.TOWR | 40870160 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2020-07-15 | ETL.5440 | PIT #6 JCT-ROUND MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870160 | 1942-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1942-01-01 | Ceramic | Suspension |  |  |  |  | 0.0059916 | 1503.2676
119231671 | E | LC | ETL.6470.POLE.WOOD | 40818515 | SACTO | SIERRA | 2020-06-29 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818515 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.10433 | 110.8102
119289903 | F | LC | ETL.6900.POLE.WOOD | 44221959 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 2 | Within Both | PEND | 44221959 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 1.3935e-05 | 63.3774
119290206 | F | LC | ETL.7300.POLE.WOOD | 40701767 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40701767 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.00070105 | 2329.3726
119290353 | E | LC | ETL.6880.POLE.WOOD | 40905738 | LAKEVLLE | SONOMA | 2020-07-01 | 2021-04-20 | ETL.6880 | FULTON-CALISTOGA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119293544 | B | LC | ETL.4680.TOWR | 40597134 | LAKEVLLE | SONOMA | 2020-07-01 | 2020-10-26 | ETL.4680 | FULTON-IGNACIO #1 | Other | Customer Issue | [Customer Refusal, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40597134 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.3131e-05 | 965.4728
119312592 | F | LC | ETL.6290.POLE.WOOD | 40809566 | TABLEMTN | NORTH VALLEY | 2020-07-03 | 2021-08-05 | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40809566 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.071201 | 5282.8242
119317108 | E | LC | ETL.8170.POLE.WOOD | 40808971 | EUREKA | HUMBOLDT | 2020-07-06 | 2020-10-28 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40808971 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.026989 | 0.065148
119325285 | E | LC | ETL.1110.INSL.CERA | 40634787 | EUREKA | HUMBOLDT | 2020-07-07 | 2021-06-25 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423330 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0011348
119325285 | E | LC | ETL.1110.INSL.CERA | 40634787 | EUREKA | HUMBOLDT | 2020-07-07 | 2021-06-25 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423330 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0011348
119331480 | E | LC | ETL.6230.POLE.WOOD | 40766550 | MOSSLNDG | CENTRAL COAST | 2020-07-08 | 2020-10-01 | ETL.6230 | BURNS-LONE STAR #1 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40766550 |  | Single Wood Pole | T2N | 2020-09-08 | Polymer | Post |  |  |  |  | 0.11198 | 63.351
119332130 | E | LC | ETL.4040.POLE.WDPS | 44552583 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-11-29 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44551613 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.051038 | 4514.9478
119337378 | F | LC | ETL.6280.POLE.WOOD | 40824641 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-07-07 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824641 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 5.0823e-05 | 4065.6267
119352965 | E | LC | ETL.6280.POLE.WOOD | 40599640 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2020-07-20 | ETL.6280 | CARIBOU #2 | Non-Routine Patrol | Investigate | [Ground Patrol] | Tier2 | Tier 2 | Within Both | DLFL | 40599640 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 3.1224e-06 | 174.0445
119363938 | E | LC | ETL.6900.POLE.WOOD | 40768049 | LAKEVLLE | SONOMA | 2020-07-13 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | PEND | 40768049 | 1974-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 2.662e-06 | 15.8932 | 4.2307e-05
119368149 | F | LC | ETL.1440.POLE.WDPS | 44740280 | SACTO | SACRAMENTO | 2020-07-09 | 2020-08-19 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119371662 | E | LC | ETL.1110.POLE.WDPS | 44424089 | TABLEMTN | HUMBOLDT | 2020-07-13 | 2021-04-12 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424087 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00094901 | 4057.0393
119377301 | E | LC | ETL.6380.POLE.NWOD | 40661647 | LAKEVLLE | SONOMA | 2020-07-15 | 2021-03-03 | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40661647 |  | Light Duty Steel Pole | TPSR - Tri Post & Susp Light |  | Polymer | [5 empty] | 2.2127e-09 | 5480.7725
119464055 | F | LC | ETL.7030.POLE.WOOD | 40701217 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-05-21 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40701217 |  | Single Wood Pole | T2N | 2021-05-17 | Polymer | Post |  |  |  |  | 0.0246 | 79.2605
119465001 | F | LC | ETL.7030.POLE.WOOD | 40877608 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-07-26 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877608 |  | Single Wood Pole | 1VP - 1 Vertical |  | Ceramic | Pin |  |  |  |  | 0.035853 | 159.1485
119467270 | E | LC | ETL.8210.POLE.WOOD | 40905583 | VICTOR | STOCKTON | 2020-06-18 | 2021-06-01 | ETL.8210 | VALLEY SPRINGS #1 | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40905583 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.018525 | 23.8355
119477262 | A | LC | ETL.7590.SWIT | 40743953 | MOSSLNDG | CENTRAL COAST | 2020-07-20 | 2020-07-30 | ETL.7590 | MONTA VISTA-BURNS | Switch | Out of Adjustment | [Repair, Completed] | Tier3 |  |  | COMP | [7 empty] | 2015-06-11 | SEECO | VACUUM INTERRUPTER (3 GAP) | SCADA Only
119480324 | E | LC | ETL.8410.POLE.WOOD | 40601570 | LAKEVLLE | SONOMA | 2020-07-21 |  | ETL.8410 | ELK-GUALALA | Vegetation | Overgrown | [Trim] | Tier2 | Tier 2 | Within Both | PEND | 40601570 | 1960-01-01 | Single Wood Pole | TPSR - Tri Post & Susp Light | 2019-09-27 | Glass | Suspension |  |  |  |  | 0.11222 | 79.143 | 8.8816
119485919 | E | LC | ETL.7340.POLE.WOOD | 40601791 | LAKEVLLE | SONOMA | 2020-07-22 | 2021-06-07 | ETL.7340 | LAKEVILLE #2 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601791 |  | Single Wood Pole | T-1 - Tri Post | 2021-05-22 | Polymer | Post |  |  |  |  | 0.0039335 | 2788.1648
119497625 | F | LC | ETL.5934.TOWR | 40858099 | FRESNO | FRESNO | 2020-07-22 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40858099 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00039646
119497625 | F | LC | ETL.5934.TOWR | 40858099 | FRESNO | FRESNO | 2020-07-22 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40858099 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.00039646
119513149 | E | LC | ETL.7590.POLE.WOOD | 40824963 | MOSSLNDG | CENTRAL COAST | 2020-07-27 | 2021-01-12 | ETL.7590 | MONTA VISTA-BURNS | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119547201 | E | LC | ETL.7030.POLE.WOOD | 40759043 | TABLEMTN | NORTH VALLEY | 2020-07-31 | 2021-07-12 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759043 |  | Single Wood Pole | T2N | 2021-06-18 | Polymer | Post |  |  |  |  | 0.0003028 | 904.5289
119574066 | E | LC | ETL.7180.POLE.WOOD | 40809520 | LAKEVLLE | NORTH BAY | 2020-08-06 | 2021-04-06 | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119577565 | F | LC | ETL.8365.POLE.WOOD | 40912631 | EUREKA | HUMBOLDT | 2020-08-07 | 2021-02-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40912631 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.085535
119592245 | F | LC | ETL.9210.POLE.WOOD | 40595780 | MIDWAY | KERN | 2020-08-10 | 2021-01-25 | ETL.9210 | TAFT-CUYAMA #2 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40595780 | 1946-01-01 | Single Wood Pole | 2P DDE - 2 Pole Double Dead End | 1946-01-01 | Ceramic | Dead End |  |  |  |  | 0.012387
119604873 | E | LC | ETL.8365.POLE.WOOD | 40906600 | EUREKA | HUMBOLDT | 2020-08-12 | 2021-05-03 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906600 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.077894
119609193 | F | LC | ETL.6950.POLE.NWOD | 44922626 | SACTO | SACRAMENTO | 2020-08-13 | 2021-04-07 | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44922626 | 2020-05-08 | Light Duty Steel Pole | SV-1B - Single Vertical Light Angle BR | 2020-05-08 | Glass | Suspension |  |  |  |  | 0.0037811 | 1313.0015
119609511 | F | LC | ETL.5463.TOWR | 40746314 | CONCORD | DIABLO | 2020-08-13 | 2021-01-19 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746314 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 1.2705e-09 | 616.8689
119643304 | B | LC | ETL.8650.POLE.NWOD | 44420156 | FRESNO | FRESNO | 2020-08-20 | 2020-12-09 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44420156 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0056224 | 207.8215
119651882 | F | LC | ETL.1330.TOWR | 40657074 | LAKEVLLE | SONOMA | 2020-08-21 | 2021-02-02 | ETL.1330 | CORTINA-MENDOCINO #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40657074 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.0003874 | 4939.8286
119658771 | A | LC | ETL.6240.POLE.WOOD | 40823337 | MOSSLNDG | CENTRAL COAST | 2020-08-22 | 2020-10-13 | ETL.6240 | BURNS-LONE STAR #2 | Emergency-Wood | Other | [Replace, Completed] | Tier3 |  |  | COMP
119679917 | E | LC | ETL.1420.INSL.NCER | 40779874 | SACTO | SACRAMENTO | 2020-08-27 | 2021-02-22 | ETL.1420 | DRUM-RIO OSO #1 | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750989 | 1965-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm | 1989-01-01 | Polymer | Post |  |  |  |  | 8.1697e-08 | 0.090454
119683060 | E | LC | ETL.4223.INSL.CERA | 42567889 | TABLEMTN | NORTH VALLEY | 2020-08-27 |  | ETL.4223 | KANAKA TAP | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 42567887 | 2013-01-01 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 9.2986e-08
119683060 | E | LC | ETL.4223.INSL.CERA | 42567889 | TABLEMTN | NORTH VALLEY | 2020-08-27 |  | ETL.4223 | KANAKA TAP | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 42567887 | 2020-06-27 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 9.2986e-08
119683060 | E | LC | ETL.4223.INSL.CERA | 42567889 | TABLEMTN | NORTH VALLEY | 2020-08-27 |  | ETL.4223 | KANAKA TAP | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 42567887 | 2013-01-01 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 9.2986e-08
119697611 | E | LC | ETL.1600.INSL.NCER | 40835398 | LAKEVLLE | SONOMA | 2020-07-28 | 2021-06-09 | ETL.1600 | FULTON-PUEBLO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119720870 | E | LC | ETL.1330.POLE.WOOD | 44645378 | LAKEVLLE | HUMBOLDT | 2020-07-28 | 2021-06-21 | ETL.1330 | CORTINA-MENDOCINO #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44645378 | 2018-08-05 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2018-08-05 | Polymer | Dead End - Suspension |  |  |  |  | 0.0006195 | 5715.6968
119721867 | A | LC | ETL.7590.POLE.WOOD | 40694947 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-10-21 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119723161 | A | LC | ETL.6240.POLE.WOOD | 40874269 | MOSSLNDG | CENTRAL COAST | 2020-09-07 | 2020-09-10 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40874269 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.19166 | 110.8153
119723664 | B | LC | ETL.8405.POLE.WOOD | 40598771 | SACTO | SIERRA | 2020-08-05 | 2020-12-29 | ETL.8405 | MIDDLE FORK #1 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40598771 |  | Single Wood Pole | T2N | 2020-12-16 | Polymer | Post |  |  |  |  | 0.17721 | 1708.8922
119743661 | E | LC | ETL.2810.INSL.NCER | 44959201 | PISMOBCH | LOS PADRES | 2020-09-10 |  | ETL.2810 | MORRO BAY-SAN LUIS OBISPO #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810415 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-07-09 | Glass | Suspension |  |  |  |  | 6.1965e-10 | 1459.0531 | 9.0411e-07
119743661 | E | LC | ETL.2810.INSL.NCER | 44959201 | PISMOBCH | LOS PADRES | 2020-09-10 |  | ETL.2810 | MORRO BAY-SAN LUIS OBISPO #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810415 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-17 | Glass | Suspension |  |  |  |  | 6.1965e-10 | 1459.0531 | 9.0411e-07
119750386 | F | LC | ETL.1400.POLE.WDPS | 44770773 | VICTOR | STOCKTON | 2020-08-12 | 2021-02-09 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install] |  | Tier 3 | Within Both | DLFL | 40643188 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.015993 | 2246.7366
119765616 | F | LC | ETL.6480.POLE.WOOD | 40766537 | SACTO | SIERRA | 2020-09-08 | 2021-06-29 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40766537 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-12-10 | Polymer | Dead End |  |  |  |  | 0.066807 | 94.9762
119774640 | E | LC | ETL.8170.POLE.WOOD | 40770500 | EUREKA | HUMBOLDT | 2020-09-09 |  | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40770500 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Non Ceramic | [5 empty] | 0.34312 | 395.7131 | 135.7783
119779917 | E | LC | ETL.6770.POLE.WOOD | 40825209 | SACTO | SIERRA | 2020-09-10 | 2021-04-26 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119803061 | F | LC | ETL.1400.POLE.NWOD | 44809965 | VICTOR | YOSEMITE | 2020-08-07 | 2021-08-26 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44809965 | 2019-08-09 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2019-08-09 | Glass | Dead End |  |  |  |  | 4.4901e-05 | 79.1724
119815993 | F | LC | ETL.5140.POLE.NWOD | 41195908 | SACTO | SIERRA | 2020-09-10 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 41195908 |  | Lattice Steel Pole | Unknown |  | Non Ceramic | [5 empty] | 0.00035205 | 186.7919
119819515 | F | LC | ETL.8290.POLE.WOOD | 40868512 | TABLEMTN | NORTH VALLEY | 2020-08-29 | 2021-06-14 | ETL.8290 | VOLTA-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40868512 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.0071443 | 762.9542
119825201 | A | LC | ETL.4221.INSL.CERA | 44398350 | TABLEMTN |  | 2020-09-28 | 2020-10-08 | ETL.4221 | SLY CREEK TAP | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119825209 | B | LC | ETL.8211.POLE.WOOD | 43197381 | VICTOR | STOCKTON | 2020-09-29 | 2020-12-01 | ETL.8211 | NEW HOGAN TAP | Switch | Out of Adjustment | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 43197381 |  | Single Wood Pole | Unknown | [8 empty] | 23.8355
119827122 | B | LC | ETL.6880.POLE.WOOD | 40751155 | LAKEVLLE | NORTH BAY | 2020-09-28 | 2020-10-20 | ETL.6880 | FULTON-CALISTOGA | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119850735 | F | LC | ETL.1400.POLE.STPS | 44384136 | VICTOR | YOSEMITE | 2020-09-17 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44384135 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.2093e-05 | 965.199
119857535 | B | LC | ETL.6720.TOWR | 44181036 | TABLEMTN | NORTH VALLEY | 2020-10-05 | 2020-10-19 | ETL.6720 | DESABLA-CENTERVILLE | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44181036 |  | LATTICE STEEL TOWER | DDE - Double Dead End | [7 empty] | 0.016476 | 118.715
119863896 | E | LC | ETL.8580.INSL.CERA | 40634991 | PISMOBCH | LOS PADRES | 2020-10-05 | 2020-12-30 | ETL.8580 | COALINGA #1-SAN MIGUEL | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119887624 | E | LC | ETL.1420.TOWR | 40660105 | SACTO | SIERRA | 2020-10-06 | 2021-03-04 | ETL.1420 | DRUM-RIO OSO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660105 | 1965-01-01 | LATTICE STEEL TOWER | FDDE - Flat Dead End Construction | 1965-01-01 | Polymer | Dead End |  |  |  |  | 4.3657e-06 | 838.4462
119914326 | F | LC | ETL.1721.TOWR | 44181040 | MOSSLNDG | CENTRAL COAST | 2020-10-16 |  | ETL.1721 | METCALF-SALINAS #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44181040 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 1.0974e-08
119914326 | F | LC | ETL.1721.TOWR | 44181040 | MOSSLNDG | CENTRAL COAST | 2020-10-16 |  | ETL.1721 | METCALF-SALINAS #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44181040 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | [5 empty] | 1.0974e-08
119914326 | F | LC | ETL.1721.TOWR | 44181040 | MOSSLNDG | CENTRAL COAST | 2020-10-16 |  | ETL.1721 | METCALF-SALINAS #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44181040 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Non Ceramic | Suspension |  |  |  |  | 1.0974e-08
119988392 | E | LC | ETL.8960.POLE.WDPS | 45020878 | FRESNO | YOSEMITE | 2020-11-04 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40652905 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00044346
120044487 | F | LC | ETL.6880.POLE.WOOD | 40911348 | LAKEVLLE | HUMBOLDT | 2020-10-06 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40911348 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.01945 | 2471.5815
120096056 | F | LC | ETL.7212.POLE.WDPS | 44384404 | METCALF | SAN JOSE | 2020-11-25 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44384401 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.29983 | 316.4883
120129535 | F | LC | ETL.7180.POLE.WOOD | 40601733 | LAKEVLLE | NORTH BAY | 2020-10-19 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40601733 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 7.6731e-06 | 142.604
120592786 | E | LC | ETL.7030.POLE.WOOD | 40816096 | TABLEMTN | NORTH VALLEY | 2021-03-02 | 2021-06-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816096 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0088018 | 1807.5773
120629872 | A | LC | ETL.1070.SWIT | 43242611 | VICTOR | STOCKTON | 2021-03-10 | 2021-03-11 | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Emergency | Storm Related | [Repair, Completed] | Tier2 |  |  | COMP | [8 empty] | PEM | VACUUM INTERRUPTER (1 GAP) | Manual
120679207 | B | LC | ETL.5630.TOWR | 40663015 | TABLEMTN | NORTH VALLEY | 2021-03-23 | 2021-04-30 | ETL.5630 | ROCK CREEK-POE | Other | Land/Enviro Issue | [Access Issue] | Tier3 | Tier 3 | Within Both | COMP | 40663015 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 2.0295e-06 | 427.2046
120689693 | F | LC | ETL.5330.TOWR | 40659295 | MOSSLNDG | CENTRAL COAST | 2021-03-24 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40659295 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-07-06 | Ceramic | Suspension |  |  |  |  | 8.1536e-08 | 111.0094 | 9.0513e-06
120695210 | F | LC | ETL.3830.TOWR | 40579613 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40579613 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.571e-06 | 2646.5061 | 0.0041577
120708234 | E | LC | ETL.3820.TOWR | 40856515 | VICTOR | STOCKTON | 2021-03-26 | 2021-04-08 | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40856515 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 2.0366e-06 | 3501.2405
120718776 | F | LC | ETL.6721.POLE.NWOD | 44815089 | TABLEMTN | NORTH VALLEY | 2021-03-30 |  | ETL.6721 | ORO FINO TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44815089 | 2019-08-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-08-18 | Glass | Dead End |  |  |  |  | 9.0027e-07 | 79.1651
120726806 | F | LC | ETL.7390.POLE.WDPS | 44412012 | LAKEVLLE | SONOMA | 2021-04-01 | 2021-04-05 | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44412009 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.053448 | 2652.9001
120726908 | E | LC | ETL.7040.POLE.WOOD | 40591259 | TABLEMTN | NORTH VALLEY | 2021-04-01 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40591259 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.05123 | 15.9447 | 0.81684
120740303 | E | LC | ETL.2900.INSL.CERA | 40835346 | MOSSLNDG | CENTRAL COAST | 2021-04-03 | 2021-04-07 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40810456 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1991-01-01 | Porcelain | Dead End |  |  |  |  | 0.0051817 | 3623.5847
120741955 | E | LC | ETL.1350.POLE.NWOD | 44993921 | TABLEMTN | NORTH VALLEY | 2021-04-05 | 2021-07-19 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993921 | 2020-06-18 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-18 | Glass | Dead End |  |  |  |  | 4.3026e-05 | 205.744
120743190 | E | LC | ETL.3700.POLE.WOOD | 40659144 | PISMOBCH | LOS PADRES | 2021-04-01 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40659144 | 1956-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1989-01-01 | Polymer | Unknown |  |  |  |  | 0.00046048 | 3706.2773 | 1.7067
120749870 | B | LC | ETL.3830.TOWR | 40872470 | VICTOR | STOCKTON | 2021-04-06 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40872470 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.2503e-08 | 3950.2275
120764364 | E | LC | ETL.7290.POLE.WOOD | 40592404 | TABLEMTN | NORTH VALLEY | 2021-04-08 |  | ETL.7290 | KILARC-CEDAR CREEK | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40592404 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.061182 | 547.6329 | 33.5054
120770661 | F | LC | ETL.7140.POLE.WDPS | 45096565 | LAKEVLLE | NORTH BAY | 2021-04-08 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41111799 |  | 3-Pole Wood | DV-DE - Double Vertical Dead End | [7 empty] | 0.0093056 | 1711.6168
120786072 | E | LC | ETL.6030.TOWR | 40872668 | MIDWAY | KERN | 2021-04-10 |  | ETL.6030 | MIDWAY-WHIRLWIND | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40872668 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 3.4984e-06 | 6985.7988 | 0.024439
120787072 | E | LC | ETL.4040.POLE.STPS | 44806637 | TABLEMTN | NORTH VALLEY | 2021-04-10 | 2021-09-14 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44779600 | 2019-05-19 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0023532 | 840.0571
120794482 | E | LC | ETL.8250.POLE.WOOD | 40904140 | VICTOR | STOCKTON | 2021-04-12 | 2021-07-22 | ETL.8250 | CLAY-MARTEL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40904140 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 4.5747e-05 | 1080.3165
120798096 | E | LC | ETL.4040.POLE.NWOD | 44964219 | TABLEMTN | NORTH VALLEY | 2021-04-12 | 2021-10-07 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44964219 | 2020-08-17 | Light Duty Steel Pole | DV - Double Vertical | 2020-08-17 | Glass | Dead End |  |  |  |  | 5.812e-07 | 0.065152 | 3.7866e-08
120833721 | E | LC | ETL.3820.TOWR | 40642918 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40642918 | 1910-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post | 1989-01-01 | Polymer | Post |  |  |  |  | 3.0476e-07 | 5966.103 | 0.0018182
120851226 | F | LC | ETL.8423.POLE.NWOD | 40614061 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.8423 | SALINAS-FORT ORD #2 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40614061 |  | Lattice Steel Pole | DCPOST - Double Circuit Post | 2020-06-02 | Ceramic | Post |  |  |  |  | 7.188e-05 | 569.4255 | 0.04093
120851226 | F | LC | ETL.8423.POLE.NWOD | 40614061 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.8423 | SALINAS-FORT ORD #2 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40614061 |  | Lattice Steel Pole | DCPOST - Double Circuit Post |  | Porcelain | [5 empty] | 7.188e-05 | 569.4255 | 0.04093
120857294 | E | LC | ETL.1400.POLE.WDPS | 44779039 | VICTOR | STOCKTON | 2021-04-14 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40744855 |  | 3-Pole Wood | DDE - Double Dead End | [7 empty] | 7.8786e-05 | 31.7081 | 0.0024981
120857766 | E | LC | ETL.2900.INSL.CERA | 40781986 | MOSSLNDG | CENTRAL COAST | 2021-04-20 | 2021-07-26 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752787 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1963-01-01 | Porcelain | Dead End |  |  |  |  | 0.08739 | 841.4142
120858629 | E | LC | ETL.9330.TOWR | 40763365 | FRESNO | FRESNO | 2021-04-21 | 2021-07-12 | ETL.9330 | WISHON-COPPERMINE | Foundation/Concrete-Tower | Earth Covered Tower | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40763365 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.0024707 | 6742.6743
120866508 | F | LC | ETL.4440.TOWR | 40589677 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40589677 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 6.7431e-08 | 1632.2432 | 0.00011006
120885691 | F | LC | ETL.1250.POLE.NWOD | 40652120 | FRESNO | YOSEMITE | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40652120 |  | Lattice Steel Pole | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 1.0386e-05 | 6932.1865
120912426 | E | LC | ETL.1730.POLE.WDPS | 44413236 | MOSSLNDG | CENTRAL COAST | 2021-05-01 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44413234 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.3474e-05 | 38.0207 | 0.0024133
120938590 | F | LC | ETL.6890.POLE.WOOD | 40581048 | LAKEVLLE | SONOMA | 2021-05-05 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40581048 | 1994-01-01 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Post |  |  |  |  | 0.00011623 | 3738.155
120952406 | E | LC | ETL.7490.POLE.WOOD | 40810438 | EUREKA | HUMBOLDT | 2021-05-08 |  | ETL.7490 | MAPLE CREEK-HOOPA | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40810438 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-08-01 | Polymer | Dead End |  |  |  |  | 0.0029217 | 221.4934 | 0.64713
120995296 | E | LC | ETL.1810.POLE.WDPS | 44322663 | EUREKA | HUMBOLDT | 2021-05-08 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44322662 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0020623 | 0.065148 | 0.00013436
121014354 | E | LC | ETL.7550.POLE.WOOD | 40697974 | LAKEVLLE | SONOMA | 2021-05-10 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40697974 |  | Single Wood Pole | TAP - Tri Arm Post |  | Polymer | [5 empty] | 0.00056564 | 0.065148 | 3.685e-05
121317229 | E | LC | ETL.1810.POLE.WDPS | 44322573 | EUREKA | HUMBOLDT | 2021-05-11 | 2021-05-21 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
121322009 | E | LC | ETL.1820.POLE.WDPS | 44560602 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560128 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.5233 | 79.1467 | 41.4171
121322055 | E | LC | ETL.1810.POLE.WDPS | 44322562 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44322561 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0030461
121338310 | E | LC | ETL.6220.POLE.WOOD | 44232135 | EUREKA | HUMBOLDT | 2021-05-13 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44232135 | 2015-07-27 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2015-07-27 | Porcelain | Dead End |  |  |  |  | 0.14907 | 810.0367 | 120.7535
121345844 | F | LC | ETL.1480.TOWR | 40808633 | LAKEVLLE | HUMBOLDT | 2021-05-14 | 2021-07-15 | ETL.1480 | EAGLE ROCK-REDBUD | Road | Grade Change | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808633 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1978-01-01 | Glass | Dead End |  |  |  |  | 0.0016372 | 712.1939
121364757 | E | LC | ETL.6280.INSL | 40634458 | TABLEMTN | NORTH VALLEY | 2021-05-19 |  | ETL.6280 | CARIBOU #2 | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40599687 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0037146 | 6616.2266 | 24.5764
121369281 | E | LC | ETL.1820.INSL.CERA | 40579069 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560159 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.11287
121369281 | E | LC | ETL.1820.INSL.CERA | 40579069 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560159 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.11287
121369281 | E | LC | ETL.1820.INSL.CERA | 40579069 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560159 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.11287
121370090 | E | LC | ETL.1250.POLE.WOOD | 40583001 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40583001 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00016144 | 4493.8192 | 0.72549
121370295 | F | LC | ETL.6880.POLE.WOOD | 40877288 | LAKEVLLE | NORTH BAY | 2021-05-01 | 2021-06-23 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
121375129 | E | LC | ETL.6760.INSL.CERA | 42549963 | SACTO | SACRAMENTO | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42549962 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0094636 | 237.3428 | 2.2461
121377601 | E | LC | ETL.6760.POLE.WOOD | 40598682 | SACTO | SIERRA | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40598682 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.036406 | 649.2313 | 23.6362
121377994 | F | LC | ETL.1820.POLE.WDPS | 44560555 | EUREKA | HUMBOLDT | 2021-05-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44560120 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.061185 | 126.6368
121380453 | E | LC | ETL.8350.POLE.NWOD | 44918821 | VICTOR | STOCKTON | 2021-05-08 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44918821 | 2020-03-03 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-03 | Polymer | Post |  |  |  |  | 1.3873e-06 | 2265.8246 | 0.0031433
121382258 | F | LC | ETL.6500.POLE.NWOD | 40664457 | TABLEMTN | NORTH VALLEY | 2021-05-10 | 2021-06-05 | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40664457 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 1.0733e-05 | 2630.0364
121383422 | E | LC | ETL.6500.POLE.WOOD | 40824171 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40824171 |  | Single Wood Pole | T2N | 2018-06-29 | Polymer | Post |  |  |  |  | 0.014036 | 4092.8162 | 57.448
121383968 | F | LC | ETL.1820.POLE.STPS | 44395397 | EUREKA | HUMBOLDT | 2021-05-22 | 2021-06-04 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44395395 | 2020-03-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00030068 | 237.3869
121388530 | F | LC | ETL.6500.POLE.WOOD | 40766513 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40766513 |  | Single Wood Pole | T2N | 2018-10-18 | Polymer | Post |  |  |  |  | 0.0027079 | 95.0648 | 0.25743
121391773 | F | LC | ETL.6760.POLE.WOOD | 40824375 | SACTO | SIERRA | 2021-05-17 | 2021-07-14 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824375 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.009064 | 34.8659
121406633 | E | LC | ETL.1430.INSL | 40843145 | SACTO | SACRAMENTO | 2021-05-26 |  | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40815310 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.0073572 | 63.348 | 0.46607
121418225 | E | LC | ETL.7000.POLE.WOOD | 40599839 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40599839 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0026879 | 0.065148 | 0.00017511
121420310 | F | LC | ETL.1400.POLE.STPS | 44381770 | VICTOR | YOSEMITE | 2021-05-26 | 2021-11-18 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44381769 | 2017-08-17 | 2-Pole Non Wood | DE - Dead End | [7 empty] | 0.00011602 | 158.2923
121420560 | E | LC | ETL.6430.INSL | 40698760 | TABLEMTN |  | 2021-05-22 |  | ETL.6430 | COLEMAN-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40667380 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0090072 | 2980.1345 | 26.8426
121436339 | E | LC | ETL.7040.POLE.WOOD | 40674186 | TABLEMTN | NORTH VALLEY | 2021-05-24 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40674186 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.14538 | 1364.1134 | 198.3171
121445845 | F | LC | ETL.6470.POLE.WOOD | 40818503 | SACTO | SIERRA | 2021-05-27 | 2021-06-11 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL | [11 empty] | 0.034596 | 727.8687
121447203 | F | LC | ETL.1820.POLE.NWOD | 44947381 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44947381 | 2018-09-14 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-09-18 | Glass | Dead End |  |  |  |  | 0.00024792 | 110.7793
121468336 | F | LC | ETL.5630.TOWR | 40814847 | TABLEMTN | NORTH VALLEY | 2021-06-02 | 2021-10-01 | ETL.5630 | ROCK CREEK-POE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40814847 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 0.00069116 | 3753.0444
121485671 | E | LC | ETL.7550.POLE.WOOD | 44172881 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44172881 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 2.6066e-05 | 3120.9548 | 0.081351
121489635 | E | LC | ETL.6110.TOWR | 40816937 | METCALF | SAN JOSE | 2021-05-27 |  | ETL.6110 | TESLA-METCALF | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40816937 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2012-01-31 | Ceramic | Suspension |  |  |  |  | 3.3518e-07 | 207.4369 | 6.9528e-05
121493507 | E | LC | ETL.7630.INSL.CERA | 40628709 | LAKEVLLE |  | 2021-06-01 |  | ETL.7630 | MONTE RIO-FULTON | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 40587311 | 1991-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2013-08-01 | Ceramic | Dead End |  |  |  |  | 0.0071779 | 94.985 | 0.68179
121493507 | E | LC | ETL.7630.INSL.CERA | 40628709 | LAKEVLLE |  | 2021-06-01 |  | ETL.7630 | MONTE RIO-FULTON | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 40587311 | 1991-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0071779 | 94.985 | 0.68179
121495970 | E | LC | ETL.9250.POLE.NWOD | 40583911 | MIDWAY | KERN | 2021-06-08 | 2021-08-17 | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40583911 |  | Light Duty Steel Pole | THDE - Tri Post Dead End 60 |  | Non Ceramic | Other |  |  |  |  | 0.0007155 | 5260.3872
121496181 | E | LC | ETL.1440.INSL | 40684221 | SACTO | SIERRA | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40654771 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.011393
121496181 | E | LC | ETL.1440.INSL | 40684221 | SACTO | SIERRA | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40654771 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.011393
121516725 | F | LC | ETL.6880.POLE.NWOD | 40601461 | LAKEVLLE | NORTH BAY | 2021-06-04 | 2021-09-27 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40601461 |  | Light Duty Steel Pole | T1DE - Tri Post Dead End 115 |  | Ceramic | Dead End |  |  |  |  | 4.2969e-06 | 1534.6033
121518468 | F | LC | ETL.1350.POLE.WDPS | 44512153 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40590563 | 1943-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.020782 | 743.6734 | 15.4548
121522128 | E | LC | ETL.5390.INSL.NCER | 45114523 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5390 | PIT #1-COTTONWOOD | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40758860 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.4981e-06 | 3248.3611 | 0.0081146
121522753 | E | LC | ETL.4440.TOWR | 40858272 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.4440 | CARIBOU-TABLE MTN | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40858272 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 1.5221e-06 | 1898.3378 | 0.0028894
121531800 | E | LC | ETL.1350.TOWR | 40868066 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.1350 | CRAG VIEW-CASCADE | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40868066 | 1944-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 2.3639e-05 | 79.1724 | 0.0018715
121538948 | E | LC | ETL.4750.INSL | 40785644 | LAKEVLLE | SONOMA | 2021-06-14 |  | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40756490 | 1971-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 9.2298e-06 | 950.5959 | 0.0087739
121543907 | F | LC | ETL.1820.POLE.STPS | 44395336 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395335 | 2020-03-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00023973 | 348.1371
121543992 | F | LC | ETL.7990.POLE.WOOD | 40908931 | SACTO | SIERRA | 2021-06-12 | 2021-10-11 | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40908931 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0015704 | 3564.1165
121544667 | F | LC | ETL.5390.POLE.STPS | 44417274 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.5390 | PIT #1-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44417273 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.173e-06 | 601.0973
121550199 | E | LC | ETL.5650.TOWR | 40762776 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40762776 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.1102e-06 | 4405.0728 | 0.0048906
121550726 | F | LC | ETL.7390.POLE.NWOD | 44412206 | LAKEVLLE | HUMBOLDT | 2021-06-13 | 2021-07-09 | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44412206 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0020171 | 143.1723
121560328 | E | LC | ETL.7990.POLE.WOOD | 40908939 | SACTO | SIERRA | 2021-06-12 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40908939 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | [5 empty] | 2.4762e-05 | 3786.353 | 0.093758
121561476 | F | LC | ETL.4771.TOWR | 40761438 | LAKEVLLE | HUMBOLDT | 2021-06-14 |  | ETL.4771 | BOTTLE ROCK TAP D.W.R. | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40761438 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 3.7522e-05 | 3665.975
121568365 | F | LC | ETL.1400.POLE.WOOD | 44948148 | VICTOR | YOSEMITE | 2021-06-15 |  | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44948148 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.0013566 | 39.6314 | 0.053764
121592098 | E | LC | ETL.6852.POLE.WOOD | 40655969 | LAKEVLLE | SONOMA | 2021-06-24 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40655969 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2011-09-29 | Ceramic | Dead End |  |  |  |  | 0.0097335 | 5905.2314 | 57.4787
121593634 | F | LC | ETL.2790.TOWR | 40819846 | CONCORD | DIABLO | 2021-06-18 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40819846 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 4.7367e-06 | 15.8932 | 7.5281e-05
121599780 | E | LC | ETL.4050.INSL.CERA | 40579434 | LAKEVLLE | HUMBOLDT | 2021-06-25 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44557894 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00032245
121599780 | E | LC | ETL.4050.INSL.CERA | 40579434 | LAKEVLLE | HUMBOLDT | 2021-06-25 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44557894 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00032245
121609375 | E | LC | ETL.1070.INSL.NCER | 40704251 | VICTOR | STOCKTON | 2021-06-22 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40645009 | 1957-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 1957-01-01 | Polymer | Dead End |  |  |  |  | 0.00023215 | 2390.8503 | 0.55503
121620498 | B | LC | ETL.1350.POLE.STPS | 45021992 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-07-26 | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45021960 | 2020-06-10 | 3-Pole Non Wood | DDE - Double Dead End | [7 empty] | 0.00014668 | 285.3068
121625388 | F | LC | ETL.4782.POLE.STPS | 45099299 | LAKEVLLE | SONOMA | 2021-06-28 | 2021-07-12 | ETL.4782 | SANTA FE GEOTHERMAL TAP | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40584987 |  | 3-Pole Non Wood | DDE-A - Double Dead End Angle | [7 empty] | 2.3657e-05 | 284.9657
121634480 | B | LC | ETL.6470.POLE.WOOD | 44684326 | SACTO | SIERRA | 2021-06-26 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44684326 | 2018-11-27 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-11-27 | Polymer | Dead End - Suspension |  |  |  |  | 0.0045921 | 189.8873
121645241 | E | LC | ETL.4040.POLE.WOOD | 40910455 | TABLEMTN | NORTH VALLEY | 2021-06-27 |  | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40910455 | 1967-01-01 | Single Wood Pole | 3P TRP D - 3 Pole Tramp Double Dead End | 1967-01-01 | Ceramic | Dead End |  |  |  |  | 0.0051945 | 3119.219 | 16.2026
121647862 | A | LC | ETL.1350.POLE.WDPS | 44549848 | TABLEMTN |  | 2021-07-01 | 2021-07-07 | ETL.1350 | CRAG VIEW-CASCADE | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
121669112 | F | LC | ETL.6880.POLE.WOOD | 44677460 | LAKEVLLE | SONOMA | 2021-07-05 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44677460 | 2017-10-21 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2017-10-21 | Ceramic | Suspension |  |  |  |  | 0.0086765 | 712.3741
121715503 | B | LC | ETL.6950.INSL.NCER | 44944274 | SACTO | SIERRA | 2021-07-12 | 2021-10-12 | ETL.6950 | GOLD HILL #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44944253 | 2020-04-22 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-04-22 | Glass | Dead End |  |  |  |  | 0.0067899 | 143.5013 | 0.97435
121717217 | E | LC | ETL.5970.TOWR | 40589502 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.5970 | DIABLO-MIDWAY #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40589502 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 1.8417e-07 | 2439.0273 | 0.0004492
121721612 | F | LC | ETL.1820.POLE.WDPS | 44560604 | EUREKA | HUMBOLDT | 2021-07-13 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44560135 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.088873 | 142.4119
121722694 | E | LC | ETL.1450.POLE.WOOD | 42572751 | SACTO | SIERRA | 2021-06-12 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42572751 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 0.0047827 | 47.5526 | 0.22743
121731641 | B | LC | ETL.6020.TOWR | 40660399 | TABLEMTN | NORTH VALLEY | 2021-07-14 | 2021-09-01 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660399 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 3.0386e-07 | 791.1504
121738574 | F | LC | ETL.1820.POLE.WDPS | 44562663 | EUREKA | HUMBOLDT | 2021-07-13 | 2021-09-23 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44562378 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.23795 | 47.5295
121748798 | F | LC | ETL.1820.POLE.WOOD | 45106289 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45106289 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Ceramic | Suspension | [5 empty] | 6300.0015
121749916 | E | LC | ETL.4040.POLE.STPS | 45100483 | TABLEMTN | NORTH VALLEY | 2021-07-14 | 2021-08-05 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | DLFL | 42622397 |  | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00090329 | 142.4582
121750073 | E | LC | ETL.1810.TOWR | 44321395 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Hardware-Tower | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44321395 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Suspension |  |  |  |  | 4.1599e-08
121750073 | E | LC | ETL.1810.TOWR | 44321395 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Hardware-Tower | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44321395 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.1599e-08
121758761 | B | LC | ETL.6280.POLE.WOOD | 40600571 | TABLEMTN | NORTH VALLEY | 2021-07-19 | 2021-10-11 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40600571 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 4.3117e-05 | 490.3705
121771795 | E | LC | ETL.1810.INSL.CERA | 40633930 | EUREKA | HUMBOLDT | 2021-07-19 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44321390 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 0.003195
121792349 | E | LC | ETL.9240.TOWR | 43249705 | PISMOBCH | LOS PADRES | 2021-07-23 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 43249705 |  | LATTICE STEEL TOWER | [9 empty] | 4561.3721
121805318 | B | LC | ETL.6290.POLE.WOOD | 40769623 | TABLEMTN | NORTH VALLEY | 2021-07-27 | 2021-10-27 | ETL.6290 | CARIBOU-PLUMAS JCT | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40769623 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.28783 | 1043.9412
121809523 | E | LC | ETL.8365.POLE.WOOD | 40912556 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40912556 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | Dead End |  |  |  |  | 0.0071613
121815433 | F | LC | ETL.8365.POLE.NWOD | 40912533 | EUREKA | HUMBOLDT | 2021-07-29 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40912533 | 2010-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.00079006
121818269 | E | LC | ETL.7390.POLE.WDPS | 44411994 | LAKEVLLE |  | 2021-07-29 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44411993 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.064411 | 1344.7017 | 86.6138
121818291 | E | LC | ETL.7390.POLE.WDPS | 44411995 | LAKEVLLE |  | 2021-07-29 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44411993 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.064411 | 1344.7017 | 86.6138
121957254 | E | LC | ETL.1440.POLE.STPS | 44963254 | SACTO | SIERRA | 2021-03-24 | 2021-11-29 | ETL.1440 | DRUM-SUMMIT #1 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44961228 | 2020-06-03 | 3-Pole Non Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 1.4832e-06 | 58.6018
122059589 | E | LC | ETL.4780.INSL.CERA | 40846232 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129388 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1984-01-01 | Glass | Dead End |  |  |  |  | 0.0012319 | 886.3674 | 1.0919
122113342 | E | LC | ETL.8170.POLE.WOOD | 40586386 | EUREKA | HUMBOLDT | 2021-09-28 |  | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | Missing | [Install] | Tier2 |  |  | PEND | [11 empty] | 0.0089525 | 79.1724 | 0.70879
118497645 | E | LC | ETL.1710.POLE.WDPS | 44510527 | MOSSLNDG | CENTRAL COAST | 2020-02-05 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44509652 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00057372 | 0.065147 | 3.7376e-05
118718179 | A | LC | ETL.1420.INSL.NCER | 40785252 | SACTO | SACRAMENTO | 2020-03-18 | 2020-04-14 | ETL.1420 | DRUM-RIO OSO #1 | Emergency-Steel | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756201 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm |  | Polymer | [5 empty] | 7.6291e-05 | 158.3103
118780058 | E | LC | ETL.1420.TOWR | 40594933 | SACTO | SACRAMENTO | 2020-04-06 | 2021-03-05 | ETL.1420 | DRUM-RIO OSO #1 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40594933 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2019-09-05 | Glass | Suspension |  |  |  |  | 0.00030944 | 33.2954
118780058 | E | LC | ETL.1420.TOWR | 40594933 | SACTO | SACRAMENTO | 2020-04-06 | 2021-03-05 | ETL.1420 | DRUM-RIO OSO #1 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40594933 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.00030944 | 33.2954
118917784 | E | LC | ETL.5100.TOWR | 40810615 | MOSSLNDG | SAN JOSE | 2020-04-14 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40810615 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2005-01-01 | Non Ceramic | Dead End |  |  |  |  | 9.7934e-08 | 1772.1183 | 0.00017355
118917784 | E | LC | ETL.5100.TOWR | 40810615 | MOSSLNDG | SAN JOSE | 2020-04-14 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40810615 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2005-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 9.7934e-08 | 1772.1183 | 0.00017355
118937524 | E | LC | ETL.1651.POLE.WOOD | 40584976 | LAKEVLLE | SONOMA | 2020-04-20 | 2021-07-10 | ETL.1651 | MISSION POWER TAP | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40584976 | 1989-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1989-01-01 | Porcelain | Dead End |  |  |  |  | 0.015035 | 2693.2188
118940538 | E | LC | ETL.6330.POLE.NWOD | 44673308 | TABLEMTN | NORTH VALLEY | 2020-04-22 | 2021-04-19 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44673308 | 2018-11-17 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-17 | Polymer | Post |  |  |  |  | 1.5213e-06 | 1502.9633
118948306 | F | LC | ETL.6220.POLE.WOOD | 40769379 | EUREKA | HUMBOLDT | 2020-04-24 | 2021-07-13 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
118977399 | F | LC | ETL.6220.POLE.WOOD | 40769396 | EUREKA | HUMBOLDT | 2020-05-03 | 2021-10-21 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40769396 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.38893 | 889.3207
118987502 | F | LC | ETL.8210.POLE.NWOD | 44845126 | VICTOR | STOCKTON | 2020-04-20 |  | ETL.8210 | VALLEY SPRINGS #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44845126 | 2019-06-05 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-06-05 | Polymer | Dead End |  |  |  |  | 0.0010934 | 4306.811
118992043 | E | LC | ETL.2720.INSL | 40773202 | CONCORD | DIABLO | 2020-05-04 | 2021-06-14 | ETL.2720 | MORAGA-OAKLAND #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40745884 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 0.00083106 | 0.065158
118993749 | E | LC | ETL.2700.TOWR | 40745853 | CONCORD | EAST BAY | 2020-05-05 | 2021-04-01 | ETL.2700 | MORAGA-CLAREMONT #1 | Connector | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40745853 | 1944-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1944-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00025656 | 0.065158
118993749 | E | LC | ETL.2700.TOWR | 40745853 | CONCORD | EAST BAY | 2020-05-05 | 2021-04-01 | ETL.2700 | MORAGA-CLAREMONT #1 | Connector | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40745853 | 1944-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1944-01-01 | Ceramic | Dead End |  |  |  |  | 0.00025656 | 0.065158
119001782 | B | LC | ETL.1110.POLE.WDPS | 44423388 | TABLEMTN | HUMBOLDT | 2020-05-08 | 2020-05-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423387 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00082433 | 6712.2026
119024790 | E | LC | ETL.5220.TOWR | 40765418 | METCALF | PENINSULA | 2020-05-12 | 2021-01-20 | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40765418 | 1963-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1963-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.012622 | 31.7081
119024790 | E | LC | ETL.5220.TOWR | 40765418 | METCALF | PENINSULA | 2020-05-12 | 2021-01-20 | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40765418 | 1963-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1963-01-01 | Ceramic | Dead End |  |  |  |  | 0.012622 | 31.7081
119035575 | E | LC | ETL.1650.POLE.WOOD | 40659189 | LAKEVLLE | SONOMA | 2020-05-11 | 2021-03-16 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40659189 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 5.3451e-05 | 3938.675
119045868 | E | LC | ETL.1420.TOWR | 40654190 | SACTO | SIERRA | 2020-05-19 | 2021-02-01 | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40654190 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm | 2015-08-13 | Polymer | Suspension |  |  |  |  | 3.3209e-07 | 0.090454
119082452 | E | LC | ETL.6220.POLE.WOOD | 40862511 | EUREKA | HUMBOLDT | 2020-05-27 | 2020-07-23 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40862511 |  | Single Wood Pole | DDE-A - Double Dead End Angle | 2019-06-29 | Glass | Dead End |  |  |  |  | 0.17924 | 633.4258
119082763 | F | LC | ETL.6760.POLE.WOOD | 40824298 | SACTO | SIERRA | 2020-05-28 | 2021-02-10 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40824298 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.028452 | 126.7574
119087427 | E | LC | ETL.6470.POLE.WOOD | 40760707 | SACTO | SIERRA | 2020-06-01 | 2020-07-02 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760707 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.022755 | 142.4317
119087897 | E | LC | ETL.6380.POLE.WOOD | 40666996 | LAKEVLLE | HUMBOLDT | 2020-05-14 | 2021-03-08 | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40666996 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 4.2281e-06 | 5275.2607
119099093 | E | LC | ETL.6520.POLE.WOOD | 40668767 | SACTO | SIERRA | 2020-06-03 | 2021-06-09 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40668767 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.003367 | 4925.5078
119105919 | E | LC | ETL.7300.POLE.WOOD | 40877870 | TABLEMTN |  | 2020-06-04 | 2021-03-26 | ETL.7300 | KILARC-DESCHUTES | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877870 |  | Single Wood Pole | T-1 - Tri Post | 2018-06-03 | Polymer | Post |  |  |  |  | 0.00011919 | 5053.5459
119112124 | F | LC | ETL.8240.POLE.WOOD | 40768897 | VICTOR | STOCKTON | 2020-06-01 | 2021-02-09 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40768897 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0039182 | 3815.678
119116060 | F | LC | ETL.5290.TOWR | 40591693 | PISMOBCH | LOS PADRES | 2020-05-26 | 2021-01-20 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591693 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-01-26 | Ceramic | Suspension |  |  |  |  | 1.248e-08 | 2599.0684
119116193 | F | LC | ETL.6720.POLE.WOOD | 40769510 | TABLEMTN | NORTH VALLEY | 2020-05-27 |  | ETL.6720 | DESABLA-CENTERVILLE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | PEND
119117331 | E | LC | ETL.1450.POLE.WOOD | 44212206 | SACTO | SIERRA | 2020-06-01 | 2020-08-19 | ETL.1450 | DRUM-SUMMIT #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44212206 | 2013-09-30 | Single Wood Pole | 3P DV - 3 Pole Double Vertical | 2013-09-30 | Ceramic | Suspension |  |  |  |  | 0.00024798 | 1344.8513
119120071 | F | LC | ETL.7930.POLE.WOOD | 40585825 | MOSSLNDG | CENTRAL COAST | 2020-06-03 |  | ETL.7930 | SALINAS-LAURELES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40585825 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 0.060918 | 190.6452
119126060 | E | LC | ETL.6280.POLE.NWOD | 40868117 | TABLEMTN | NORTH VALLEY | 2020-06-03 |  | ETL.6280 | CARIBOU #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40868117 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Non Ceramic | Pin |  |  |  |  | 0.00032849 | 4683.9302 | 1.5386
119140015 | E | LC | ETL.8170.POLE.WOOD | 40585387 | EUREKA | HUMBOLDT | 2020-06-03 | 2021-11-17 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585387 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.14685 | 553.6737 | 81.3091
119164323 | E | LC | ETL.8170.INSL.CERA | 40699975 | EUREKA | HUMBOLDT | 2020-06-14 | 2021-11-09 | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564282 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.057067
119164323 | E | LC | ETL.8170.INSL.CERA | 40699975 | EUREKA | HUMBOLDT | 2020-06-14 | 2021-11-09 | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564282 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.057067
119164323 | E | LC | ETL.8170.INSL.CERA | 40699975 | EUREKA | HUMBOLDT | 2020-06-14 | 2021-11-09 | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564282 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.057067
119165388 | F | LC | ETL.7270.POLE.WDPS | 44421139 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2020-07-27 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44421138 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0030242 | 3563.1055
119184249 | B | LC | ETL.6470.POLE.WOOD | 40593299 | SACTO | SIERRA | 2020-06-17 | 2020-07-14 | ETL.6470 | COLGATE-ALLEGHANY | Switch-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119188471 | E | LC | ETL.6220.POLE.WOOD | 40752629 | EUREKA | HUMBOLDT | 2020-06-19 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40752629 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.15763 | 3423.78 | 539.7045
119195923 | F | LC | ETL.6470.POLE.WOOD | 40767336 | SACTO | SIERRA | 2020-06-22 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767336 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.034596 | 727.8687
119195927 | E | LC | ETL.6470.POLE.WOOD | 40590443 | SACTO | SIERRA | 2020-06-22 | 2021-07-29 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.069484 | 142.5149
119198884 | E | LC | ETL.1710.INSL.NCER | 44879495 | MOSSLNDG | CENTRAL COAST | 2020-06-22 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44879477 | 2019-07-26 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | 2019-07-26 | Polymer | Suspension |  |  |  |  | 8.7427e-08
119198884 | E | LC | ETL.1710.INSL.NCER | 44879495 | MOSSLNDG | CENTRAL COAST | 2020-06-22 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44879477 | 2019-07-26 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | 2019-07-26 | Polymer | Suspension |  |  |  |  | 8.7427e-08
119198884 | E | LC | ETL.1710.INSL.NCER | 44879495 | MOSSLNDG | CENTRAL COAST | 2020-06-22 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44879477 | 2019-07-26 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | 2019-07-26 | Polymer | Suspension |  |  |  |  | 8.7427e-08
119199547 | E | LC | ETL.6470.POLE.WOOD | 40760745 | SACTO | SIERRA | 2020-06-23 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760745 |  | Single Wood Pole | T2N | 2021-07-13 | Polymer | Post |  |  |  |  | 0.20217 | 158.2723
119200231 | E | LC | ETL.5440.POLE.WDPS | 44558389 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-08-25 | ETL.5440 | PIT #6 JCT-ROUND MTN | Vegetation | Overgrown | [Trim, No Action Taken] | Tier2 |  |  | CNCL
119205605 | F | LC | ETL.7290.POLE.WOOD | 40817426 | TABLEMTN | NORTH VALLEY | 2020-06-24 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40817426 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.015644 | 1333.3085
119209668 | E | LC | ETL.4950.TOWR | 40812167 | LAKEVLLE | SONOMA | 2020-06-25 | 2021-06-22 | ETL.4950 | FULTON-LAKEVILLE | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40812167 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 4.5529e-05 | 15.891
119232861 | E | LC | ETL.7640.POLE.WOOD | 44825353 | TABLEMTN | NORTH VALLEY | 2020-06-29 |  | ETL.7640 | MTN GATE JCT-CASCADE | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44825353 | 2019-07-18 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-07-18 | Glass | Double Dead End |  |  |  |  | 0.00015415 | 47.5422 | 0.0073288
119235699 | B | LC | ETL.7270.POLE.WOOD | 40908541 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2020-08-12 | ETL.7270 | KESWICK-TRINITY | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908541 |  | Single Wood Pole | TRP DE - Tramp Dead End |  | Porcelain | [5 empty] | 0.018656 | 4067.0386
119295873 | E | LC | ETL.6900.INSL.NCER | 40699139 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Insulator-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | PEND | 40667740 | 1932-01-01 | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.00010231 | 1171.3424 | 0.11984
119308494 | E | LC | ETL.8060.POLE.WOOD | 40602276 | SACTO | SIERRA | 2020-07-02 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40602276 |  | Single Wood Pole | T2N | 2021-08-18 | Polymer | Post |  |  |  |  | 0.010644 | 696.1766
119315104 | E | LC | ETL.7140.POLE.WOOD | 40585006 | LAKEVLLE | NORTH BAY | 2020-07-06 | 2021-04-29 | ETL.7140 | IGNACIO-BOLINAS #1 | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585006 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 0.0043533 | 2487.8337
119325842 | E | LC | ETL.7180.POLE.WOOD | 40751211 | LAKEVLLE | SONOMA | 2020-07-07 | 2021-04-21 | ETL.7180 | IGNACIO-BOLINAS #2 | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751211 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Glass | [5 empty] | 7.2628e-06 | 1698.0013
119326036 | F | LC | ETL.1710.TOWR | 40815170 | MOSSLNDG | CENTRAL COAST | 2020-07-07 | 2021-03-24 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40815170 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-06 | Glass | Double Dead End |  |  |  |  | 2.2668e-06 | 0.065147
119326036 | F | LC | ETL.1710.TOWR | 40815170 | MOSSLNDG | CENTRAL COAST | 2020-07-07 | 2021-03-24 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40815170 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-05 | Glass | Dead End |  |  |  |  | 2.2668e-06 | 0.065147
119329462 | F | LC | ETL.8170.POLE.WDPS | 44769574 | EUREKA | HUMBOLDT | 2020-07-07 | 2021-06-14 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906466 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.029769 | 0.065152
119332652 | B | LC | ETL.1650.POLE.WDPS | 44510877 | LAKEVLLE | SONOMA | 2020-07-08 | 2020-12-30 | ETL.1650 | GEYSERS #3-CLOVERDALE | Other | Customer Issue | [Customer Refusal] | Tier3 | Tier 3 | Within Both | COMP | 44510877 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00044737
119332652 | B | LC | ETL.1650.POLE.WDPS | 44510877 | LAKEVLLE | SONOMA | 2020-07-08 | 2020-12-30 | ETL.1650 | GEYSERS #3-CLOVERDALE | Other | Customer Issue | [Customer Refusal] | Tier3 | Tier 3 | Within Both | COMP | 44510877 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00044737
119335935 | F | LC | ETL.6900.POLE.WOOD | 40616449 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-06-30 | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Vegetation | Overgrown | [Trim, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40616449 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 3.0106e-05 | 0.065158
119336154 | E | LC | ETL.6300.POLE.WOOD | 40600738 | TABLEMTN |  | 2020-07-07 | 2021-07-15 | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119338799 | E | LC | ETL.7590.POLE.WOOD | 40874222 | MOSSLNDG | DE ANZA | 2020-07-08 | 2020-09-09 | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40874222 |  | Single Wood Pole | 3P DDE-A - 3 Pole Double Dead End Angle |  | Non Ceramic | Double Dead End |  |  |  |  | 0.020687 | 1140.4965
119340322 | F | LC | ETL.6280.POLE.WOOD | 40758659 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40758659 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 4.4843e-06 | 1202.1041
119351144 | B | LC | ETL.7180.POLE.WOOD | 40825721 | LAKEVLLE | SONOMA | 2020-07-10 | 2020-09-24 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825721 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Glass | [5 empty] | 5.6785e-06 | 1379.035
119359579 | F | LC | ETL.7030.POLE.WOOD | 40827590 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40827590 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0025404 | 5598.0385
119376560 | E | LC | ETL.1440.POLE.WDPS | 44837655 | SACTO | SACRAMENTO | 2020-07-14 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40654770 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00051276 | 1819.4475
119376866 | F | LC | ETL.2770.TOWR | 40581569 | CONCORD | DIABLO | 2020-07-15 | 2021-03-16 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581569 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 5.3268e-07 | 15.8932
119379118 | E | LC | ETL.8170.POLE.WOOD | 40870163 | EUREKA | HUMBOLDT | 2020-07-15 | 2020-09-28 | ETL.8170 | TRINITY-MAPLE CREEK | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40870163 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.010603 | 6060.7563
119475345 | F | LC | ETL.3742.TOWR | 41135456 | CONCORD | DIABLO | 2020-07-20 |  | ETL.3742 | SOBRANTE-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41135456 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 6.341e-07 | 23.8277 | 1.5109e-05
119477228 | E | LC | ETL.1440.POLE.WDPS | 44765209 | SACTO | SACRAMENTO | 2020-07-20 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 40876963 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0020261 | 731.1277
119479204 | E | LC | ETL.8960.POLE.STPS | 44236987 | FRESNO | FRESNO | 2020-07-21 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44236985 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.8436e-07
119485549 | E | LC | ETL.6890.POLE.WOOD | 43250137 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-08-18 | ETL.6890 | FULTON-HOPLAND | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43250137 |  | Single Wood Pole | TP - Tri Pin | [7 empty] | 0.0016316 | 1361.9498
119510094 | F | LC | ETL.5440.POLE.STPS | 44931541 | TABLEMTN | NORTH VALLEY | 2020-07-22 | 2020-08-19 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Tier 2 | Within Both | COMP | 44931492 | 2020-05-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.3277e-05 | 2217.3672
119536304 | E | LC | ETL.5650.TOWR | 40597312 | TABLEMTN | NORTH VALLEY | 2020-07-31 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40597312 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 2.296e-06 | 1301.1877 | 0.0029876
119556862 | E | LC | ETL.8170.POLE.WOOD | 40906421 | EUREKA | HUMBOLDT | 2020-08-04 | 2021-06-21 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906421 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0050233 | 348.1371
119597664 | F | LC | ETL.7590.POLE.WOOD | 40665299 | MOSSLNDG | CENTRAL COAST | 2020-08-10 | 2020-08-12 | ETL.7590 | MONTA VISTA-BURNS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
119603983 | E | LC | ETL.6222.POLE.WOOD | 40808365 | EUREKA | HUMBOLDT | 2020-08-10 |  | ETL.6222 | FORT SEWARD TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40808365 | 1952-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0019762
119627916 | E | LC | ETL.4392.TOWR | 41129347 | LAKEVLLE | SONOMA | 2020-08-17 | 2021-04-12 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129347 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 4.6517e-05 | 842.1265
119627916 | E | LC | ETL.4392.TOWR | 41129347 | LAKEVLLE | SONOMA | 2020-08-17 | 2021-04-12 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129347 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-05-31 | Glass | Suspension |  |  |  |  | 4.6517e-05 | 842.1265
119629199 | F | LC | ETL.6870.POLE.WOOD | 40693782 | SACTO | SIERRA | 2020-08-17 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40693782 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.043642 | 0.065152
119630690 | F | LC | ETL.6870.POLE.WOOD | 40751842 | SACTO | SIERRA | 2020-08-17 | 2021-04-03 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119636067 | E | LC | ETL.6870.POLE.WOOD | 40664841 | SACTO | SIERRA | 2020-08-17 | 2021-05-20 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664841 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.30504 | 0.065152
119649206 | E | LC | ETL.5930.TOWR | 40600036 | CONCORD | DIABLO | 2020-08-21 | 2020-11-02 | ETL.5930 | PARKWAY-MORAGA | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40600036 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.0324e-06 | 15.8932
119649206 | E | LC | ETL.5930.TOWR | 40600036 | CONCORD | DIABLO | 2020-08-21 | 2020-11-02 | ETL.5930 | PARKWAY-MORAGA | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40600036 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.0324e-06 | 15.8932
119656329 | A | LC | ETL.7590.POLE.WOOD | 40678356 | MOSSLNDG | CENTRAL COAST | 2020-08-21 | 2020-10-01 | ETL.7590 | MONTA VISTA-BURNS | Emergency-Wood | Other | [Replace, Completed] | Tier3 |  |  | COMP
119671886 | F | LC | ETL.1110.POLE.WDPS | 44423934 | TABLEMTN | HUMBOLDT | 2020-08-24 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44423932 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012442 | 6191.3389
119679461 | E | LC | ETL.1110.POLE.WDPS | 44423329 | TABLEMTN | HUMBOLDT | 2020-08-26 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423327 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0016128 | 6191.5791
119685827 | E | LC | ETL.1110.POLE.WDPS | 44423907 | TABLEMTN | HUMBOLDT | 2020-08-25 | 2021-04-13 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44423905 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012629 | 6615.6465
119697323 | A | LC | ETL.6230.POLE.WOOD | 40618238 | MOSSLNDG | CENTRAL COAST | 2020-08-31 | 2020-09-19 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119699905 | E | LC | ETL.8253.POLE.WOOD | 40580314 | VICTOR | STOCKTON | 2020-08-29 |  | ETL.8253 | IONE TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40580314 | 1987-01-01 | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00051216 | 2266.8525 | 1.161
119709621 | F | LC | ETL.1421.TOWR | 40581248 | SACTO | SIERRA | 2020-08-29 | 2021-03-08 | ETL.1421 | DUTCH FLAT #2 TAP | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581248 | 1966-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | [7 empty] | 0.001368 | 664.5352
119720329 | E | LC | ETL.7820.POLE.WOOD | 40768596 | LAKEVLLE | HUMBOLDT | 2020-06-22 | 2021-03-11 | ETL.7820 | POTTER VALLEY-WILLITS | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40768596 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0019656 | 650.3827
119720479 | A | LC | ETL.6240.POLE.WOOD | 40599250 | MOSSLNDG | CENTRAL COAST | 2020-09-05 | 2020-10-01 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40599250 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.15789 | 110.8153
119721444 | F | LC | ETL.1400.POLE.WDPS | 44986665 | VICTOR | YOSEMITE | 2020-07-28 | 2021-05-13 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40856833 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.0071474 | 63.3763
119727800 | A | LC | ETL.7590.POLE.WOOD | 40665307 | MOSSLNDG | CENTRAL COAST | 2020-09-08 | 2020-10-21 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119750999 | E | LC | ETL.6310.POLE.WOOD | 40868663 | TABLEMTN | NORTH VALLEY | 2020-08-13 | 2021-08-19 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.4401e-05 | 3691.8762
119765501 | F | LC | ETL.6470.POLE.WOOD | 40760719 | SACTO | SIERRA | 2020-09-08 | 2021-02-12 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL | [12 empty] | 544.4154
119768780 | E | LC | ETL.8170.POLE.WOOD | 40877935 | EUREKA | HUMBOLDT | 2020-09-09 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40877935 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Ceramic | [5 empty] | 0.85257 | 158.2535 | 134.922
119777378 | F | LC | ETL.7490.POLE.STPS | 44963242 | EUREKA | HUMBOLDT | 2020-08-12 |  | ETL.7490 | MAPLE CREEK-HOOPA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44957534 | 2020-08-04 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.002957 | 110.7793
119780374 | E | LC | ETL.6770.POLE.WOOD | 40862142 | SACTO | SIERRA | 2020-09-10 | 2021-04-21 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119788233 | E | LC | ETL.5140.POLE.WDPS | 44557510 | SACTO | SACRAMENTO | 2020-09-17 | 2021-11-17 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44553905 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012243 | 71.3655 | 0.087372
119788554 | F | LC | ETL.8060.POLE.WOOD | 44156137 | SACTO | SIERRA | 2020-09-17 | 2021-08-23 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44156137 | 2013-09-20 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2013-09-20 | Polymer | Suspension |  |  |  |  | 0.0059948 | 15.8859
119788677 | E | LC | ETL.4392.INSL.NCER | 40893646 | LAKEVLLE | SONOMA | 2020-09-15 | 2021-03-25 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119789026 | E | LC | ETL.1450.POLE.WDPS | 44557544 | SACTO | SACRAMENTO | 2020-09-18 |  | ETL.1450 | DRUM-SUMMIT #2 | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44553957 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.00064757 | 95.0021 | 0.061521
119790599 | F | LC | ETL.8365.POLE.WOOD | 40906654 | EUREKA | HUMBOLDT | 2020-09-17 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40906654 |  | Single Wood Pole | T2N | 2021-04-25 | Polymer | Post |  |  |  |  | 0.018253
119794506 | E | LC | ETL.1600.TOWR | 40587741 | LAKEVLLE | SONOMA | 2020-09-21 | 2020-10-07 | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587741 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-06-20 | Glass | Suspension |  |  |  |  | 3.142e-05 | 174.2843
119794506 | E | LC | ETL.1600.TOWR | 40587741 | LAKEVLLE | SONOMA | 2020-09-21 | 2020-10-07 | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587741 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 3.142e-05 | 174.2843
119818785 | F | LC | ETL.8060.POLE.WOOD | 40681441 | SACTO | SIERRA | 2020-08-28 | 2021-07-06 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40681441 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.058307 | 125.0488
119837053 | E | LC | ETL.1073.POLE.WDPS | 40744854 | VICTOR | YOSEMITE | 2020-09-29 | 2021-03-17 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40744854 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0019221
119837053 | E | LC | ETL.1073.POLE.WDPS | 40744854 | VICTOR | YOSEMITE | 2020-09-29 | 2021-03-17 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40744854 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0019221
119866604 | B | LC | ETL.7850.INSL.CERA | 40855033 | EUREKA | HUMBOLDT | 2020-10-07 | 2020-11-30 | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Damper-Wood | Missing | [Install, Completed] | Tier2 |  |  | COMP
119983671 | E | LC | ETL.6220.POLE.WOOD | 40614552 | EUREKA | HUMBOLDT | 2020-11-02 | 2021-01-27 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40614552 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.25682
120044107 | F | LC | ETL.6880.POLE.WOOD | 40912458 | LAKEVLLE | NORTH BAY | 2020-10-06 | 2021-04-19 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40912458 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2020-03-03 | Glass | Dead End |  |  |  |  | 0.012743 | 1709.667
120107890 | E | LC | ETL.3170.INSL | 40773418 | CONCORD | EAST BAY | 2020-11-19 |  | ETL.3170 | OLEUM-MARTINEZ | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40746029 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 2.6332e-05 | 47.7671 | 0.0012578
120107890 | E | LC | ETL.3170.INSL | 40773418 | CONCORD | EAST BAY | 2020-11-19 |  | ETL.3170 | OLEUM-MARTINEZ | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40746029 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 2.6332e-05 | 47.7671 | 0.0012578
120133943 | F | LC | ETL.6280.POLE.WOOD | 40614985 | TABLEMTN | NORTH VALLEY | 2020-10-21 | 2021-09-14 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 2.9953e-05 | 844.7215
120164961 | F | LC | ETL.1450.POLE.STPS | 44339153 | SACTO | SIERRA | 2020-12-05 | 2021-06-30 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44339151 | 2018-12-13 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.8817e-06 | 2056.7583
120189172 | E | LC | ETL.8650.POLE.NWOD | 44420200 | FRESNO | FRESNO | 2020-12-11 |  | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44420200 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0058416 | 2214.1416 | 12.9342
120200129 | F | LC | ETL.1600.TOWR | 40762239 | LAKEVLLE | SONOMA | 2020-12-14 | 2021-02-21 | ETL.1600 | FULTON-PUEBLO | Fence / Gate | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762239 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 6.8886e-09 | 79.1687
120200129 | F | LC | ETL.1600.TOWR | 40762239 | LAKEVLLE | SONOMA | 2020-12-14 | 2021-02-21 | ETL.1600 | FULTON-PUEBLO | Fence / Gate | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762239 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-06-20 | Glass | Suspension |  |  |  |  | 6.8886e-09 | 79.1687
120232526 | F | LC | ETL.8365.POLE.NWOD | 40912590 | EUREKA | HUMBOLDT | 2020-11-20 | 2021-07-19 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40912590 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End | 2021-04-22 | Glass Silicone Coated | Dead End |  |  |  |  | 0.00071448
120232889 | E | LC | ETL.3020.INSL.CERA | 40671458 | CONCORD | EAST BAY | 2020-12-23 |  | ETL.3020 | NEWARK-JARVIS #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40644301 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.7919e-06
120232889 | E | LC | ETL.3020.INSL.CERA | 40671458 | CONCORD | EAST BAY | 2020-12-23 |  | ETL.3020 | NEWARK-JARVIS #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40644301 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-11-03 | Ceramic | Dead End |  |  |  |  | 3.7919e-06
120252862 | F | LC | ETL.5770.TOWR | 40604771 | CONCORD | DIABLO | 2020-12-14 |  | ETL.5770 | TIDEWATER-SOBRANTE | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40604771 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2017-09-13 | Ceramic | Suspension |  |  |  |  | 1.1572e-07 | 0.066432
120447777 | F | LC | ETL.2141.POLE.WOOD | 40669197 | MIDWAY | KERN | 2021-01-19 | 2021-04-05 | ETL.2141 | VEDDER TAP | Road | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40669197 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 7.2746e-05 | 6742.7881
120541651 | E | LC | ETL.1450.POLE.WDPS | 44561212 | SACTO | SACRAMENTO | 2020-07-08 | 2021-11-08 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44559159 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.018236 | 47.5273 | 0.86671
120658284 | F | LC | ETL.4223.POLE.WOOD | 40753186 | TABLEMTN | NORTH VALLEY | 2021-03-18 |  | ETL.4223 | KANAKA TAP | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 |  |  | PEND
120659174 | F | LC | ETL.5100.TOWR | 40753006 | MOSSLNDG | SAN JOSE | 2021-03-18 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40753006 | 1950-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2005-01-01 | Non Ceramic | Dead End |  |  |  |  | 6.8379e-08 | 2214.6096 | 0.00015143
120680443 | E | LC | ETL.2540.POLE.WOOD | 40585532 | MOSSLNDG | SAN JOSE | 2021-03-22 | 2021-09-23 | ETL.2540 | METCALF-GREEN VALLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40585532 | 1952-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1952-01-01 | Polymer | Double Dead End - Suspension |  |  |  |  | 0.29604 | 2452.0347
120696336 | E | LC | ETL.4040.POLE.STPS | 44923034 | TABLEMTN | NORTH VALLEY | 2021-03-26 | 2021-09-15 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44922940 | 2020-03-31 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.7636e-05 | 2010.385
120697188 | E | LC | ETL.3830.INSL | 40795274 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40764244 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 0.00014179 | 4005.7028 | 0.56799
120719429 | E | LC | ETL.7390.POLE.WOOD | 40860893 | LAKEVLLE | SONOMA | 2021-03-31 | 2021-06-29 | ETL.7390 | LAYTONVILLE-COVELO | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860893 |  | Single Wood Pole | T2N | 2021-06-22 | Polymer | Post |  |  |  |  | 0.013557 | 696.1808
120719726 | E | LC | ETL.4590.INSL.CERA | 40849159 | TABLEMTN | NORTH VALLEY | 2021-03-31 |  | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40820395 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 1.0223e-07 | 4925.1411 | 0.00050348
120720996 | E | LC | ETL.7390.POLE.WOOD | 40768639 | LAKEVLLE | SONOMA | 2021-03-31 | 2021-07-26 | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
120734671 | E | LC | ETL.4040.POLE.STPS | 44647085 | TABLEMTN | NORTH VALLEY | 2021-04-02 | 2021-09-11 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44646910 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00021353 | 541.2549
120735525 | E | LC | ETL.1070.POLE.WOOD | 40587319 | VICTOR | STOCKTON | 2021-04-02 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40587319 | 1998-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1998-01-01 | Polymer | Post |  |  |  |  | 0.00013003 | 2393.3862 | 0.3112
120737348 | E | LC | ETL.7390.POLE.WOOD | 40876449 | LAKEVLLE | SONOMA | 2021-04-02 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40876449 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.089062
120743367 | F | LC | ETL.5960.TOWR | 40760918 | PISMOBCH | LOS PADRES | 2021-04-05 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40760918 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-08-05 | Glass | Suspension |  |  |  |  | 2.2892e-08 | 5161.2417 | 0.00011815
120744607 | E | LC | ETL.1350.POLE.NWOD | 44993891 | TABLEMTN | NORTH VALLEY | 2021-04-05 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993891 | 2020-06-16 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-16 | Glass | Dead End |  |  |  |  | 0.0002501 | 142.6993
120750687 | F | LC | ETL.3820.TOWR | 40658613 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40658613 | 1962-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1989-01-01 | Glass | Dead End |  |  |  |  | 8.828e-08 | 1962.8882 | 0.00017328
120750840 | E | LC | ETL.7590.POLE.WOOD | 40767268 | MOSSLNDG | CENTRAL COAST | 2021-04-06 |  | ETL.7590 | MONTA VISTA-BURNS | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40767268 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Double Dead End |  |  |  |  | 0.15498 | 63.351 | 9.8179
120754514 | B | LC | ETL.3830.INSL | 40703058 | VICTOR | STOCKTON | 2021-04-06 | 2021-06-03 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40642845 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.1099e-08 | 3950.2275
120761526 | E | LC | ETL.6510.POLE.WOOD | 40599469 | SACTO | SACRAMENTO | 2021-04-07 |  | ETL.6510 | COLGATE-SMARTVILLE #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40599469 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.0065e-05 | 1711.8802 | 0.01723
120767251 | E | LC | ETL.8240.POLE.WOOD | 40600041 | VICTOR | STOCKTON | 2021-04-08 | 2021-08-30 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600041 | 1995-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0040148 | 2535.9104
120771611 | B | LC | ETL.3190.TOWR | 40910325 | TABLEMTN | NORTH VALLEY | 2021-04-08 | 2021-06-24 | ETL.3190 | CARIBOU-PALERMO | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910325 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 0.1149 | 4523.73
120771774 | E | LC | ETL.5934.INSL.CERA | 40829383 | FRESNO | FRESNO | 2021-04-09 |  | ETL.5934 | TEMPLETON-GATES | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40805225 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.0020904
120785789 | E | LC | ETL.8250.POLE.WOOD | 40821935 | VICTOR | STOCKTON | 2021-04-10 | 2021-08-25 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40821935 | 1957-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 5.7796e-05 | 1460.6149
120808382 | E | LC | ETL.1450.POLE.WDPS | 44549922 | SACTO | SACRAMENTO | 2021-04-13 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44549464 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014354 | 47.5526 | 0.068255
120808946 | F | LC | ETL.8365.POLE.NWOD | 44634855 | EUREKA | HUMBOLDT | 2021-04-13 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44634855 | 2018-07-11 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2018-07-11 | Polymer | Suspension |  |  |  |  | 0.00020656
120810892 | F | LC | ETL.3820.TOWR | 40579598 | VICTOR | STOCKTON | 2021-04-13 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40579598 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-05-11 | Glass | Suspension |  |  |  |  | 4.0685e-06 | 4353.7114 | 0.017713
120810892 | F | LC | ETL.3820.TOWR | 40579598 | VICTOR | STOCKTON | 2021-04-13 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40579598 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | [5 empty] | 4.0685e-06 | 4353.7114 | 0.017713
120811929 | F | LC | ETL.8060.POLE.WOOD | 40681421 | SACTO | SACRAMENTO | 2021-04-14 | 2021-08-27 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40681421 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.029141 | 981.4936
120812754 | F | LC | ETL.9100.POLE.WOOD | 42574218 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 42574218 |  | Single Wood Pole | TPAT - Tri Pin Arm Tramp |  | Porcelain | [5 empty] | 1.0265e-05 | 2740.4846
120813265 | E | LC | ETL.5300.INSL | 40619809 | PISMOBCH | LOS PADRES | 2021-04-14 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40593894 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 2.8871e-07 | 1333.1163 | 0.00038489
120817468 | E | LC | ETL.5850.TOWR | 40603687 | LAKEVLLE | SACRAMENTO | 2021-04-14 | 2021-10-20 | ETL.5850 | VACA-PARKWAY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40603687 | 1946-01-01 | LATTICE STEEL TOWER | Unknown | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.9042e-07 | 4861.7715 | 0.0028705
120821020 | E | LC | ETL.1680.TOWR | 40818237 | LAKEVLLE | SONOMA | 2021-04-15 | 2021-08-04 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818237 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1978-01-01 | Glass | Other |  |  |  |  | 1.744e-06 | 5274.8779
120821020 | E | LC | ETL.1680.TOWR | 40818237 | LAKEVLLE | SONOMA | 2021-04-15 | 2021-08-04 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818237 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1978-01-01 | Glass | Dead End |  |  |  |  | 1.744e-06 | 5274.8779
120831491 | E | LC | ETL.4392.INSL.NCER | 45131108 | LAKEVLLE | SONOMA | 2021-04-16 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40659289 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-03-23 | Glass | Suspension |  |  |  |  | 4.4865e-06 | 110.894 | 0.00049752
120839391 | E | LC | ETL.5980.TOWR | 40761101 | PISMOBCH | LOS PADRES | 2021-04-19 |  | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40761101 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-03 | Glass | Suspension |  |  |  |  | 1.0764e-10 | 3325.55 | 3.5797e-07
120859995 | F | LC | ETL.4440.TOWR | 40591411 | TABLEMTN | NORTH VALLEY | 2021-04-13 | 2021-07-19 | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40591411 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 4.0548e-06 | 617.2722
120861068 | B | LC | ETL.8365.POLE.WOOD | 40906654 | EUREKA | HUMBOLDT | 2021-04-21 | 2021-05-06 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906654 |  | Single Wood Pole | T2N | 2021-04-25 | Polymer | Post |  |  |  |  | 0.018253
120861318 | E | LC | ETL.8365.POLE.WOOD | 40906655 | EUREKA | HUMBOLDT | 2021-04-21 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Vegetation | Overgrown | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40906655 |  | Single Wood Pole | T1DE - Tri Post Dead End 115 | 2021-04-25 | Glass | Dead End |  |  |  |  | 0.19321
120867390 | E | LC | ETL.8423.INSL.CERA | 40640149 | MOSSLNDG | CENTRAL COAST | 2021-04-22 | 2021-06-09 | ETL.8423 | SALINAS-FORT ORD #2 | Splice-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120874879 | F | LC | ETL.9250.POLE.WOOD | 40749544 | MIDWAY | KERN | 2021-04-22 |  | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40749544 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.044573 | 4848.7817
120874905 | F | LC | ETL.1820.POLE.NWOD | 45018607 | EUREKA | HUMBOLDT | 2021-04-23 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 45018607 | 2017-10-06 | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2017-10-06 | Ceramic | Dead End |  |  |  |  | 0.066848 | 23.8261
120874914 | E | LC | ETL.9250.POLE.WOOD | 40749544 | MIDWAY | KERN | 2021-04-22 | 2021-08-12 | ETL.9250 | TEJON-LEBEC | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40749544 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.044573 | 4848.7817
120880795 | E | LC | ETL.3500.INSL | 40773544 | VICTOR | STOCKTON | 2021-04-24 | 2021-06-17 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40745464 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 2.4057e-05 | 158.3482
120880853 | E | LC | ETL.3500.INSL | 40879090 | VICTOR | STOCKTON | 2021-04-24 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40856683 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 1.8428e-05 | 2626.3723 | 0.048398
120885357 | F | LC | ETL.5510.TOWR | 40590917 | CONCORD | DIABLO | 2021-04-26 | 2021-07-20 | ETL.5510 | PITTSBURG-TESLA #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40590917 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 1.655e-06 | 4876.8511
120895461 | F | LC | ETL.1530.POLE.NWOD | 40662294 | SACTO | SIERRA | 2021-04-13 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40662294 | 1980-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 7.8483e-08 | 743.5351
120900826 | E | LC | ETL.5300.INSL | 40792155 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40762076 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 1.2931e-06 | 5604.0952 | 0.0072467
120903615 | E | LC | ETL.3960.INSL.CERA | 40896178 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40870995 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 1.1373e-08 | 4544.6704 | 5.1685e-05
120903615 | E | LC | ETL.3960.INSL.CERA | 40896178 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40870995 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 1.1373e-08 | 4544.6704 | 5.1685e-05
120911605 | E | LC | ETL.5930.TOWR | 40817006 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40817006 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-29 | Glass | Suspension |  |  |  |  | 4.4213e-07 | 1553.9977 | 0.00068706
120911605 | E | LC | ETL.5930.TOWR | 40817006 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40817006 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-30 | Glass | Suspension |  |  |  |  | 4.4213e-07 | 1553.9977 | 0.00068706
120913765 | F | LC | ETL.6450.POLE.WOOD | 40770130 | TABLEMTN | NORTH VALLEY | 2021-05-01 | 2021-06-25 | ETL.6450 | COLEMAN-SOUTH | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40770130 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00040647 | 6175.3105
120927057 | F | LC | ETL.9100.POLE.WOOD | 44191897 | PISMOBCH | LOS PADRES | 2021-05-01 | 2021-06-29 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL | [11 empty] | 2.6602e-05 | 1746.7943
120932273 | E | LC | ETL.1422.INSL | 40728932 | SACTO | SACRAMENTO | 2021-05-03 |  | ETL.1422 | BRUNSWICK #1 TAP | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40689219 | 1975-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1975-01-01 | Ceramic | Dead End |  |  |  |  | 1.6012e-05 | 287.9709 | 0.0046109
121086095 | E | LC | ETL.1530.INSL.CERA | 40678262 | SACTO | SIERRA | 2021-04-19 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40650093 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 4.2365e-05 | 134.5539 | 0.0057004
121086095 | E | LC | ETL.1530.INSL.CERA | 40678262 | SACTO | SIERRA | 2021-04-19 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40650093 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 4.2365e-05 | 134.5539 | 0.0057004
121190546 | E | LC | ETL.4440.TOWR | 40649851 | TABLEMTN | NORTH VALLEY | 2021-05-11 |  | ETL.4440 | CARIBOU-TABLE MTN | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40649851 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 5.1177e-07 | 4196.3833 | 0.0021476
121321848 | E | LC | ETL.1810.POLE.WDPS | 44557534 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44554035 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.011922
121344564 | E | LC | ETL.6370.SWIT | 43242816 | CONCORD | EAST BAY | 2021-05-17 |  | ETL.6370 | CHRISTIE-WILLOW PASS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | PEND | [8 empty] | KPF | ARCING HORNS ONLY | Manual
121361434 | E | LC | ETL.5920.INSL | 40724817 | CONCORD | EAST BAY | 2021-04-29 |  | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40681921 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-03-22 | Glass | Dead End |  |  |  |  | 9.9409e-07 | 763.1666 | 0.00075866
121361434 | E | LC | ETL.5920.INSL | 40724817 | CONCORD | EAST BAY | 2021-04-29 |  | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40681921 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.9409e-07 | 763.1666 | 0.00075866
121363965 | E | LC | ETL.6880.POLE.WOOD | 40751147 | LAKEVLLE | SONOMA | 2021-05-01 | 2021-08-09 | ETL.6880 | FULTON-CALISTOGA | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL | [12 empty] | 269.1549
121370312 | F | LC | ETL.9340.POLE.NWOD | 40651944 | FRESNO | YOSEMITE | 2021-05-03 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40651944 |  | Light Duty Steel Pole | TH - TriAngle Post 70 | 1925-01-01 | Polymer | Pin |  |  |  |  | 0.0022481 | 5454.9422
121373766 | E | LC | ETL.4550.TOWR | 40817926 | TABLEMTN | NORTH VALLEY | 2021-05-03 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40817926 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 9.3251e-06 | 4895.8999 | 0.045655
121376529 | E | LC | ETL.6760.POLE.WOOD | 40766668 | SACTO | SIERRA | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40766668 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.033304 | 15.8837 | 0.52899
121392171 | E | LC | ETL.1420.TOWR | 40644901 | SACTO | SIERRA | 2021-05-15 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40644901 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-10-20 | Glass | Suspension |  |  |  |  | 7.5863e-05 | 158.3103 | 0.01201
121393237 | E | LC | ETL.5640.TOWR | 40598890 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40598890 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 1.2735e-07 | 4294.4004 | 0.00054688
121397767 | F | LC | ETL.8060.POLE.WOOD | 40828163 | SACTO | SIERRA | 2021-05-18 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40828163 |  | Single Wood Pole | T2N | 2020-10-28 | Polymer | Post |  |  |  |  | 0.010004 | 63.3733
121405588 | E | LC | ETL.6640.POLE.WOOD | 40827036 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Vegetation | Overgrown | [Trim] | Tier2 | Tier 2 | HFRA Removal | PEND | 40827036 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0040489 | 666.0034 | 2.6966
121417846 | E | LC | ETL.5230.INSL | 40796156 | METCALF | DE ANZA | 2021-05-27 |  | ETL.5230 | MONTA VISTA-JEFFERSON #2 | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40765418 | 1963-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1963-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.012622 | 31.7081 | 0.40023
121417846 | E | LC | ETL.5230.INSL | 40796156 | METCALF | DE ANZA | 2021-05-27 |  | ETL.5230 | MONTA VISTA-JEFFERSON #2 | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40765418 | 1963-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1963-01-01 | Ceramic | Dead End |  |  |  |  | 0.012622 | 31.7081 | 0.40023
121427720 | F | LC | ETL.1430.TOWR | 40660193 | SACTO | SIERRA | 2021-05-27 | 2021-11-04 | ETL.1430 | DRUM-RIO OSO #2 | Marker (i.e. signs)-Steel | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660193 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-03-13 | Glass | Dead End |  |  |  |  | 0.0016085 | 269.0173
121493146 | E | LC | ETL.1820.POLE.NWOD | 44395113 | EUREKA | HUMBOLDT | 2021-06-01 |  | ETL.1820 | HUMBOLDT-TRINITY | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44395113 | 2017-09-07 | Light Duty Steel Pole | 3HP - 3 Horizontal Post | 2017-09-07 | Polymer | Post |  |  |  |  | 0.0042546 | 47.5118 | 0.20214
121493375 | F | LC | ETL.5310.POLE.NWOD | 44671296 | PISMOBCH | LOS PADRES | 2021-06-01 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44671296 | 2018-10-29 | Tubular Steel Pole | DV-DE - Double Vertical Dead End | 2018-10-29 | Glass | Dead End |  |  |  |  | 1.0127e-06 | 144.5242
121493628 | F | LC | ETL.5390.TOWR | 40589646 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5390 | PIT #1-COTTONWOOD | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40589646 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Dead End |  |  |  |  | 2.7611e-07 | 183.8632
121496571 | E | LC | ETL.6760.INSL.NCER | 40888983 | SACTO | SACRAMENTO | 2021-06-07 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40611276 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.04852 | 63.3392 | 3.0732
121498019 | F | LC | ETL.1820.POLE.WDPS | 44562991 | EUREKA | HUMBOLDT | 2021-06-09 | 2021-06-23 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44562370 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.088913 | 47.5141
121516075 | E | LC | ETL.4221.INSL.NCER | 40630348 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.4221 | SLY CREEK TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44559142 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.00085112
121516075 | E | LC | ETL.4221.INSL.NCER | 40630348 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.4221 | SLY CREEK TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44559142 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.00085112
121516290 | E | LC | ETL.6110.TOWR | 40753750 | METCALF | SAN JOSE | 2021-05-28 |  | ETL.6110 | TESLA-METCALF | Structure-Tower | Anti-Climbing Guard | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753750 | 1966-01-01 | LATTICE STEEL TOWER | SUSP-A - Suspension Angle (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 4.2938e-07 | 1824.418
121516536 | E | LC | ETL.1600.TOWR | 40808845 | LAKEVLLE | SONOMA | 2021-06-05 |  | ETL.1600 | FULTON-PUEBLO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40808845 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 9.0814e-05 | 142.5877 | 0.012949
121516536 | E | LC | ETL.1600.TOWR | 40808845 | LAKEVLLE | SONOMA | 2021-06-05 |  | ETL.1600 | FULTON-PUEBLO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40808845 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 9.0814e-05 | 142.5877 | 0.012949
121516635 | F | LC | ETL.4393.POLE.STPS | 45074557 | SACTO | SIERRA | 2021-06-07 |  | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45074122 | 2021-03-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.1454e-05 | 180.4213
121516703 | F | LC | ETL.1600.TOWR | 40751499 | LAKEVLLE | SONOMA | 2021-06-05 | 2021-09-30 | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40751499 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1997-01-01 | Polymer | Dead End |  |  |  |  | 9.6128e-05 | 110.9048
121516703 | F | LC | ETL.1600.TOWR | 40751499 | LAKEVLLE | SONOMA | 2021-06-05 | 2021-09-30 | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40751499 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1997-01-01 | Porcelain | Dead End |  |  |  |  | 9.6128e-05 | 110.9048
121519290 | F | LC | ETL.5780.TOWR | 40593868 | VICTOR | STOCKTON | 2021-06-07 |  | ETL.5780 | TIGER CREEK-ELECTRA | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40593868 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 1.2535e-07 | 1075.7617 | 0.00013485
121519619 | B | LC | ETL.5650.INSL | 40852021 | TABLEMTN | NORTH VALLEY | 2021-06-10 | 2021-07-01 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40822880 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 2.7684e-06 | 3961.7507
121524525 | E | LC | ETL.1710.POLE.WDPS | 44510825 | MOSSLNDG | CENTRAL COAST | 2021-06-12 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44509642 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 8.1282e-05 | 174.0283 | 0.014145
121533665 | E | LC | ETL.6480.POLE.WOOD | 40866889 | SACTO | SIERRA | 2021-06-09 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40866889 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | Dead End |  |  |  |  | 0.19045 | 316.448 | 60.269
121538289 | E | LC | ETL.6350.POLE.WDPS | 44560523 | CONCORD | DIABLO | 2021-06-15 |  | ETL.6350 | CHRISTIE-FRANKLIN #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560143 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00014476 | 127.6204 | 0.018474
121544940 | F | LC | ETL.5420.POLE.WDPS | 44562909 | TABLEMTN | NORTH VALLEY | 2021-06-14 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44562393 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.026582 | 411.4355
121547496 | E | LC | ETL.6220.POLE.WDPS | 44402627 | EUREKA | HUMBOLDT | 2021-06-14 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44402624 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.123 | 332.7496 | 40.9296
121548598 | F | LC | ETL.4040.POLE.NWOD | 44646843 | TABLEMTN | NORTH VALLEY | 2021-06-12 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44646843 | 2018-08-17 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2018-08-17 | Ceramic | Suspension |  |  |  |  | 5.0249e-05 | 110.4421
121550789 | E | LC | ETL.7990.POLE.WOOD | 40908938 | SACTO | SIERRA | 2021-06-12 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40908938 |  | Single Wood Pole | TP - Tri Pin | 2015-10-02 | Porcelain | Post |  |  |  |  | 0.00025324 | 3786.353 | 0.95885
121557215 | F | LC | ETL.9061.POLE.NWOD | 40596826 | FRESNO | FRESNO | 2021-06-16 | 2021-09-01 | ETL.9061 | DUNLAP TAP | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40596826 |  | Light Duty Steel Pole | TAP - Tri Arm Post | 1964-01-01 | Non Ceramic | Other |  |  |  |  | 1.5114e-06 | 6331.5015
121561634 | F | LC | ETL.6760.POLE.NWOD | 45072086 | SACTO | SIERRA | 2021-06-15 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45072086 | 2020-04-21 | Light Duty Steel Pole | T2N | 2020-04-21 | Polymer | Post |  |  |  |  | 0.005497 | 949.3081
121568573 | E | LC | ETL.1350.POLE.WDPS | 44552366 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44551515 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.022433 | 506.6299 | 11.365
121574989 | F | LC | ETL.4040.POLE.STPS | 44647110 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44646846 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.5456e-05 | 129.5341
121582527 | B | LC | ETL.6070.INSL | 40726271 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-07-19 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40684114 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00071626 | 397.6502
121585731 | B | LC | ETL.7380.INSL.CERA | 44974719 | MOSSLNDG | CENTRAL COAST | 2021-06-15 | 2021-07-13 | ETL.7380 | LAURELES-OTTER | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44974709 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.57639 | 285.4165
121586230 | E | LC | ETL.5452.TOWR | 40581891 | CONCORD | DIABLO | 2021-04-21 |  | ETL.5452 | CONTRA COSTA-MORAGA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40581891 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-01-01 | Ceramic | Suspension |  |  |  |  | 1.0769e-08 | 4307.3882 | 4.6388e-05
121587608 | F | LC | ETL.5640.TOWR | 40816239 | TABLEMTN | NORTH VALLEY | 2021-06-22 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40816239 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 1.2941e-06 | 2599.3877 | 0.0033639
121588016 | B | LC | ETL.6370.INSL.CERA | 40901451 | CONCORD | EAST BAY | 2021-06-22 | 2021-08-05 | ETL.6370 | CHRISTIE-WILLOW PASS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40875576 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.21333 | 0.16637
121596664 | F | LC | ETL.7000.POLE.WOOD | 40616810 | TABLEMTN | NORTH VALLEY | 2021-06-22 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40616810 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0020326 | 664.3499
121596746 | F | LC | ETL.8250.POLE.NWOD | 40907125 | VICTOR | STOCKTON | 2021-06-17 |  | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40907125 |  | Tubular Steel Pole | DDE - Double Dead End |  | Polymer | Post |  |  |  |  | 5.4851e-09 | 4437.8529
121598634 | B | LC | ETL.5960.INSL.CERA | 44374373 | PISMOBCH | LOS PADRES | 2021-06-24 | 2021-07-13 | ETL.5960 | DIABLO-GATES #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40863951 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-04-12 | Ceramic | Suspension |  |  |  |  | 2.0251e-09 | 1504.8148
121616752 | E | LC | ETL.4340.INSL | 40726168 | LAKEVLLE | NORTH BAY | 2021-06-26 |  | ETL.4340 | BAHIA-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40683915 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.1093e-06 | 174.3384 | 0.0001934
121616752 | E | LC | ETL.4340.INSL | 40726168 | LAKEVLLE | NORTH BAY | 2021-06-26 |  | ETL.4340 | BAHIA-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40683915 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.1093e-06 | 174.3384 | 0.0001934
121616752 | E | LC | ETL.4340.INSL | 40726168 | LAKEVLLE | NORTH BAY | 2021-06-26 |  | ETL.4340 | BAHIA-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40683915 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-26 | Glass | Dead End |  |  |  |  | 1.1093e-06 | 174.3384 | 0.0001934
121616752 | E | LC | ETL.4340.INSL | 40726168 | LAKEVLLE | NORTH BAY | 2021-06-26 |  | ETL.4340 | BAHIA-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40683915 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-26 | Glass | Dead End |  |  |  |  | 1.1093e-06 | 174.3384 | 0.0001934
121621204 | E | LC | ETL.7130.INSL.NCER | 44315169 | EUREKA | HUMBOLDT | 2021-06-28 | 2021-08-02 | ETL.7130 | HUMBOLDT-MAPLE CREEK | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44315160 | 2013-10-26 | 3-Pole Wood | SVDE - Single Vertical Dead End | 2013-10-26 | Non Ceramic | Dead End |  |  |  |  | 0.0095661
121621204 | E | LC | ETL.7130.INSL.NCER | 44315169 | EUREKA | HUMBOLDT | 2021-06-28 | 2021-08-02 | ETL.7130 | HUMBOLDT-MAPLE CREEK | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44315160 | 2013-10-26 | 3-Pole Wood | SVDE - Single Vertical Dead End | 2013-10-26 | Non Ceramic | Dead End |  |  |  |  | 0.0095661
121621204 | E | LC | ETL.7130.INSL.NCER | 44315169 | EUREKA | HUMBOLDT | 2021-06-28 | 2021-08-02 | ETL.7130 | HUMBOLDT-MAPLE CREEK | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44315160 | 2013-10-26 | 3-Pole Wood | SVDE - Single Vertical Dead End | 2013-10-26 | Non Ceramic | Dead End |  |  |  |  | 0.0095661
121665945 | E | LC | ETL.1440.POLE.WOOD | 40663006 | SACTO | SIERRA | 2021-06-28 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40663006 | 1956-01-01 | Single Wood Pole | 3P TRP D - 3 Pole Tramp Double Dead End | 2015-09-23 | Ceramic | Dead End |  |  |  |  | 0.018604 | 0.066431 | 0.0012359
121707208 | E | LC | ETL.5934.TOWR | 40858176 | PISMOBCH | FRESNO | 2021-07-06 |  | ETL.5934 | TEMPLETON-GATES | Hardware-Tower | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40858176 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00013311
121735580 | E | LC | ETL.6710.POLE.WOOD | 40768285 | MOSSLNDG | CENTRAL COAST | 2021-07-15 |  | ETL.6710 | DEL MONTE-VIEJO | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40768285 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2021-07-11 | Glass | Suspension |  |  |  |  | 0.98019 | 0.066432 | 0.065116
121748106 | F | LC | ETL.1820.POLE.WOOD | 45102076 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45102076 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2021-03-05 | Glass | Suspension |  |  |  |  | 0.019762 | 4621.6372
121749071 | F | LC | ETL.1810.POLE.WDPS | 44322257 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44322256 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0068813
121750221 | E | LC | ETL.6760.INSL.NCER | 45056349 | SACTO | SIERRA | 2021-07-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40824368 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-03-16 | Glass | Dead End |  |  |  |  | 0.25828 | 110.8706 | 28.6356
121753964 | E | LC | ETL.6480.INSL.NCER | 45100615 | SACTO | SIERRA | 2021-07-15 |  | ETL.6480 | COLGATE-CHALLENGE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40664715 |  | Single Wood Pole | T-1 - Tri Post | 2021-06-12 | Polymer | Post |  |  |  |  | 0.13551 | 348.1483 | 47.1763
121768113 | F | LC | ETL.4590.TOWR | 40907018 | TABLEMTN | NORTH VALLEY | 2021-07-20 |  | ETL.4590 | CRESTA-RIO OSO | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40907018 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-10-30 | Ceramic | Suspension |  |  |  |  | 0.00017529 | 3986.9912 | 0.69888
121768114 | E | LC | ETL.2390.INSL.NCER | 40773477 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391157 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.00011789
121768114 | E | LC | ETL.2390.INSL.NCER | 40773477 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391157 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.00011789
121769052 | B | LC | ETL.6020.INSL | 40845622 | TABLEMTN | NORTH VALLEY | 2021-07-19 | 2021-09-01 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817707 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.6554e-08 | 379.78
121770346 | E | LC | ETL.2390.POLE.WDPS | 44390966 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44390965 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 8.3378e-05 | 4273.2705 | 0.3563
121789404 | F | LC | ETL.9240.TOWR | 43249609 | PISMOBCH | LOS PADRES | 2021-07-22 | 2021-10-08 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 43249609 |  | LATTICE STEEL TOWER | [9 empty] | 397.9478
121816237 | E | LC | ETL.6470.POLE.WOOD | 40664742 | SACTO | SIERRA | 2021-07-26 |  | ETL.6470 | COLGATE-ALLEGHANY | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40664742 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.25187 | 221.5931 | 55.812
121821186 | E | LC | ETL.6760.POLE.WOOD | 44670510 | SACTO | SIERRA | 2021-07-29 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44670510 | 2018-11-05 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-11-05 | Ceramic | Dead End - Suspension |  |  |  |  | 0.024076 | 332.2538 | 7.9994
121822866 | E | LC | ETL.2770.TOWR | 40804655 | CONCORD | EAST BAY | 2021-07-30 |  | ETL.2770 | MORAGA-SAN LEANDRO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40804655 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 1.573e-06 | 0.065147 | 1.0248e-07
121860126 | B | LC | ETL.6300.POLE.WOOD | 44191024 | TABLEMTN | NORTH VALLEY | 2021-08-07 | 2021-09-13 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.2182e-05 | 15.8815
121985520 | E | LC | ETL.8290.POLE.WOOD | 40828866 | TABLEMTN | NORTH VALLEY | 2021-09-01 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40828866 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00011628 | 2148.4816 | 0.24983
122103924 | E | LC | ETL.6280.POLE.WOOD | 40751748 | TABLEMTN | NORTH VALLEY | 2021-09-27 |  | ETL.6280 | CARIBOU #2 | Damper-Steel | Missing | [Install] | Tier2 |  |  | PEND | [11 empty] | 2.1763e-05 | 680.1661 | 0.014802
122161616 | E | LC | ETL.4392.INSL.NCER | 45109938 | LAKEVLLE | SONOMA | 2021-10-07 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Emergency | Storm Related | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40648681 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Glass | Dead End |  |  |  |  | 0.00012908 | 1930.6907 | 0.24922
118437882 | E | LC | ETL.4040.INSL.CERA | 42622829 | TABLEMTN | NORTH VALLEY | 2020-01-08 | 2020-11-19 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
118498639 | A | LC | ETL.7630.POLE.NWOD | 44178496 | LAKEVLLE | SONOMA | 2020-02-05 | 2020-02-07 | ETL.7630 | MONTE RIO-FULTON | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44178496 | 2014-10-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2014-10-11 | Ceramic | Dead End |  |  |  |  | 0.0022039 | 158.265
118939995 | E | LC | ETL.7510.POLE.WDPS | 44218390 | LAKEVLLE | SONOMA | 2020-04-22 | 2020-07-03 | ETL.7510 | MENDOCINO-HARTLEY | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44218387 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00015326 | 4355.1782
118951224 | E | LC | ETL.1650.POLE.WOOD | 40603864 | LAKEVLLE | SONOMA | 2020-04-23 | 2020-06-22 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40603864 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Porcelain | Suspension |  |  |  |  | 8.5479e-05 | 3483.3848
118960136 | F | LC | ETL.4750.TOWR | 40654437 | LAKEVLLE | SONOMA | 2020-04-29 | 2020-06-18 | ETL.4750 | GEYSERS #12-FULTON | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40654437 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 4.1888e-09 | 1838.3041
118971827 | F | LC | ETL.7550.POLE.WDPS | 44211118 | LAKEVLLE |  | 2020-04-29 | 2021-09-23 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Marker (i.e. signs)-Wood | Missing | [Install] |  | Tier 3 | Within Both | DLFL | 44211117 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00027863 | 348.2242
119003006 | F | LC | ETL.9100.POLE.WOOD | 44191949 | PISMOBCH | LOS PADRES | 2020-05-06 | 2021-06-30 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL | [11 empty] | 0.00013268 | 1946.175
119036465 | F | LC | ETL.4220.POLE.WDPS | 44557515 | TABLEMTN |  | 2020-05-11 | 2020-06-10 | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] |  | Tier 3 | Within Both | COMP | 44553930 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.085564 | 205.7755
119049540 | E | LC | ETL.1430.TOWR | 40761902 | SACTO | SIERRA | 2020-05-19 | 2021-02-22 | ETL.1430 | DRUM-RIO OSO #2 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40761902 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical | 2016-11-14 | Non Ceramic | Post |  |  |  |  | 0.00036694 | 0.090454
119060417 | F | LC | ETL.1430.POLE.STPS | 44304977 | SACTO | SACRAMENTO | 2020-05-19 | 2021-05-08 | ETL.1430 | DRUM-RIO OSO #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44304976 | 2016-11-14 | 2-Pole Non Wood | 2PS TRP - 2 Pole SUSP. Transposition | [7 empty] | 0.00072986 | 0.075274
119084536 | F | LC | ETL.8405.POLE.WOOD | 40810143 | SACTO | SIERRA | 2020-05-28 | 2021-02-10 | ETL.8405 | MIDDLE FORK #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40810143 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0025365 | 2468.2347
119086582 | E | LC | ETL.1730.POLE.WDPS | 44413409 | MOSSLNDG | CENTRAL COAST | 2020-05-29 | 2020-08-25 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44413407 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00085574 | 0.065275
119097455 | F | LC | ETL.1402.POLE.STPS | 44161080 | VICTOR | STOCKTON | 2020-05-04 |  | ETL.1402 | SPRING GAP TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44161079 | 2016-11-15 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.2682e-05 | 1329.0924
119105356 | F | LC | ETL.6720.POLE.WDPS | 44926546 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2021-09-16 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42578821 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 6.5736e-05 | 949.264
119113060 | B | LC | ETL.4393.INSL.NCER | 40712519 | SACTO | SACRAMENTO | 2020-06-04 | 2020-06-15 | ETL.4393 | DRUM-HIGGINS | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119117299 | E | LC | ETL.8290.POLE.WOOD | 40615918 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-27 | ETL.8290 | VOLTA-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40615918 |  | Single Wood Pole | T2N | 2021-04-21 | Polymer | Post |  |  |  |  | 0.00057161 | 620.4352
119117318 | E | LC | ETL.7290.POLE.WOOD | 40752215 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-02-26 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40752215 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Unknown |  |  |  |  | 0.0056667 | 1634.3816
119119032 | F | LC | ETL.1400.POLE.WDPS | 45087027 | VICTOR | YOSEMITE | 2020-05-27 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40680180 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.029584 | 31.7207
119130809 | F | LC | ETL.1430.TOWR | 40815312 | SACTO | SIERRA | 2020-06-04 | 2021-02-22 | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40815312 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.0020207 | 205.7345
119142976 | E | LC | ETL.8365.POLE.WOOD | 40761558 | EUREKA | HUMBOLDT | 2020-06-08 | 2021-04-29 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40761558 |  | Single Wood Pole | TRP DE - Tramp Dead End |  | Polymer | [5 empty] | 0.0035861
119144945 | F | LC | ETL.1240.POLE.STPS | 44197141 | TABLEMTN |  | 2020-06-02 | 2020-06-15 | ETL.1240 | CASCADE-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install] |  | Tier 2 | Within Both | DLFL | 44197140 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.4282e-09 | 4142.56
119148529 | E | LC | ETL.7260.POLE.WOOD | 40827863 | TABLEMTN | NORTH VALLEY | 2020-06-09 | 2021-01-22 | ETL.7260 | KESWICK-CASCADE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40827863 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Pin |  |  |  |  | 0.00015065 | 2218.4589
119178532 | E | LC | ETL.9340.POLE.NWOD | 44663899 | FRESNO | FRESNO | 2020-06-17 | 2020-08-06 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44663899 | 2018-10-03 | Light Duty Steel Pole | T-1 - Tri Post | 2018-10-03 | Polymer | Post |  |  |  |  | 0.0022466 | 3246.6982
119180984 | E | LC | ETL.6480.POLE.WOOD | 40693047 | SACTO | SIERRA | 2020-06-15 | 2021-06-23 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119182518 | F | LC | ETL.6310.POLE.WOOD | 40592328 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2020-11-09 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40592328 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 2.0442e-05 | 7306.2056
119185337 | F | LC | ETL.6470.POLE.WOOD | 40817361 | SACTO | SACRAMENTO | 2020-06-18 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40817361 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.12912 | 269.0426
119186814 | E | LC | ETL.6310.POLE.WOOD | 41177753 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-08-19 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41177753 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 8.4371e-06 | 3030.0661
119187890 | E | LC | ETL.6440.POLE.WOOD | 41144123 | TABLEMTN | NORTH VALLEY | 2020-06-19 | 2020-06-25 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Rotten | [Stub] | Tier2 | Tier 2 | Within Both | DLFL | 41144123 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.00056823 | 3637.6521
119197932 | F | LC | ETL.6470.POLE.WOOD | 40593294 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40593294 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.042016 | 205.7851
119200495 | E | LC | ETL.6470.POLE.WOOD | 40593302 | SACTO | SIERRA | 2020-06-23 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593302 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.13681 | 110.8102
119300824 | E | LC | ETL.8060.POLE.WOOD | 40861937 | SACTO | SIERRA | 2020-07-02 | 2021-05-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.008989 | 31.7066
119301305 | E | LC | ETL.1110.POLE.WDPS | 44423892 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-04-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44423890 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.001521 | 4248.359
119311442 | E | LC | ETL.8060.POLE.WOOD | 40586118 | SACTO | SIERRA | 2020-07-02 | 2021-05-04 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586118 |  | Single Wood Pole | T2N | 2019-07-29 | Polymer | Post |  |  |  |  | 0.0079013 | 31.7066
119317701 | F | LC | ETL.7270.POLE.NWOD | 44649335 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44649335 | 2018-08-17 | Light Duty Steel Pole | T2N | 2018-08-17 | Polymer | Post |  |  |  |  | 0.00066947 | 1076.101
119325547 | F | LC | ETL.1110.POLE.WDPS | 44424377 | EUREKA | NORTH VALLEY | 2020-07-07 | 2021-06-23 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44424375 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0006709 | 284.9484
119327746 | F | LC | ETL.6280.POLE.NWOD | 40876557 | TABLEMTN | NORTH VALLEY | 2020-07-07 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40876557 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Pin |  |  |  |  | 2.1148e-05 | 3795.9778
119330693 | E | LC | ETL.6300.POLE.WOOD | 44191099 | TABLEMTN | NORTH VALLEY | 2020-07-08 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44191099 |  | Single Wood Pole | T-1 - Tri Post | [7 empty] | 9.4896e-06 | 31.6978 | 0.0003008
119341792 | F | LC | ETL.5140.POLE.WDPS | 44553721 | SACTO | SACRAMENTO | 2020-07-08 | 2021-04-29 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119368460 | F | LC | ETL.1440.POLE.WOOD | 40814972 | SACTO | SIERRA | 2020-07-14 | 2020-11-12 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40814972 | 1956-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00023456 | 427.3257
119380681 | F | LC | ETL.7030.POLE.WOOD | 40817147 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40817147 |  | Single Wood Pole | T2N | 2017-09-27 | Polymer | Post |  |  |  |  | 0.0074675 | 47.5207
119484100 | E | LC | ETL.1430.TOWR | 40590432 | SACTO | SACRAMENTO | 2020-07-21 | 2021-03-03 | ETL.1430 | DRUM-RIO OSO #2 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40590432 | 1913-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-07-13 | Glass | Suspension |  |  |  |  | 0.011364 | 2056.7583
119495711 | E | LC | ETL.9200.POLE.WOOD | 40583961 | MIDWAY | KERN | 2020-07-22 | 2021-04-29 | ETL.9200 | TAFT-CUYAMA #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40583961 | 1962-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-04-19 | Glass | Dead End |  |  |  |  | 0.019016
119504907 | F | LC | ETL.9210.POLE.WOOD | 40685717 | MIDWAY | KERN | 2020-07-23 |  | ETL.9210 | TAFT-CUYAMA #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Non-HFTD | HFRA Addition | PEND | 40685717 | 1946-01-01 | Single Wood Pole | TPAT - Tri Pin Arm Tramp | 1946-01-01 | Ceramic | Pin |  |  |  |  | 0.0092553
119506374 | E | LC | ETL.8060.POLE.WOOD | 40618262 | SACTO | SACRAMENTO | 2020-07-24 | 2021-08-04 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.012928 | 31.7066
119537773 | E | LC | ETL.6480.POLE.NWOD | 44695496 | SACTO | SACRAMENTO | 2020-07-31 | 2021-06-23 | ETL.6480 | COLGATE-CHALLENGE | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44695496 | 2018-12-10 | Light Duty Steel Pole | T2N | 2018-12-10 | Polymer | Post |  |  |  |  | 0.021949 | 348.1483
119568842 | F | LC | ETL.1073.POLE.STPS | 44385261 | VICTOR | STOCKTON | 2020-08-06 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Steel | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | PEND | 44385260 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.4275e-05 | 31.7081
119569653 | F | LC | ETL.6980.POLE.WOOD | 40808307 | LAKEVLLE | HUMBOLDT | 2020-08-06 |  | ETL.6980 | FORT ROSS-GUALALA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40808307 | 1984-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.050579 | 807.4984
119569873 | E | LC | ETL.6880.INSL.CERA | 40640977 | LAKEVLLE | NORTH BAY | 2020-08-06 | 2021-07-26 | ETL.6880 | FULTON-CALISTOGA | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119574063 | E | LC | ETL.7180.POLE.WOOD | 40770135 | LAKEVLLE | NORTH BAY | 2020-08-06 | 2021-04-26 | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119575920 | F | LC | ETL.7180.POLE.WOOD | 40825724 | LAKEVLLE | NORTH BAY | 2020-08-07 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40825724 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 2.7565e-05 | 197.8149
119608400 | B | LC | ETL.8650.TOWR | 40871684 | FRESNO | FRESNO | 2020-08-13 | 2020-12-08 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871684 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-11-18 | Glass | Dead End |  |  |  |  | 0.023248 | 0.065147
119630765 | F | LC | ETL.1470.POLE.WOOD | 41176385 | LAKEVLLE | HUMBOLDT | 2020-07-31 | 2020-11-10 | ETL.1470 | EAGLE ROCK-CORTINA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 41176385 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Porcelain | Post |  |  |  |  | 0.012698 | 3314.8676
119631624 | E | LC | ETL.1470.POLE.WOOD | 41176371 | LAKEVLLE | HUMBOLDT | 2020-07-30 | 2021-03-16 | ETL.1470 | EAGLE ROCK-CORTINA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41176371 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Porcelain | Post |  |  |  |  | 0.013665 | 5434.1055
119632734 | B | LC | ETL.8365.POLE.WOOD | 40912602 | EUREKA | HUMBOLDT | 2020-08-18 | 2020-11-16 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912602 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Polymer | [5 empty] | 0.028594
119633640 | E | LC | ETL.7510.POLE.NWOD | 40811110 | LAKEVLLE | SONOMA | 2020-08-18 | 2020-09-01 | ETL.7510 | MENDOCINO-HARTLEY | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40811110 | 2011-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 2.0572e-08 | 896.303
119637772 | E | LC | ETL.1110.POLE.STPS | 44425590 | EUREKA | HUMBOLDT | 2020-08-19 | 2021-07-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44425589 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.0186e-05 | 189.9114
119638637 | F | LC | ETL.7490.POLE.WOOD | 44429888 | EUREKA | HUMBOLDT | 2020-08-19 | 2021-04-28 | ETL.7490 | MAPLE CREEK-HOOPA | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44429888 | 2018-08-10 | Single Wood Pole | T-1 - Tri Post | 2018-08-10 | Polymer | Post |  |  |  |  | 0.0020998 | 96.5446
119639274 | E | LC | ETL.1110.POLE.NWOD | 40676686 | TABLEMTN | HUMBOLDT | 2020-07-20 | 2021-07-26 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | Earth Covered Tower | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676686 |  | Lattice Steel Pole | DDE - Double Dead End | 2020-10-12 | Glass | Dead End |  |  |  |  | 1.8407e-05 | 126.6368
119639928 | B | LC | ETL.8650.TOWR | 40859330 | FRESNO | FRESNO | 2020-08-19 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40859330 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.013743 | 5066.0874
119639929 | B | LC | ETL.1112.POLE.NWOD | 44420216 | FRESNO | FRESNO | 2020-08-19 | 2020-12-14 | ETL.1112 | INDIAN FLAT-YOSEMITE | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420216 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.00040565 | 5471.0873
119644999 | B | LC | ETL.8650.TOWR | 40606165 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40606165 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0051682 | 4649.6255
119649479 | E | LC | ETL.2660.TOWR | 40660285 | SACTO | SACRAMENTO | 2020-08-21 | 2021-02-11 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660285 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Ceramic | Suspension |  |  |  |  | 1.6919e-08 | 2452.9336
119649479 | E | LC | ETL.2660.TOWR | 40660285 | SACTO | SACRAMENTO | 2020-08-21 | 2021-02-11 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660285 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Porcelain | Suspension |  |  |  |  | 1.6919e-08 | 2452.9336
119677876 | E | LC | ETL.7780.POLE.WOOD | 40762814 | LAKEVLLE | HUMBOLDT | 2020-08-25 | 2021-03-22 | ETL.7780 | PHILO JCT-ELK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119678909 | E | LC | ETL.1420.INSL.CERA | 40888171 | SACTO | SACRAMENTO | 2020-08-27 | 2021-02-24 | ETL.1420 | DRUM-RIO OSO #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119679107 | E | LC | ETL.1420.TOWR | 40670134 | SACTO | SACRAMENTO | 2020-08-27 | 2021-01-27 | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40670134 | 1913-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2019-08-30 | Glass | Dead End |  |  |  |  | 4.8222e-07 | 0.075274
119685166 | F | LC | ETL.1440.POLE.WDPS | 44162080 | SACTO | SACRAMENTO | 2020-08-25 | 2021-06-30 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Tier 3 | Within Both | COMP | 44162079 | 2013-09-22 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0022384 | 2056.7583
119685406 | E | LC | ETL.6870.POLE.WOOD | 40767454 | SACTO | SIERRA | 2020-07-14 | 2021-10-14 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Rotten | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.11213 | 0.065152 | 0.0073058
119718687 | F | LC | ETL.1252.POLE.NWOD | 40652284 | FRESNO | YOSEMITE | 2020-07-27 | 2021-04-19 | ETL.1252 | OAKHURST TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40652284 | 1996-01-01 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 1996-01-01 | Polymer | Dead End |  |  |  |  | 5.6659e-09 | 5559.7377
119720186 | E | LC | ETL.6290.POLE.WOOD | 40675189 | TABLEMTN | NORTH VALLEY | 2020-09-03 | 2021-08-15 | ETL.6290 | CARIBOU-PLUMAS JCT | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40675189 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.3274 | 1043.9412
119723043 | F | LC | ETL.8290.POLE.NWOD | 44949885 | TABLEMTN | NORTH VALLEY | 2020-08-10 | 2021-04-19 | ETL.8290 | VOLTA-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44949885 | 2019-06-10 | Light Duty Steel Pole | T2N | 2019-06-10 | Polymer | Post |  |  |  |  | 2.0641e-06 | 3500.5698
119723176 | F | LC | ETL.1730.POLE.WDPS | 44413439 | MOSSLNDG | CENTRAL COAST | 2020-08-05 | 2020-11-03 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Tier 2 | Within Both | COMP | 44413438 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.434e-05 | 0.066432
119751329 | E | LC | ETL.4220.POLE.WDPS | 44942610 | TABLEMTN | NORTH VALLEY | 2020-08-04 |  | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | PEND | 42568045 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.010746 | 1328.9435 | 14.2807
119753888 | F | LC | ETL.7520.POLE.NWOD | 40820915 | LAKEVLLE | HUMBOLDT | 2020-09-03 | 2021-09-08 | ETL.7520 | MENDOCINO-PHILO JCT-HOPLAND | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40820915 |  | Lattice Steel Pole | TPSRD - Tramp Double Dead End | 2020-06-08 | Glass | Double Dead End |  |  |  |  | 2.8067e-05 | 3404.2203
119753888 | F | LC | ETL.7520.POLE.NWOD | 40820915 | LAKEVLLE | HUMBOLDT | 2020-09-03 | 2021-09-08 | ETL.7520 | MENDOCINO-PHILO JCT-HOPLAND | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40820915 |  | Lattice Steel Pole | TPSRD - Tramp Double Dead End | 2019-06-25 | Porcelain | Dead End |  |  |  |  | 2.8067e-05 | 3404.2203
119755701 | E | LC | ETL.8640.INSL.NCER | 44282602 | FRESNO | FRESNO | 2020-06-23 |  | ETL.8640 | EXCHEQUER-MARIPOSA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44282587 | 2015-12-04 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2015-12-04 | Polymer | Suspension |  |  |  |  | 3.7498e-10 | 300.8885 | 1.1283e-07
119758513 | F | LC | ETL.7300.POLE.WOOD | 41190225 | TABLEMTN |  | 2020-09-11 | 2021-03-31 | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41190225 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 0.00033239 | 5053.5459
119763251 | E | LC | ETL.8240.POLE.WOOD | 40758491 | VICTOR | STOCKTON | 2020-09-14 | 2021-01-28 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758491 | 1969-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0014308 | 2804.8376
119809677 | F | LC | ETL.6280.POLE.WOOD | 40585997 | TABLEMTN | NORTH VALLEY | 2020-08-18 | 2021-09-14 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40585997 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Other |  |  |  |  | 0.00015238 | 126.5956
119809872 | F | LC | ETL.6290.POLE.WOOD | 42721909 | TABLEMTN | NORTH VALLEY | 2020-08-18 | 2021-08-05 | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42721909 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.047494 | 47.5141
119818180 | F | LC | ETL.7030.POLE.WOOD | 40817145 | TABLEMTN | NORTH VALLEY | 2020-09-11 | 2021-06-30 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817145 |  | Single Wood Pole | T2N | 2015-02-10 | Polymer | Post |  |  |  |  | 0.0065138 | 0.06515
119820023 | F | LC | ETL.6290.POLE.WOOD | 40824675 | TABLEMTN | NORTH VALLEY | 2020-08-31 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40824675 | 1962-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.092518 | 1376.0835
119898231 | F | LC | ETL.8170.POLE.WOOD | 40906450 | EUREKA | HUMBOLDT | 2020-10-07 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906450 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.026982 | 94.9939
119898458 | E | LC | ETL.8170.POLE.WOOD | 40906272 | EUREKA | HUMBOLDT | 2020-10-07 | 2021-03-02 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906272 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | Post |  |  |  |  | 0.032192 | 648.7573
119981888 | E | LC | ETL.7560.POLE.WDPS | 44414808 | SACTO | SACRAMENTO | 2020-08-25 | 2021-04-26 | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120079139 | E | LC | ETL.6490.POLE.WOOD | 40679384 | SACTO | SACRAMENTO | 2020-10-23 | 2021-09-13 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Rotten | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40679384 |  | Single Wood Pole | T2N | 2021-02-16 | Polymer | Post |  |  |  |  | 0.071889 | 2815.7598
120088690 | E | LC | ETL.3180.TOWR | 40761569 | CONCORD | EAST BAY | 2020-11-17 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761569 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-03-23 | Glass Silicone Coated | Suspension |  |  |  |  | 4.8766e-05 | 31.9508 | 0.0015581
120088690 | E | LC | ETL.3180.TOWR | 40761569 | CONCORD | EAST BAY | 2020-11-17 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761569 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.8766e-05 | 31.9508 | 0.0015581
120114201 | E | LC | ETL.6490.POLE.WOOD | 40818423 | SACTO | SIERRA | 2020-10-21 | 2021-06-02 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Rotten | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818423 |  | Single Wood Pole | T-1 - Tri Post | 2019-07-20 | Polymer | Post |  |  |  |  | 0.28933 | 1203.8537
120237278 | F | LC | ETL.1650.POLE.WOOD | 44298417 | LAKEVLLE | SONOMA | 2020-12-01 | 2021-07-02 | ETL.1650 | GEYSERS #3-CLOVERDALE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44298417 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 0.00026466 | 2393.1714
120679751 | E | LC | ETL.4040.POLE.STPS | 44784243 | TABLEMTN | NORTH VALLEY | 2021-03-23 | 2021-10-07 | ETL.4040 | TRINITY-COTTONWOOD | Hardware-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44784108 | 2019-07-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.6776e-05 | 263.432 | 0.009688
120705279 | F | LC | ETL.3820.TOWR | 40856496 | VICTOR | STOCKTON | 2021-03-26 | 2021-09-28 | ETL.3820 | STANISLAUS-MANTECA #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40856496 | 1910-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post | 1989-01-01 | Polymer | Post |  |  |  |  | 8.9956e-05 | 1962.8882
120705279 | F | LC | ETL.3820.TOWR | 40856496 | VICTOR | STOCKTON | 2021-03-26 | 2021-09-28 | ETL.3820 | STANISLAUS-MANTECA #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40856496 | 1910-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post | 1989-01-01 | Polymer | Suspension |  |  |  |  | 8.9956e-05 | 1962.8882
120706692 | E | LC | ETL.4960.INSL | 40618889 | CONCORD |  | 2021-03-24 |  | ETL.4960 | LAKEVILLE-SOBRANTE #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40593169 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.0063267 | 16.3243 | 0.10328
120707637 | E | LC | ETL.3770.TOWR | 40804917 | CONCORD | DIABLO | 2021-03-29 | 2021-09-21 | ETL.3770 | SOBRANTE-R #1 | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40804917 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-08-29 | Glass | Double Dead End |  |  |  |  | 2.5573e-06 | 300.5749
120707753 | E | LC | ETL.3840.INSL.CERA | 40850625 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40821758 | 1910-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1989-01-01 | Glass | Dead End |  |  |  |  | 1.4017e-05 | 6204.2363 | 0.086966
120718575 | E | LC | ETL.5540.TOWR | 40815739 | TABLEMTN | NORTH VALLEY | 2021-03-31 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40815739 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 4.1572e-07 | 6089.749 | 0.0025316
120723834 | F | LC | ETL.3830.TOWR | 40646070 | VICTOR | STOCKTON | 2021-03-31 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40646070 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.7134e-06 | 47.5729 | 0.00012908
120724702 | F | LC | ETL.2900.TOWR | 40594669 | MOSSLNDG | CENTRAL COAST | 2021-04-01 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40594669 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0023895 | 158.922 | 0.37974
120724759 | E | LC | ETL.3700.POLE.WOOD | 40585699 | PISMOBCH | LOS PADRES | 2021-04-01 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40585699 | 1989-01-01 | Single Wood Pole | SV-PJ-90 - Single Vertical Post Jumper 90 | 1989-01-01 | Porcelain | Dead End |  |  |  |  | 2.9576e-05 | 3878.2041 | 0.1147
120738889 | E | LC | ETL.5340.INSL | 40690386 | MOSSLNDG | CENTRAL COAST | 2021-04-02 |  | ETL.5340 | MOSS LANDING-LAS AGUILAS SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40659872 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 5.0782e-05 | 982.1789 | 0.049877
120739806 | E | LC | ETL.6760.POLE.WOOD | 40674411 | SACTO | SACRAMENTO | 2021-04-03 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40674411 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0068285 | 110.7947 | 0.75656
120752306 | B | LC | ETL.3820.TOWR | 40860910 | VICTOR | STOCKTON | 2021-04-06 | 2021-05-19 | ETL.3820 | STANISLAUS-MANTECA #2 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860910 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 2.0601e-07 | 533.0465
120754535 | E | LC | ETL.4770.INSL | 40839400 | LAKEVLLE | SONOMA | 2021-04-06 |  | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40813798 | 1971-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension | [5 empty] | 1252.5039
120757550 | E | LC | ETL.1350.POLE.STPS | 44993135 | TABLEMTN | NORTH VALLEY | 2021-04-07 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993113 | 2020-06-04 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.5698e-05 | 0.065152
120760103 | E | LC | ETL.5510.TOWR | 40586628 | CONCORD | DIABLO | 2021-04-07 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40586628 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 3.2247e-06 | 5177.3608 | 0.016696
120766624 | E | LC | ETL.7380.POLE.WDPS | 44563008 | MOSSLNDG | CENTRAL COAST | 2021-04-08 |  | ETL.7380 | LAURELES-OTTER | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44562410 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.62913 | 0.065148 | 0.040987
120787787 | E | LC | ETL.2900.TOWR | 40752794 | MOSSLNDG | CENTRAL COAST | 2021-04-10 | 2021-07-12 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752794 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Polymer | Suspension |  |  |  |  | 0.00084988 | 396.6885
120787787 | E | LC | ETL.2900.TOWR | 40752794 | MOSSLNDG | CENTRAL COAST | 2021-04-10 | 2021-07-12 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752794 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-08-06 | Polymer | Suspension |  |  |  |  | 0.00084988 | 396.6885
120794758 | E | LC | ETL.8250.INSL.CERA | 40918589 | VICTOR | STOCKTON | 2021-04-12 | 2021-08-17 | ETL.8250 | CLAY-MARTEL | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908870 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 3.3017e-05 | 2742.4761
120800017 | E | LC | ETL.4590.INSL.CERA | 40894458 | TABLEMTN | NORTH VALLEY | 2021-04-12 |  | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40870609 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 6.248e-07 | 3801.4019 | 0.0023751
120800017 | E | LC | ETL.4590.INSL.CERA | 40894458 | TABLEMTN | NORTH VALLEY | 2021-04-12 |  | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40870609 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-06-19 | Glass | Suspension |  |  |  |  | 6.248e-07 | 3801.4019 | 0.0023751
120801658 | B | LC | ETL.3830.INSL | 40703044 | VICTOR | STOCKTON | 2021-04-12 | 2021-05-27 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40642817 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 0.0002199 | 4559.6204
120811684 | E | LC | ETL.8180.POLE.WOOD | 40763686 | LAKEVLLE | SONOMA | 2021-04-14 | 2021-09-01 | ETL.8180 | TULUCAY-NAPA #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40763686 | 1967-01-01 | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.02098 | 4036.2856
120815796 | B | LC | ETL.4316.INSL.CERA | 44652085 | TABLEMTN |  | 2021-04-14 | 2021-04-27 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40755640 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-05-07 | Ceramic | Suspension |  |  |  |  | 0.065122 | 4481.9458
120816456 | E | LC | ETL.3750.TOWR | 40804897 | CONCORD | DIABLO | 2021-04-14 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40804897 | 1932-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 3.1951e-05 | 1568.8029 | 0.050125
120827529 | E | LC | ETL.4316.INSL.CERA | 40841203 | TABLEMTN |  | 2021-04-15 | 2021-08-02 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120831345 | F | LC | ETL.5780.TOWR | 40752887 | VICTOR | STOCKTON | 2021-04-16 |  | ETL.5780 | TIGER CREEK-ELECTRA | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40752887 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.0194e-06 | 243.9041
120835157 | F | LC | ETL.4050.POLE.WOOD | 40584965 | LAKEVLLE | SONOMA | 2021-04-17 | 2021-06-10 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40584965 | 1970-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1970-01-01 | Ceramic | Post |  |  |  |  | 0.00029518 | 2089.8596
120845210 | F | LC | ETL.5300.TOWR | 40592078 | PISMOBCH | LOS PADRES | 2021-04-12 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40592078 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00040445 | 982.0776 | 0.39721
120845210 | F | LC | ETL.5300.TOWR | 40592078 | PISMOBCH | LOS PADRES | 2021-04-12 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40592078 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-30 | Glass | Suspension |  |  |  |  | 0.00040445 | 982.0776 | 0.39721
120850085 | F | LC | ETL.3720.TOWR | 40581004 | CONCORD | DIABLO | 2021-04-20 |  | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40581004 | 1968-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | Double Dead End |  |  |  |  | 0.0013788 | 199.5872 | 0.2752
120858251 | F | LC | ETL.1820.POLE.WDPS | 44562208 | EUREKA | HUMBOLDT | 2021-04-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Right of Way | Encroachment | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40770507 | 1949-01-01 | 2-Pole Wood | 2P DDE-A - 2 Pole Double Dead End Angle | [7 empty] | 0.069514 | 63.3274
120864701 | E | LC | ETL.5540.TOWR | 40753052 | TABLEMTN | NORTH VALLEY | 2021-04-21 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753052 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-07-16 | Glass | Suspension |  |  |  |  | 1.0863e-06 | 2298.8216 | 0.0024971
120864701 | E | LC | ETL.5540.TOWR | 40753052 | TABLEMTN | NORTH VALLEY | 2021-04-21 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753052 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-03-15 | Porcelain | Suspension |  |  |  |  | 1.0863e-06 | 2298.8216 | 0.0024971
120875898 | E | LC | ETL.6470.POLE.WOOD | 40658308 | SACTO | SIERRA | 2021-04-23 | 2021-07-15 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40658308 |  | Single Wood Pole | T2N | 2021-07-13 | Polymer | Post |  |  |  |  | 0.051935 | 79.2067
120876607 | F | LC | ETL.7550.POLE.NWOD | 44172882 | LAKEVLLE | SONOMA | 2021-04-23 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44172882 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.386e-11 | 7039.9185
120879910 | E | LC | ETL.3720.INSL.CERA | 40671713 | CONCORD | EAST BAY | 2021-04-23 |  | ETL.3720 | SOBRANTE-G #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40644467 | 1968-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | [5 empty] | 3.2831e-07 | 110.7919 | 3.6374e-05
120883649 | E | LC | ETL.4880.INSL | 40726377 | FRESNO | FRESNO | 2021-04-21 |  | ETL.4880 | HELMS-GREGG #2 | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40684265 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.6528e-07 | 5556.3848 | 0.00091838
120884209 | F | LC | ETL.6890.POLE.NWOD | 44713014 | LAKEVLLE | SONOMA | 2021-04-26 |  | ETL.6890 | FULTON-HOPLAND | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44713014 | 2019-02-16 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-02-16 | Ceramic | Suspension |  |  |  |  | 9.8206e-08 | 2931.5991
120885023 | F | LC | ETL.6470.POLE.WOOD | 40767343 | SACTO | SACRAMENTO | 2021-04-26 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40767343 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 0.013569 | 1278.2538
120898454 | E | LC | ETL.2400.INSL.NCER | 40838926 | VICTOR | STOCKTON | 2021-04-28 |  | ETL.2400 | MELONES-RACETRACK | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40811616 | 1980-01-01 | Single Wood Pole | DDE - Double Dead End | 1980-01-01 | Polymer | Dead End |  |  |  |  | 2.2329e-05 | 6204.6068 | 0.13854
120909291 | E | LC | ETL.5090.INSL | 40690376 | MOSSLNDG | CENTRAL COAST | 2021-04-14 |  | ETL.5090 | MONTA VISTA-COYOTE SW STA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40659866 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0073882 | 20.633 | 0.15244
120929600 | E | LC | ETL.3830.TOWR | 40803321 | VICTOR | STOCKTON | 2021-05-04 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40803321 | 1910-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 1.9987e-05 | 3450.5452 | 0.068967
120938566 | F | LC | ETL.6890.POLE.WOOD | 44804164 | LAKEVLLE | SONOMA | 2021-05-05 |  | ETL.6890 | FULTON-HOPLAND | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44804164 | 2019-04-30 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-04-30 | Polymer | Dead End |  |  |  |  | 1.7292e-05 | 3643.2947
120954275 | A | LC | ETL.7300.POLE.WOOD | 40602054 | TABLEMTN | NORTH VALLEY | 2021-05-09 | 2021-05-11 | ETL.7300 | KILARC-DESCHUTES | Emergency | Storm Related | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602054 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.010514 | 79.1904
121037191 | E | LC | ETL.6470.POLE.WOOD | 40658284 | SACTO | SIERRA | 2021-05-10 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40658284 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.22453 | 585.35 | 131.4311
121326477 | E | LC | ETL.2750.INSL.NCER | 40828534 | CONCORD | DIABLO | 2021-04-21 |  | ETL.2750 | MORAGA-OAKLAND #4 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40804641 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1960-01-01 | Polymer | Suspension |  |  |  |  | 0.00011193 | 0.065147 | 7.292e-06
121326576 | E | LC | ETL.3500.TOWR | 40803565 | VICTOR | STOCKTON | 2021-04-21 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40803565 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 0.0072854 | 6855.1987 | 49.9427
121351066 | F | LC | ETL.4870.TOWR | 40805393 | FRESNO | FRESNO | 2021-04-27 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40805393 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 1.6167e-07 | 588.9716 | 9.5219e-05
121352436 | A | LC | ETL.7930.SWIT | 40744051 | MOSSLNDG | CENTRAL COAST | 2021-05-17 | 2021-05-20 | ETL.7930 | SALINAS-LAURELES | Emergency | Storm Related | [Repair, Completed] | Tier2 |  |  | COMP | [9 empty] | HIGH VELOCITY INTERRUPTER | Manual
121352999 | E | LC | ETL.3500.TOWR | 40856714 | VICTOR | STOCKTON | 2021-04-26 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40856714 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 7.9993e-06 | 1740.3693 | 0.013922
121358781 | E | LC | ETL.8060.POLE.WOOD | 40828181 | SACTO | SIERRA | 2021-05-18 | 2021-06-02 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
121363538 | E | LC | ETL.1820.POLE.WDPS | 44563016 | EUREKA | HUMBOLDT | 2021-05-19 | 2021-08-30 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44562387 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.070289 | 6332.6187
121365309 | E | LC | ETL.1650.POLE.WOOD | 40819426 | LAKEVLLE | SONOMA | 2021-05-03 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40819426 | 1990-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1978-01-01 | Porcelain | Dead End |  |  |  |  | 0.0014366 | 2802.2717 | 4.0258
121370350 | F | LC | ETL.1250.POLE.NWOD | 40594425 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40594425 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 6.9545e-06 | 5917.1871
121373525 | F | LC | ETL.4550.TOWR | 40818683 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40818683 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.7916e-06 | 4310.3408 | 0.012033
121381111 | F | LC | ETL.6500.POLE.WOOD | 40757110 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40757110 |  | Single Wood Pole | T2N | 2018-07-10 | Polymer | Post |  |  |  |  | 0.03134 | 1080.3545
121384562 | E | LC | ETL.6500.INSL.CERA | 42564757 | SACTO | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42564752 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.0020096 | 1997.6459 | 4.0145
121384720 | F | LC | ETL.6500.POLE.WOOD | 40590401 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40590401 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | Pin |  |  |  |  | 0.0015772 | 1890.832
121385109 | E | LC | ETL.4393.INSL.NCER | 43209732 | SACTO | SACRAMENTO | 2021-05-12 |  | ETL.4393 | DRUM-HIGGINS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40586122 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 1.1469e-05 | 269.0937 | 0.0030863
121391705 | F | LC | ETL.1420.TOWR | 40822768 | SACTO | SIERRA | 2021-05-15 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40822768 | 1913-01-01 | LATTICE STEEL TOWER | Other | 2019-08-30 | Polymer | Post |  |  |  |  | 7.4986e-05 | 1993.4753 | 0.14948
121392219 | F | LC | ETL.6760.POLE.WOOD | 44964269 | SACTO | SIERRA | 2021-05-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44964269 |  | Light Duty Steel Pole | T2N | 2020-04-03 | Polymer | Post |  |  |  |  | 0.011253 | 110.7947
121392262 | F | LC | ETL.6480.POLE.NWOD | 45122776 | SACTO | NORTH VALLEY | 2021-05-14 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45122776 | 2021-06-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-06-11 | Glass | Dead End | [5 empty] | 253.2372
121397865 | F | LC | ETL.6480.POLE.NWOD | 45122791 | SACTO | NORTH VALLEY | 2021-05-14 | 2021-10-14 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 45122791 | 2021-06-20 | Light Duty Steel Pole | T-1 - Tri Post | 2021-06-20 | Polymer | Post | [5 empty] | 253.3131
121404093 | F | LC | ETL.6660.POLE.NWOD | 45086308 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45086308 | 2021-03-04 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-04 | Polymer | Post |  |  |  |  | 1.8222e-11 | 2996.0371
121404743 | F | LC | ETL.1070.POLE.WOOD | 40593489 | VICTOR | STOCKTON | 2021-05-20 | 2021-10-18 | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40593489 | 1998-01-01 | Single Wood Pole | TPSR - Tri Post & Susp Light | 1957-01-01 | Polymer | Dead End |  |  |  |  | 0.00016244 | 3105.197
121405036 | E | LC | ETL.7290.POLE.WOOD | 41119877 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41119877 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.4601 | 2436.0542 | 1120.8355
121405171 | F | LC | ETL.6870.POLE.WOOD | 40660023 | SACTO | SIERRA | 2021-05-19 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40660023 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post | 2019-05-13 | Polymer | Post |  |  |  |  | 0.030328 | 205.7471
121417830 | F | LC | ETL.6640.POLE.WOOD | 40760086 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40760086 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0011994 | 3249.6929
121417855 | E | LC | ETL.8405.INSL.CERA | 40610570 | SACTO | SACRAMENTO | 2021-05-27 |  | ETL.8405 | MIDDLE FORK #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40586049 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.77211 | 2531.4304 | 1954.5524
121420387 | F | LC | ETL.6640.POLE.WOOD | 40603065 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40603065 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.014402 | 3249.6929
121422403 | E | LC | ETL.7000.POLE.WOOD | 40591857 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591857 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00061903 | 0.065148 | 4.0329e-05
121428228 | F | LC | ETL.1400.POLE.WDPS | 44774095 | VICTOR | STOCKTON | 2021-05-26 | 2021-09-16 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
121428284 | F | LC | ETL.1400.POLE.STPS | 44810086 | VICTOR | STOCKTON | 2021-05-26 | 2021-10-07 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44810009 | 2019-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.6327e-05 | 47.5548
121430761 | E | LC | ETL.1400.POLE.WDPS | 44774109 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40803418 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0052916 | 31.7334 | 0.16792
121437435 | E | LC | ETL.7390.POLE.WOOD | 40824436 | LAKEVLLE | HUMBOLDT | 2021-05-27 |  | ETL.7390 | LAYTONVILLE-COVELO | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40824436 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.1962 | 363.8909 | 71.3937
121455610 | E | LC | ETL.6290.POLE.WOOD | 40666903 | TABLEMTN | NORTH VALLEY | 2021-05-29 | 2021-08-18 | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL | [11 empty] | 0.092559 | 126.5956
121471182 | E | LC | ETL.8365.POLE.WOOD | 40750527 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40750527 | 2010-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.023018 | 300.6168 | 6.9195
121475479 | E | LC | ETL.7550.POLE.WOOD | 40750952 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40750952 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 6.0987e-05 | 4117.8877 | 0.25114
121483854 | F | LC | ETL.1600.TOWR | 40752652 | LAKEVLLE | NORTH BAY | 2021-06-07 |  | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40752652 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 7.5307e-07 | 6270.9932 | 0.0047225
121485839 | E | LC | ETL.6980.POLE.WOOD | 40648481 | LAKEVLLE | HUMBOLDT | 2021-06-01 |  | ETL.6980 | FORT ROSS-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40648481 | 1953-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.068944 | 728.2747 | 50.2103
121499845 | F | LC | ETL.5650.TOWR | 40675885 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40675885 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 2.5666e-06 | 2505.4126 | 0.0064303
121512427 | B | LC | ETL.4750.INSL.CERA | 41129162 | LAKEVLLE | SONOMA | 2021-06-09 | 2021-09-01 | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129172 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | Dead End |  |  |  |  | 0.00039529 | 1172.524
121512816 | B | LC | ETL.1450.INSL.CERA | 40619935 | SACTO | SIERRA | 2021-06-04 | 2021-09-01 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549456 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Double Dead End |  |  |  |  | 8.6548e-05
121512816 | B | LC | ETL.1450.INSL.CERA | 40619935 | SACTO | SIERRA | 2021-06-04 | 2021-09-01 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549456 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Double Dead End |  |  |  |  | 8.6548e-05
121512816 | B | LC | ETL.1450.INSL.CERA | 40619935 | SACTO | SIERRA | 2021-06-04 | 2021-09-01 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549456 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Double Dead End |  |  |  |  | 8.6548e-05
121517141 | E | LC | ETL.1350.POLE.WDPS | 44513777 | TABLEMTN |  | 2021-06-04 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44512267 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.030806 | 205.744 | 6.3381
121518353 | F | LC | ETL.6721.POLE.WOOD | 40771383 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.6721 | ORO FINO TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40771383 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.0040054 | 79.1651 | 0.31709
121518581 | E | LC | ETL.1600.INSL.CERA | 40725375 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40682785 | 1946-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1946-01-01 | Porcelain | Dead End |  |  |  |  | 4.2691e-05 | 3369.7969 | 0.14386
121520106 | E | LC | ETL.1450.POLE.WDPS | 44552484 | SACTO | SACRAMENTO | 2021-06-11 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44551582 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.015408 | 31.7066 | 0.48854
121524041 | B | LC | ETL.4550.TOWR | 40595141 | TABLEMTN | NORTH VALLEY | 2021-05-04 | 2021-07-27 | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40595141 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.6257e-07 | 4705.9995
121525044 | F | LC | ETL.4040.POLE.WDPS | 44557718 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44553952 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.02083 | 3941.2444
121536904 | F | LC | ETL.6760.POLE.WOOD | 40591319 | SACTO | SIERRA | 2021-06-10 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40591319 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.010312 | 253.1613
121547799 | F | LC | ETL.6750.POLE.WDPS | 44561496 | TABLEMTN | NORTH VALLEY | 2021-06-16 | 2021-07-21 | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44560759 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 4.5189e-05 | 47.5295
121568893 | E | LC | ETL.8405.POLE.WOOD | 42569712 | SACTO | SIERRA | 2021-06-15 | 2021-07-01 | ETL.8405 | MIDDLE FORK #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 42569712 |  | Single Wood Pole | Unknown |  | Polymer | [5 empty] | 0.023403 | 6902.4902
121568993 | E | LC | ETL.4750.INSL.CERA | 40609332 | LAKEVLLE | SONOMA | 2021-06-09 |  | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129171 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2019-12-16 | Glass | Dead End |  |  |  |  | 0.0040823 | 1725.5695 | 7.0443
121568993 | E | LC | ETL.4750.INSL.CERA | 40609332 | LAKEVLLE | SONOMA | 2021-06-09 |  | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129171 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | Dead End |  |  |  |  | 0.0040823 | 1725.5695 | 7.0443
121580071 | F | LC | ETL.7550.POLE.WOOD | 40861425 | LAKEVLLE | HUMBOLDT | 2021-06-10 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40861425 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 8.9219e-05 | 110.7947
121582463 | B | LC | ETL.6040.INSL | 40783480 | MOSSLNDG | CENTRAL COAST | 2021-06-22 | 2021-07-07 | ETL.6040 | MOSS LANDING-LOS BANOS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40753855 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 0.00013013 | 3115.7767
121586289 | B | LC | ETL.6020.INSL | 40714539 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-07-15 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40663427 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.8353e-07 | 1412.459
121588318 | F | LC | ETL.2790.TOWR | 40587936 | CONCORD | EAST BAY | 2021-06-22 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587936 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 7.9186e-07 | 63.3245 | 5.0144e-05
121593234 | E | LC | ETL.7180.INSL.CERA | 40779566 | LAKEVLLE | NORTH BAY | 2021-06-23 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 44360889 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 0.00022684
121593234 | E | LC | ETL.7180.INSL.CERA | 40779566 | LAKEVLLE | NORTH BAY | 2021-06-23 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 44360889 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 0.00022684
121603701 | F | LC | ETL.5630.TOWR | 40599004 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.5630 | ROCK CREEK-POE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40599004 | 1950-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1950-01-01 | Ceramic | Dead End |  |  |  |  | 3.6411e-05 | 601.2112 | 0.021891
121624073 | B | LC | ETL.6760.INSL.NCER | 40849868 | SACTO | SACRAMENTO | 2021-06-28 | 2021-07-06 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40822644 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.014509 | 7.9744
121634701 | F | LC | ETL.7490.POLE.WDPS | 44743796 | EUREKA | HUMBOLDT | 2021-06-23 | 2021-07-09 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL | [12 empty] | 0.065148
121646379 | E | LC | ETL.2395.POLE.WOOD | 45001468 | TABLEMTN | NORTH VALLEY | 2021-06-26 |  | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45001468 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.00026134 | 79.172 | 0.020691
121684965 | E | LC | ETL.3700.INSL.CERA | 42574175 | PISMOBCH | LOS PADRES | 2021-06-30 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44296813 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 2.9923e-05
121684965 | E | LC | ETL.3700.INSL.CERA | 42574175 | PISMOBCH | LOS PADRES | 2021-06-30 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44296813 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 2.9923e-05
121684965 | E | LC | ETL.3700.INSL.CERA | 42574175 | PISMOBCH | LOS PADRES | 2021-06-30 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44296813 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 2.9923e-05
121705713 | F | LC | ETL.5934.TOWR | 40818496 | PISMOBCH | FRESNO | 2021-07-06 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40818496 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.00013158
121705713 | F | LC | ETL.5934.TOWR | 40818496 | PISMOBCH | FRESNO | 2021-07-06 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40818496 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00013158
121720021 | B | LC | ETL.9240.TOWR | 43249707 | PISMOBCH | LOS PADRES | 2021-07-13 | 2021-07-27 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249707 |  | LATTICE STEEL TOWER | [9 empty] | 4307.811
121721919 | E | LC | ETL.1450.INSL.CERA | 42573095 | SACTO | SIERRA | 2021-06-12 |  | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42572750 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 0.0047828 | 47.5526 | 0.22743
121725195 | E | LC | ETL.1250.POLE.WOOD | 40876900 | FRESNO | YOSEMITE | 2021-07-07 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40876900 |  | Single Wood Pole | T-1 - Tri Post | 2018-04-14 | Polymer | Post |  |  |  |  | 0.0008961 | 6505.4771 | 5.8295
121732105 | E | LC | ETL.6380.POLE.WDPS | 44235467 | LAKEVLLE |  | 2021-07-08 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44235466 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.4144e-05 | 5950.5616 | 0.084165
121733472 | E | LC | ETL.6020.INSL | 40790047 | TABLEMTN | NORTH VALLEY | 2021-07-15 |  | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40759950 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.7218e-05 | 1202.6853 | 0.032734
121741784 | E | LC | ETL.1820.POLE.WDPS | 44557584 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44553997 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.9749 | 253.1639 | 246.8088
121743700 | F | LC | ETL.2390.POLE.WDPS | 44391007 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Right of Way | Encroachment | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44391006 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.8356e-06 | 2546.2529
121746454 | F | LC | ETL.4393.POLE.NWOD | 45078754 | SACTO | SIERRA | 2021-07-16 |  | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45078754 | 2020-09-02 | Light Duty Steel Pole | DDE - Double Dead End | 2020-09-02 | Glass | Double Dead End |  |  |  |  | 0.00032628 | 2056.7583
121766651 | B | LC | ETL.8264.POLE.WOOD | 40904822 | VICTOR | STOCKTON | 2021-06-12 | 2021-08-30 | ETL.8264 | VALLEY SPRINGS-CLAY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40904822 | 1998-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 6.7425e-06 | 3414.477
121781812 | F | LC | ETL.2390.POLE.WDPS | 44391048 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391046 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.001057 | 3292.7512 | 3.4803
121788085 | B | LC | ETL.6280.POLE.WOOD | 40862065 | TABLEMTN | NORTH VALLEY | 2021-07-23 |  | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 |  |  | PEND | [11 empty] | 1.4368e-05 | 711.7988 | 0.010227
121794700 | F | LC | ETL.4040.POLE.STPS | 45151848 | TABLEMTN | NORTH VALLEY | 2021-07-21 |  | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45151848 | 2020-08-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-08-06 | Glass | Suspension
121794700 | F | LC | ETL.4040.POLE.STPS | 45151848 | TABLEMTN | NORTH VALLEY | 2021-07-21 |  | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45151848 | 2020-08-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-08-06 | Glass | Suspension
121800596 | E | LC | ETL.8365.POLE.NWOD | 44974331 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44974331 | 2020-09-04 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-09-04 | Glass | Dead End |  |  |  |  | 0.010283
121814228 | E | LC | ETL.1400.POLE.WDPS | 45051011 | VICTOR | YOSEMITE | 2021-07-26 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40661820 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0047609 | 221.5655 | 1.0549
121815598 | E | LC | ETL.4410.TOWR | 40810180 | CONCORD | DIABLO | 2021-07-29 |  | ETL.4410 | BRENTWOOD-KELSO | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810180 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 0.0004021 | 5145.7153 | 2.0691
121820759 | E | LC | ETL.6280.POLE.WOOD | 40666795 | TABLEMTN | NORTH VALLEY | 2021-07-30 |  | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40666795 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 2.5741e-05 | 174.0445 | 0.00448
121822720 | E | LC | ETL.8365.POLE.NWOD | 45083300 | EUREKA | HUMBOLDT | 2021-07-28 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 45083300 | 2021-04-21 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-04-21 | Glass | Dead End |  |  |  |  | 0.0057372
121838868 | E | LC | ETL.8060.POLE.WOOD | 40770670 | SACTO | SACRAMENTO | 2021-08-03 |  | ETL.8060 | SPAULDING-SUMMIT | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40770670 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | [5 empty] | 0.072811 | 0.065152 | 0.0047438
121953131 | E | LC | ETL.5220.INSL | 40782411 | METCALF | DE ANZA | 2021-08-25 |  | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | PEND | 40753082 | 1963-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1963-01-01 | Ceramic | Suspension |  |  |  |  | 0.0062294 | 1234.1384 | 7.6879
122069417 | B | LC | ETL.1422.SWIT | 40743226 | SACTO | SACRAMENTO | 2021-09-18 | 2021-09-27 | ETL.1422 | BRUNSWICK #1 TAP | Switch | Out of Adjustment | [Repair, Completed] | Tier3 |  |  | COMP | [8 empty] | Other | HIGH VELOCITY INTERRUPTER | Manual
122073420 | E | LC | ETL.5980.INSL.NCER | 45009312 | PISMOBCH | LOS PADRES | 2021-09-20 |  | ETL.5980 | DIABLO-MIDWAY #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587709 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-10-16 | Glass Silicone Coated | Suspension |  |  |  |  | 1.4905e-06 | 777.7842 | 0.0011593
122193137 | F | LC | ETL.7560.POLE.STPS | 44924471 | SACTO | SIERRA | 2021-10-07 |  | ETL.7560 | WEIMAR #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44923837 | 2019-08-07 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00040309 | 79.1577
118576595 | B | LC | ETL.4340.INSL | 40899265 | CONCORD |  | 2020-02-25 | 2020-04-07 | ETL.4340 | BAHIA-MORAGA | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873496 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-30 | Glass | Suspension |  |  |  |  | 4.3582e-09 | 1692.6119
118576595 | B | LC | ETL.4340.INSL | 40899265 | CONCORD |  | 2020-02-25 | 2020-04-07 | ETL.4340 | BAHIA-MORAGA | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873496 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 4.3582e-09 | 1692.6119
118729009 | B | LC | ETL.7930.POLE.WOOD | 40680282 | MOSSLNDG | CENTRAL COAST | 2020-03-20 | 2020-04-28 | ETL.7930 | SALINAS-LAURELES | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40680282 |  | Single Wood Pole | T-1 - Tri Post | 2020-03-22 | Polymer | Post |  |  |  |  | 0.0014633 | 111.5028
118931425 | E | LC | ETL.1670.POLE.WOOD | 40819419 | LAKEVLLE | SONOMA | 2020-04-18 | 2021-01-14 | ETL.1670 | GEYSERS #5-GEYSERS #3 | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40819419 | 1991-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.00072884 | 5607.6411
118944749 | F | LC | ETL.4750.TOWR | 41129184 | LAKEVLLE | SONOMA | 2020-04-23 | 2020-05-11 | ETL.4750 | GEYSERS #12-FULTON | Structure-Tower | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129184 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.0022144 | 1646.4998
118944749 | F | LC | ETL.4750.TOWR | 41129184 | LAKEVLLE | SONOMA | 2020-04-23 | 2020-05-11 | ETL.4750 | GEYSERS #12-FULTON | Structure-Tower | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129184 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-02-07 | Glass | Dead End |  |  |  |  | 0.0022144 | 1646.4998
118949765 | E | LC | ETL.4392.TOWR | 41129318 | LAKEVLLE | SONOMA | 2020-04-26 | 2021-03-03 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129318 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-08-18 | Glass | Double Dead End |  |  |  |  | 4.657e-05 | 3054.8015
118949765 | E | LC | ETL.4392.TOWR | 41129318 | LAKEVLLE | SONOMA | 2020-04-26 | 2021-03-03 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129318 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 4.657e-05 | 3054.8015
118952480 | F | LC | ETL.3740.TOWR | 40646528 | CONCORD | EAST BAY | 2020-04-23 | 2021-04-14 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40646528 | 1922-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1991-01-01 | Porcelain | Suspension |  |  |  |  | 0.10834 | 0.065158
118966770 | E | LC | ETL.8410.POLE.WDPS | 44764254 | LAKEVLLE |  | 2020-05-01 |  | ETL.8410 | ELK-GUALALA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40660623 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.18755 | 205.6675 | 38.5729
118993836 | F | LC | ETL.5930.TOWR | 40868391 | CONCORD | DIABLO | 2020-05-04 | 2021-03-29 | ETL.5930 | PARKWAY-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40868391 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2017-10-27 | Glass | Dead End |  |  |  |  | 2.4053e-07 | 712.379
118993836 | F | LC | ETL.5930.TOWR | 40868391 | CONCORD | DIABLO | 2020-05-04 | 2021-03-29 | ETL.5930 | PARKWAY-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40868391 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.4053e-07 | 712.379
119000027 | E | LC | ETL.5430.INSL | 40726253 | TABLEMTN |  | 2020-05-08 | 2020-10-09 | ETL.5430 | PIT #5-ROUND MTN #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119004875 | E | LC | ETL.6770.POLE.WOOD | 40586058 | SACTO | SACRAMENTO | 2020-05-09 | 2021-04-19 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119005216 | E | LC | ETL.1400.POLE.WOOD | 40744851 | VICTOR | YOSEMITE | 2020-05-04 | 2020-06-18 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40744851 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010808
119005216 | E | LC | ETL.1400.POLE.WOOD | 40744851 | VICTOR | YOSEMITE | 2020-05-04 | 2020-06-18 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40744851 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010808
119029635 | E | LC | ETL.9460.POLE.WOOD | 44635907 | VICTOR | STOCKTON | 2020-05-11 | 2021-01-14 | ETL.9460 | VALLEY SPRINGS #2 | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119031184 | E | LC | ETL.8410.POLE.WOOD | 40605939 | LAKEVLLE | HUMBOLDT | 2020-05-06 | 2021-05-27 | ETL.8410 | ELK-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119036995 | F | LC | ETL.1450.POLE.WDPS | 44549912 | SACTO | SACRAMENTO | 2020-05-16 | 2020-08-17 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549500 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0096095 | 522.1488
119036995 | F | LC | ETL.1450.POLE.WDPS | 44549912 | SACTO | SACRAMENTO | 2020-05-16 | 2020-08-17 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549500 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0096095 | 522.1488
119043338 | E | LC | ETL.2060.INSL | 40640220 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-09-01 | ETL.2060 | FORT BRAGG-ELK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119076284 | E | LC | ETL.1050.INSL.CERA | 40607230 | FRESNO | FRESNO | 2020-05-27 | 2021-07-22 | ETL.1050 | BALCH-SANGER | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119083178 | F | LC | ETL.5290.TOWR | 40595487 | PISMOBCH | LOS PADRES | 2020-05-18 | 2021-01-22 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40595487 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 7.3823e-08 | 1804.9929
119084740 | F | LC | ETL.8405.POLE.NWOD | 44810014 | SACTO | SIERRA | 2020-05-29 |  | ETL.8405 | MIDDLE FORK #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44810014 | 2019-08-02 | Light Duty Steel Pole | T-1 - Tri Post | 2019-08-02 | Polymer | Post |  |  |  |  | 3.5415e-06 | 6902.4902
119086214 | F | LC | ETL.1330.TOWR | 40819332 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-04-12 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40819332 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Ceramic | Dead End |  |  |  |  | 0.00016791 | 3104.3772
119086214 | F | LC | ETL.1330.TOWR | 40819332 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-04-12 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40819332 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00016791 | 3104.3772
119086716 | F | LC | ETL.6720.POLE.WDPS | 44949077 | TABLEMTN | NORTH VALLEY | 2020-05-27 | 2021-09-01 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42578833 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0004205 | 2104.1226
119098458 | E | LC | ETL.6520.POLE.WOOD | 40644594 | SACTO | SIERRA | 2020-06-02 | 2021-06-09 | ETL.6520 | COLGATE-SMARTVILLE #2 | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119103297 | E | LC | ETL.6720.POLE.NWOD | 40700298 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-02-22 | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40700298 | 1998-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 4.2449e-05 | 0.065151
119108848 | F | LC | ETL.7540.POLE.WOOD | 40577241 | LAKEVLLE | HUMBOLDT | 2020-05-21 | 2021-05-03 | ETL.7540 | MENDOCINO-WILLITS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119115193 | E | LC | ETL.7290.POLE.WOOD | 40877889 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-03-01 | ETL.7290 | KILARC-CEDAR CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40877889 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0022358 | 588.7952
119116182 | F | LC | ETL.6330.POLE.WOOD | 40868156 | TABLEMTN | NORTH VALLEY | 2020-05-28 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40868156 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00074674 | 1502.9633
119116949 | F | LC | ETL.7560.POLE.NWOD | 44263384 | SACTO | SIERRA | 2020-05-29 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44263384 |  | Light Duty Steel Pole | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.0075317 | 6059.3994
119117562 | F | LC | ETL.1400.POLE.WDPS | 44776447 | VICTOR | STOCKTON | 2020-05-26 | 2021-08-26 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40643737 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.0013675 | 31.7334
119119155 | E | LC | ETL.8650.TOWR | 40748165 | FRESNO | YOSEMITE | 2020-06-01 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40748165 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1929-01-01 | Porcelain | Suspension |  |  |  |  | 0.0078722 | 6847.8872
119141761 | F | LC | ETL.6220.POLE.NWOD | 40810933 | EUREKA | HUMBOLDT | 2020-06-05 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40810933 |  | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 0.052215 | 546.5756
119150584 | F | LC | ETL.8170.POLE.WOOD | 40906465 | EUREKA | HUMBOLDT | 2020-06-03 | 2021-09-23 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40906465 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.030022 | 0.065152
119156553 | F | LC | ETL.7270.POLE.WOOD | 40877837 | TABLEMTN | NORTH VALLEY | 2020-06-05 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40877837 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.044519 | 3809.4433
119162717 | F | LC | ETL.7390.POLE.NWOD | 44836560 | LAKEVLLE | HUMBOLDT | 2020-06-09 |  | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44836560 | 2019-10-17 | Light Duty Steel Pole | DDE - Double Dead End | 2019-07-17 | Glass | Dead End - Suspension |  |  |  |  | 0.00055721
119174955 | F | LC | ETL.8170.POLE.WDPS | 44420629 | EUREKA | HUMBOLDT | 2020-06-12 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44420626 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0095642 | 1092.4791
119175075 | E | LC | ETL.8170.POLE.WDPS | 44420645 | EUREKA | HUMBOLDT | 2020-06-12 | 2021-06-21 | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420642 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.012887 | 189.9226
119180029 | F | LC | ETL.1073.POLE.WDPS | 44385287 | VICTOR | YOSEMITE | 2020-06-17 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44385285 | 2017-08-17 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.1659e-05 | 2672.7844
119182370 | F | LC | ETL.5452.TOWR | 40804966 | CONCORD | DIABLO | 2020-06-17 | 2021-01-20 | ETL.5452 | CONTRA COSTA-MORAGA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40804966 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-01-01 | Ceramic | Suspension |  |  |  |  | 2.1602e-07 | 23.797
119183446 | E | LC | ETL.1050.TOWR | 40682227 | FRESNO | FRESNO | 2020-06-18 | 2020-11-17 | ETL.1050 | BALCH-SANGER | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40682227 | 1927-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1927-01-01 | Porcelain | Dead End |  |  |  |  | 0.0026228 | 5667.3623
119199035 | F | LC | ETL.6310.POLE.WOOD | 44274796 | TABLEMTN | NORTH VALLEY | 2020-06-22 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44274796 | 2015-12-14 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.00011817 | 4594.916
119231860 | E | LC | ETL.7270.POLE.STPS | 44201737 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2021-09-01 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44201734 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.4676e-05 | 2025.7803
119238540 | E | LC | ETL.8170.POLE.WDPS | 44565570 | EUREKA | HUMBOLDT | 2020-06-30 | 2021-10-11 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | DLFL | 44564206 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.028619 | 553.6737
119290745 | E | LC | ETL.1370.INSL.CERA | 40786866 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-06-21 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119293984 | F | LC | ETL.7180.POLE.WDPS | 44360864 | LAKEVLLE | SONOMA | 2020-07-01 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Tier 3 | Within Both | PEND | 44360863 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00011258 | 1565.7461
119301264 | F | LC | ETL.8060.POLE.WOOD | 40668697 | SACTO | SIERRA | 2020-06-29 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40668697 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.05494 | 0.24228
119301916 | F | LC | ETL.4393.POLE.WDPS | 44199668 | SACTO | SACRAMENTO | 2020-06-30 | 2021-03-29 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119309985 | F | LC | ETL.8060.POLE.WOOD | 40826183 | SACTO | SIERRA | 2020-07-02 | 2021-05-11 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826183 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.023813 | 981.4936
119310037 | F | LC | ETL.6861.POLE.WOOD | 40615074 | LAKEVLLE | SONOMA | 2020-07-03 |  | ETL.6861 | KONOCTI-EAGLE ROCK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40615074 |  | Single Wood Pole | T2N | 2018-11-06 | Polymer | Post |  |  |  |  | 0.00010941 | 6411.6025
119316932 | F | LC | ETL.7270.POLE.WOOD | 40909524 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-08-30 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40909524 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2017-01-27 | Polymer | Dead End |  |  |  |  | 0.0015497 | 4968.3677
119317263 | F | LC | ETL.8170.POLE.WOOD | 40906462 | EUREKA | HUMBOLDT | 2020-07-06 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906462 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.24189 | 0.065152
119317803 | F | LC | ETL.7270.POLE.WOOD | 40906479 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906479 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0039405 | 1758.3086
119318194 | E | LC | ETL.8170.POLE.WDPS | 44565620 | EUREKA | HUMBOLDT | 2020-06-30 | 2021-08-18 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564294 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0088171 | 2425.2515
119328375 | F | LC | ETL.8060.POLE.WOOD | 40864061 | SACTO | SIERRA | 2020-07-07 | 2021-05-12 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40864061 | 1996-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0067454 | 348.1462
119335264 | E | LC | ETL.7030.POLE.WOOD | 40656905 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-06-09 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656905 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0065138 | 159.1485
119339747 | F | LC | ETL.6280.POLE.NWOD | 44259058 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-09-15 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44259058 | 2020-07-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-07-16 | Polymer | Dead End |  |  |  |  | 2.5138e-10 | 300.5749
119341621 | F | LC | ETL.6280.POLE.WOOD | 40811551 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40811551 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Other |  |  |  |  | 5.0512e-05 | 4729.1396
119358208 | F | LC | ETL.1440.POLE.WOOD | 42572650 | SACTO | SIERRA | 2020-07-10 | 2021-05-05 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119359704 | E | LC | ETL.7030.POLE.WOOD | 40616865 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-05-19 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119359757 | F | LC | ETL.7270.POLE.WOOD | 40752146 | TABLEMTN | NORTH VALLEY | 2020-07-13 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40752146 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0052472 | 477.4416
119374024 | E | LC | ETL.7490.POLE.WDPS | 44743796 | EUREKA | HUMBOLDT | 2020-07-13 | 2021-01-25 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL | [12 empty] | 0.065148
119377385 | F | LC | ETL.7030.POLE.WOOD | 40656896 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-07-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656896 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.037393 | 0.06515
119461735 | E | LC | ETL.7030.POLE.WOOD | 40877470 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-06-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877470 |  | Single Wood Pole | T2N | 2021-05-18 | Polymer | Post |  |  |  |  | 0.024382 | 126.76
119476469 | E | LC | ETL.6760.POLE.WOOD | 44178360 | SACTO | SACRAMENTO | 2020-07-20 | 2020-12-14 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44178360 | 2015-03-25 | Single Wood Pole | TH - TriAngle Post 70 | 2015-03-25 | Polymer | Post |  |  |  |  | 0.012679 | 94.9894
119478996 | E | LC | ETL.1110.INSL | 40799052 | EUREKA | HUMBOLDT | 2020-07-20 | 2021-08-09 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768277 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.5487e-05 | 0.065152
119483555 | E | LC | ETL.6290.POLE.WOOD | 40751784 | TABLEMTN | NORTH VALLEY | 2020-07-21 | 2021-01-25 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40751784 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.25251 | 1043.9412
119487596 | E | LC | ETL.1370.POLE.WOOD | 44296268 | PISMOBCH | LOS PADRES | 2020-07-22 | 2021-05-06 | ETL.1370 | DIVIDE-CABRILLO #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44296268 |  | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 2018-07-27 | Porcelain | Suspension - Post |  |  |  |  | 0.029201 | 1348.3113
119488783 | F | LC | ETL.8170.POLE.WOOD | 40906297 | EUREKA | HUMBOLDT | 2020-07-21 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40906297 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.045729 | 1504.1785
119489894 | F | LC | ETL.8060.POLE.WOOD | 40826231 | SACTO | SIERRA | 2020-07-22 | 2021-08-23 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826231 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Polymer | [5 empty] | 0.026376 | 3274.9534
119491919 | E | LC | ETL.9200.POLE.WOOD | 40654430 | MIDWAY | KERN | 2020-07-22 |  | ETL.9200 | TAFT-CUYAMA #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40654430 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Ceramic | Pin |  |  |  |  | 0.11638
119519420 | B | LC | ETL.3190.TOWR | 40758632 | TABLEMTN | NORTH VALLEY | 2020-07-28 | 2020-08-21 | ETL.3190 | CARIBOU-PALERMO | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758632 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.68383 | 4528.1333
119524938 | E | LC | ETL.6490.POLE.WOOD | 40612744 | SACTO | SACRAMENTO | 2020-07-29 | 2021-03-15 | ETL.6490 | COLGATE-GRASS VALLEY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40612744 |  | Single Wood Pole | T-1 - Tri Post | 2020-07-19 | Polymer | Post |  |  |  |  | 0.003244 | 4888.1362
119573910 | E | LC | ETL.6980.POLE.WOOD | 40750307 | LAKEVLLE | HUMBOLDT | 2020-08-06 | 2021-06-30 | ETL.6980 | FORT ROSS-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750307 | 1953-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1953-01-01 | Polymer | Suspension |  |  |  |  | 0.27046 | 824.8841
119590964 | F | LC | ETL.6911.POLE.WOOD | 41101271 | LAKEVLLE | SONOMA | 2020-08-07 |  | ETL.6911 | WASHOE TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41101271 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 1.8427e-05 | 1141.3943
119611241 | E | LC | ETL.1600.TOWR | 40761516 | LAKEVLLE | SONOMA | 2020-08-13 | 2020-10-15 | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | DLFL | 40761516 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-03-27 | Glass | Suspension |  |  |  |  | 2.1517e-07 | 31.7331
119611241 | E | LC | ETL.1600.TOWR | 40761516 | LAKEVLLE | SONOMA | 2020-08-13 | 2020-10-15 | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | DLFL | 40761516 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 2.1517e-07 | 31.7331
119665056 | F | LC | ETL.1330.TOWR | 40587900 | LAKEVLLE | SONOMA | 2020-08-24 |  | ETL.1330 | CORTINA-MENDOCINO #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40587900 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 1.1054e-05 | 6597.5997
119666860 | F | LC | ETL.6950.POLE.NWOD | 44919756 | SACTO | SACRAMENTO | 2020-08-25 |  | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44919756 | 2020-04-22 | Light Duty Steel Pole | T2N | 2020-04-22 | Polymer | Post |  |  |  |  | 8.0157e-05 | 221.7394
119695280 | E | LC | ETL.7290.POLE.WOOD | 44645363 | TABLEMTN | NORTH VALLEY | 2020-08-29 | 2021-03-01 | ETL.7290 | KILARC-CEDAR CREEK | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44645363 | 2018-08-05 | Single Wood Pole | T2N | 2018-08-05 | Polymer | Post |  |  |  |  | 0.011488 | 158.265
119702146 | E | LC | ETL.7390.POLE.NWOD | 44837898 | LAKEVLLE | SONOMA | 2020-09-01 | 2021-03-22 | ETL.7390 | LAYTONVILLE-COVELO | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44837898 | 2019-07-30 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-07-30 | Polymer | Post |  |  |  |  | 0.022502 | 3280.324
119727777 | A | LC | ETL.7590.POLE.WOOD | 40577156 | MOSSLNDG | CENTRAL COAST | 2020-09-08 | 2020-10-21 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119781030 | E | LC | ETL.8240.POLE.WOOD | 40825817 | VICTOR | STOCKTON | 2020-09-12 | 2021-03-30 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825817 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 2015-05-12 | Polymer | Post |  |  |  |  | 0.0007817 | 1600.2018
119808758 | F | LC | ETL.5140.POLE.STPS | 44690648 | SACTO | SIERRA | 2020-08-13 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44141418 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.243e-08 | 2246.6448
119818020 | F | LC | ETL.6950.POLE.WOOD | 40768214 | SACTO | SIERRA | 2020-09-11 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40768214 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0032325 | 1379.443
119829907 | E | LC | ETL.1073.POLE.WDPS | 44385267 | VICTOR | YOSEMITE | 2020-09-29 | 2021-08-25 | ETL.1073 | MI-WUK-CURTIS | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44385266 | 2017-08-17 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00072916 | 15.88
119873145 | B | LC | ETL.7780.POLE.WOOD | 40614159 | LAKEVLLE | HUMBOLDT | 2020-10-07 | 2020-11-24 | ETL.7780 | PHILO JCT-ELK | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40614159 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2015-02-07 | Ceramic | Double Dead End - Pin |  |  |  |  | 1.479e-05 | 174.0688
119891551 | E | LC | ETL.4000.POLE.WOOD | 44253831 | VICTOR | YOSEMITE | 2020-10-12 | 2021-10-12 | ETL.4000 | TESLA-SALADO-MANTECA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44253831 | 2013-04-22 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2013-04-22 | Porcelain | Suspension |  |  |  |  | 0.0012716 | 1254.9044 | 1.5957
119906605 | F | LC | ETL.8170.POLE.WOOD | 40862464 | EUREKA | HUMBOLDT | 2020-10-07 | 2021-09-23 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40862464 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.011192 | 6461.5288
119917760 | F | LC | ETL.8580.TOWR | 40582579 | FRESNO | FRESNO | 2020-09-25 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | PEND | 40582579 | 1969-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1969-01-01 | Porcelain | Dead End |  |  |  |  | 1.056e-06
119918025 | F | LC | ETL.6480.POLE.NWOD | 45122780 | SACTO | NORTH VALLEY | 2020-09-21 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45122780 | 2021-06-30 | Light Duty Steel Pole | T2N | 2021-06-30 | Polymer | Post | [5 empty] | 458.8146
120046236 | B | LC | ETL.7210.TOWR | 40594840 | METCALF | SAN JOSE | 2020-11-16 | 2020-12-01 | ETL.7210 | MARTIN-SNEATH LANE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | HFRA Removal | COMP | 40594840 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-14 | Glass | Suspension |  |  |  |  | 2.6986e-05 | 0.067704
120136327 | E | LC | ETL.7590.INSL.NCER | 42565658 | MOSSLNDG | CENTRAL COAST | 2020-11-30 | 2021-03-25 | ETL.7590 | MONTA VISTA-BURNS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 42565532 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.23518
120136327 | E | LC | ETL.7590.INSL.NCER | 42565658 | MOSSLNDG | CENTRAL COAST | 2020-11-30 | 2021-03-25 | ETL.7590 | MONTA VISTA-BURNS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 42565532 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.23518
120136327 | E | LC | ETL.7590.INSL.NCER | 42565658 | MOSSLNDG | CENTRAL COAST | 2020-11-30 | 2021-03-25 | ETL.7590 | MONTA VISTA-BURNS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 42565532 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.23518
120144446 | F | LC | ETL.8960.POLE.NWOD | 40588555 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40588555 |  | Tubular Steel Pole | SV1 - Angle 0-30 Degrees | 1974-01-01 | Polymer | Suspension |  |  |  |  | 3.4792e-08
120243104 | F | LC | ETL.8250.POLE.WOOD | 40908830 | VICTOR | STOCKTON | 2020-12-31 | 2021-01-11 | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908830 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 8.6465e-05 | 1759.9811
120558186 | A | LC | ETL.8960.POLE.WOOD | 40764661 | FRESNO | FRESNO | 2021-02-21 | 2021-02-23 | ETL.8960 | LOS BANOS-PACHECO | Emergency | Storm Related | [Repair, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40764661 | 1979-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1979-01-01 | Porcelain | Post |  |  |  |  | 0.00031589
120654108 | E | LC | ETL.7180.INSL.CERA | 40699538 | LAKEVLLE | NORTH BAY | 2021-03-17 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40668138 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.0658e-05 | 2537.4253 | 0.027045
120671479 | E | LC | ETL.4316.INSL | 40736143 | TABLEMTN | NORTH VALLEY | 2021-03-16 | 2021-08-12 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120672422 | E | LC | ETL.8290.POLE.WOOD | 40650371 | TABLEMTN | NORTH VALLEY | 2021-03-22 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40650371 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0014283 | 4767.2183 | 6.8092
120683814 | B | LC | ETL.1110.POLE.STPS | 44565796 | TABLEMTN | HUMBOLDT | 2021-03-17 | 2021-05-17 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44565729 | 2021-05-28 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.7975e-05 | 4417.5273
120685961 | E | LC | ETL.5790.INSL.CERA | 40838438 | VICTOR | STOCKTON | 2021-03-24 | 2021-06-17 | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40811326 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 1.1356e-07 | 1075.7365
120691628 | F | LC | ETL.1530.POLE.NWOD | 40681898 | SACTO | SACRAMENTO | 2021-03-25 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40681898 | 1980-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2021-03-29 | Glass | Suspension |  |  |  |  | 0.0019957 | 490.4389 | 0.97877
120691628 | F | LC | ETL.1530.POLE.NWOD | 40681898 | SACTO | SACRAMENTO | 2021-03-25 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40681898 | 1980-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 0.0019957 | 490.4389 | 0.97877
120720578 | E | LC | ETL.1820.INSL.CERA | 40637023 | EUREKA | HUMBOLDT | 2021-03-31 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | PEND
120725062 | E | LC | ETL.3700.POLE.WOOD | 40809277 | PISMOBCH | LOS PADRES | 2021-04-01 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40809277 | 1956-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1989-01-01 | Porcelain | Unknown |  |  |  |  | 0.00066254 | 2218.6458 | 1.4699
120738954 | E | LC | ETL.6040.TOWR | 40805585 | MOSSLNDG | CENTRAL COAST | 2021-04-02 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Anchor-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40805585 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.3946e-06
120745840 | F | LC | ETL.1070.POLE.WOOD | 40764840 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40764840 | 1998-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1957-01-01 | Polymer | Dead End |  |  |  |  | 1.8287e-05 | 2393.3862
120761783 | E | LC | ETL.7140.POLE.STPS | 44850454 | LAKEVLLE | SONOMA | 2021-04-07 | 2021-07-26 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44799547 | 2019-06-06 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00061045 | 4560.6943
120794890 | E | LC | ETL.6760.POLE.WOOD | 40824302 | SACTO | SACRAMENTO | 2021-04-12 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40824302 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | [5 empty] | 0.11358 | 110.8228 | 12.5874
120821528 | F | LC | ETL.5090.TOWR | 40863206 | MOSSLNDG | DE ANZA | 2021-04-08 |  | ETL.5090 | MONTA VISTA-COYOTE SW STA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40863206 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0097916 | 316.4942 | 3.099
120841565 | F | LC | ETL.1810.TOWR | 44321402 | EUREKA | HUMBOLDT | 2021-04-19 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Steel | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44321402 |  | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 9.9725e-06
120841565 | F | LC | ETL.1810.TOWR | 44321402 | EUREKA | HUMBOLDT | 2021-04-19 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Steel | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44321402 |  | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 9.9725e-06
120843370 | B | LC | ETL.1540.INSL | 40791863 | SACTO | SIERRA | 2021-04-16 | 2021-04-27 | ETL.1540 | EL DORADO-MISSOURI FLAT #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761888 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1980-01-01 | Ceramic | Double Dead End |  |  |  |  | 8.6843e-06 | 2309.6055
120846271 | E | LC | ETL.3500.TOWR | 40643018 | VICTOR | STOCKTON | 2021-04-19 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40643018 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 8.721e-05 | 142.4769 | 0.012425
120855380 | E | LC | ETL.1070.POLE.WOOD | 40580426 | VICTOR | YOSEMITE | 2021-04-12 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40580426 | 1957-01-01 | Single Wood Pole | SUSP - Suspension (TWR) | 1957-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.1792e-05 | 2155.5173 | 0.025417
120865996 | E | LC | ETL.3820.TOWR | 40821758 | VICTOR | STOCKTON | 2021-04-22 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40821758 | 1910-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1989-01-01 | Glass | Dead End |  |  |  |  | 1.4017e-05 | 6204.2363 | 0.086966
120878750 | B | LC | ETL.5091.INSL | 41122539 | MOSSLNDG | CENTRAL COAST | 2021-04-23 | 2021-05-20 | ETL.5091 | METCALF-MONTA VISTA #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40858040 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.020467 | 47.5295
120882381 | B | LC | ETL.6890.POLE.NWOD | 44713030 | LAKEVLLE | SONOMA | 2021-04-23 | 2021-05-19 | ETL.6890 | FULTON-HOPLAND | Insulator | Contaminated | [Ground Wash, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44713030 | 2019-02-16 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-02-16 | Ceramic | Suspension |  |  |  |  | 9.769e-08 | 949.8
120898888 | E | LC | ETL.5250.TOWR | 40756487 | CONCORD | DIABLO | 2021-04-28 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40756487 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.0138e-07 | 2103.6333 | 0.00084436
120898888 | E | LC | ETL.5250.TOWR | 40756487 | CONCORD | DIABLO | 2021-04-28 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40756487 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 4.0138e-07 | 2103.6333 | 0.00084436
120910684 | F | LC | ETL.7550.POLE.WOOD | 40649110 | LAKEVLLE | SONOMA | 2021-04-30 | 2021-06-02 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40649110 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Porcelain | [5 empty] | 0.00023537 | 1202.3098
120910709 | E | LC | ETL.7550.POLE.WOOD | 40666561 | LAKEVLLE | SONOMA | 2021-04-30 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40666561 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | [5 empty] | 0.00049471 | 110.7947 | 0.054811
120919617 | E | LC | ETL.5250.TOWR | 40816974 | CONCORD | DIABLO | 2021-05-01 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40816974 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.2432e-06 | 506.1398 | 0.0016415
120919617 | E | LC | ETL.5250.TOWR | 40816974 | CONCORD | DIABLO | 2021-05-01 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40816974 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-07-09 | Porcelain | Suspension |  |  |  |  | 3.2432e-06 | 506.1398 | 0.0016415
120922679 | B | LC | ETL.5140.POLE.WDPS | 44558403 | SACTO | SIERRA | 2021-05-03 | 2021-06-29 | ETL.5140 | MIDDLE FORK-GOLD HILL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44557916 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0022469 | 2404.7568
120929906 | B | LC | ETL.4550.TOWR | 40871679 | TABLEMTN | NORTH VALLEY | 2021-05-04 | 2021-06-16 | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871679 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.1753e-07 | 4895.8999
120931782 | E | LC | ETL.1820.INSL.CERA | 44395664 | EUREKA | HUMBOLDT | 2021-05-04 |  | ETL.1820 | HUMBOLDT-TRINITY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395398 | 2020-03-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-03-04 | Ceramic | Suspension |  |  |  |  | 0.00028685
120931782 | E | LC | ETL.1820.INSL.CERA | 44395664 | EUREKA | HUMBOLDT | 2021-05-04 |  | ETL.1820 | HUMBOLDT-TRINITY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395398 | 2020-03-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-03-04 | Ceramic | Suspension |  |  |  |  | 0.00028685
120933007 | F | LC | ETL.7550.POLE.WOOD | 40808825 | LAKEVLLE | SONOMA | 2021-05-04 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40808825 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 7.984e-05 | 15.8837
120991249 | E | LC | ETL.6470.POLE.WOOD | 40873678 | SACTO | SIERRA | 2021-05-07 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40873678 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.18701 | 443.0832 | 82.8626
121030928 | B | LC | ETL.8250.POLE.WOOD | 40663785 | VICTOR | STOCKTON | 2021-05-08 | 2021-06-28 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121031301 | E | LC | ETL.7550.POLE.WOOD | 40750982 | LAKEVLLE | SONOMA | 2021-05-10 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40750982 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 6.8496e-06 | 0.065148 | 4.4623e-07
121191108 | E | LC | ETL.3820.INSL.CERA | 40832700 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40808244 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 1.1055e-05 | 5033.749 | 0.05565
121329722 | F | LC | ETL.9250.POLE.WOOD | 40749385 | MIDWAY | KERN | 2021-04-22 |  | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40749385 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Pin |  |  |  |  | 0.024943 | 9424.9238
121340820 | F | LC | ETL.4870.TOWR | 40761392 | FRESNO | FRESNO | 2021-05-15 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40761392 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 1.57e-07 | 731.474 | 0.00011484
121341018 | E | LC | ETL.6500.INSL.CERA | 40684540 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40655085 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | Pin |  |  |  |  | 0.0085947 | 2118.558 | 18.2084
121363844 | E | LC | ETL.5970.INSL | 40623648 | PISMOBCH | LOS PADRES | 2021-04-30 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40597158 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 9.1281e-09 | 2785.5378 | 2.5427e-05
121372769 | E | LC | ETL.6950.INSL.CERA | 44172783 | SACTO | SACRAMENTO | 2021-05-01 | 2021-08-02 | ETL.6950 | GOLD HILL #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121373204 | E | LC | ETL.4550.INSL | 40789209 | TABLEMTN | NORTH VALLEY | 2021-05-04 | 2021-06-23 | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759833 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.5703e-07 | 4959.2188
121379813 | B | LC | ETL.4440.POLE.NWOD | 44190871 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-30 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44190871 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 4.1728e-06 | 2072.0388
121382048 | E | LC | ETL.8250.POLE.WOOD | 40904098 | VICTOR | STOCKTON | 2021-05-11 | 2021-08-09 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40904098 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.4842e-05 | 3580.2988
121383131 | F | LC | ETL.8350.POLE.WOOD | 44918810 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44918810 | 2020-03-03 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-03 | Polymer | Post |  |  |  |  | 2.9015e-07 | 753.0561
121385204 | F | LC | ETL.6760.POLE.WOOD | 40824284 | SACTO | SIERRA | 2021-05-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40824284 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.09684 | 2158.0108
121385824 | F | LC | ETL.6760.POLE.WOOD | 40865391 | SACTO | SIERRA | 2021-05-13 | 2021-06-25 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40865391 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.20875 | 47.5526
121391622 | E | LC | ETL.7550.POLE.WOOD | 40600395 | LAKEVLLE | HUMBOLDT | 2021-05-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40600395 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 1.3971e-05 | 1456.3043 | 0.020346
121404661 | E | LC | ETL.6280.POLE.WOOD | 44217540 | TABLEMTN | NORTH VALLEY | 2021-05-19 |  | ETL.6280 | CARIBOU #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44217540 | 2014-11-25 | Single Wood Pole | T2N | 2014-11-25 | Non Ceramic | Post |  |  |  |  | 7.5925e-05 | 5950.0312 | 0.45176
121405145 | F | LC | ETL.8290.POLE.WOOD | 40769426 | TABLEMTN | NORTH VALLEY | 2021-05-20 | 2021-06-07 | ETL.8290 | VOLTA-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40769426 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0076838 | 398.6012
121405487 | E | LC | ETL.8250.POLE.WOOD | 40908883 | VICTOR | STOCKTON | 2021-05-21 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40908883 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.00023503 | 2614.054 | 0.61438
121418232 | F | LC | ETL.1070.POLE.WOOD | 40745398 | VICTOR | STOCKTON | 2021-05-21 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40745398 | 1998-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1957-01-01 | Polymer | Dead End |  |  |  |  | 8.9058e-06 | 2171.9446
121422765 | E | LC | ETL.6640.POLE.WOOD | 40752163 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40752163 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.0064304 | 933.8852 | 6.0052
121428831 | F | LC | ETL.1710.POLE.WDPS | 44696026 | MOSSLNDG | CENTRAL COAST | 2021-05-26 | 2021-06-23 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 42567475 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.00013371 | 47.5096
121430869 | E | LC | ETL.7590.POLE.WDPS | 44632192 | MOSSLNDG | CENTRAL COAST | 2021-05-26 | 2021-07-26 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44631825 | 2018-07-23 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.049429 | 110.8153
121446061 | B | LC | ETL.1401.POLE.STPS | 44889239 | VICTOR | YOSEMITE | 2021-06-01 | 2021-07-22 | ETL.1401 | BEARDSLEY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44889223 | 2019-09-24 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.4675e-05 | 253.2337
121447628 | E | LC | ETL.1820.POLE.WDPS | 44560608 | EUREKA | HUMBOLDT | 2021-06-01 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560166 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.83949 | 648.7573 | 544.6255
121466839 | F | LC | ETL.8365.POLE.NWOD | 44356195 | EUREKA | HUMBOLDT | 2021-06-03 | 2021-09-23 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | DLFL | 44356195 | 2016-06-21 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2016-06-21 | Polymer | Post |  |  |  |  | 0.026366
121469318 | E | LC | ETL.6110.TOWR | 40664355 | METCALF | SAN JOSE | 2021-05-28 | 2021-08-10 | ETL.6110 | TESLA-METCALF | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40664355 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.1678e-08 | 367.8685
121475887 | E | LC | ETL.6750.POLE.WDPS | 44214440 | TABLEMTN | NORTH VALLEY | 2021-06-05 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44214438 | 2016-10-18 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0077513 | 490.5302 | 3.8022
121480523 | A | LC | ETL.7140.INSL.CERA | 40629581 | LAKEVLLE | NORTH BAY | 2021-06-04 | 2021-06-10 | ETL.7140 | IGNACIO-BOLINAS #1 | Emergency-Wood | Other | [Replace, Completed] | Tier3 |  |  | COMP
121493350 | E | LC | ETL.1350.POLE.WDPS | 45065793 | TABLEMTN | NORTH VALLEY | 2021-06-01 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40600870 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.010573 | 0.066431 | 0.00070236
121496271 | B | LC | ETL.1440.INSL.NCER | 44768873 | SACTO | SIERRA | 2021-06-08 | 2021-09-07 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
121497596 | E | LC | ETL.1350.POLE.WDPS | 44513786 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44512268 |  | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.052408 | 221.5655 | 11.6118
121514221 | E | LC | ETL.1600.INSL | 40611457 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40586773 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 4.6457e-05 | 2438.3081 | 0.11328
121536604 | E | LC | ETL.1600.POLE.WOOD | 40649046 | LAKEVLLE | NORTH BAY | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40649046 | 1977-01-01 | Single Wood Pole | T1DE - Tri Post Dead End 115 | 1977-01-01 | Polymer | Post |  |  |  |  | 6.7897e-05 | 332.2847 | 0.022561
121542598 | B | LC | ETL.6880.INSL.NCER | 45071373 | LAKEVLLE | SONOMA | 2021-06-15 | 2021-06-23 | ETL.6880 | FULTON-CALISTOGA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 45071342 | 2020-03-05 | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 2020-03-05 | Glass | Suspension |  |  |  |  | 2.8325e-05 | 221.6343
121543048 | F | LC | ETL.7550.POLE.NWOD | 44660770 | LAKEVLLE | HUMBOLDT | 2021-06-10 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44660770 | 2018-09-14 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-09-14 | Polymer | Dead End - Suspension |  |  |  |  | 2.6075e-11 | 47.5118
121543726 | F | LC | ETL.1820.POLE.NWOD | 44324171 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44324171 | 2015-12-01 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2015-12-01 | Ceramic | Suspension |  |  |  |  | 0.0085686 | 94.9939
121543940 | F | LC | ETL.1350.POLE.NWOD | 44993098 | TABLEMTN | NORTH VALLEY | 2021-06-12 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44993098 | 2020-06-04 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-04 | Glass | Dead End |  |  |  |  | 6.2682e-05 | 0.065152
121547357 | E | LC | ETL.7640.POLE.WDPS | 44565399 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564298 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 6.3368e-05 | 3880.9729 | 0.24593
121553051 | E | LC | ETL.6110.INSL | 40680660 | METCALF | SAN JOSE | 2021-06-16 |  | ETL.6110 | TESLA-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40651768 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.2238e-07 | 728.3589 | 0.00016197
121556040 | E | LC | ETL.1350.INSL.CERA | 40893267 | TABLEMTN |  | 2021-06-04 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44551510 |  | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.011537
121556040 | E | LC | ETL.1350.INSL.CERA | 40893267 | TABLEMTN |  | 2021-06-04 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44551510 |  | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.011537
121564910 | E | LC | ETL.9200.POLE.WDPS | 44986439 | MIDWAY | KERN | 2021-06-18 |  | ETL.9200 | TAFT-CUYAMA #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44985745 | 1962-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.040024
121575608 | E | LC | ETL.7550.POLE.NWOD | 44172883 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44172883 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | [7 empty] | 2.2483e-09 | 7039.9185 | 1.5828e-05
121583252 | B | LC | ETL.6050.INSL | 40839411 | MOSSLNDG | CENTRAL COAST | 2021-06-18 | 2021-07-13 | ETL.6050 | MOSS LANDING-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40811994 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 3.3391e-07 | 775.3163
121590798 | B | LC | ETL.5390.INSL.NCER | 45114530 | TABLEMTN | NORTH VALLEY | 2021-06-23 | 2021-09-23 | ETL.5390 | PIT #1-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873580 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.824e-05 | 5133.3115
121599759 | E | LC | ETL.6020.INSL.NCER | 44838815 | TABLEMTN | NORTH VALLEY | 2021-06-24 |  | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41111817 | 1965-01-01 | LATTICE STEEL TOWER | Unknown |  | Unknown | Suspension |  |  |  |  | 2.9935e-06 | 791.1378 | 0.0023683
121623510 | B | LC | ETL.6070.INSL | 40842550 | TABLEMTN | NORTH VALLEY | 2021-06-27 | 2021-07-15 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40816739 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 2.8124e-06 | 3658.251
121624652 | E | LC | ETL.7220.POLE.WOOD | 40755202 | METCALF | SAN JOSE | 2021-06-28 |  | ETL.7220 | JEFFERSON-STANFORD | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40755202 |  | Single Wood Pole | 1VPS - 1 Vertical Short Post |  | Porcelain | [5 empty] | 0.0004505 | 0.065147 | 2.9349e-05
121624661 | E | LC | ETL.2390.POLE.WDPS | 44390957 | VICTOR | STOCKTON | 2021-06-14 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44390956 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.6762e-06 | 1505.5992 | 0.013063
121631262 | E | LC | ETL.2390.POLE.WDPS | 44391124 | VICTOR | STOCKTON | 2021-06-15 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391123 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00018876 | 5396.2627 | 1.0186
121662144 | E | LC | ETL.1730.INSL.NCER | 40802875 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44413313 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Polymer | Double Dead End |  |  |  |  | 0.0016022
121662144 | E | LC | ETL.1730.INSL.NCER | 40802875 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44413313 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Polymer | Double Dead End |  |  |  |  | 0.0016022
121669069 | E | LC | ETL.6880.INSL.CERA | 44677497 | LAKEVLLE | SONOMA | 2021-07-05 |  | ETL.6880 | FULTON-CALISTOGA | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44677460 | 2017-10-21 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2017-10-21 | Ceramic | Suspension |  |  |  |  | 0.0086765 | 712.3741 | 6.1809
121679152 | E | LC | ETL.3700.POLE.WDPS | 44296834 | PISMOBCH | LOS PADRES | 2021-06-30 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44296833 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00016183 | 4022.5613 | 0.65095
121734216 | F | LC | ETL.9250.POLE.NWOD | 40749442 | MIDWAY | KERN | 2021-07-14 | 2021-08-19 | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40749442 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Pin |  |  |  |  | 0.0020211 | 3313.4712
121737243 | F | LC | ETL.1820.POLE.STPS | 44395507 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-09 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44395506 | 2020-03-03 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.011298 | 4462.79
121742588 | E | LC | ETL.3720.INSL.CERA | 40671721 | CONCORD | EAST BAY | 2021-07-13 |  | ETL.3720 | SOBRANTE-G #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40644471 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1968-01-01 | Porcelain | Suspension |  |  |  |  | 6.0395e-05 | 269.6005 | 0.016283
121752959 | E | LC | ETL.7390.POLE.NWOD | 45114393 | LAKEVLLE | HUMBOLDT | 2021-07-08 | 2021-08-23 | ETL.7390 | LAYTONVILLE-COVELO | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 45114393 | 2021-06-21 | Light Duty Steel Pole | T2N | 2021-06-21 | Polymer | Post | [5 empty] | 696.1808
121781375 | E | LC | ETL.6020.INSL | 40722250 | TABLEMTN | NORTH VALLEY | 2021-07-22 |  | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40677675 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00010188 | 411.4735 | 0.04192
121785338 | E | LC | ETL.5980.TOWR | 40740588 | PISMOBCH | LOS PADRES | 2021-07-23 |  | ETL.5980 | DIABLO-MIDWAY #3 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40740588 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 8.4675e-06 | 823.3094 | 0.0069714
121787011 | E | LC | ETL.4316.POLE.NWOD | 42567091 | TABLEMTN | NORTH VALLEY | 2021-07-21 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 42567091 | 2011-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | Unknown |  |  |  |  | 0.0086628 | 230.1254 | 1.9935
121790045 | E | LC | ETL.6040.TOWR | 40746828 | MOSSLNDG | YOSEMITE | 2021-07-24 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40746828 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 4.2414e-05 | 807.9712 | 0.034269
121800795 | B | LC | ETL.6280.POLE.WOOD | 44259126 | TABLEMTN | NORTH VALLEY | 2021-07-26 | 2021-09-21 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 4.164e-06 | 695.9825
121810655 | E | LC | ETL.8000.POLE.NWOD | 44646202 | SACTO | SIERRA | 2021-07-27 |  | ETL.8000 | SMARTVILLE-NICOLAUS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44646202 | 2018-06-06 | Light Duty Steel Pole | T1DE - Tri Post Dead End 115 | 2018-06-06 | Polymer | Dead End |  |  |  |  | 4.4971e-07 | 4949.689 | 0.0022259
121812473 | E | LC | ETL.8630.POLE.WDPS | 44565451 | PISMOBCH | LOS PADRES | 2021-07-28 |  | ETL.8630 | DIVIDE-VANDENBERG #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44564225 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014458 | 3863.4768 | 5.5856
121823106 | B | LC | ETL.1810.POLE.STPS | 44996083 | EUREKA | HUMBOLDT | 2021-07-29 | 2021-08-12 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44996003 | 2020-04-27 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00010282
121823257 | E | LC | ETL.6690.INSL | 40797552 | SACTO | SIERRA | 2021-07-30 |  | ETL.6690 | DEER CREEK-DRUM | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40766815 |  | Single Wood Pole | 3P DDE-A - 3 Pole Double Dead End Angle |  | Ceramic | [5 empty] | 0.082724 | 63.3607 | 5.2414
121824217 | E | LC | ETL.7390.POLE.WOOD | 40824455 | LAKEVLLE | HUMBOLDT | 2021-07-29 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40824455 |  | Single Wood Pole | T2N | 2021-01-28 | Polymer | Post |  |  |  |  | 0.24944 | 458.8146 | 114.447
121897689 | E | LC | ETL.4620.INSL | 40896691 | PISMOBCH | LOS PADRES | 2021-08-13 |  | ETL.4620 | DIABLO-MESA | FAA Lighting-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40872452 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.2732e-08 | 2724.3408
121897689 | E | LC | ETL.4620.INSL | 40896691 | PISMOBCH | LOS PADRES | 2021-08-13 |  | ETL.4620 | DIABLO-MESA | FAA Lighting-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40872452 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Other |  |  |  |  | 1.2732e-08 | 2724.3408
121907810 | F | LC | ETL.6720.POLE.NWOD | 42578804 | TABLEMTN | NORTH VALLEY | 2021-08-13 |  | ETL.6720 | DESABLA-CENTERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 42578804 | 2019-08-29 | Light Duty Steel Pole | FSS - Field Switch Structure | [7 empty] | 1.1085e-07 | 23.7951
122058093 | E | LC | ETL.4780.INSL.NCER | 45128990 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129353 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 1.8675e-05 | 3439.0496 | 0.064223
122058093 | E | LC | ETL.4780.INSL.NCER | 45128990 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129353 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 1.8675e-05 | 3439.0496 | 0.064223
118397741 | E | LC | ETL.4460.TOWR | 40753659 | MOSSLNDG | CENTRAL COAST | 2020-01-06 | 2020-05-12 | ETL.4460 | COBURN-LAS AGUILAS SW STA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40753659 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 5.8259e-07 | 48.4459
118752270 | E | LC | ETL.4316.POLE.NWOD | 40618578 | TABLEMTN | NORTH VALLEY | 2020-03-27 | 2021-08-24 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40618578 |  | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2021-07-30 | Glass | Double Dead End |  |  |  |  | 0.0020484 | 63.3451
118788645 | E | LC | ETL.6320.POLE.WOOD | 44384843 | TABLEMTN | NORTH VALLEY | 2020-04-07 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44384843 | 2018-10-04 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-10-04 | Polymer | Dead End |  |  |  |  | 0.013985 | 271.6997 | 3.7997
118946896 | F | LC | ETL.1252.POLE.NWOD | 40575874 | FRESNO | FRESNO | 2020-04-24 | 2021-04-07 | ETL.1252 | OAKHURST TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40575874 | 1996-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 2.5207e-07 | 47.5096
118947297 | F | LC | ETL.1252.POLE.NWOD | 40868548 | FRESNO | FRESNO | 2020-04-24 | 2021-07-20 | ETL.1252 | OAKHURST TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40868548 | 2005-01-01 | Light Duty Steel Pole | TPS - Tri Post & Susp (1-3) | 2005-01-01 | Polymer | Suspension |  |  |  |  | 2.4481e-07 | 47.5096
118948270 | F | LC | ETL.4392.TOWR | 41129185 | LAKEVLLE | SONOMA | 2020-04-24 | 2020-05-11 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Tower | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129185 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2020-04-16 | Glass | Dead End |  |  |  |  | 0.015336 | 3637.895
118948270 | F | LC | ETL.4392.TOWR | 41129185 | LAKEVLLE | SONOMA | 2020-04-24 | 2020-05-11 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Tower | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129185 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1973-01-01 | Porcelain | Dead End |  |  |  |  | 0.015336 | 3637.895
118956666 | E | LC | ETL.1402.POLE.WOOD | 44549849 | VICTOR | STOCKTON | 2020-04-28 | 2021-05-18 | ETL.1402 | SPRING GAP TAP | Structure-Wood | Rotten | [Replace, Completed] | Tier3 |  |  | COMP
118964671 | F | LC | ETL.1330.TOWR | 40808529 | LAKEVLLE | HUMBOLDT | 2020-04-24 | 2021-04-01 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40808529 | 1972-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2020-07-23 | Glass Silicone Coated | Dead End |  |  |  |  | 0.0039632 | 5438.4172
118964671 | F | LC | ETL.1330.TOWR | 40808529 | LAKEVLLE | HUMBOLDT | 2020-04-24 | 2021-04-01 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40808529 | 1972-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1972-01-01 | Ceramic | Dead End |  |  |  |  | 0.0039632 | 5438.4172
118975684 | F | LC | ETL.2660.POLE.NWOD | 40862236 | SACTO | SIERRA | 2020-04-30 |  | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40862236 | 1967-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Ceramic | Suspension |  |  |  |  | 1.502e-09 | 142.5076
118975684 | F | LC | ETL.2660.POLE.NWOD | 40862236 | SACTO | SIERRA | 2020-04-30 |  | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40862236 | 1967-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Porcelain | Suspension |  |  |  |  | 1.502e-09 | 142.5076
118978598 | E | LC | ETL.4393.INSL.CERA | 40883864 | SACTO | SACRAMENTO | 2020-05-04 | 2021-01-21 | ETL.4393 | DRUM-HIGGINS | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
118981597 | E | LC | ETL.1330.TOWR | 40808931 | LAKEVLLE | HUMBOLDT | 2020-04-24 | 2021-04-01 | ETL.1330 | CORTINA-MENDOCINO #1 | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40808931 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.0044213 | 5596.7471
118993010 | E | LC | ETL.8650.TOWR | 40859318 | FRESNO | YOSEMITE | 2020-05-01 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40859318 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-11-18 | Glass | Double Dead End - Suspension |  |  |  |  | 0.020961 | 4433.5317
119000451 | E | LC | ETL.2730.INSL | 40775598 | CONCORD | EAST BAY | 2020-05-01 | 2021-06-16 | ETL.2730 | MORAGA-OAKLAND #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119004836 | E | LC | ETL.4620.INSL | 40611912 | PISMOBCH | LOS PADRES | 2020-05-06 | 2021-06-17 | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587104 | 1971-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-06-02 | Glass | Double Dead End |  |  |  |  | 5.1296e-10 | 2247.7324
119004836 | E | LC | ETL.4620.INSL | 40611912 | PISMOBCH | LOS PADRES | 2020-05-06 | 2021-06-17 | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587104 | 1971-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.1296e-10 | 2247.7324
119014267 | F | LC | ETL.1890.TOWR | 40863764 | FRESNO | FRESNO | 2020-05-11 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Structure-Steel | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40863764 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1986-01-01 | Porcelain | Suspension |  |  |  |  | 7.9278e-07 | 5936.0293
119033676 | E | LC | ETL.1240.POLE.WOOD | 44386012 | TABLEMTN | NORTH VALLEY | 2020-05-13 | 2020-06-09 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44386012 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | Double Dead End |  |  |  |  | 3.1812e-05 | 8495.9658
119037071 | F | LC | ETL.4050.POLE.STPS | 44660829 | LAKEVLLE | SONOMA | 2020-05-07 | 2020-11-10 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44660733 | 2018-09-30 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 8.1841e-09 | 4040.4441
119040195 | F | LC | ETL.5354.TOWR | 41152670 | CONCORD | DIABLO | 2020-05-18 |  | ETL.5354 | TESLA-NEWARK #2 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 41152670 | 1930-01-01 | LATTICE STEEL TOWER | Unknown | 2004-01-01 | Non Ceramic | Other |  |  |  |  | 2.8446e-05 | 3295.094 | 0.093732
119059712 | F | LC | ETL.4220.POLE.WOOD | 40585897 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-06-23 | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585897 | 1962-01-01 | Single Wood Pole | T-1 - Tri Post | 1962-01-01 | Ceramic | Post |  |  |  |  | 0.006536 | 4086.2002
119062524 | F | LC | ETL.1240.POLE.STPS | 44200917 | TABLEMTN | NORTH VALLEY | 2020-05-18 | 2020-07-13 | ETL.1240 | CASCADE-COTTONWOOD | Marker (i.e. signs)-Steel | Missing | [Install, Completed] |  | Tier 2 | Within Both | COMP | 44200916 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.4234e-09 | 3783.1921
119081489 | F | LC | ETL.1600.TOWR | 40656848 | LAKEVLLE | SONOMA | 2020-05-27 | 2021-04-08 | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40656848 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 1.7125e-05 | 95.0507
119081489 | F | LC | ETL.1600.TOWR | 40656848 | LAKEVLLE | SONOMA | 2020-05-27 | 2021-04-08 | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40656848 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-10-27 | Glass | Suspension |  |  |  |  | 1.7125e-05 | 95.0507
119104428 | F | LC | ETL.1110.POLE.WDPS | 44424496 | TABLEMTN | HUMBOLDT | 2020-05-19 | 2021-07-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424495 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00084562 | 4066.2923
119111425 | E | LC | ETL.2540.POLE.WDPS | 44401551 | MOSSLNDG | CENTRAL COAST | 2020-05-20 | 2021-01-27 | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44401549 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.002431 | 474.5354
119111967 | E | LC | ETL.8290.POLE.WOOD | 40577284 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2020-12-08 | ETL.8290 | VOLTA-DESCHUTES | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40577284 |  | Single Wood Pole | DDE-A - Double Dead End Angle | 2021-04-21 | Glass | Dead End |  |  |  |  | 0.0026845 | 367.404
119112739 | E | LC | ETL.1880.TOWR | 40807000 | FRESNO | FRESNO | 2020-06-05 |  | ETL.1880 | KERCKHOFF #1-KERCKHOFF #2 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40807000 | 1940-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2002-01-01 | Polymer | Dead End |  |  |  |  | 5.8678e-07 | 4069.8035 | 0.0023881
119112739 | E | LC | ETL.1880.TOWR | 40807000 | FRESNO | FRESNO | 2020-06-05 |  | ETL.1880 | KERCKHOFF #1-KERCKHOFF #2 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40807000 | 1940-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | [5 empty] | 5.8678e-07 | 4069.8035 | 0.0023881
119115034 | F | LC | ETL.2540.POLE.NWOD | 40822517 | MOSSLNDG | SAN JOSE | 2020-05-20 | 2021-08-09 | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822517 |  | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2021-08-01 | Glass | Double Dead End |  |  |  |  | 0.00078394 | 47.5295
119118761 | F | LC | ETL.8290.POLE.WOOD | 40867836 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-02-08 | ETL.8290 | VOLTA-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40867836 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.0009602 | 2249.2227
119123236 | B | LC | ETL.1050.TOWR | 40652364 | FRESNO | FRESNO | 2020-06-08 | 2020-12-14 | ETL.1050 | BALCH-SANGER | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40652364 | 1969-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1969-01-01 | Porcelain | Dead End |  |  |  |  | 0.00059883 | 7774.5303
119125825 | E | LC | ETL.6280.POLE.WOOD | 40769460 | TABLEMTN | NORTH VALLEY | 2020-06-03 |  | ETL.6280 | CARIBOU #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40769460 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 4.8742e-06 | 174.0445 | 0.00084832
119142602 | E | LC | ETL.6220.POLE.WOOD | 40810943 | EUREKA | HUMBOLDT | 2020-06-05 | 2021-01-25 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40810943 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.084481
119148357 | E | LC | ETL.6470.POLE.WOOD | 40602520 | SACTO | SIERRA | 2020-06-10 | 2021-07-27 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119149449 | E | LC | ETL.7140.POLE.WOOD | 40750697 | LAKEVLLE | NORTH BAY | 2020-06-11 | 2020-07-03 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
119174982 | F | LC | ETL.6480.POLE.WOOD | 40866900 | SACTO | NORTH VALLEY | 2020-06-15 | 2020-11-12 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40866900 |  | Single Wood Pole | T-1 - Tri Post | 2021-06-12 | Polymer | Post |  |  |  |  | 0.057106 | 253.2625
119176369 | E | LC | ETL.7180.POLE.WDPS | 44360928 | LAKEVLLE | NORTH BAY | 2020-06-12 | 2021-04-22 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44360928 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 0.00012364
119176369 | E | LC | ETL.7180.POLE.WDPS | 44360928 | LAKEVLLE | NORTH BAY | 2020-06-12 | 2021-04-22 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44360928 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 0.00012364
119176840 | F | LC | ETL.6280.POLE.WOOD | 40815838 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40815838 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Other |  |  |  |  | 4.4307e-05 | 126.5956
119179322 | F | LC | ETL.6280.POLE.WOOD | 40824627 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40824627 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00013392 | 6679.6816
119180185 | E | LC | ETL.2720.TOWR | 40805690 | CONCORD | DIABLO | 2020-06-17 | 2021-03-04 | ETL.2720 | MORAGA-OAKLAND #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805690 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-03 | Polymer | Suspension |  |  |  |  | 6.1461e-05 | 0.065158
119180185 | E | LC | ETL.2720.TOWR | 40805690 | CONCORD | DIABLO | 2020-06-17 | 2021-03-04 | ETL.2720 | MORAGA-OAKLAND #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805690 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-01 | Polymer | Suspension |  |  |  |  | 6.1461e-05 | 0.065158
119180427 | E | LC | ETL.7300.POLE.WOOD | 40817230 | TABLEMTN |  | 2020-06-16 | 2021-03-18 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
119180958 | E | LC | ETL.8253.POLE.WOOD | 40745286 | VICTOR | STOCKTON | 2020-06-17 | 2020-09-28 | ETL.8253 | IONE TAP | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40745286 | 1987-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-05-02 | Glass | Double Dead End |  |  |  |  | 8.7431e-05 | 1143.8286
119185140 | F | LC | ETL.5660.TOWR | 40594312 | CONCORD | MISSION | 2020-06-18 | 2021-02-03 | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594312 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 5.0915e-06 | 2727.2507
119185915 | F | LC | ETL.5100.TOWR | 40863082 | MOSSLNDG | SAN JOSE | 2020-06-18 | 2021-02-01 | ETL.5100 | METCALF-MOSS LANDING #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40863082 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2005-01-01 | Non Ceramic | Suspension |  |  |  |  | 4.6473e-06 | 996.8166
119196158 | E | LC | ETL.6470.POLE.WOOD | 40817357 | SACTO | SIERRA | 2020-06-22 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.036916 | 79.2067
119196504 | F | LC | ETL.6470.POLE.WOOD | 40598572 | SACTO | SIERRA | 2020-06-19 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40598572 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.088008 | 221.6184
119198033 | F | LC | ETL.6470.POLE.WOOD | 40766725 | SACTO | SIERRA | 2020-06-19 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40766725 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.03655 | 79.2067
119207627 | E | LC | ETL.4220.POLE.WOOD | 42568016 | TABLEMTN | NORTH VALLEY | 2020-06-24 | 2020-08-27 | ETL.4220 | WOODLEAF-PALERMO | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 |  |  | CNCL
119233866 | F | LC | ETL.8060.POLE.WOOD | 40771538 | SACTO | SIERRA | 2020-06-29 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771538 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.21835 | 617.0731
119236596 | E | LC | ETL.6880.POLE.WOOD | 40588847 | LAKEVLLE | SONOMA | 2020-06-30 | 2021-08-04 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
119238574 | E | LC | ETL.7140.POLE.WOOD | 40588059 | LAKEVLLE | SONOMA | 2020-06-30 | 2021-05-24 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119294709 | F | LC | ETL.6900.POLE.WOOD | 40876021 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 40876021 | 1932-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 3.4951e-05 | 395.7669
119294728 | F | LC | ETL.8170.POLE.WOOD | 40861537 | EUREKA | HUMBOLDT | 2020-07-01 |  | ETL.8170 | TRINITY-MAPLE CREEK | Animal Guard-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40861537 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.05248 | 17.4631 | 0.91646
119295183 | E | LC | ETL.7030.POLE.WOOD | 40667991 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-06-15 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | DLFL | 40667991 |  | Single Wood Pole | T2N | 2020-06-17 | Polymer | Post |  |  |  |  | 0.0029918
119295400 | F | LC | ETL.7300.POLE.NWOD | 44810004 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44810004 | 2019-05-20 | Light Duty Steel Pole | T2N | 2019-05-20 | Polymer | Post |  |  |  |  | 1.0128e-06 | 635.0785
119299716 | E | LC | ETL.7270.POLE.NWOD | 44649299 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-07-28 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44649299 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.00023965 | 205.7693
119300301 | E | LC | ETL.8060.POLE.WOOD | 40618241 | SACTO | SIERRA | 2020-06-29 | 2021-08-30 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.059897 | 617.0731
119300622 | E | LC | ETL.6950.POLE.WOOD | 44437420 | SACTO | SACRAMENTO | 2020-07-02 | 2021-10-11 | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44437420 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End - Suspension |  |  |  |  | 0.0016478 | 1593.2229 | 2.6253
119302370 | E | LC | ETL.6760.POLE.WOOD | 40756220 | SACTO | SACRAMENTO | 2020-07-02 | 2021-03-22 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119303168 | E | LC | ETL.6380.POLE.WOOD | 40615187 | LAKEVLLE | SONOMA | 2020-07-02 | 2021-05-11 | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40615187 |  | Single Wood Pole | T2N | 2018-09-29 | Polymer | Post |  |  |  |  | 4.9312e-05 | 5952.5078
119303343 | E | LC | ETL.7300.POLE.WOOD | 40826839 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-04-26 | ETL.7300 | KILARC-DESCHUTES | Vegetation | Overgrown | [Trim, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826839 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00052354 | 5813.5391
119304433 | E | LC | ETL.7270.POLE.NWOD | 44649373 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-07-28 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44649373 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.00030014 | 126.6494
119309311 | F | LC | ETL.6980.POLE.WOOD | 40820182 | LAKEVLLE | SONOMA | 2020-07-03 |  | ETL.6980 | FORT ROSS-GUALALA | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40820182 | 1984-01-01 | Single Wood Pole | TPSR - Tri Post & Susp Light | 2010-01-01 | Polymer | Other |  |  |  |  | 0.46849 | 23.8246 | 11.1617
119309365 | F | LC | ETL.6290.POLE | 40675186 | TABLEMTN | NORTH VALLEY | 2020-07-02 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 40675186 | 1962-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1962-01-01 | Porcelain | Dead End |  |  |  |  | 0.15201 | 5538.7192
119315431 | F | LC | ETL.7560.POLE.WOOD | 40611406 | SACTO | SACRAMENTO | 2020-07-06 | 2021-02-23 | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40611406 |  | Single Wood Pole | T2N | 2019-08-19 | Polymer | Post |  |  |  |  | 0.041613 | 212.0395
119325740 | E | LC | ETL.6650.POLE.WDPS | 44386833 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44386831 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0095839 | 491.2338 | 4.7079
119325956 | F | LC | ETL.6280.POLE.NWOD | 40600559 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-01-20 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40600559 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 0.00018934 | 5538.7192
119330251 | E | LC | ETL.5960.TOWR | 40605011 | PISMOBCH | LOS PADRES | 2020-07-08 | 2021-05-10 | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40605011 | 1973-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1973-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.038e-08 | 3611.3252
119341030 | E | LC | ETL.6890.POLE.WOOD | 40677898 | LAKEVLLE | SONOMA | 2020-07-09 | 2021-10-21 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.0058614 | 981.3776 | 5.7522
119341231 | F | LC | ETL.6290.POLE.WOOD | 44168158 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44168158 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.026359 | 304.2946
119350429 | F | LC | ETL.7980.POLE.NWOD | 44991377 | SACTO | SIERRA | 2020-07-07 |  | ETL.7980 | SMARTVILLE-MARYSVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44991377 | 2020-08-18 | Light Duty Steel Pole | T-1 - Tri Post | 2020-08-18 | Polymer | Post |  |  |  |  | 0.0016128 | 2710.6582
119353293 | B | LC | ETL.1250.INSL.CERA | 44319380 | FRESNO | FRESNO | 2020-07-10 | 2020-10-12 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40582955 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2015-03-03 | Ceramic | Suspension |  |  |  |  | 3.2043e-07 | 5176.9556
119353293 | B | LC | ETL.1250.INSL.CERA | 44319380 | FRESNO | FRESNO | 2020-07-10 | 2020-10-12 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40582955 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2002-01-01 | Porcelain | Suspension |  |  |  |  | 3.2043e-07 | 5176.9556
119357102 | B | LC | ETL.7030.POLE.WOOD | 40616829 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2020-09-29 | ETL.7030 | HAT CREEK #1-WESTWOOD | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40616829 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0092222 | 1981.2402
119363185 | F | LC | ETL.1110.POLE.WDPS | 44424112 | TABLEMTN | HUMBOLDT | 2020-07-13 | 2021-07-06 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424111 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012407 | 3898.5583
119367961 | E | LC | ETL.1110.POLE.WDPS | 44232660 | TABLEMTN | HUMBOLDT | 2020-07-14 | 2021-04-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44232659 | 2014-10-28 | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.0012206 | 3154.0374
119368283 | E | LC | ETL.7490.POLE.STPS | 44324523 | EUREKA | HUMBOLDT | 2020-07-13 | 2021-10-06 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44324520 | 2016-08-03 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.19927 | 118.8456 | 23.6824
119371786 | E | LC | ETL.5980.INSL | 40724334 | PISMOBCH | LOS PADRES | 2020-07-14 | 2021-05-20 | ETL.5980 | DIABLO-MIDWAY #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119380928 | F | LC | ETL.8960.POLE.WOOD | 40588550 | FRESNO | FRESNO | 2020-07-16 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40588550 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 2.4417e-05
119473067 | F | LC | ETL.7160.POLE.WOOD | 44871177 | LAKEVLLE | NORTH BAY | 2020-07-20 |  | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871177 | 2019-09-19 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2019-09-19 | Glass | Dead End |  |  |  |  | 0.23317 | 743.3749
119478092 | E | LC | ETL.1430.INSL | 40889172 | SACTO | SACRAMENTO | 2020-07-20 | 2021-04-06 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119480437 | F | LC | ETL.8960.POLE.WOOD | 40596616 | FRESNO | FRESNO | 2020-07-21 | 2021-04-20 | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40596616 |  | Single Wood Pole | WB - Wishbone | 1974-01-01 | Porcelain | Dead End |  |  |  |  | 0.00014565
119547622 | B | LC | ETL.7140.POLE.WOOD | 40588047 | LAKEVLLE | SONOMA | 2020-07-31 | 2020-11-18 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40588047 |  | Single Wood Pole | TPS1D - Tri Post & Susp DDE 115 KV |  | Ceramic | Double Dead End |  |  |  |  | 0.012567 | 984.3435
119556897 | B | LC | ETL.8170.POLE.WOOD | 40701832 | EUREKA | HUMBOLDT | 2020-08-03 | 2021-09-21 | ETL.8170 | TRINITY-MAPLE CREEK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40701832 |  | Single Wood Pole | T-1 - Tri Post | 2021-08-17 | Polymer | Post |  |  |  |  | 0.044883 | 822.5129
119566929 | E | LC | ETL.6300.POLE.WOOD | 40862089 | TABLEMTN |  | 2020-08-05 |  | ETL.6300 | CARIBOU-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40862089 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Pin |  |  |  |  | 2.8391e-05 | 3036.7952 | 0.086218
119608825 | B | LC | ETL.8650.TOWR | 40646339 | FRESNO | FRESNO | 2020-08-13 | 2020-12-08 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40646339 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-11-18 | Glass | Suspension |  |  |  |  | 0.016587 | 6723.7635
119615565 | E | LC | ETL.1401.POLE.WDPS | 44390887 | VICTOR | STOCKTON | 2020-08-14 | 2021-03-17 | ETL.1401 | BEARDSLEY TAP | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] |  | Tier 3 | Within Both | COMP | 44390886 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0003764 | 1497.7366
119623120 | E | LC | ETL.7490.POLE.WOOD | 40602064 | EUREKA | HUMBOLDT | 2020-08-16 | 2021-09-27 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602064 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-09-10 | Glass | Post |  |  |  |  | 0.01276 | 47.5141
119637434 | F | LC | ETL.6310.POLE.WOOD | 40657165 | TABLEMTN | NORTH VALLEY | 2020-08-19 | 2021-04-07 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40657165 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.1364e-05 | 5196.2129
119645072 | F | LC | ETL.1330.TOWR | 40750585 | LAKEVLLE | SONOMA | 2020-08-20 |  | ETL.1330 | CORTINA-MENDOCINO #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40750585 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 4.2446e-05 | 7721.1523
119657676 | E | LC | ETL.1420.TOWR | 40871371 | SACTO | SACRAMENTO | 2020-08-22 | 2021-02-16 | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40871371 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm | 2016-08-08 | Polymer | Post |  |  |  |  | 5.3062e-06 | 63.348
119665345 | A | LC | ETL.5091.INSL | 41122477 | MOSSLNDG | CENTRAL COAST | 2020-08-24 | 2020-08-26 | ETL.5091 | METCALF-MONTA VISTA #3 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40862880 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0025847 | 15.8866
119667658 | E | LC | ETL.1450.POLE.WDPS | 44558954 | SACTO | SACRAMENTO | 2020-08-24 | 2021-10-12 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] |  | Tier 2 | Within Both | COMP | 44558463 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0019214 | 1260.556
119709541 | E | LC | ETL.6710.POLE.WOOD | 40824143 | MOSSLNDG | CENTRAL COAST | 2020-08-31 |  | ETL.6710 | DEL MONTE-VIEJO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40824143 |  | Single Wood Pole | SVDE - Single Vertical Dead End |  | Ceramic | [5 empty] | 0.24565 | 0.065148 | 0.016003
119720800 | A | LC | ETL.6240.POLE.STPS | 44802707 | MOSSLNDG | CENTRAL COAST | 2020-09-05 | 2020-10-22 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 44802690 | 2019-05-27 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.090299 | 253.1024
119722809 | E | LC | ETL.7140.POLE.WOOD | 40668093 | LAKEVLLE | NORTH BAY | 2020-08-06 | 2021-05-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119781050 | E | LC | ETL.7390.POLE.WDPS | 44412039 | LAKEVLLE |  | 2020-09-11 | 2021-03-03 | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44412036 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.12177
119788541 | E | LC | ETL.8365.POLE.NWOD | 40906598 | EUREKA | HUMBOLDT | 2020-09-16 | 2021-03-24 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906598 | 2010-01-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 0.0017684
119825194 | F | LC | ETL.8580.TOWR | 40748092 | FRESNO | FRESNO | 2020-09-28 | 2021-02-09 | ETL.8580 | COALINGA #1-SAN MIGUEL | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40748092 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.001059
119851420 | F | LC | ETL.6300.POLE.WOOD | 40815702 | TABLEMTN |  | 2020-09-17 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40815702 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 6.4523e-07 | 0.065148
119851973 | F | LC | ETL.2790.TOWR | 40857658 | CONCORD | DIABLO | 2020-09-18 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40857658 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 1.9481e-07 | 31.6978 | 6.175e-06
119851973 | F | LC | ETL.2790.TOWR | 40857658 | CONCORD | DIABLO | 2020-09-18 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40857658 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 1.9481e-07 | 31.6978 | 6.175e-06
119937179 | A | LC | ETL.7810.POLE.WOOD | 40750296 | LAKEVLLE | SONOMA | 2020-10-22 | 2020-10-27 | ETL.7810 | POTTER VALLEY-MENDOCINO | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750296 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2017-04-03 | Ceramic | Dead End |  |  |  |  | 0.00022091 | 1028.2683
119942887 | E | LC | ETL.1350.POLE.WOOD | 42611947 | TABLEMTN | NORTH VALLEY | 2020-10-23 | 2021-08-22 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.017385 | 519.5952
120011414 | E | LC | ETL.6020.TOWR | 40740258 | TABLEMTN | NORTH VALLEY | 2020-11-06 | 2021-07-26 | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40740258 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.0062913 | 427.2444
120050202 | F | LC | ETL.6480.POLE.WOOD | 40693129 | SACTO | NORTH VALLEY | 2020-11-13 | 2021-06-04 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
120133346 | F | LC | ETL.3020.TOWR | 40745980 | CONCORD | MISSION | 2020-10-22 | 2021-03-22 | ETL.3020 | NEWARK-JARVIS #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40745980 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.2954e-08 | 95.4016
120133346 | F | LC | ETL.3020.TOWR | 40745980 | CONCORD | MISSION | 2020-10-22 | 2021-03-22 | ETL.3020 | NEWARK-JARVIS #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40745980 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-11-03 | Ceramic | Dead End |  |  |  |  | 2.2954e-08 | 95.4016
120204557 | E | LC | ETL.7030.POLE.WOOD | 40757927 | TABLEMTN | NORTH VALLEY | 2020-12-15 | 2021-06-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40757927 |  | Single Wood Pole | T2N | 2021-05-05 | Polymer | Post |  |  |  |  | 0.0032239 | 6268.4326
120229640 | F | LC | ETL.6280.POLE.NWOD | 45020850 | TABLEMTN | NORTH VALLEY | 2020-11-19 | 2021-09-15 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45020850 | 2018-11-07 | Light Duty Steel Pole | DDE - Double Dead End | 2018-11-07 | Ceramic | Dead End |  |  |  |  | 2.0134e-07 | 1581.6954
120604032 | E | LC | ETL.5800.INSL | 40789159 | LAKEVLLE | NORTH BAY | 2021-03-04 |  | ETL.5800 | TULUCAY-VACA | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40663082 | 1956-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 2.4919e-09 | 6174.2476 | 1.5386e-05
120681991 | F | LC | ETL.7380.POLE.WDPS | 44562661 | MOSSLNDG | CENTRAL COAST | 2021-03-23 |  | ETL.7380 | LAURELES-OTTER | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44562332 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.19456 | 31.6978
120688946 | E | LC | ETL.4870.TOWR | 40869053 | FRESNO | FRESNO | 2021-03-24 |  | ETL.4870 | HELMS-GREGG #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40869053 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.1472e-08 | 5730.5 | 0.00035226
120696574 | B | LC | ETL.3830.INSL | 40703060 | VICTOR | STOCKTON | 2021-03-26 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40642849 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.9529e-05 | 5336.0039
120704982 | B | LC | ETL.3830.TOWR | 40596299 | VICTOR | STOCKTON | 2021-03-26 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40596299 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.6254e-05 | 5967.0518
120718408 | F | LC | ETL.2900.TOWR | 40662258 | MOSSLNDG | CENTRAL COAST | 2021-03-31 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40662258 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0011156 | 906.4992 | 1.0113
120726299 | F | LC | ETL.2540.POLE.WOOD | 40809602 | MOSSLNDG | CENTRAL COAST | 2021-04-01 |  | ETL.2540 | METCALF-GREEN VALLEY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40809602 | 1952-01-01 | Single Wood Pole | T-1 - Tri Post | 1952-01-01 | Ceramic | Post |  |  |  |  | 0.038646 | 158.2797
120746052 | F | LC | ETL.8365.POLE.WOOD | 44141973 | EUREKA | HUMBOLDT | 2021-04-05 | 2021-06-10 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44141973 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Dead End |  |  |  |  | 0.031219 | 2151.1467
120747457 | B | LC | ETL.3840.INSL.CERA | 40771610 | VICTOR | STOCKTON | 2021-04-05 | 2021-05-20 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40744463 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 5.0878e-06 | 3195.5342
120748886 | F | LC | ETL.7140.POLE.NWOD | 45017303 | LAKEVLLE | SONOMA | 2021-04-06 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45017303 | 2020-06-21 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-06-21 | Glass | Suspension |  |  |  |  | 0.00031505 | 1552.1321
120804864 | E | LC | ETL.6900.INSL.NCER | 44944265 | LAKEVLLE | SONOMA | 2021-04-13 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44944250 | 2020-07-21 | Single Wood Pole | T-1 - Tri Post | 2020-07-21 | Polymer | Post |  |  |  |  | 2.0451e-06 | 1789.3021 | 0.0036593
120808169 | F | LC | ETL.5463.TOWR | 40746312 | CONCORD | DIABLO | 2021-04-13 |  | ETL.5463 | PITTSBURG-SAN MATEO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40746312 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 9.7162e-08 | 3154.5959
120845857 | B | LC | ETL.1073.POLE.WDPS | 44774773 | VICTOR | STOCKTON | 2021-04-19 | 2021-07-26 | ETL.1073 | MI-WUK-CURTIS | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120847537 | F | LC | ETL.1400.POLE.WDPS | 44986666 | VICTOR | STOCKTON | 2021-04-19 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40856833 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.0071474 | 63.3763
120850238 | E | LC | ETL.3820.TOWR | 40642816 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40642816 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2015-08-16 | Polymer | Post |  |  |  |  | 1.81e-08 | 1728.9346 | 3.1293e-05
120850238 | E | LC | ETL.3820.TOWR | 40642816 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40642816 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2015-10-16 | Polymer | Post |  |  |  |  | 1.81e-08 | 1728.9346 | 3.1293e-05
120851364 | E | LC | ETL.8060.POLE.WOOD | 40593597 | SACTO | SACRAMENTO | 2021-04-20 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40593597 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Polymer | [5 empty] | 0.098351 | 0.24228
120859852 | F | LC | ETL.4440.TOWR | 40809497 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40809497 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 1.189e-06 | 3420.8628 | 0.0040674
120866590 | E | LC | ETL.1220.INSL | 40844050 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.1220 | CAMP EVERS-PAUL SWEET | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40816121 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-04-23 | Glass | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147 | 4.5491e-09
120866590 | E | LC | ETL.1220.INSL | 40844050 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.1220 | CAMP EVERS-PAUL SWEET | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40816121 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147 | 4.5491e-09
120866699 | B | LC | ETL.3830.INSL.NCER | 44942011 | VICTOR | STOCKTON | 2021-04-06 | 2021-05-26 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40856450 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-12 | Glass | Suspension |  |  |  |  | 4.2589e-07 | 4716.1616
120893444 | E | LC | ETL.3840.INSL.NCER | 40630092 | VICTOR | STOCKTON | 2021-04-27 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40589041 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 6.2635e-05 | 0.077799 | 4.873e-06
120912100 | F | LC | ETL.8060.POLE.WOOD | 44145235 | SACTO | SACRAMENTO | 2021-05-01 |  | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44145235 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0033733 | 0.065152
120923234 | E | LC | ETL.8650.POLE.NWOD | 44420156 | FRESNO | YOSEMITE | 2021-04-14 |  | ETL.8650 | EXCHEQUER-INDIAN FLAT | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44420156 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0056224 | 207.8215 | 1.1685
120931441 | B | LC | ETL.4550.TOWR | 40750979 | TABLEMTN | NORTH VALLEY | 2021-05-04 | 2021-06-16 | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750979 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.3508e-06 | 5070.043
120945307 | E | LC | ETL.6890.POLE.WOOD | 40759956 | LAKEVLLE | SONOMA | 2021-05-06 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40759956 | 1990-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.0031481 | 2314.6917 | 7.2869
120946270 | E | LC | ETL.4870.TOWR | 40576600 | FRESNO | FRESNO | 2021-05-06 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576600 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.00057664 | 31.6978 | 0.018278
121188330 | F | LC | ETL.1810.POLE.WDPS | 44322610 | EUREKA | HUMBOLDT | 2021-05-10 | 2021-07-06 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44322609 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.02339 | 142.4559
121188906 | F | LC | ETL.6500.POLE.WOOD | 40610852 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40610852 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | Pin |  |  |  |  | 0.0012226 | 602.0115
121322432 | E | LC | ETL.6470.POLE.WOOD | 40905844 | SACTO | SACRAMENTO | 2021-05-12 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40905844 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.10967 | 110.8608 | 12.1578
121370286 | F | LC | ETL.1250.POLE.NWOD | 40859547 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40859547 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.6483e-07 | 4175.8375
121373350 | E | LC | ETL.5640.POLE.WDPS | 45082082 | TABLEMTN | NORTH VALLEY | 2021-05-21 | 2021-06-09 | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 45082069 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0026847 | 2847.8424
121376442 | E | LC | ETL.3700.POLE.WOOD | 40659119 | PISMOBCH | LOS PADRES | 2021-05-06 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40659119 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Porcelain | Post |  |  |  |  | 0.00031063 | 3263.2344 | 1.0137
121384769 | E | LC | ETL.6520.POLE.WOOD | 44964276 | SACTO | SIERRA | 2021-05-12 | 2021-06-24 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44964276 | 2020-08-08 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-08-08 | Glass | Dead End |  |  |  |  | 0.0031504 | 5004.7632
121393519 | E | LC | ETL.5640.TOWR | 40597493 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40597493 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 4.6543e-09 | 4262.7344 | 1.984e-05
121404533 | A | LC | ETL.4040.SWIT | 42682159 | TABLEMTN | NORTH VALLEY | 2021-05-26 | 2021-06-01 | ETL.4040 | TRINITY-COTTONWOOD | Emergency | Storm Related | [Repair, Completed] | Tier3 |  |  | COMP | [10 empty] | Manual
121405356 | F | LC | ETL.6640.POLE.WOOD | 44761236 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44761236 | 2019-03-16 | Single Wood Pole | T-1 - Tri Post | 2019-03-16 | Polymer | Post |  |  |  |  | 0.0010056 | 7591.7544
121407883 | F | LC | ETL.6430.POLE.WOOD | 40615792 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6430 | COLEMAN-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40615792 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0021299 | 4017.4044
121418208 | F | LC | ETL.1400.POLE.WDPS | 44770782 | VICTOR | STOCKTON | 2021-05-26 | 2021-09-28 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40803711 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0078569 | 31.7207
121420206 | F | LC | ETL.1430.TOWR | 40655121 | SACTO | SIERRA | 2021-05-26 |  | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40655121 | 1913-01-01 | LATTICE STEEL TOWER | Unknown | 2016-11-14 | Non Ceramic | Post |  |  |  |  | 0.008427 | 142.4516 | 1.2004
121422372 | F | LC | ETL.7040.POLE.WOOD | 40674166 | TABLEMTN | NORTH VALLEY | 2021-05-24 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40674166 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.032475 | 3531.9717
121422744 | F | LC | ETL.1420.TOWR | 40587526 | SACTO | SIERRA | 2021-05-26 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40587526 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-03 | Glass | Suspension |  |  |  |  | 7.7421e-06 | 142.4516 | 0.0011029
121428400 | E | LC | ETL.1400.POLE.WDPS | 44770793 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40744847 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0096467 | 965.199 | 9.311
121428525 | F | LC | ETL.1400.POLE.STPS | 44239779 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44239778 | 2016-03-22 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.5288e-05 | 2246.7366
121436336 | E | LC | ETL.1450.POLE.WDPS | 44553754 | SACTO | SACRAMENTO | 2021-06-01 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553189 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0023818 | 174.093 | 0.41465
121450263 | E | LC | ETL.1440.POLE.WOOD | 40762382 | SACTO | SACRAMENTO | 2021-05-10 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40762382 | 1956-01-01 | Single Wood Pole | 3P DV - 3 Pole Double Vertical | 1956-01-01 | Ceramic | Dead End |  |  |  |  | 0.01816 | 99.9029 | 1.8142
121450376 | B | LC | ETL.6020.TOWR | 41162595 | TABLEMTN | NORTH VALLEY | 2021-06-01 | 2021-06-14 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41162595 | 1965-01-01 | LATTICE STEEL TOWER | Unknown | [7 empty] | 4.6399e-09 | 1380.2244
121475564 | E | LC | ETL.6110.TOWR | 40664335 | METCALF | SAN JOSE | 2021-05-28 | 2021-08-10 | ETL.6110 | TESLA-METCALF | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40664335 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 7.7106e-09 | 3470.1958
121484596 | E | LC | ETL.1350.POLE.WDPS | 44552322 | TABLEMTN |  | 2021-05-28 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44551517 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.016196 | 3256.1765 | 52.7371
121492162 | B | LC | ETL.1820.INSL.NCER | 44844549 | EUREKA | HUMBOLDT | 2021-06-08 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44837597 |  | LATTICE STEEL TOWER | Unknown |  | Unknown | Unknown |  |  |  |  | 0.19941 | 2009.6299 | 400.7469
121493254 | E | LC | ETL.6979.POLE.WOOD | 40825465 | LAKEVLLE | SONOMA | 2021-06-01 |  | ETL.6979 | MONTE RIO-FORT ROSS | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40825465 | 1984-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.11332 | 1551.3604 | 175.8046
121498082 | E | LC | ETL.6852.POLE.NWOD | 44667819 | LAKEVLLE | SONOMA | 2021-06-09 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44667819 | 2018-11-01 | Light Duty Steel Pole | T2N | 2018-11-01 | Polymer | Post |  |  |  |  | 0.0046773 | 6506.4966 | 30.4326
121518442 | F | LC | ETL.6330.POLE.NWOD | 44673308 | TABLEMTN | NORTH VALLEY | 2021-06-04 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44673308 | 2018-11-17 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-17 | Polymer | Post |  |  |  |  | 1.5213e-06 | 1502.9633
121518611 | E | LC | ETL.4950.INSL | 41130057 | LAKEVLLE |  | 2021-06-03 |  | ETL.4950 | FULTON-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40593051 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.0090983 | 1327.7751 | 12.0805
121518892 | E | LC | ETL.1440.POLE.WDPS | 44162099 | SACTO | SACRAMENTO | 2021-06-04 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44162097 | 2013-09-22 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00075906 | 205.7724 | 0.15619
121523383 | B | LC | ETL.8365.INSL.NCER | 44460328 | EUREKA | HUMBOLDT | 2021-06-10 | 2021-06-22 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44459765 | 2016-01-15 | Tubular Steel Pole | DDE-A - Double Dead End Angle |  | Polymer | Dead End |  |  |  |  | 8.9375e-05 | 412.5736
121526396 | E | LC | ETL.1720.POLE.WDPS | 44401038 | MOSSLNDG | CENTRAL COAST | 2021-06-08 | 2021-10-04 | ETL.1720 | GREEN VALLEY-LLAGAS | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44401037 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00010468 | 316.4942 | 0.03313
121536601 | F | LC | ETL.1440.POLE.WDPS | 44762531 | SACTO | SACRAMENTO | 2021-06-08 | 2021-07-06 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
121544172 | E | LC | ETL.7990.POLE.WOOD | 40905873 | SACTO | SIERRA | 2021-06-12 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40905873 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | [5 empty] | 8.3525e-05 | 3276.345 | 0.27366
121550571 | F | LC | ETL.5960.TOWR | 40873355 | PISMOBCH | LOS PADRES | 2021-06-16 |  | ETL.5960 | DIABLO-GATES #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40873355 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 1.4226e-07 | 2373.7322 | 0.00033768
121551098 | E | LC | ETL.1450.INSL | 40606811 | SACTO | SIERRA | 2021-06-12 |  | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40582705 | 1948-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 1948-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010888 | 31.7066 | 0.034524
121551098 | E | LC | ETL.1450.INSL | 40606811 | SACTO | SIERRA | 2021-06-12 |  | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40582705 | 1948-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 1948-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010888 | 31.7066 | 0.034524
121555181 | F | LC | ETL.6750.POLE.WDPS | 44562160 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44561592 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.015918 | 174.1138
121568432 | E | LC | ETL.2395.INSL.NCER | 40854307 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.2395 | GRIZZLY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550856 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.0057803
121568432 | E | LC | ETL.2395.INSL.NCER | 40854307 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.2395 | GRIZZLY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550856 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.0057803
121568995 | F | LC | ETL.7560.POLE.NWOD | 45070112 | SACTO | SIERRA | 2021-06-15 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45070112 | 2021-03-30 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-30 | Polymer | Post |  |  |  |  | 0.14153 | 2768.4309
121586118 | F | LC | ETL.6500.POLE.NWOD | 45099316 | SACTO | NORTH VALLEY | 2021-06-12 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45099316 | 2020-08-08 | Light Duty Steel Pole | T-1 - Tri Post | 2020-08-08 | Polymer | Post |  |  |  |  | 0.0015733 | 2013.7876
121589355 | F | LC | ETL.8423.POLE.NWOD | 40594116 | MOSSLNDG | CENTRAL COAST | 2021-06-23 |  | ETL.8423 | SALINAS-FORT ORD #2 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40594116 |  | Lattice Steel Pole | DCPOST - Double Circuit Post | 2021-06-04 | Polymer | Post |  |  |  |  | 5.4914e-07 | 0.065148
121589355 | F | LC | ETL.8423.POLE.NWOD | 40594116 | MOSSLNDG | CENTRAL COAST | 2021-06-23 |  | ETL.8423 | SALINAS-FORT ORD #2 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40594116 |  | Lattice Steel Pole | DCPOST - Double Circuit Post |  | Porcelain | [5 empty] | 5.4914e-07 | 0.065148
121607944 | E | LC | ETL.1530.TOWR | 40817559 | SACTO | SIERRA | 2021-06-23 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40817559 | 1980-01-01 | LATTICE STEEL TOWER | Unknown | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 7.877e-08 | 743.5351 | 5.8568e-05
121608681 | E | LC | ETL.6050.TOWR | 40762127 | MOSSLNDG | SAN JOSE | 2021-06-17 |  | ETL.6050 | MOSS LANDING-METCALF | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40762127 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 4.8338e-10 | 1178.8911 | 5.6986e-07
121628381 | F | LC | ETL.6510.POLE.WDPS | 44399441 | SACTO | SACRAMENTO | 2021-06-29 |  | ETL.6510 | COLGATE-SMARTVILLE #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44399440 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0006726 | 269.2076
121639862 | F | LC | ETL.8170.POLE.WOOD | 40604691 | EUREKA | HUMBOLDT | 2021-06-23 | 2021-09-14 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40604691 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.051003 | 6475.8594
121653522 | E | LC | ETL.7212.POLE.WOOD | 40865026 | METCALF | PENINSULA | 2021-06-27 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40865026 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2019-11-14 | Glass | Suspension |  |  |  |  | 0.083643 | 506.7344 | 42.3845
121679562 | E | LC | ETL.9240.TOWR | 43249577 | PISMOBCH | LOS PADRES | 2021-07-07 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249577 |  | LATTICE STEEL TOWER | [9 empty] | 285.5604
121689448 | E | LC | ETL.6750.POLE.WDPS | 44374915 | TABLEMTN |  | 2021-07-06 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44374914 | 2012-08-04 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 2.5737e-05 | 23.8011 | 0.00061257
121690645 | B | LC | ETL.6750.INSL.CERA | 43703469 | TABLEMTN | NORTH VALLEY | 2021-07-09 | 2021-08-12 | ETL.6750 | DELTA-MTN GATE JCT | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44214438 | 2016-10-18 | 2-Pole Wood | 2PS - 2 Pole SUSP | 2016-10-18 | Ceramic | Suspension |  |  |  |  | 0.0077513
121690645 | B | LC | ETL.6750.INSL.CERA | 43703469 | TABLEMTN | NORTH VALLEY | 2021-07-09 | 2021-08-12 | ETL.6750 | DELTA-MTN GATE JCT | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44214438 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 2016-10-18 | Ceramic | Suspension |  |  |  |  | 0.0077513
121715810 | B | LC | ETL.1820.INSL.NCER | 44845773 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44562350 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2019-09-12 | Glass | Suspension |  |  |  |  | 0.043602
121715810 | B | LC | ETL.1820.INSL.NCER | 44845773 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44562350 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2019-09-12 | Glass | Suspension |  |  |  |  | 0.043602
121715810 | B | LC | ETL.1820.INSL.NCER | 44845773 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44562350 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2019-09-12 | Glass | Suspension |  |  |  |  | 0.043602
121722149 | E | LC | ETL.7640.POLE.WDPS | 44565618 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44564237 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 0.00041278 | 506.6299 | 0.20912
121725058 | E | LC | ETL.1400.POLE.WDPS | 45087051 | VICTOR | YOSEMITE | 2021-07-07 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40744839 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00080083 | 1848.0461 | 1.48
121725400 | F | LC | ETL.4040.POLE.STPS | 44646920 | TABLEMTN | NORTH VALLEY | 2021-07-08 | 2021-07-26 | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44646920 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | 2018-08-17 | Ceramic | Double Dead End |  |  |  |  | 0.00010378
121725400 | F | LC | ETL.4040.POLE.STPS | 44646920 | TABLEMTN | NORTH VALLEY | 2021-07-08 | 2021-07-26 | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44646920 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | 2018-08-17 | Ceramic | Double Dead End |  |  |  |  | 0.00010378
121730234 | F | LC | ETL.1820.POLE.STPS | 44395240 | EUREKA | HUMBOLDT | 2021-06-17 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395239 | 2020-03-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00080558 | 395.5107
121730234 | F | LC | ETL.1820.POLE.STPS | 44395240 | EUREKA | HUMBOLDT | 2021-06-17 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395239 | 2020-03-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00080558 | 395.5107
121732297 | E | LC | ETL.4392.INSL.NCER | 44189789 | LAKEVLLE |  | 2021-06-12 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44192005 |  | Tubular Steel Pole | SV-PJ-90 - Single Vertical Post Jumper 90 |  | Polymer | Dead End |  |  |  |  | 0.0012263 | 886.3674 | 1.087
121732297 | E | LC | ETL.4392.INSL.NCER | 44189789 | LAKEVLLE |  | 2021-06-12 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44192005 |  | Tubular Steel Pole | SV-PJ-90 - Single Vertical Post Jumper 90 |  | Polymer | Dead End |  |  |  |  | 0.0012263 | 886.3674 | 1.087
121742023 | B | LC | ETL.6880.POLE.WOOD | 40827217 | LAKEVLLE | SONOMA | 2021-07-16 | 2021-07-27 | ETL.6880 | FULTON-CALISTOGA | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827217 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Porcelain | [5 empty] | 3.7362e-06 | 356.6019
121742242 | F | LC | ETL.1420.TOWR | 40756197 | SACTO | SIERRA | 2021-07-13 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40756197 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 7.8585e-05 | 2942.8272 | 0.23126
121742263 | E | LC | ETL.1820.POLE.STPS | 44395324 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395321 | 2020-03-09 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0010597 | 189.9226 | 0.20126
121785297 | E | LC | ETL.7380.INSL.NCER | 44974714 | MOSSLNDG | CENTRAL COAST | 2021-07-21 | 2021-08-10 | ETL.7380 | LAURELES-OTTER | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44974704 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.52941 | 15.8815
121794251 | B | LC | ETL.6280.POLE.WOOD | 40876632 | TABLEMTN | NORTH VALLEY | 2021-07-25 | 2021-10-14 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40876632 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 8.7139e-06 | 63.3304
121802010 | B | LC | ETL.1402.POLE.NWOD | 45099344 | VICTOR | YOSEMITE | 2021-07-26 | 2021-08-18 | ETL.1402 | SPRING GAP TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 45099344 | 2021-05-13 | Light Duty Steel Pole | DV - Double Vertical | 2021-05-13 | Glass | Dead End |  |  |  |  | 0.0010315 | 2765.7156
121815914 | E | LC | ETL.7140.POLE.WOOD | 40576059 | LAKEVLLE | NORTH BAY | 2021-07-29 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | PEND | 40576059 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.01403 | 41.1971 | 0.57799
121822280 | E | LC | ETL.6760.POLE.WOOD | 44178366 | SACTO | SIERRA | 2021-07-29 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44178366 | 2015-03-25 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2015-03-25 | Porcelain | Dead End |  |  |  |  | 0.033774 | 1.647 | 0.055626
121856898 | E | LC | ETL.6880.POLE.NWOD | 44947418 | LAKEVLLE | SONOMA | 2021-08-06 |  | ETL.6880 | FULTON-CALISTOGA | Anchor-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44947418 | 2020-05-12 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-12 | Glass | Dead End |  |  |  |  | 6.0505e-08 | 0.065152 | 3.942e-09
121905795 | B | LC | ETL.2420.POLE.STPS | 44923817 | LAKEVLLE | SONOMA | 2021-08-16 | 2021-09-27 | ETL.2420 | MENDOCINO-UKIAH | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44923817 | 2020-04-25 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-04-25 | Glass | Suspension |  |  |  |  | 1.3571e-06
121905795 | B | LC | ETL.2420.POLE.STPS | 44923817 | LAKEVLLE | SONOMA | 2021-08-16 | 2021-09-27 | ETL.2420 | MENDOCINO-UKIAH | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44923817 | 2020-04-25 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-04-25 | Glass | Suspension |  |  |  |  | 1.3571e-06
122018166 | E | LC | ETL.6300.POLE.WOOD | 40768930 | TABLEMTN | NORTH VALLEY | 2021-09-09 | 2021-11-18 | ETL.6300 | CARIBOU-WESTWOOD | Guy Wire-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768930 |  | Single Wood Pole | TH - TriAngle Post 70 | 2014-11-07 | Non Ceramic | Post |  |  |  |  | 0.00015988 | 0.065148
122018166 | E | LC | ETL.6300.POLE.WOOD | 40768930 | TABLEMTN | NORTH VALLEY | 2021-09-09 | 2021-11-18 | ETL.6300 | CARIBOU-WESTWOOD | Guy Wire-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768930 |  | Single Wood Pole | TH - TriAngle Post 70 | 2014-11-07 | Non Ceramic | Post |  |  |  |  | 0.00015988 | 0.065148
122216743 | B | LC | ETL.1810.INSL.NCER | 40629576 | EUREKA | HUMBOLDT | 2021-10-16 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | PEND
118396181 | E | LC | ETL.2170.TOWR | 40597221 | SACTO | SACRAMENTO | 2020-01-06 | 2020-04-13 | ETL.2170 | MADISON-VACA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40597221 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-04-30 | Glass | Suspension |  |  |  |  | 4.411e-08 | 6221.8149
118423705 | E | LC | ETL.1240.POLE.WDPS | 44386064 | TABLEMTN | NORTH VALLEY | 2020-01-11 | 2020-04-24 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118473480 | E | LC | ETL.7490.POLE.WOOD | 40591321 | EUREKA | HUMBOLDT | 2020-01-27 | 2020-05-11 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118595958 | B | LC | ETL.2270.INSL.CERA | 44737529 | CONCORD | EAST BAY | 2020-03-02 | 2020-05-21 | ETL.2270 | MARTINEZ-SOBRANTE | Animal Guard-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40745842 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.695e-06 | 16.3369
118595958 | B | LC | ETL.2270.INSL.CERA | 44737529 | CONCORD | EAST BAY | 2020-03-02 | 2020-05-21 | ETL.2270 | MARTINEZ-SOBRANTE | Animal Guard-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40745842 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1941-01-01 | Ceramic | Suspension |  |  |  |  | 2.695e-06 | 16.3369
118681789 | A | LC | ETL.7160.TOWR | 44340984 | LAKEVLLE | SONOMA | 2020-03-11 | 2020-03-19 | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44340984 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 0.31154 | 174.0409
118747616 | E | LC | ETL.1420.TOWR | 40871293 | SACTO | SACRAMENTO | 2020-03-26 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40871293 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.00084023 | 1845.9058 | 1.551
118747616 | E | LC | ETL.1420.TOWR | 40871293 | SACTO | SACRAMENTO | 2020-03-26 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40871293 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-01 | Glass | Suspension |  |  |  |  | 0.00084023 | 1845.9058 | 1.551
118912313 | E | LC | ETL.4590.TOWR | 40910173 | TABLEMTN | NORTH VALLEY | 2020-04-11 | 2020-06-23 | ETL.4590 | CRESTA-RIO OSO | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910173 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.5278e-07 | 126.625
118926141 | F | LC | ETL.1720.POLE.WDPS | 44985733 | MOSSLNDG | CENTRAL COAST | 2020-04-15 | 2021-09-29 | ETL.1720 | GREEN VALLEY-LLAGAS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42567598 | 1948-01-01 | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.0012434 | 1234.1384
118926761 | E | LC | ETL.7212.POLE.WDPS | 44384387 | METCALF | SAN JOSE | 2020-04-13 | 2021-05-18 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44384387 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 2021-05-06 | Glass | Dead End |  |  |  |  | 0.31987
118926761 | E | LC | ETL.7212.POLE.WDPS | 44384387 | METCALF | SAN JOSE | 2020-04-13 | 2021-05-18 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44384387 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 2021-05-06 | Glass | Dead End |  |  |  |  | 0.31987
118949762 | F | LC | ETL.4750.TOWR | 40664073 | LAKEVLLE | SONOMA | 2020-04-26 | 2021-04-15 | ETL.4750 | GEYSERS #12-FULTON | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40664073 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 2.2694e-07 | 2200.2283
118957189 | E | LC | ETL.6980.POLE.WOOD | 40808290 | LAKEVLLE | SONOMA | 2020-04-27 | 2021-07-10 | ETL.6980 | FORT ROSS-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118957442 | E | LC | ETL.1330.TOWR | 40657040 | LAKEVLLE | HUMBOLDT | 2020-04-23 | 2021-07-12 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | Missing | [Install, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40657040 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 0.00092778 | 6301.0049
118957442 | E | LC | ETL.1330.TOWR | 40657040 | LAKEVLLE | HUMBOLDT | 2020-04-23 | 2021-07-12 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | Missing | [Install, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40657040 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.00092778 | 6301.0049
118980506 | E | LC | ETL.6980.POLE.WOOD | 40821470 | LAKEVLLE | SONOMA | 2020-04-24 | 2021-01-14 | ETL.6980 | FORT ROSS-GUALALA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40821470 | 1969-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 1969-01-01 | Polymer | Suspension |  |  |  |  | 0.18417 | 792.0737
118981599 | E | LC | ETL.2410.INSL | 40835508 | LAKEVLLE |  | 2020-04-24 | 2021-03-03 | ETL.2410 | MENDOCINO-REDBUD | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40808931 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.0044213 | 5596.7471
119004620 | E | LC | ETL.8480.POLE.WOOD | 40819611 | PISMOBCH | LOS PADRES | 2020-05-06 | 2021-02-17 | ETL.8480 | ATASCADERO-CAYUCOS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40819611 | 1954-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2020-05-15 | Glass | Suspension - Post |  |  |  |  | 0.0024027 | 695.9683
119005037 | F | LC | ETL.4220.POLE.STPS | 44388406 | TABLEMTN |  | 2020-05-06 | 2020-06-01 | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Steel | Missing | [Install, Completed] |  | Tier 3 | Within Both | COMP | 44388405 | 2017-09-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.2188e-05 | 174.0849
119029326 | B | LC | ETL.8405.POLE.WOOD | 40874900 | SACTO | SACRAMENTO | 2020-05-14 | 2020-08-05 | ETL.8405 | MIDDLE FORK #1 | Guy Wire-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40874900 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0031317 | 2610.7236
119047976 | E | LC | ETL.5140.POLE.WDPS | 44551678 | SACTO | SIERRA | 2020-05-20 | 2020-06-02 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119059237 | F | LC | ETL.6440.POLE.WOOD | 40760275 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-06-15 | ETL.6440 | COLEMAN-RED BLUFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760275 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0046335 | 4800.9653
119059949 | B | LC | ETL.6760.POLE.NWOD | 40867759 | SACTO | SACRAMENTO | 2020-05-22 | 2020-06-01 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Switch | Out of Adjustment | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40867759 | 2011-01-01 | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 0.00056772 | 31.7022
119068460 | F | LC | ETL.7510.POLE.WOOD | 40600972 | LAKEVLLE | HUMBOLDT | 2020-05-26 | 2020-06-22 | ETL.7510 | MENDOCINO-HARTLEY | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600972 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 7.8493e-05 | 2977.4116
119082767 | B | LC | ETL.7380.POLE.WOOD | 40876411 | MOSSLNDG | CENTRAL COAST | 2020-05-29 | 2020-08-25 | ETL.7380 | LAURELES-OTTER | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40876411 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.65979 | 31.6978
119094684 | F | LC | ETL.5250.TOWR | 40813796 | CONCORD | MISSION | 2020-05-27 | 2021-03-29 | ETL.5250 | MORAGA-CASTRO VALLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40813796 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 1.9502e-07 | 237.3762
119102568 | F | LC | ETL.6720.POLE.WDPS | 44984426 | TABLEMTN | NORTH VALLEY | 2020-05-28 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 42578805 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0041322 | 0.065151
119115588 | E | LC | ETL.6470.POLE.WOOD | 40822600 | SACTO | SIERRA | 2020-06-01 | 2021-08-03 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822600 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.19115 | 522.076
119118207 | F | LC | ETL.6470.POLE.WOOD | 40875293 | SACTO | SIERRA | 2020-05-29 | 2021-02-10 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL | [12 empty] | 2784.1987
119118266 | F | LC | ETL.6470.POLE.WOOD | 40767346 | SACTO | SIERRA | 2020-05-29 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40767346 |  | Single Wood Pole | T2N | 2021-07-19 | Polymer | Post |  |  |  |  | 0.0073189 | 221.5243
119119470 | F | LC | ETL.7560.POLE.WOOD | 42568924 | SACTO | SIERRA | 2020-06-01 | 2021-08-17 | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119119972 | E | LC | ETL.7300.POLE.WOOD | 40817199 | TABLEMTN |  | 2020-06-03 | 2021-03-22 | ETL.7300 | KILARC-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817199 |  | Single Wood Pole | T2N | 2021-03-11 | Polymer | Post |  |  |  |  | 0.01287 | 601.6622
119127506 | F | LC | ETL.7380.POLE.WOOD | 40771085 | MOSSLNDG | CENTRAL COAST | 2020-05-29 |  | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40771085 |  | Single Wood Pole | FIG4W - Wood X Arm |  | Ceramic | [5 empty] | 0.35692 | 31.6978
119158796 | E | LC | ETL.8170.POLE.WOOD | 40605815 | EUREKA | HUMBOLDT | 2020-06-02 | 2021-06-16 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40605815 |  | Single Wood Pole | 3P DDE - 3 Pole Double Dead End |  | Ceramic | [5 empty] | 0.061156 | 4621.6372
119163091 | F | LC | ETL.6750.POLE.NWOD | 44922913 | TABLEMTN | NORTH VALLEY | 2020-06-13 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 44922913 | 2020-05-28 | Light Duty Steel Pole | T-1 - Tri Post | 2020-05-28 | Polymer | Post |  |  |  |  | 9.2796e-07 | 221.5655 | 0.0002056
119166020 | E | LC | ETL.8300.POLE.WOOD | 40770138 | TABLEMTN | NORTH VALLEY | 2020-06-11 | 2021-08-23 | ETL.8300 | VOLTA-SOUTH | Structure-Wood | Rotten | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770138 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0079086 | 3802.1997
119176169 | F | LC | ETL.8170.POLE.WDPS | 44565515 | EUREKA | HUMBOLDT | 2020-06-12 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564267 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.028949 | 158.2408
119179616 | F | LC | ETL.6280.POLE.WOOD | 40600611 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600611 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 5.0942e-05 | 6679.6816
119185962 | F | LC | ETL.2790.TOWR | 40745893 | CONCORD | DIABLO | 2020-04-07 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40745893 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.9518e-07 | 474.9144 | 9.2694e-05
119194892 | B | LC | ETL.6470.POLE.WOOD | 40760731 | SACTO | SIERRA | 2020-06-22 | 2020-07-02 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760731 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.08614 | 142.5149
119198875 | F | LC | ETL.3530.TOWR | 40658779 | PISMOBCH | LOS PADRES | 2020-06-22 | 2021-02-04 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40658779 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 1.9052e-07 | 2785.3594
119198875 | F | LC | ETL.3530.TOWR | 40658779 | PISMOBCH | LOS PADRES | 2020-06-22 | 2021-02-04 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40658779 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2016-07-13 | Glass | Suspension |  |  |  |  | 1.9052e-07 | 2785.3594
119199320 | E | LC | ETL.6470.INSL.CERA | 40625292 | SACTO | SACRAMENTO | 2020-06-23 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119200208 | F | LC | ETL.6280.POLE.WOOD | 40664902 | TABLEMTN | NORTH VALLEY | 2020-06-22 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40664902 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Other |  |  |  |  | 1.5074e-05 | 632.7172
119201119 | E | LC | ETL.1370.POLE.WOOD | 40702312 | PISMOBCH | LOS PADRES | 2020-06-23 | 2021-08-19 | ETL.1370 | DIVIDE-CABRILLO #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40702312 | 1960-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 1988-01-01 | Porcelain | Suspension |  |  |  |  | 0.019568 | 1237.4922
119201175 | F | LC | ETL.6470.POLE.WOOD | 40869667 | SACTO | SIERRA | 2020-06-23 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40869667 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.063644 | 158.2723
119220587 | E | LC | ETL.7270.POLE.NWOD | 45014843 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2021-09-01 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45014843 | 2020-06-26 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-02-26 | Glass | Dead End |  |  |  |  | 0.0011781 | 1076.101
119232424 | E | LC | ETL.8170.POLE.WOOD | 40617873 | EUREKA | HUMBOLDT | 2020-06-29 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40617873 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.002483 | 2704.6782 | 6.7158
119295903 | F | LC | ETL.4393.POLE.WDPS | 44172277 | SACTO | SACRAMENTO | 2020-06-30 | 2021-02-11 | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
119301955 | E | LC | ETL.7140.POLE.WOOD | 40860973 | LAKEVLLE | SONOMA | 2020-07-02 | 2021-08-30 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Rotten | [Replace, Completed, Completed] | Tier3 |  |  | COMP | [12 empty] | 728.338
119301990 | E | LC | ETL.7140.POLE.WOOD | 40588050 | LAKEVLLE | SONOMA | 2020-07-02 | 2021-05-07 | ETL.7140 | IGNACIO-BOLINAS #1 | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40588050 |  | Single Wood Pole | DV - Double Vertical | 2021-06-08 | Glass | Dead End |  |  |  |  | 0.88927 | 728.338
119302801 | F | LC | ETL.8170.POLE.WDPS | 44771073 | EUREKA | HUMBOLDT | 2020-07-01 | 2021-04-14 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40752192 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.016313 | 142.4582
119303128 | E | LC | ETL.7780.POLE.WOOD | 40614237 | LAKEVLLE | SONOMA | 2020-07-02 | 2021-04-26 | ETL.7780 | PHILO JCT-ELK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119317260 | E | LC | ETL.8170.POLE.WOOD | 40906460 | EUREKA | HUMBOLDT | 2020-07-06 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40906460 |  | Single Wood Pole | T-1 - Tri Post | 2019-11-20 | Polymer | Post |  |  |  |  | 0.029289 | 664.5661 | 19.4642
119323638 | F | LC | ETL.1470.POLE.WOOD | 41176315 | LAKEVLLE | SONOMA | 2020-07-07 |  | ETL.1470 | EAGLE ROCK-CORTINA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41176315 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Polymer | Post |  |  |  |  | 0.0055269 | 0.065149
119326905 | E | LC | ETL.6870.POLE.WOOD | 40751836 | SACTO | SACRAMENTO | 2020-07-07 | 2020-12-02 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40751836 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.068254 | 0.065152
119332259 | B | LC | ETL.3960.TOWR | 40861814 | PISMOBCH | LOS PADRES | 2020-07-08 | 2020-12-16 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40861814 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-04-10 | Glass | Suspension |  |  |  |  | 6.4042e-05 | 79.1593
119334728 | E | LC | ETL.6760.POLE.WOOD | 40664665 | SACTO | SACRAMENTO | 2020-07-08 | 2021-03-24 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119338766 | E | LC | ETL.6861.POLE.STPS | 44679459 | LAKEVLLE | HUMBOLDT | 2020-07-09 | 2021-08-17 | ETL.6861 | KONOCTI-EAGLE ROCK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44679443 | 2018-10-25 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00011326 | 3532.2563
119350126 | F | LC | ETL.6300.POLE.WOOD | 40698922 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40698922 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0035876 | 63.3304
119356404 | E | LC | ETL.1480.TOWR | 40812430 | LAKEVLLE | SONOMA | 2020-07-10 | 2020-09-14 | ETL.1480 | EAGLE ROCK-REDBUD | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40812430 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 0.015321 | 2358.4949
119357169 | E | LC | ETL.1430.TOWR | 40871467 | SACTO | SACRAMENTO | 2020-07-10 | 2021-03-01 | ETL.1430 | DRUM-RIO OSO #2 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40871467 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical | 1990-01-01 | Ceramic | Post |  |  |  |  | 0.0035313 | 490.5074
119357668 | F | LC | ETL.7560.POLE.NWOD | 44662501 | SACTO | SIERRA | 2020-07-08 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44662501 | 2018-09-29 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-09-29 | Polymer | Dead End - Suspension |  |  |  |  | 0.0069035 | 3116.3115
119358107 | F | LC | ETL.8170.POLE.WOOD | 40809961 | EUREKA | HUMBOLDT | 2020-07-10 | 2021-09-13 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.004435
119359551 | E | LC | ETL.7030.POLE.WOOD | 40667942 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-06-23 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40667942 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.018262 | 142.4317
119374044 | E | LC | ETL.1440.POLE.WDPS | 44837678 | SACTO | SACRAMENTO | 2020-07-13 | 2021-08-09 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40618783 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0030716 | 31.7066
119403697 | F | LC | ETL.6222.POLE.WOOD | 40667645 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6222 | FORT SEWARD TAP | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40667645 | 1952-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0061393
119461744 | F | LC | ETL.8170.POLE.WOOD | 40871013 | EUREKA | HUMBOLDT | 2020-07-16 | 2021-08-17 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL | [11 empty] | 0.0092084 | 6300.0015
119467298 | E | LC | ETL.6222.POLE.WOOD | 40700552 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6222 | FORT SEWARD TAP | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40700552 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0092799
119471075 | F | LC | ETL.6290.POLE.WOOD | 40876656 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-02-11 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40876656 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.048073 | 3621.9985
119474758 | F | LC | ETL.8960.POLE.WDPS | 44236938 | FRESNO | FRESNO | 2020-07-20 | 2021-04-20 | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44236936 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 6.8261e-05
119480829 | E | LC | ETL.2790.INSL | 40623971 | CONCORD | EAST BAY | 2020-07-21 | 2021-06-01 | ETL.2790 | MORAGA-SAN LEANDRO #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119493156 | E | LC | ETL.1110.POLE.WDPS | 44424085 | TABLEMTN | HUMBOLDT | 2020-07-22 | 2021-04-06 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424084 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014805 | 3848.7012
119509423 | F | LC | ETL.1110.POLE.WDPS | 44424445 | TABLEMTN | HUMBOLDT | 2020-07-23 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
119538269 | E | LC | ETL.7380.POLE.WDPS | 44562890 | MOSSLNDG | CENTRAL COAST | 2020-07-31 | 2021-04-05 | ETL.7380 | LAURELES-OTTER | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44562404 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.86278 | 15.8815
119549488 | F | LC | ETL.6380.POLE.WOOD | 40860830 | LAKEVLLE | HUMBOLDT | 2020-07-31 | 2021-04-12 | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860830 |  | Single Wood Pole | T2N | 2018-09-29 | Polymer | Post |  |  |  |  | 6.8048e-05 | 4718.7593
119570069 | E | LC | ETL.6880.POLE.WOOD | 40905741 | LAKEVLLE | HUMBOLDT | 2020-08-06 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | CNCL | 40905741 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0040479 | 4800.3047 | 19.4309
119593106 | E | LC | ETL.7590.POLE.WOOD | 40823297 | MOSSLNDG | CENTRAL COAST | 2020-08-10 | 2021-01-12 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119607598 | F | LC | ETL.6222.POLE.WOOD | 40616324 | EUREKA | HUMBOLDT | 2020-08-12 | 2021-10-06 | ETL.6222 | FORT SEWARD TAP | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40616324 | 1952-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 1952-01-01 | Ceramic | Dead End |  |  |  |  | 0.0015368
119635791 | B | LC | ETL.6870.POLE.WOOD | 40598754 | SACTO | SIERRA | 2020-08-18 | 2020-10-06 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Tie Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40598754 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.12286 | 79.2067
119642238 | F | LC | ETL.6310.POLE.WOOD | 40650234 | TABLEMTN | NORTH VALLEY | 2020-08-20 | 2021-09-01 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 1.4897e-05 | 4198.4414
119649145 | F | LC | ETL.8365.POLE.WOOD | 40912513 | EUREKA | HUMBOLDT | 2020-08-21 | 2021-06-23 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40912513 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.081425
119649280 | F | LC | ETL.8365.POLE.NWOD | 40912526 | EUREKA | HUMBOLDT | 2020-08-21 | 2021-04-29 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912526 | 2010-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0069772
119659872 | A | LC | ETL.7590.POLE.WDPS | 44949089 | MOSSLNDG | CENTRAL COAST | 2020-08-23 | 2020-08-26 | ETL.7590 | MONTA VISTA-BURNS | Emergency-Wood | Other | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44949089 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.34141
119659872 | A | LC | ETL.7590.POLE.WDPS | 44949089 | MOSSLNDG | CENTRAL COAST | 2020-08-23 | 2020-08-26 | ETL.7590 | MONTA VISTA-BURNS | Emergency-Wood | Other | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44949089 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.34141
119659872 | A | LC | ETL.7590.POLE.WDPS | 44949089 | MOSSLNDG | CENTRAL COAST | 2020-08-23 | 2020-08-26 | ETL.7590 | MONTA VISTA-BURNS | Emergency-Wood | Other | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44949089 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.34141
119670305 | B | LC | ETL.7180.POLE.WOOD | 40588975 | LAKEVLLE | SONOMA | 2020-08-25 | 2020-10-19 | ETL.7180 | IGNACIO-BOLINAS #2 | Other | Customer Issue | [Customer Refusal] | Tier2 | Tier 2 | Within Both | COMP | 40588975 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 5.7177e-05 | 2140.7224
119695543 | B | LC | ETL.1120.INSL.CERA | 40773102 | CONCORD | EAST BAY | 2020-08-29 | 2020-11-05 | ETL.1120 | BRIGHTON-CLAYTON #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119698929 | B | LC | ETL.6280.INSL.NCER | 44667896 | TABLEMTN |  | 2020-08-31 | 2020-11-19 | ETL.6280 | CARIBOU #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119706102 | B | LC | ETL.5440.POLE.WDPS | 44557865 | TABLEMTN | NORTH VALLEY | 2020-09-02 | 2020-09-17 | ETL.5440 | PIT #6 JCT-ROUND MTN | Damper-Wood | Missing | [Install, Completed] | Tier2 |  |  | COMP
119721292 | E | LC | ETL.5920.INSL | 40774648 | CONCORD | EAST BAY | 2020-07-29 | 2021-08-31 | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119722935 | E | LC | ETL.7300.POLE.WOOD | 40770407 | TABLEMTN |  | 2020-08-06 | 2021-03-29 | ETL.7300 | KILARC-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770407 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-03-23 | Glass | Dead End |  |  |  |  | 0.00023272 | 2885.3079
119723735 | E | LC | ETL.6720.POLE.NWOD | 44324218 | TABLEMTN | NORTH VALLEY | 2020-08-05 | 2021-02-22 | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44324218 | 2015-11-03 | Fiberglass | TPD - Tri Post Dead End Construction | 2015-11-03 | Ceramic | Suspension |  |  |  |  | 1.6294e-05 | 237.4243
119730522 | A | LC | ETL.6230.POLE.WOOD | 40598510 | MOSSLNDG | CENTRAL COAST | 2020-09-09 | 2020-10-23 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40598510 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Ceramic | Post |  |  |  |  | 0.20119 | 44.3652
119763865 | E | LC | ETL.7030.POLE.WOOD | 40701325 | TABLEMTN | NORTH VALLEY | 2020-09-08 | 2021-06-22 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40701325 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.018504 | 47.5207
119764465 | B | LC | ETL.9460.POLE.WOOD | 40911400 | VICTOR | STOCKTON | 2020-09-08 | 2020-11-25 | ETL.9460 | VALLEY SPRINGS #2 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40911400 | 1991-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0025797 | 3801.7695
119781094 | E | LC | ETL.7030.POLE.WOOD | 40770765 | TABLEMTN | NORTH VALLEY | 2020-09-12 | 2021-06-23 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770765 |  | Single Wood Pole | T2N | 2021-06-17 | Polymer | Post |  |  |  |  | 0.0059805 | 0.06515
119800345 | F | LC | ETL.7180.POLE.WOOD | 40617135 | LAKEVLLE | NORTH BAY | 2020-08-06 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40617135 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | [5 empty] | 5.0105e-05 | 94.9794
119834949 | F | LC | ETL.6470.POLE.WOOD | 40664607 | SACTO | SIERRA | 2020-09-08 | 2021-06-16 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] |  | Tier 3 | Within Both | DLFL | 40664607 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.064247 | 427.3383
119877388 | E | LC | ETL.1690.TOWR | 40642738 | VICTOR | STOCKTON | 2020-10-09 |  | ETL.1690 | GOLD HILL-BELLOTA-LOCKEFORD | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Non-HFTD | Non-HFRA | PEND | 40642738 | 1917-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1917-01-01 | Ceramic | Dead End |  |  |  |  | 2.9589e-07
119896555 | E | LC | ETL.8365.POLE.NWOD | 44241872 | EUREKA | HUMBOLDT | 2020-10-12 | 2021-04-26 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44241872 | 2018-09-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-09-18 | Non Ceramic | Dead End |  |  |  |  | 0.0014066
119917480 | F | LC | ETL.8290.POLE.NWOD | 44252217 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44252217 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.00019075 | 3057.9141
119920091 | B | LC | ETL.1810.INSL.CERA | 40633948 | EUREKA | HUMBOLDT | 2020-10-16 | 2020-12-08 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40598279 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Porcelain | Suspension |  |  |  |  | 9.7335e-05
119926929 | E | LC | ETL.6220.POLE.WOOD | 40875287 | EUREKA | HUMBOLDT | 2020-10-19 | 2021-04-21 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40875287 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-10-21 | Glass | Double Dead End |  |  |  |  | 0.10359 | 839.2908
119966873 | E | LC | ETL.4316.TOWR | 40816520 | TABLEMTN | NORTH VALLEY | 2020-10-28 | 2021-06-27 | ETL.4316 | PARADISE-TABLE MTN | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816520 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Suspension |  |  |  |  | 0.00037262 | 2501.2377
119968140 | A | LC | ETL.7140.POLE.WOOD | 40809056 | LAKEVLLE | SONOMA | 2020-10-31 | 2020-11-05 | ETL.7140 | IGNACIO-BOLINAS #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809056 |  | Single Wood Pole | FIG4W - Wood X Arm | 2020-11-04 | Glass | Suspension |  |  |  |  | 0.032558 | 94.9668
119988069 | E | LC | ETL.8580.TOWR | 40765603 | FRESNO | FRESNO | 2020-11-04 | 2021-02-01 | ETL.8580 | COALINGA #1-SAN MIGUEL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40765603 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-12-12 | Glass | Suspension |  |  |  |  | 1.2851e-05
120008373 | B | LC | ETL.4870.TOWR | 40688615 | FRESNO | FRESNO | 2020-11-06 | 2021-02-03 | ETL.4870 | HELMS-GREGG #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40688615 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 5.2486e-06
120061421 | B | LC | ETL.1650.POLE.NWOD | 44784148 | LAKEVLLE | SONOMA | 2020-11-18 | 2020-11-24 | ETL.1650 | GEYSERS #3-CLOVERDALE | Other | Customer Issue | [Customer Refusal, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44784148 | 2019-06-14 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-06-14 | Polymer | Suspension |  |  |  |  | 4.4057e-09 | 4055.4705
120108821 | E | LC | ETL.6280.POLE.WOOD | 40675360 | TABLEMTN | NORTH VALLEY | 2020-11-20 |  | ETL.6280 | CARIBOU #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40675360 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00065682 | 174.0445 | 0.11432
120120911 | F | LC | ETL.7590.POLE.STPS | 44945893 | MOSSLNDG | DE ANZA | 2020-12-01 |  | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44935264 | 2020-07-20 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [8 empty] | 522.1984
120120933 | E | LC | ETL.3020.INSL.NCER | 40774137 | CONCORD | EAST BAY | 2020-11-25 |  | ETL.3020 | NEWARK-JARVIS #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40745960 | 1966-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2015-11-03 | Polymer | Dead End |  |  |  |  | 1.2353e-06 | 95.4016 | 0.00011785
120120933 | E | LC | ETL.3020.INSL.NCER | 40774137 | CONCORD | EAST BAY | 2020-11-25 |  | ETL.3020 | NEWARK-JARVIS #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40745960 | 1966-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1966-01-01 | Porcelain | Dead End |  |  |  |  | 1.2353e-06 | 95.4016 | 0.00011785
120124959 | E | LC | ETL.7590.POLE.WDPS | 44950346 | MOSSLNDG | CENTRAL COAST | 2020-11-30 | 2021-03-23 | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44949085 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.24308 | 110.8153
120659851 | B | LC | ETL.6050.TOWR | 40811996 | MOSSLNDG | CENTRAL COAST | 2021-03-18 | 2021-04-12 | ETL.6050 | MOSS LANDING-METCALF | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40811996 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 4.8259e-09 | 3024.1367
120687009 | B | LC | ETL.6330.POLE.NWOD | 40656578 | TABLEMTN | NORTH VALLEY | 2021-03-24 | 2021-06-15 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40656578 | 1998-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Non Ceramic | Post |  |  |  |  | 1.7631e-06 | 474.6646
120692955 | E | LC | ETL.5540.TOWR | 40663013 | TABLEMTN | NORTH VALLEY | 2021-03-25 |  | ETL.5540 | POE-RIO OSO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40663013 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 4.8781e-06 | 2883.9575 | 0.014068
120708868 | B | LC | ETL.3830.INSL | 40669651 | VICTOR | STOCKTON | 2021-03-26 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40642779 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 6.5152e-07 | 5033.749
120712629 | E | LC | ETL.3700.INSL.CERA | 40701118 | PISMOBCH | LOS PADRES | 2021-03-30 | 2021-11-04 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40669522 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Porcelain | Post |  |  |  |  | 2.0683e-05 | 5176.7542 | 0.10707
120740272 | F | LC | ETL.7390.POLE.WOOD | 44948577 | LAKEVLLE | SONOMA | 2021-04-03 |  | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44948577 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Unknown | Suspension |  |  |  |  | 0.1032
120747459 | E | LC | ETL.3820.TOWR | 40744463 | VICTOR | STOCKTON | 2021-04-05 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40744463 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 5.0878e-06 | 3195.5342 | 0.016258
120747851 | B | LC | ETL.3830.TOWR | 40594247 | VICTOR | STOCKTON | 2021-04-05 | 2021-05-26 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40594247 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 6.5313e-07 | 47.5096
120751410 | E | LC | ETL.1350.POLE.STPS | 44993134 | TABLEMTN | NORTH VALLEY | 2021-04-06 | 2021-06-30 | ETL.1350 | CRAG VIEW-CASCADE | Anchor-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993115 | 2020-06-04 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00010615 | 34.8723
120763457 | E | LC | ETL.6870.POLE.WOOD | 44190886 | SACTO | SACRAMENTO | 2021-04-08 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44190886 |  | Single Wood Pole | Unknown | [7 empty] | 0.042419 | 142.4895 | 6.0442
120763590 | E | LC | ETL.4392.INSL.NCER | 41117762 | LAKEVLLE | SONOMA | 2021-04-08 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40770880 | 1999-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 4.87e-05 | 4672.6953 | 0.22756
120764966 | E | LC | ETL.6870.POLE.WOOD | 40664815 | SACTO | SIERRA | 2021-04-08 | 2021-04-15 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40664815 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.11972 | 332.3381
120771009 | E | LC | ETL.9250.POLE.WOOD | 40586214 | MIDWAY | KERN | 2021-04-09 | 2021-08-14 | ETL.9250 | TEJON-LEBEC | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586214 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | [5 empty] | 0.017912 | 4976.3872
120787977 | B | LC | ETL.8250.POLE.WOOD | 44399682 | VICTOR | STOCKTON | 2021-04-10 | 2021-06-01 | ETL.8250 | CLAY-MARTEL | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44399682 | 2015-10-09 | Single Wood Pole | T-1 - Tri Post | 2015-10-09 | Polymer | Post |  |  |  |  | 0.00020902 | 1318.29
120794804 | F | LC | ETL.3830.TOWR | 40861800 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40861800 | 1989-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 3.7342e-05 | 5823.2505 | 0.21745
120804750 | E | LC | ETL.7140.POLE.WOOD | 40876293 | LAKEVLLE | SONOMA | 2021-04-13 | 2021-09-14 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40876293 |  | Single Wood Pole | FIG4W - Wood X Arm |  | Ceramic | Other |  |  |  |  | 0.032785 | 47.5223
120804789 | E | LC | ETL.1430.TOWR | 40746580 | SACTO | SACRAMENTO | 2021-04-13 |  | ETL.1430 | DRUM-RIO OSO #2 | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier3 | Tier 3 | Within Both | PEND | 40746580 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2016-11-14 | Ceramic | Suspension |  |  |  |  | 0.0010538 | 15.9216 | 0.016778
120808257 | E | LC | ETL.7590.POLE.WDPS | 44965629 | MOSSLNDG | SAN JOSE | 2021-04-13 |  | ETL.7590 | MONTA VISTA-BURNS | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42565758 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.44389 | 126.6368 | 56.2132
120812646 | E | LC | ETL.5090.INSL | 40782449 | MOSSLNDG | CENTRAL COAST | 2021-04-08 |  | ETL.5090 | MONTA VISTA-COYOTE SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40753103 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0071317 | 316.4942 | 2.2572
120826846 | B | LC | ETL.6880.POLE.NWOD | 45071349 | LAKEVLLE | SONOMA | 2021-04-16 | 2021-05-04 | ETL.6880 | FULTON-CALISTOGA | Other | Customer Issue | [Access Issue] | Tier3 | Tier 3 | Within Both | COMP | 45071349 | 2020-03-05 | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 2020-03-05 | Glass | Suspension |  |  |  |  | 6.0354e-05 | 142.516
120831739 | F | LC | ETL.3820.TOWR | 40579640 | VICTOR | STOCKTON | 2021-04-16 | 2021-05-17 | ETL.3820 | STANISLAUS-MANTECA #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40579640 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.6366e-06 | 253.1151
120839935 | F | LC | ETL.3830.POLE.NWOD | 44737518 | VICTOR | STOCKTON | 2021-04-09 | 2021-08-12 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44737518 |  | Tubular Steel Pole | SS1 - Susp. Steel Single. CIR | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.2488e-08 | 4716.1616
120861236 | E | LC | ETL.5490.INSL | 40604988 | CONCORD | EAST BAY | 2021-04-21 |  | ETL.5490 | PITTSBURG-SAN RAMON | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40581143 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0027336 | 1203.7072 | 3.2905
120861236 | E | LC | ETL.5490.INSL | 40604988 | CONCORD | EAST BAY | 2021-04-21 |  | ETL.5490 | PITTSBURG-SAN RAMON | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40581143 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 0.0027336 | 1203.7072 | 3.2905
120871984 | F | LC | ETL.3500.TOWR | 40579795 | VICTOR | STOCKTON | 2021-04-22 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40579795 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 0.00024567 | 6523.0078 | 1.6025
120874021 | E | LC | ETL.8060.POLE.WOOD | 40602260 | SACTO | SACRAMENTO | 2021-04-23 | 2021-08-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.076337 | 63.348
120883937 | E | LC | ETL.1600.INSL | 40893757 | LAKEVLLE | SONOMA | 2021-04-13 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40870153 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Dead End |  |  |  |  | 1.1124e-07 | 4468.1562 | 0.00049705
120889645 | F | LC | ETL.6470.POLE.WOOD | 40824246 | SACTO | SACRAMENTO | 2021-04-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40824246 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.018478 | 1961.6868
120899946 | E | LC | ETL.1530.TOWR | 40810211 | SACTO | SIERRA | 2021-04-27 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40810211 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00011054 | 332.3128 | 0.036732
120900818 | E | LC | ETL.3830.INSL.NCER | 40626065 | VICTOR | STOCKTON | 2021-04-13 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40599421 | 1927-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1999-01-01 | Polymer | Dead End |  |  |  |  | 4.0504e-08 | 5127.0312 | 0.00020767
120911437 | E | LC | ETL.5930.TOWR | 40872756 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40872756 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-29 | Glass | Suspension |  |  |  |  | 4.5296e-06 | 303.0547 | 0.0013727
120911437 | E | LC | ETL.5930.TOWR | 40872756 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40872756 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 4.5296e-06 | 303.0547 | 0.0013727
120912127 | E | LC | ETL.3830.INSL.NCER | 40623436 | VICTOR | STOCKTON | 2021-05-01 | 2021-05-28 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40597003 | 1927-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 7.0696e-09 | 3814.4824
120938104 | E | LC | ETL.4316.INSL.CERA | 40788736 | TABLEMTN | NORTH VALLEY | 2021-05-05 |  | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758646 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0020407
120938104 | E | LC | ETL.4316.INSL.CERA | 40788736 | TABLEMTN | NORTH VALLEY | 2021-05-05 |  | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758646 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0020407
120938104 | E | LC | ETL.4316.INSL.CERA | 40788736 | TABLEMTN | NORTH VALLEY | 2021-05-05 |  | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758646 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0020407
120944357 | E | LC | ETL.6160.SWIT | 43242955 | CONCORD | DIABLO | 2021-05-06 | 2021-09-30 | ETL.6160 | LONE TREE-CAYETANO | Switch | Out of Adjustment | [Repair, Completed] | Tier3 |  |  | COMP | [7 empty] | 2011-09-27 | SEECO | ARCING HORNS | SCADA Only
120995279 | F | LC | ETL.1810.POLE.WDPS | 44322669 | EUREKA | HUMBOLDT | 2021-05-08 | 2021-06-02 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
121190719 | E | LC | ETL.6470.INSL.NCER | 40723244 | SACTO | SACRAMENTO | 2021-05-11 |  | ETL.6470 | COLGATE-ALLEGHANY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40679414 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.012228 | 550.7998 | 6.735
121338283 | F | LC | ETL.4393.TOWR | 40865240 | SACTO | SIERRA | 2021-05-13 |  | ETL.4393 | DRUM-HIGGINS | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40865240 |  | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End |  | Porcelain | [5 empty] | 1.6245e-05 | 707.2537 | 0.011489
121348305 | E | LC | ETL.1420.TOWR | 40582451 | SACTO | SIERRA | 2021-05-15 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40582451 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-05 | Glass | Suspension |  |  |  |  | 1.2878e-05 | 142.4642 | 0.0018346
121351454 | B | LC | ETL.4392.INSL.NCER | 44388711 | LAKEVLLE | SONOMA | 2021-05-18 | 2021-06-21 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40872724 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2019-06-20 | Glass | Dead End |  |  |  |  | 0.00014014 | 110.8893
121351454 | B | LC | ETL.4392.INSL.NCER | 44388711 | LAKEVLLE | SONOMA | 2021-05-18 | 2021-06-21 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40872724 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1997-01-01 | Porcelain | Dead End |  |  |  |  | 0.00014014 | 110.8893
121359597 | E | LC | ETL.4870.TOWR | 40576891 | FRESNO | FRESNO | 2021-05-19 | 2021-07-29 | ETL.4870 | HELMS-GREGG #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40576891 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 2021-07-21 | Glass Silicone Coated | Double Dead End |  |  |  |  | 1.0799e-05 | 2957.7136
121363714 | E | LC | ETL.1250.POLE.WOOD | 40859549 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40859549 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.00015548 | 5920.3032 | 0.92046
121374873 | E | LC | ETL.4580.TOWR | 40760052 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40760052 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Porcelain | Suspension |  |  |  |  | 6.4302e-06 | 5070.043 | 0.032601
121374873 | E | LC | ETL.4580.TOWR | 40760052 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40760052 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 6.4302e-06 | 5070.043 | 0.032601
121376396 | E | LC | ETL.6040.INSL.CERA | 45098650 | MOSSLNDG | CENTRAL COAST | 2021-05-21 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40689554 | 1966-01-01 | LATTICE STEEL TOWER | SUSP-A - Suspension Angle (TWR) | 2021-05-21 | Porcelain | Double Dead End |  |  |  |  | 1.2314e-07 | 113.7675 | 1.401e-05
121381012 | F | LC | ETL.6500.POLE.WOOD | 40767113 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40767113 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00050701 | 79.1957
121382406 | F | LC | ETL.8350.POLE.NWOD | 44920055 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44920055 | 2020-01-15 | Light Duty Steel Pole | T1-1A | 2020-01-15 | Polymer | Post |  |  |  |  | 4.1695e-07 | 256.7166 | 0.00010704
121384330 | E | LC | ETL.7380.POLE.WOOD | 40827809 | MOSSLNDG | CENTRAL COAST | 2021-05-12 |  | ETL.7380 | LAURELES-OTTER | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40827809 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.59074 | 47.5141 | 28.0687
121385589 | E | LC | ETL.1480.INSL.NCER | 43218455 | LAKEVLLE |  | 2021-05-13 |  | ETL.1480 | EAGLE ROCK-REDBUD | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41115612 | 2005-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2005-01-01 | Polymer | Suspension |  |  |  |  | 0.0022473 | 2358.8699 | 5.3012
121387906 | E | LC | ETL.8170.POLE.NWOD | 44618206 | EUREKA | HUMBOLDT | 2021-05-21 |  | ETL.8170 | TRINITY-MAPLE CREEK | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44618206 | 2018-06-10 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-06-10 | Polymer | Dead End |  |  |  |  | 0.00019348 | 5842.8242 | 1.1305
121404131 | F | LC | ETL.1820.POLE.WDPS | 44765645 | EUREKA | HUMBOLDT | 2021-05-26 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40617979 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.15496 | 2425.2515 | 375.8068
121409155 | E | LC | ETL.7040.POLE.WOOD | 40867045 | TABLEMTN | NORTH VALLEY | 2021-05-24 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40867045 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.18023 | 144.7905 | 26.096
121421938 | F | LC | ETL.7000.POLE.WOOD | 40877436 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-10-04 | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40877436 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0012 | 205.6771
121424832 | F | LC | ETL.4050.POLE.WOOD | 40584965 | LAKEVLLE | SONOMA | 2021-05-27 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40584965 | 1970-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1970-01-01 | Ceramic | Post |  |  |  |  | 0.00029518 | 2089.8596 | 0.61688
121428662 | E | LC | ETL.6980.POLE.WOOD | 40587392 | LAKEVLLE | HUMBOLDT | 2021-05-21 | 2021-09-01 | ETL.6980 | FORT ROSS-GUALALA | Hardware-Wood | Missing | [Install, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587392 | 1953-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.21886 | 47.5538
121475343 | E | LC | ETL.7550.POLE.WOOD | 40875212 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40875212 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.1893e-05 | 3416.6756 | 0.040636
121475406 | E | LC | ETL.1250.POLE.WDPS | 44319508 | FRESNO | FRESNO | 2021-05-28 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44319506 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.2086e-06 | 4323.0181 | 0.031163
121481177 | E | LC | ETL.2770.INSL.NCER | 44434925 | CONCORD | EAST BAY | 2021-06-03 | 2021-09-07 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40644210 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2017-10-21 | Ceramic | Suspension |  |  |  |  | 0.00079452 | 0.065147
121492608 | E | LC | ETL.7930.POLE.WOOD | 40861936 | MOSSLNDG | CENTRAL COAST | 2021-06-01 |  | ETL.7930 | SALINAS-LAURELES | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40861936 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Double Dead End |  |  |  |  | 0.065836 | 15.8926 | 1.0463
121510617 | F | LC | ETL.6470.POLE.WOOD | 40822612 | SACTO | SIERRA | 2021-06-09 | 2021-06-23 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40822612 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.18576 | 427.3383
121511340 | E | LC | ETL.3745.TOWR | 40863265 | LAKEVLLE | NORTH BAY | 2021-06-08 |  | ETL.3745 | LAKEVILLE-IGNACIO #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40863265 | 1956-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2017-07-11 | Ceramic | Suspension |  |  |  |  | 2.0553e-05 | 94.985 | 0.0019523
121519513 | E | LC | ETL.7000.POLE.WOOD | 40816870 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40816870 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0091827 | 15.8815 | 0.14583
121533427 | F | LC | ETL.6240.POLE.WOOD | 40587847 | MOSSLNDG | CENTRAL COAST | 2021-06-09 |  | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40587847 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Polymer | [5 empty] | 0.36063 | 1028.9148
121536769 | F | LC | ETL.5390.TOWR | 40605548 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40605548 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.6596e-08 | 1871.8424
121538075 | E | LC | ETL.2390.INSL.NCER | 40772606 | VICTOR | STOCKTON | 2021-06-15 | 2021-07-26 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44391116 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 0.0013099
121538075 | E | LC | ETL.2390.INSL.NCER | 40772606 | VICTOR | STOCKTON | 2021-06-15 | 2021-07-26 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44391116 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 0.0013099
121538075 | E | LC | ETL.2390.INSL.NCER | 40772606 | VICTOR | STOCKTON | 2021-06-15 | 2021-07-26 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44391116 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 0.0013099
121547461 | F | LC | ETL.1250.POLE.NWOD | 40584905 | FRESNO | YOSEMITE | 2021-06-11 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40584905 |  | Light Duty Steel Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 8.6079e-06 | 6647.8232
121569281 | F | LC | ETL.1440.POLE.STPS | 44961398 | SACTO | SIERRA | 2021-06-15 |  | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44961226 | 2020-05-27 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.4334e-07 | 363.9416
121575309 | E | LC | ETL.1110.POLE.WDPS | 44424560 | TABLEMTN | HUMBOLDT | 2021-06-17 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44424559 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0001343 | 316.4038 | 0.042494
121586789 | E | LC | ETL.1372.POLE.STPS | 45132351 | PISMOBCH | LOS PADRES | 2021-06-23 |  | ETL.1372 | MANVILLE TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45132260 | 2021-06-24 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [8 empty] | 3578.2026
121587574 | B | LC | ETL.2760.INSL.CERA | 40895785 | CONCORD | EAST BAY | 2021-06-22 | 2021-09-08 | ETL.2760 | MORAGA-OAKLAND J | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121606443 | E | LC | ETL.6510.POLE.WDPS | 44399445 | SACTO | SACRAMENTO | 2021-06-26 |  | ETL.6510 | COLGATE-SMARTVILLE #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44399444 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00012381 | 302.3122 | 0.03743
121609458 | E | LC | ETL.6050.TOWR | 40811992 | MOSSLNDG | SAN JOSE | 2021-06-26 |  | ETL.6050 | MOSS LANDING-METCALF | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40811992 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 3.3612e-05 | 490.5807 | 0.016489
121651687 | F | LC | ETL.4040.POLE.NWOD | 44874417 | TABLEMTN | NORTH VALLEY | 2021-06-28 |  | ETL.4040 | TRINITY-COTTONWOOD | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44874417 | 2020-01-26 | Light Duty Steel Pole | 3P DDE - 3 Pole Double Dead End | 2020-01-26 | Glass | Double Dead End |  |  |  |  | 6.0541e-05 | 253.2084 | 0.01533
121658092 | F | LC | ETL.6220.POLE.WOOD | 40752604 | EUREKA | HUMBOLDT | 2021-06-29 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40752604 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.027731 | 1189.0208 | 32.9733
121682145 | E | LC | ETL.5970.INSL | 40886030 | PISMOBCH | LOS PADRES | 2021-07-07 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40863569 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 0.0001307 | 523.3949 | 0.068407
121688465 | E | LC | ETL.5420.POLE.WDPS | 44559047 | TABLEMTN | NORTH VALLEY | 2021-07-06 | 2021-07-14 | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [12 empty] | 952.427
121705249 | F | LC | ETL.1400.POLE.WDPS | 45087031 | VICTOR | YOSEMITE | 2021-07-08 | 2021-07-26 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40643733 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0010846 | 31.7334
121732471 | E | LC | ETL.2420.POLE.WDPS | 44217983 | LAKEVLLE |  | 2021-07-09 |  | ETL.2420 | MENDOCINO-UKIAH | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44217982 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.0838e-05 | 2752.4858 | 0.029832
121748613 | F | LC | ETL.1350.POLE.NWOD | 45093840 | TABLEMTN | NORTH VALLEY | 2021-07-15 | 2021-09-30 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 45093840 | 2019-05-02 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2019-05-02 | Polymer | Dead End |  |  |  |  | 5.9419e-05 | 79.1724
121750532 | B | LC | ETL.6220.INSL.CERA | 40640362 | EUREKA | HUMBOLDT | 2021-07-17 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40614565 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.6121
121766659 | B | LC | ETL.9240.POLE.WOOD | 43250299 | PISMOBCH | LOS PADRES | 2021-07-19 | 2021-07-26 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43250299 |  | Single Wood Pole | WB - Wishbone | [8 empty] | 761.3521
121781766 | E | LC | ETL.2390.INSL.NCER | 40848771 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391251 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 5.5722e-05
121781766 | E | LC | ETL.2390.INSL.NCER | 40848771 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391251 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 5.5722e-05
121818106 | B | LC | ETL.7290.INSL.NCER | 45054669 | TABLEMTN | NORTH VALLEY | 2021-07-29 | 2021-09-01 | ETL.7290 | KILARC-CEDAR CREEK | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 45054662 | 2021-02-22 | Light Duty Steel Pole | T2N | 2021-02-22 | Polymer | Post |  |  |  |  | 0.00011354 | 588.7952
121818541 | E | LC | ETL.5430.POLE.WDPS | 44562238 | TABLEMTN | NORTH VALLEY | 2021-07-29 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40759551 | 1964-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0044717 | 475.4552 | 2.1261
121824273 | E | LC | ETL.2395.POLE.WDPS | 44551471 | TABLEMTN | NORTH VALLEY | 2021-07-30 |  | ETL.2395 | GRIZZLY TAP | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550861 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0081083 | 300.6002 | 2.4374
121890421 | E | LC | ETL.4040.POLE.WDPS | 44557640 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553913 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.074947 | 1791.3177 | 134.2539
122289485 | E | LC | ETL.9340.POLE.NWOD | 45173208 | FRESNO | YOSEMITE | 2021-11-02 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45173208 | 2021-10-18 | Light Duty Steel Pole | T-1 - Tri Post | 2021-10-18 | Polymer | Post
118572297 | E | LC | ETL.7510.POLE.WDPS | 44218341 | LAKEVLLE |  | 2020-02-10 | 2020-06-16 | ETL.7510 | MENDOCINO-HARTLEY | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 44218338 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.2082e-05 | 672.7756
118606097 | E | LC | ETL.9040.POLE.WOOD | 40765674 | MIDWAY | KERN | 2020-03-04 |  | ETL.9040 | TULE-SPRINGVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40765674 |  | Single Wood Pole | T-1 - Tri Post | 2020-02-13 | Polymer | Post |  |  |  |  | 9.1143e-05 | 5145.313 | 0.46896
118701352 | E | LC | ETL.7060.POLE.WOOD | 40588879 | METCALF | SAN JOSE | 2020-03-13 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40588879 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0016889 | 458.7332 | 0.77477
118776158 | F | LC | ETL.5090.TOWR | 40862880 | MOSSLNDG | DE ANZA | 2020-04-03 | 2020-04-22 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40862880 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0025847 | 15.8866
118940825 | E | LC | ETL.7510.POLE.NWOD | 40615248 | LAKEVLLE | SONOMA | 2020-04-22 | 2020-06-23 | ETL.7510 | MENDOCINO-HARTLEY | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118944451 | F | LC | ETL.5940.TOWR | 40593206 | PISMOBCH | LOS PADRES | 2020-04-22 | 2020-06-30 | ETL.5940 | DIABLO UNIT #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593206 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-10-13 | Glass Silicone Coated | Suspension |  |  |  |  | 2.4976e-06 | 1061
118947099 | E | LC | ETL.8290.POLE.WOOD | 40877247 | TABLEMTN | NORTH VALLEY | 2020-04-24 | 2020-05-08 | ETL.8290 | VOLTA-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40877247 |  | Single Wood Pole | T2N | 2019-06-06 | Polymer | Post |  |  |  |  | 0.00021049 | 999.4442
118990221 | E | LC | ETL.7950.POLE.WOOD | 40823384 | METCALF | SAN JOSE | 2020-05-06 |  | ETL.7950 | SAN MATEO-HILLSDALE JCT | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | HFRA Removal | PEND | 40823384 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Other |  |  |  |  | 0.085534 | 498.9879 | 42.6804
118993094 | E | LC | ETL.8060.POLE.WOOD | 40668705 | SACTO | SACRAMENTO | 2020-05-06 | 2021-09-29 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0075916 | 95.0021
119002569 | E | LC | ETL.1730.POLE.WDPS | 44515869 | MOSSLNDG | CENTRAL COAST | 2020-05-08 | 2020-07-08 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44515869 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 2020-08-11 | Glass | Suspension |  |  |  |  | 4.6739e-05
119002569 | E | LC | ETL.1730.POLE.WDPS | 44515869 | MOSSLNDG | CENTRAL COAST | 2020-05-08 | 2020-07-08 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44515869 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 2020-08-11 | Glass | Suspension |  |  |  |  | 4.6739e-05
119002887 | B | LC | ETL.1710.POLE.WDPS | 44513752 | MOSSLNDG | CENTRAL COAST | 2020-05-05 | 2021-06-16 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119081268 | E | LC | ETL.1730.INSL.CERA | 40853667 | MOSSLNDG | CENTRAL COAST | 2020-05-28 | 2020-08-25 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119082168 | E | LC | ETL.9100.POLE.WOOD | 44191865 | PISMOBCH | LOS PADRES | 2020-05-22 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 0.0007444 | 2503.7137
119082204 | E | LC | ETL.7490.POLE.NWOD | 40876584 | EUREKA | HUMBOLDT | 2020-05-29 | 2020-08-25 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40876584 | 2011-01-01 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2020-08-09 | Polymer | Dead End |  |  |  |  | 0.00018867 | 188.2791
119082978 | F | LC | ETL.4220.POLE.WOOD | 40758033 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2020-08-24 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119083501 | B | LC | ETL.5290.INSL | 40838474 | PISMOBCH | LOS PADRES | 2020-05-26 | 2020-09-02 | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40811351 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-22 | Glass | Suspension |  |  |  |  | 6.6221e-10 | 268.9426
119083501 | B | LC | ETL.5290.INSL | 40838474 | PISMOBCH | LOS PADRES | 2020-05-26 | 2020-09-02 | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40811351 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 6.6221e-10 | 268.9426
119097064 | E | LC | ETL.4070.INSL.NCER | 44969884 | SACTO | SACRAMENTO | 2020-06-02 | 2021-09-09 | ETL.4070 | VACA-SUISUN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40597218 | 1922-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-02-20 | Glass | Suspension |  |  |  |  | 1.9857e-06 | 5534.8257
119097064 | E | LC | ETL.4070.INSL.NCER | 44969884 | SACTO | SACRAMENTO | 2020-06-02 | 2021-09-09 | ETL.4070 | VACA-SUISUN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40597218 | 1922-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-08-11 | Glass | Suspension |  |  |  |  | 1.9857e-06 | 5534.8257
119116154 | E | LC | ETL.1112.POLE.NWOD | 44420230 | FRESNO | YOSEMITE | 2020-06-04 |  | ETL.1112 | INDIAN FLAT-YOSEMITE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44420230 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.00059495 | 4306.9175 | 2.5624
119116317 | E | LC | ETL.7290.POLE.WOOD | 40770427 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-03-01 | ETL.7290 | KILARC-CEDAR CREEK | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40770427 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.015701 | 1158.6814
119117330 | F | LC | ETL.1450.POLE.WOOD | 44212206 | SACTO | SIERRA | 2020-06-01 | 2020-08-10 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44212206 | 2013-09-30 | Single Wood Pole | 3P DV - 3 Pole Double Vertical | 2013-09-30 | Ceramic | Suspension |  |  |  |  | 0.00024798 | 1344.8513
119117695 | F | LC | ETL.5290.TOWR | 40576412 | PISMOBCH | LOS PADRES | 2020-05-26 | 2021-09-27 | ETL.5290 | MORRO BAY-MESA | Structure-Steel | Anti-Climbing Guard | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40576412 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-07-18 | Ceramic | Suspension |  |  |  |  | 6.3424e-07 | 2250.2754
119118338 | F | LC | ETL.6720.POLE.WOOD | 40861819 | TABLEMTN | NORTH VALLEY | 2020-05-28 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40861819 |  | Single Wood Pole | LB - Line and Buck |  | Ceramic | Suspension |  |  |  |  | 0.008936 | 0.065151
119118338 | F | LC | ETL.6720.POLE.WOOD | 40861819 | TABLEMTN | NORTH VALLEY | 2020-05-28 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40861819 |  | Single Wood Pole | LB - Line and Buck |  | Ceramic | Pin |  |  |  |  | 0.008936 | 0.065151
119118941 | F | LC | ETL.7300.POLE.WOOD | 40867888 | TABLEMTN |  | 2020-06-03 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40867888 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0014195 | 1821.5391
119119859 | E | LC | ETL.6761.POLE.WOOD | 44355526 | SACTO | SIERRA | 2020-06-04 |  | ETL.6761 | CAPE HORN TAP | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44355526 | 2017-04-28 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2017-04-28 | Polymer | Post |  |  |  |  | 0.00016465 | 31.7022 | 0.0052197
119124411 | E | LC | ETL.8365.POLE.WOOD | 40912599 | EUREKA | HUMBOLDT | 2020-06-08 | 2021-05-10 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Hardware-Wood | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912599 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2021-05-03 | Glass | Suspension |  |  |  |  | 0.031128
119127025 | F | LC | ETL.1422.TOWR | 40751877 | SACTO | SIERRA | 2020-06-04 | 2021-03-01 | ETL.1422 | BRUNSWICK #1 TAP | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751877 | 1975-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | [5 empty] | 1.2082e-06 | 15.8837
119130281 | E | LC | ETL.7300.POLE.WOOD | 40602004 | TABLEMTN |  | 2020-06-04 | 2021-03-22 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602004 |  | Single Wood Pole | T2N | 2021-03-05 | Polymer | Post |  |  |  |  | 0.0014306 | 2853.7749
119144205 | E | LC | ETL.4040.POLE.WDPS | 44557538 | TABLEMTN | NORTH VALLEY | 2020-06-10 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553985 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.01322 | 3611.4148 | 47.7421
119146863 | F | LC | ETL.6880.POLE.NWOD | 40679489 | LAKEVLLE | SONOMA | 2020-06-08 | 2020-11-10 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 |  |  | DLFL
119150124 | F | LC | ETL.9100.POLE.WOOD | 44191411 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-26 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.00026505 | 1613.8738
119161063 | E | LC | ETL.7260.POLE.WOOD | 40876460 | TABLEMTN | NORTH VALLEY | 2020-06-09 |  | ETL.7260 | KESWICK-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40876460 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 2.0441e-05 | 3722.593 | 0.076094
119167031 | F | LC | ETL.6480.POLE.NWOD | 44695497 | SACTO | SIERRA | 2020-06-15 | 2021-02-10 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44695497 | 2018-12-10 | Light Duty Steel Pole | T2N | 2018-12-10 | Polymer | Post |  |  |  |  | 0.021949 | 348.1483
119168584 | F | LC | ETL.6280.POLE.WOOD | 40868137 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40868137 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 4.9819e-06 | 569.452
119174429 | F | LC | ETL.6280.POLE.WOOD | 40614827 | TABLEMTN | NORTH VALLEY | 2020-06-16 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40614827 |  | Single Wood Pole | TH - TriAngle Post 70 | 2014-08-27 | Polymer | Suspension |  |  |  |  | 5.8877e-06 | 363.8401
119178622 | E | LC | ETL.8210.POLE.WOOD | 40907073 | VICTOR | STOCKTON | 2020-06-16 | 2021-09-13 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0035152 | 4148.5234
119180519 | E | LC | ETL.6220.POLE.WDPS | 44402615 | EUREKA | HUMBOLDT | 2020-06-15 | 2021-02-04 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44402612 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.14499
119180982 | E | LC | ETL.6480.INSL.CERA | 40731009 | SACTO | SACRAMENTO | 2020-06-15 | 2020-10-05 | ETL.6480 | COLGATE-CHALLENGE | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119185117 | F | LC | ETL.8210.POLE.WOOD | 40908255 | VICTOR | STOCKTON | 2020-06-16 |  | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908255 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0018487 | 259.0096
119198968 | E | LC | ETL.6470.POLE.WOOD | 40664652 | SACTO | SIERRA | 2020-06-23 | 2021-08-02 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119199479 | F | LC | ETL.6470.POLE.WOOD | 40822634 | SACTO | SIERRA | 2020-06-23 | 2021-02-11 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40822634 |  | Single Wood Pole | T2N | 2021-07-16 | Polymer | Post |  |  |  |  | 0.082852 | 158.2723
119201062 | E | LC | ETL.9340.POLE.NWOD | 44663902 | FRESNO | FRESNO | 2020-06-23 | 2021-11-08 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44663902 | 2018-10-03 | Light Duty Steel Pole | T-1 - Tri Post | 2018-10-03 | Polymer | Post |  |  |  |  | 0.035733 | 5445.5674 | 194.589
119203343 | B | LC | ETL.4220.POLE.WOOD | 44621396 | TABLEMTN | NORTH VALLEY | 2020-06-24 | 2020-10-26 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44621396 | 2017-02-05 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 2017-02-05 | Polymer | Post |  |  |  |  | 0.0033729 | 1886.254
119211889 | E | LC | ETL.7270.POLE.WOOD | 40758301 | TABLEMTN | NORTH VALLEY | 2020-06-25 | 2021-10-11 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758301 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.049137 | 744.5844
119221233 | E | LC | ETL.1110.POLE.STPS | 44424640 | EUREKA | NORTH VALLEY | 2020-06-26 | 2021-08-11 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Crossarm-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424637 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.6692e-06 | 657.3666
119230318 | E | LC | ETL.1650.POLE.WOOD | 40657208 | LAKEVLLE | SONOMA | 2020-06-29 | 2020-09-21 | ETL.1650 | GEYSERS #3-CLOVERDALE | Vegetation | Overgrown | [Trim, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40657208 | 1980-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1980-01-01 | Porcelain | Dead End |  |  |  |  | 6.0002e-06 | 1361.9498
119230396 | B | LC | ETL.8170.POLE.WOOD | 40770472 | EUREKA | HUMBOLDT | 2020-06-29 | 2020-08-03 | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770472 |  | Single Wood Pole | T-1 - Tri Post | 2019-08-03 | Polymer | Post |  |  |  |  | 0.12435 | 79.1467
119231770 | E | LC | ETL.8170.POLE.WOOD | 40826094 | EUREKA | HUMBOLDT | 2020-06-29 | 2021-08-17 | ETL.8170 | TRINITY-MAPLE CREEK | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826094 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-08-10 | Glass | Dead End |  |  |  |  | 0.16712 | 31.6978
119238313 | E | LC | ETL.7340.POLE.WOOD | 40876368 | LAKEVLLE | SONOMA | 2020-06-30 | 2021-05-25 | ETL.7340 | LAKEVILLE #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876368 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0017693 | 567.2149
119291266 | E | LC | ETL.6490.POLE.WOOD | 40823561 | SACTO | SIERRA | 2020-07-01 | 2021-03-04 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119291998 | E | LC | ETL.1650.POLE.WDPS | 44512129 | LAKEVLLE |  | 2020-06-30 | 2020-07-21 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44510877 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00044737 | 4036.5188
119295180 | F | LC | ETL.6020.TOWR | 40862229 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-02-11 | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40862229 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 5.4354e-07 | 205.8832
119295408 | E | LC | ETL.4392.TOWR | 41129326 | LAKEVLLE | SONOMA | 2020-07-01 | 2021-07-19 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129326 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-06-01 | Glass | Dead End |  |  |  |  | 0.00023592 | 3246.7576
119295408 | E | LC | ETL.4392.TOWR | 41129326 | LAKEVLLE | SONOMA | 2020-07-01 | 2021-07-19 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129326 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2019-11-22 | Glass | Dead End |  |  |  |  | 0.00023592 | 3246.7576
119295877 | E | LC | ETL.4393.POLE.WDPS | 44172276 | SACTO | SACRAMENTO | 2020-06-30 | 2021-03-09 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119315447 | E | LC | ETL.7270.POLE.WOOD | 40908530 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-08-07 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908530 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-02-29 | Glass | Dead End |  |  |  |  | 0.0067097 | 4367.7598
119317063 | F | LC | ETL.7300.POLE.NWOD | 44809979 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44809979 | 2019-05-24 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2019-05-24 | Polymer | Post |  |  |  |  | 4.0428e-06 | 3833.8523
119350197 | E | LC | ETL.1110.POLE.WOOD | 42603533 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119359493 | E | LC | ETL.7030.POLE.WOOD | 40770068 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-05-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770068 |  | Single Wood Pole | T2N | 2021-05-03 | Polymer | Post |  |  |  |  | 0.015305 | 5604.2109
119359553 | E | LC | ETL.7030.POLE.WOOD | 40759025 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-06-15 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119361170 | E | LC | ETL.4221.POLE.WDPS | 44561407 | TABLEMTN |  | 2020-07-08 | 2020-08-18 | ETL.4221 | SLY CREEK TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119361779 | B | LC | ETL.7630.POLE.WOOD | 40877373 | LAKEVLLE | SONOMA | 2020-07-13 | 2020-09-30 | ETL.7630 | MONTE RIO-FULTON | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40877373 | 1990-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.11092 | 31.7051
119364334 | E | LC | ETL.1430.TOWR | 40655122 | SACTO | SACRAMENTO | 2020-07-13 | 2021-03-09 | ETL.1430 | DRUM-RIO OSO #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40655122 | 1913-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-02-24 | Glass | Dead End |  |  |  |  | 0.047141 | 1993.4753
119364511 | F | LC | ETL.6280.POLE.WOOD | 40588944 | TABLEMTN | NORTH VALLEY | 2020-07-13 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40588944 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 6.9056e-06 | 5520.0938
119379284 | F | LC | ETL.7030.POLE.WOOD | 40592097 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-06-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592097 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0098027 | 0.06515
119469962 | F | LC | ETL.7030.POLE.WOOD | 40876213 | TABLEMTN | NORTH VALLEY | 2020-07-17 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40876213 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0093624 | 0.06515
119478203 | E | LC | ETL.6290.POLE.WOOD | 40758602 | TABLEMTN | NORTH VALLEY | 2020-07-20 | 2021-11-29 | ETL.6290 | CARIBOU-PLUMAS JCT | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40758602 | 1962-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 1962-01-01 | Porcelain | Dead End |  |  |  |  | 0.29874 | 775.8105
119480012 | E | LC | ETL.9200.POLE.WOOD | 40583998 | MIDWAY | KERN | 2020-07-21 |  | ETL.9200 | TAFT-CUYAMA #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40583998 | 1962-01-01 | Single Wood Pole | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.0213
119498024 | F | LC | ETL.1110.POLE.WDPS | 44424594 | TABLEMTN | NORTH VALLEY | 2020-07-23 | 2021-04-14 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119535394 | F | LC | ETL.4440.TOWR | 40683805 | TABLEMTN | NORTH VALLEY | 2020-07-30 | 2020-08-10 | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40683805 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 2.1569e-06 | 617.2722
119551478 | B | LC | ETL.4040.POLE.WDPS | 44557904 | TABLEMTN | NORTH VALLEY | 2020-07-31 | 2020-08-06 | ETL.4040 | TRINITY-COTTONWOOD | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44557904 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.01271
119551478 | B | LC | ETL.4040.POLE.WDPS | 44557904 | TABLEMTN | NORTH VALLEY | 2020-07-31 | 2020-08-06 | ETL.4040 | TRINITY-COTTONWOOD | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44557904 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.01271
119565496 | E | LC | ETL.8210.POLE.WOOD | 40908274 | VICTOR | STOCKTON | 2020-08-05 | 2021-07-06 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908274 | 1984-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0021347 | 2712.7373
119574381 | F | LC | ETL.6490.POLE.WOOD | 40768246 | SACTO | SACRAMENTO | 2020-08-07 |  | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40768246 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.018343 | 26.9566
119600574 | F | LC | ETL.9210.POLE.WOOD | 40685721 | MIDWAY | KERN | 2020-08-11 | 2021-01-25 | ETL.9210 | TAFT-CUYAMA #2 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40685721 | 1946-01-01 | Single Wood Pole | 2P DDE - 2 Pole Double Dead End | 1946-01-01 | Ceramic | Dead End |  |  |  |  | 0.29538
119608830 | B | LC | ETL.8650.TOWR | 40582621 | FRESNO | FRESNO | 2020-08-13 | 2020-12-08 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40582621 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-11-18 | Glass | Dead End |  |  |  |  | 0.052158 | 4725.8886
119623589 | F | LC | ETL.8170.POLE.WOOD | 40906415 | EUREKA | HUMBOLDT | 2020-08-03 | 2021-08-26 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40906415 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0041966 | 1613.8785
119636068 | E | LC | ETL.6870.POLE.WOOD | 40664841 | SACTO | SIERRA | 2020-08-17 | 2021-05-19 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664841 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.30504 | 0.065152
119636935 | F | LC | ETL.6480.POLE.WOOD | 40597563 | SACTO | SACRAMENTO | 2020-08-19 | 2021-02-12 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119658782 | A | LC | ETL.6240.POLE.WOOD | 40599249 | MOSSLNDG | CENTRAL COAST | 2020-08-22 | 2020-09-19 | ETL.6240 | BURNS-LONE STAR #2 | Emergency-Wood | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40599249 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.14965 | 110.8153
119699029 | B | LC | ETL.1110.INSL.NCER | 40617834 | TABLEMTN | HUMBOLDT | 2020-08-26 | 2020-10-14 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423235 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.004149
119699029 | B | LC | ETL.1110.INSL.NCER | 40617834 | TABLEMTN | HUMBOLDT | 2020-08-26 | 2020-10-14 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423235 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.004149
119704056 | F | LC | ETL.8270.POLE.WOOD | 40751532 | MOSSLNDG | CENTRAL COAST | 2020-08-31 | 2020-11-19 | ETL.8270 | VIEJO-MONTEREY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751532 |  | Single Wood Pole | DV - Double Vertical |  | Ceramic | [5 empty] | 0.55871 | 0.065148
119720286 | B | LC | ETL.1440.INSL.CERA | 44149486 | SACTO | SACRAMENTO | 2020-08-12 | 2020-10-14 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44149437 | 2013-11-06 | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0010784
119720286 | B | LC | ETL.1440.INSL.CERA | 44149486 | SACTO | SACRAMENTO | 2020-08-12 | 2020-10-14 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44149437 | 2013-11-06 | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0010784
119720822 | F | LC | ETL.1730.POLE.WOOD | 40876809 | MOSSLNDG | CENTRAL COAST | 2020-07-27 | 2021-06-21 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40876809 | 1972-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2014-04-23 | Polymer | Dead End |  |  |  |  | 0.00015674 | 0.065147
119753886 | E | LC | ETL.7530.INSL.CERA | 44870396 | LAKEVLLE | HUMBOLDT | 2020-09-03 |  | ETL.7530 | MENDOCINO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40820915 |  | Lattice Steel Pole | TPSRD - Tramp Double Dead End | 2020-06-08 | Glass | Double Dead End |  |  |  |  | 2.8067e-05 | 3404.2203 | 0.095547
119753886 | E | LC | ETL.7530.INSL.CERA | 44870396 | LAKEVLLE | HUMBOLDT | 2020-09-03 |  | ETL.7530 | MENDOCINO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40820915 |  | Lattice Steel Pole | TPSRD - Tramp Double Dead End | 2019-06-25 | Porcelain | Dead End |  |  |  |  | 2.8067e-05 | 3404.2203 | 0.095547
119758880 | E | LC | ETL.1400.POLE.WOOD | 40764834 | VICTOR | YOSEMITE | 2020-08-18 | 2021-05-19 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40764834 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0054306
119758880 | E | LC | ETL.1400.POLE.WOOD | 40764834 | VICTOR | YOSEMITE | 2020-08-18 | 2021-05-19 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40764834 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0054306
119758881 | E | LC | ETL.1400.POLE.STPS | 44418040 | VICTOR | YOSEMITE | 2020-08-18 | 2021-05-19 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44418040 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 3.3105e-05
119758881 | E | LC | ETL.1400.POLE.STPS | 44418040 | VICTOR | YOSEMITE | 2020-08-18 | 2021-05-19 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44418040 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 3.3105e-05
119762532 | B | LC | ETL.6220.INSL.CERA | 40835197 | EUREKA | HUMBOLDT | 2020-09-14 | 2020-10-13 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40810322 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 0.014293 | 1189.0208
119768840 | F | LC | ETL.6760.POLE.WOOD | 40767282 | SACTO | SIERRA | 2020-09-08 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40767282 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0063376 | 0.06515
119787072 | F | LC | ETL.6470.POLE.WOOD | 40912097 | SACTO | SIERRA | 2020-09-18 | 2021-02-12 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40912097 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0029541 | 680.261
119788336 | E | LC | ETL.5930.TOWR | 40592002 | CONCORD | DIABLO | 2020-09-15 | 2021-02-11 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40592002 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.6848e-08 | 175.6638
119788336 | E | LC | ETL.5930.TOWR | 40592002 | CONCORD | DIABLO | 2020-09-15 | 2021-02-11 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40592002 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.6848e-08 | 175.6638
119809956 | F | LC | ETL.6280.POLE.WOOD | 40656552 | TABLEMTN | NORTH VALLEY | 2020-08-18 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND | [11 empty] | 2.8823e-07 | 205.6771
119826209 | B | LC | ETL.6880.POLE.WOOD | 40861400 | LAKEVLLE | NORTH BAY | 2020-09-28 | 2020-10-16 | ETL.6880 | FULTON-CALISTOGA | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119848583 | F | LC | ETL.7780.POLE.WOOD | 40876304 | LAKEVLLE | HUMBOLDT | 2020-09-15 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40876304 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 1.4883e-05 | 411.3464
119850808 | F | LC | ETL.8365.POLE.NWOD | 40906640 | EUREKA | HUMBOLDT | 2020-09-17 | 2021-10-11 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40906640 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0010249
119874664 | B | LC | ETL.4780.INSL.CERA | 44942677 | LAKEVLLE | SONOMA | 2020-10-08 | 2020-11-23 | ETL.4780 | GEYSERS #9-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119878588 | E | LC | ETL.9340.POLE.WOOD | 40819801 | FRESNO | YOSEMITE | 2020-10-01 | 2021-10-26 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.031925 | 5231.8582 | 167.0287
119916942 | F | LC | ETL.7030.POLE.WOOD | 40600247 | TABLEMTN | NORTH VALLEY | 2020-09-19 | 2021-07-07 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600247 |  | Single Wood Pole | TPA - Tri Pin Arm | 2013-06-21 | Ceramic | Pin |  |  |  |  | 0.00964 | 64.0224
120049708 | B | LC | ETL.6290.POLE.WOOD | 40591667 | TABLEMTN | NORTH VALLEY | 2020-11-12 | 2020-12-15 | ETL.6290 | CARIBOU-PLUMAS JCT | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591667 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.071992 | 4824.2021
120124953 | E | LC | ETL.8170.POLE.WOOD | 44420778 | EUREKA | HUMBOLDT | 2020-11-30 | 2021-06-03 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120139203 | F | LC | ETL.7290.POLE.WOOD | 40816388 | TABLEMTN | NORTH VALLEY | 2020-10-28 |  | ETL.7290 | KILARC-CEDAR CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40816388 |  | Single Wood Pole | T-1 - Tri Post | 2019-06-10 | Polymer | Post |  |  |  |  | 0.0040679 | 1080.2521
120204671 | F | LC | ETL.6060.TOWR | 40762957 | TABLEMTN | NORTH VALLEY | 2020-12-15 | 2021-06-30 | ETL.6060 | ROUND MTN-TABLE MTN #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762957 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.6086e-05 | 1506.4426
120472032 | A | LC | ETL.6750.POLE.WDPS | 44374914 | TABLEMTN | NORTH VALLEY | 2021-01-27 | 2021-02-02 | ETL.6750 | DELTA-MTN GATE JCT | Emergency | Storm Related | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44374914 | 2012-08-04 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 2.5737e-05
120472032 | A | LC | ETL.6750.POLE.WDPS | 44374914 | TABLEMTN | NORTH VALLEY | 2021-01-27 | 2021-02-02 | ETL.6750 | DELTA-MTN GATE JCT | Emergency | Storm Related | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44374914 | 2012-08-04 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 2.5737e-05
120472032 | A | LC | ETL.6750.POLE.WDPS | 44374914 | TABLEMTN | NORTH VALLEY | 2021-01-27 | 2021-02-02 | ETL.6750 | DELTA-MTN GATE JCT | Emergency | Storm Related | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44374914 | 2012-08-04 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 2.5737e-05
120582581 | E | LC | ETL.5640.TOWR | 40813970 | TABLEMTN | NORTH VALLEY | 2021-02-26 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40813970 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-09 | Glass Silicone Coated | Suspension |  |  |  |  | 1.6675e-10 | 6592.9951 | 1.0994e-06
120654488 | F | LC | ETL.4920.TOWR | 40760556 | LAKEVLLE | SONOMA | 2021-03-17 |  | ETL.4920 | IGNACIO-SOBRANTE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40760556 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 8.5185e-05 | 63.3304 | 0.0053948
120654488 | F | LC | ETL.4920.TOWR | 40760556 | LAKEVLLE | SONOMA | 2021-03-17 |  | ETL.4920 | IGNACIO-SOBRANTE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40760556 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Dead End |  |  |  |  | 8.5185e-05 | 63.3304 | 0.0053948
120657638 | F | LC | ETL.6880.POLE.NWOD | 45071341 | LAKEVLLE | SONOMA | 2021-03-18 |  | ETL.6880 | FULTON-CALISTOGA | Right of Way | Encroachment | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45071341 | 2020-03-05 | Lattice Steel Pole | DC-DDE - Double Circuit Double Dead End | 2020-03-05 | Glass | Dead End |  |  |  |  | 2.8325e-05 | 221.6343
120680778 | E | LC | ETL.5540.TOWR | 40757176 | TABLEMTN | NORTH VALLEY | 2021-03-23 | 2021-03-24 | ETL.5540 | POE-RIO OSO | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40757176 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-12 | Glass | Dead End |  |  |  |  | 2.5941e-07 | 174.6669
120684206 | E | LC | ETL.6720.POLE.WDPS | 44950330 | TABLEMTN | NORTH VALLEY | 2021-03-24 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Rotten | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 42578835 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00032825 | 2104.1226 | 0.69069
120684379 | E | LC | ETL.6520.POLE.WDPS | 45015268 | SACTO | SIERRA | 2020-08-10 | 2021-06-16 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
120686934 | F | LC | ETL.6890.POLE.WOOD | 40766460 | LAKEVLLE | SONOMA | 2021-03-24 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40766460 | 1980-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Ceramic | Other |  |  |  |  | 0.00012514 | 395.7669
120689691 | F | LC | ETL.5330.TOWR | 40753154 | MOSSLNDG | CENTRAL COAST | 2021-03-24 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753154 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1969-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.2047e-09 | 111.0094 | 5.7778e-07
120689691 | F | LC | ETL.5330.TOWR | 40753154 | MOSSLNDG | CENTRAL COAST | 2021-03-24 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753154 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1969-01-01 | Ceramic | Other |  |  |  |  | 5.2047e-09 | 111.0094 | 5.7778e-07
120711093 | E | LC | ETL.3830.TOWR | 40803322 | VICTOR | STOCKTON | 2021-03-26 | 2021-07-19 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40803322 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 3.7615e-06 | 5823.2505
120712759 | E | LC | ETL.1650.POLE.WOOD | 40750646 | LAKEVLLE | SONOMA | 2021-03-30 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40750646 | 1966-01-01 | Single Wood Pole | WB - Wishbone | 1966-01-01 | Porcelain | Suspension |  |  |  |  | 0.00013117 | 1551.4763 | 0.2035
120713040 | E | LC | ETL.3840.INSL.NCER | 40639679 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40612631 | 1927-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Glass | Suspension |  |  |  |  | 6.8358e-07 | 5144.5415 | 0.0035167
120713040 | E | LC | ETL.3840.INSL.NCER | 40639679 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40612631 | 1927-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 6.8358e-07 | 5144.5415 | 0.0035167
120713041 | E | LC | ETL.3830.TOWR | 40612631 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40612631 | 1927-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Glass | Suspension |  |  |  |  | 6.8358e-07 | 5144.5415 | 0.0035167
120713041 | E | LC | ETL.3830.TOWR | 40612631 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40612631 | 1927-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 6.8358e-07 | 5144.5415 | 0.0035167
120714970 | F | LC | ETL.5980.TOWR | 40664640 | PISMOBCH | LOS PADRES | 2021-03-30 |  | ETL.5980 | DIABLO-MIDWAY #3 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40664640 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 2.2273e-06 | 2027.5646 | 0.004516
120750249 | B | LC | ETL.3830.INSL | 40827021 | VICTOR | STOCKTON | 2021-04-06 | 2021-05-26 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803314 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.8076e-07 | 632.6837
120751022 | F | LC | ETL.2660.TOWR | 40810225 | SACTO | SACRAMENTO | 2021-04-06 |  | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40810225 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Ceramic | Suspension |  |  |  |  | 7.456e-09 | 5936.4092 | 4.4262e-05
120751022 | F | LC | ETL.2660.TOWR | 40810225 | SACTO | SACRAMENTO | 2021-04-06 |  | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40810225 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-07-21 | Glass | Suspension |  |  |  |  | 7.456e-09 | 5936.4092 | 4.4262e-05
120764927 | B | LC | ETL.3190.TOWR | 40910300 | TABLEMTN | NORTH VALLEY | 2021-04-08 | 2021-06-25 | ETL.3190 | CARIBOU-PALERMO | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910300 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2017-07-28 | Ceramic | Suspension |  |  |  |  | 0.00043269 | 363.8401
120772903 | E | LC | ETL.3820.INSL.CERA | 40669695 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40642810 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 5.6698e-06 | 300.5596 | 0.0017041
120785588 | E | LC | ETL.8365.POLE.WOOD | 40808839 | EUREKA | HUMBOLDT | 2021-04-09 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40808839 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0095752 | 1139.0485 | 10.9067
120801582 | B | LC | ETL.4100.INSL.NCER | 44962276 | LAKEVLLE | SACRAMENTO | 2021-04-12 | 2021-04-28 | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40767770 | 1913-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2018-05-28 | Glass | Suspension |  |  |  |  | 1.7604e-07 | 5890.1841
120803077 | F | LC | ETL.4750.TOWR | 40869471 | LAKEVLLE | SONOMA | 2021-04-12 |  | ETL.4750 | GEYSERS #12-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40869471 | 1971-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 1.6141e-07 | 1300.3347 | 0.00020988
120805206 | E | LC | ETL.5970.INSL | 40884360 | PISMOBCH | LOS PADRES | 2021-04-13 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40862388 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 9.862e-10 | 2104.1462 | 2.0751e-06
120805800 | E | LC | ETL.4316.INSL.CERA | 40614244 | TABLEMTN |  | 2021-04-07 | 2021-08-26 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120807115 | B | LC | ETL.5330.INSL | 40845475 | MOSSLNDG | CENTRAL COAST | 2021-04-13 | 2021-07-06 | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818889 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1969-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.0666e-06 | 238.11
120807115 | B | LC | ETL.5330.INSL | 40845475 | MOSSLNDG | CENTRAL COAST | 2021-04-13 | 2021-07-06 | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818889 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1969-01-01 | Ceramic | Other |  |  |  |  | 1.0666e-06 | 238.11
120815467 | E | LC | ETL.5463.TOWR | 40582085 | CONCORD | DIABLO | 2021-04-14 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40582085 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 3.7361e-07 | 3043.1921 | 0.001137
120818983 | E | LC | ETL.6330.INSL.NCER | 40853290 | TABLEMTN | NORTH VALLEY | 2021-04-14 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40824053 | 1998-01-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Double Dead End |  |  |  |  | 1.7414e-06 | 308.9596 | 0.00053802
120840570 | E | LC | ETL.4040.POLE.STPS | 44647520 | TABLEMTN | NORTH VALLEY | 2021-04-19 | 2021-09-23 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44646872 | 2018-08-17 | 3-Pole Non Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.00012646 | 270.1179
120844842 | B | LC | ETL.4870.INSL | 40881228 | FRESNO | FRESNO | 2021-04-19 | 2021-06-04 | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40858331 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.8357e-08 | 5240.2021
120852849 | E | LC | ETL.7560.POLE.STPS | 44924475 | SACTO | SIERRA | 2021-04-20 | 2021-08-17 | ETL.7560 | WEIMAR #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44923855 | 2020-05-06 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.032851 | 980.8127
120858963 | F | LC | ETL.3830.TOWR | 43249438 | VICTOR | STOCKTON | 2021-04-21 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 43249438 | 1970-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | [7 empty] | 2.9043e-08 | 4907.2686
120859691 | E | LC | ETL.4050.POLE.WOOD | 40745246 | LAKEVLLE | SONOMA | 2021-04-21 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40745246 | 1970-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1970-01-01 | Ceramic | Post |  |  |  |  | 2.7309e-05 | 2248.4673 | 0.061403
120861324 | B | LC | ETL.4870.INSL | 40774317 | FRESNO | FRESNO | 2021-04-21 | 2021-06-17 | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40746623 | 1985-01-01 | LATTICE STEEL TOWER | SUSP-A - Suspension Angle (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 5.2317e-06 | 6774.1143
120876638 | F | LC | ETL.5510.TOWR | 40593857 | CONCORD | DIABLO | 2021-04-23 |  | ETL.5510 | PITTSBURG-TESLA #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40593857 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 3.0306e-07 | 4832.7637
120878227 | B | LC | ETL.7590.INSL | 40798010 | MOSSLNDG | DE ANZA | 2021-04-23 | 2021-07-22 | ETL.7590 | MONTA VISTA-BURNS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767268 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Double Dead End |  |  |  |  | 0.15498 | 63.351
120879320 | F | LC | ETL.1810.POLE.STPS | 44994670 | EUREKA | HUMBOLDT | 2021-04-22 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44994626 | 2020-10-21 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.00065825
120889685 | E | LC | ETL.6470.POLE.WOOD | 40822719 | SACTO | SACRAMENTO | 2021-04-27 | 2021-08-02 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822719 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0092617 | 870.1591
120892794 | E | LC | ETL.3700.POLE.WOOD | 40816917 | PISMOBCH | LOS PADRES | 2021-04-27 | 2021-10-06 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816917 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Porcelain | Post |  |  |  |  | 4.4724e-05 | 7061.4551 | 0.31582
120897731 | E | LC | ETL.5390.TOWR | 40817598 | TABLEMTN | NORTH VALLEY | 2021-04-28 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40817598 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 0.00017224 | 506.3134 | 0.087207
120912984 | F | LC | ETL.6890.POLE.WOOD | 41172071 | LAKEVLLE | SONOMA | 2021-05-01 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41172071 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.00042983 | 1614.3784
120913981 | F | LC | ETL.6890.POLE.WOOD | 40587790 | LAKEVLLE | SONOMA | 2021-05-01 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40587790 | 1976-01-01 | Single Wood Pole | TPS1D - Tri Post & Susp DDE 115 KV |  | Ceramic | Other |  |  |  |  | 0.00015745 | 3613.6854
120919854 | E | LC | ETL.4620.INSL.NCER | 40785373 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40756267 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 5.9218e-06 | 619.5195 | 0.0036687
120920463 | E | LC | ETL.6880.POLE.NWOD | 44668642 | LAKEVLLE | SONOMA | 2021-05-03 | 2021-07-27 | ETL.6880 | FULTON-CALISTOGA | Jumper-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44668642 | 2018-11-05 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-11-05 | Polymer | Dead End - Suspension |  |  |  |  | 3.684e-06 | 458.8659
120942285 | E | LC | ETL.2700.INSL | 40773179 | CONCORD | EAST BAY | 2021-04-21 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40745866 | 1944-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1944-01-01 | Ceramic | Suspension |  |  |  |  | 2.1543e-05 | 0.065158 | 1.4037e-06
120943107 | E | LC | ETL.3820.INSL.CERA | 40780151 | VICTOR | STOCKTON | 2021-05-06 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40751251 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | [5 empty] | 7.6657e-05 | 838.5675 | 0.064282
120943220 | F | LC | ETL.6470.POLE.WOOD | 40868956 | SACTO | SACRAMENTO | 2021-05-04 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40868956 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.22024 | 474.8005
120948707 | F | LC | ETL.5300.TOWR | 40651382 | PISMOBCH | LOS PADRES | 2021-04-15 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40651382 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 2.7747e-07 | 652.484 | 0.00018104
120949832 | E | LC | ETL.8264.POLE.WOOD | 40904713 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8264 | VALLEY SPRINGS-CLAY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40904713 | 1991-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 0.00095812 | 6185.1016 | 5.9261
121061192 | E | LC | ETL.5390.TOWR | 40758866 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40758866 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.9455e-05 | 4009.509 | 0.1181
121324502 | E | LC | ETL.6890.POLE.WOOD | 40592670 | LAKEVLLE | SONOMA | 2021-05-12 | 2021-06-04 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40592670 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0016431 | 1366.627
121329568 | E | LC | ETL.1820.POLE.WDPS | 44560656 | EUREKA | HUMBOLDT | 2021-05-13 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560076 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.22338 | 15.8815 | 3.5475
121329721 | F | LC | ETL.9250.POLE.WOOD | 40749385 | MIDWAY | KERN | 2021-04-22 |  | ETL.9250 | TEJON-LEBEC | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40749385 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Pin |  |  |  |  | 0.024943 | 9424.9238
121337844 | F | LC | ETL.6890.POLE.NWOD | 44712998 | LAKEVLLE | SONOMA | 2021-04-26 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44712998 | 2019-02-16 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-02-16 | Ceramic | Suspension |  |  |  |  | 2.2551e-08 | 882.2992
121364190 | E | LC | ETL.5250.TOWR | 40589810 | CONCORD | MISSION | 2021-04-29 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40589810 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.0242e-05 | 126.5838 | 0.0012965
121372717 | B | LC | ETL.7290.INSL.CERA | 40699826 | TABLEMTN | NORTH VALLEY | 2021-05-20 | 2021-06-14 | ETL.7290 | KILARC-CEDAR CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40668411 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.044097 | 110.843
121374598 | E | LC | ETL.4550.TOWR | 40759831 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40759831 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 8.345e-08 | 4452.8057 | 0.00037159
121378045 | E | LC | ETL.1820.POLE.WDPS | 44560543 | EUREKA | HUMBOLDT | 2021-05-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560113 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.026773 | 205.715 | 5.5076
121378106 | F | LC | ETL.6880.POLE.NWOD | 44989198 | LAKEVLLE | NORTH BAY | 2021-05-06 |  | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44989198 | 2020-05-18 | Light Duty Steel Pole | T1-1A | 2020-05-18 | Polymer | Post |  |  |  |  | 2.0451e-06 | 110.8668
121381185 | F | LC | ETL.8350.POLE.NWOD | 44920062 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44920062 | 2020-01-15 | Light Duty Steel Pole | T-1 - Tri Post | 2020-01-15 | Polymer | Post |  |  |  |  | 1.9421e-06 | 95.3431
121384310 | F | LC | ETL.8250.POLE.WOOD | 40912843 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40912843 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 2.5325e-05 | 2140.0149
121385730 | F | LC | ETL.6760.POLE.WOOD | 40913016 | SACTO | SIERRA | 2021-05-12 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40913016 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | Unknown |  |  |  |  | 0.012151 | 408.1827
121391806 | E | LC | ETL.1480.INSL.CERA | 40739303 | LAKEVLLE |  | 2021-05-13 |  | ETL.1480 | EAGLE ROCK-REDBUD | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40648890 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1978-01-01 | Glass | Dead End |  |  |  |  | 0.0081755 | 4728.469 | 38.6577
121393151 | E | LC | ETL.8060.POLE.WOOD | 40590010 | SACTO | SIERRA | 2021-05-18 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40590010 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.051465 | 63.348 | 3.2602
121397833 | F | LC | ETL.3740.TOWR | 40761864 | CONCORD | DIABLO | 2021-05-19 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40761864 | 1922-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 0.038472 | 445.731
121402931 | E | LC | ETL.6770.POLE.NWOD | 44923380 | SACTO | SIERRA | 2021-05-19 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44923380 | 2020-05-28 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2020-05-28 | Polymer | Post |  |  |  |  | 0.00029526 | 3069.2839 | 0.90625
121405578 | E | LC | ETL.7550.POLE.WOOD | 40876383 | LAKEVLLE | HUMBOLDT | 2021-05-21 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40876383 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 3.8309e-05 | 3890.0607 | 0.14902
121409195 | F | LC | ETL.6640.POLE.WOOD | 40615992 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40615992 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0012714 | 692.7915
121418147 | F | LC | ETL.6470.POLE.WOOD | 40611344 | SACTO | SIERRA | 2021-05-27 | 2021-07-12 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40611344 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.30511 | 189.9644
121420709 | F | LC | ETL.4316.POLE.STPS | 44674922 | TABLEMTN |  | 2021-05-25 |  | ETL.4316 | PARADISE-TABLE MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44674842 | 2018-11-18 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0084676 | 0.065151
121422099 | F | LC | ETL.4750.TOWR | 40813804 | LAKEVLLE | SONOMA | 2021-05-27 |  | ETL.4750 | GEYSERS #12-FULTON | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40813804 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Porcelain | Suspension |  |  |  |  | 3.2267e-06 | 3246.7576
121427817 | F | LC | ETL.1400.POLE.STPS | 44384142 | VICTOR | YOSEMITE | 2021-05-26 | 2021-07-12 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44384142 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 4.2217e-05
121427817 | F | LC | ETL.1400.POLE.STPS | 44384142 | VICTOR | YOSEMITE | 2021-05-26 | 2021-07-12 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44384142 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 4.2217e-05
121430694 | E | LC | ETL.6470.POLE.WOOD | 40611186 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40611186 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.06793 | 142.4516 | 9.6768
121471467 | E | LC | ETL.4580.TOWR | 40869558 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40869558 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Porcelain | Suspension |  |  |  |  | 6.5721e-07 | 2963.4478 | 0.0019476
121471467 | E | LC | ETL.4580.TOWR | 40869558 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40869558 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 6.5721e-07 | 2963.4478 | 0.0019476
121474307 | A | LC | ETL.1680.POLE.WDPS | 44298672 | LAKEVLLE | SONOMA | 2021-06-04 | 2021-06-08 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Emergency-Wood | Other | [Replace, Completed, Completed] |  | Tier 3 | Within Both | COMP | 44298670 |  | 3-Pole Wood | FSS - Field Switch Structure | [7 empty] | 0.0013052 | 4639.9287
121474380 | B | LC | ETL.1820.POLE.WDPS | 44562880 | EUREKA | HUMBOLDT | 2021-06-04 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562403 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.072013 | 0.065148
121493150 | E | LC | ETL.4580.TOWR | 40593929 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40593929 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1956-01-01 | Porcelain | Suspension |  |  |  |  | 8.4432e-07 | 3012.2939 | 0.0025433
121493150 | E | LC | ETL.4580.TOWR | 40593929 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40593929 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 8.4432e-07 | 3012.2939 | 0.0025433
121500434 | E | LC | ETL.8365.POLE.WOOD | 40912658 | EUREKA | HUMBOLDT | 2021-06-03 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40912658 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.18975
121514193 | E | LC | ETL.6640.POLE.WOOD | 40770193 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40770193 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-07-22 | Glass | Dead End |  |  |  |  | 0.00099121 | 3249.6929 | 3.2211
121518982 | F | LC | ETL.4550.TOWR | 40762893 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762893 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.8811e-07 | 3391.7021 | 0.00097719
121524955 | E | LC | ETL.1810.POLE.WDPS | 44322607 | EUREKA | HUMBOLDT | 2021-06-08 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44322605 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.065924 | 142.4597 | 9.3915
121525959 | E | LC | ETL.6500.SWIT | 40743585 | SACTO | SACRAMENTO | 2021-06-09 |  | ETL.6500 | COLGATE-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | PEND | [7 empty] | 2017-09-29 | SEECO | VACUUM INTERRUPTER (3 GAP) | SCADA Only
121527085 | E | LC | ETL.1350.POLE.WDPS | 44512149 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40660364 | 2012-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.020648 | 194.6766 | 4.0197
121534209 | E | LC | ETL.1610.INSL.CERA | 40781838 | LAKEVLLE | SONOMA | 2021-06-10 | 2021-08-30 | ETL.1610 | SILVERADO-FULTON JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40752656 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 1.4163e-08 | 838.7772
121543341 | F | LC | ETL.1450.POLE.NWOD | 44270074 | SACTO | SIERRA | 2021-06-12 |  | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44270074 |  | Light Duty Steel Pole | Other |  | Ceramic | Suspension |  |  |  |  | 3.0451e-06 | 348.1462 | 0.0010602
121544144 | F | LC | ETL.5630.TOWR | 40762683 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5630 | ROCK CREEK-POE | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40762683 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.3649e-06 | 6331.4321
121595990 | E | LC | ETL.6020.TOWR | 40868382 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40868382 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.9028e-06 | 1725.6576 | 0.0032836
121627607 | E | LC | ETL.1070.POLE.NWOD | 45073099 | VICTOR | STOCKTON | 2021-06-22 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45073099 | 2021-03-05 | Light Duty Steel Pole | TPS1D - Tri Post & Susp DDE 115 KV | 2021-03-05 | Glass | Dead End - Suspension |  |  |  |  | 4.8291e-10 | 2633.8957 | 1.2719e-06
121649127 | F | LC | ETL.6520.POLE.NWOD | 44962167 | SACTO | SIERRA | 2021-06-28 |  | ETL.6520 | COLGATE-SMARTVILLE #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44962167 | 2020-08-13 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-08-13 | Polymer | Post |  |  |  |  | 0.0023876 | 1585.8888
121662882 | E | LC | ETL.7550.POLE.WOOD | 40875188 | LAKEVLLE | HUMBOLDT | 2021-07-02 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40875188 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 5.3941e-05 | 142.4053 | 0.0076815
121679087 | F | LC | ETL.9240.TOWR | 43249717 | PISMOBCH | LOS PADRES | 2021-07-07 | 2021-10-06 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249717 |  | LATTICE STEEL TOWER | [9 empty] | 2470.1736
121705853 | E | LC | ETL.4316.POLE.STPS | 45074892 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.4316 | PARADISE-TABLE MTN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40758646 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0020407 | 2995.1147 | 6.112
121720593 | B | LC | ETL.5650.INSL | 40894185 | TABLEMTN | NORTH VALLEY | 2021-07-13 | 2021-07-27 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40870436 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 2.5971e-07 | 968.9049
121741319 | F | LC | ETL.7390.POLE.NWOD | 44837773 | LAKEVLLE | HUMBOLDT | 2021-07-14 |  | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44837773 | 2019-07-24 | Light Duty Steel Pole | T-1 - Tri Post | 2019-07-24 | Polymer | Post |  |  |  |  | 0.028213
121750545 | F | LC | ETL.2395.POLE.WOOD | 45105245 | TABLEMTN | NORTH VALLEY | 2021-07-15 | 2021-08-12 | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45105245 |  | Single Wood Pole | SVDE - Single Vertical Dead End |  | Ceramic | Dead End | [5 empty] | 292.6794
121758641 | B | LC | ETL.6280.POLE.WOOD | 40816774 | TABLEMTN | NORTH VALLEY | 2021-07-19 | 2021-10-11 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40816774 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0024683 | 1739.9091
121769890 | E | LC | ETL.1820.INSL.CERA | 40630997 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44560163 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.058623
121769890 | E | LC | ETL.1820.INSL.CERA | 40630997 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44560163 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.058623
121790562 | B | LC | ETL.5091.INSL | 41122479 | MOSSLNDG | CENTRAL COAST | 2021-07-24 | 2021-08-24 | ETL.5091 | METCALF-MONTA VISTA #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40591720 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.024278 | 0.065152
121797466 | E | LC | ETL.9240.TOWR | 43249601 | PISMOBCH | LOS PADRES | 2021-07-26 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 43249601 |  | LATTICE STEEL TOWER | [9 empty] | 4576.4678
121800777 | B | LC | ETL.6280.POLE.WOOD | 44259127 | TABLEMTN | NORTH VALLEY | 2021-07-26 | 2021-09-22 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 4.1639e-06 | 695.9825
121816418 | E | LC | ETL.6220.POLE.NWOD | 45033612 | EUREKA | HUMBOLDT | 2021-07-29 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 45033612 | 2021-01-23 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-01-23 | Glass | Dead End |  |  |  |  | 0.13804
121820749 | E | LC | ETL.6280.POLE.WOOD | 40751734 | TABLEMTN | NORTH VALLEY | 2021-07-30 | 2021-11-16 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40751734 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 5.0586e-06 | 63.3304
121890712 | E | LC | ETL.1350.POLE.WDPS | 44512147 | TABLEMTN |  | 2021-05-29 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40657292 | 2012-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.012475 | 2918.4626 | 36.4087
118442559 | E | LC | ETL.5440.POLE.WDPS | 44558201 | TABLEMTN |  | 2020-01-18 | 2020-05-29 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118758398 | E | LC | ETL.4316.POLE.STPS | 44712238 | TABLEMTN | NORTH VALLEY | 2020-03-31 |  | ETL.4316 | PARADISE-TABLE MTN | Conductor-Steel | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 3 | Within Both | PEND | 44712219 | 2019-02-13 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0021453 | 1963.0586 | 4.2114
118899788 | E | LC | ETL.4391.POLE.NWOD | 40770880 | LAKEVLLE | SONOMA | 2020-04-09 | 2020-06-03 | ETL.4391 | GEYSERS #11-EAGLE ROCK | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40770880 | 1999-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 4.87e-05 | 4672.6953
118913550 | F | LC | ETL.6375.POLE.NWOD | 43196980 | SACTO | SACRAMENTO | 2020-04-11 |  | ETL.6375 | DRUM PH #2 TAP | GO95 / Anti Climb | Ground / Clearance | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43196980 |  | Lattice Steel Pole | DE - Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00015641 | 2056.7583
118914184 | E | LC | ETL.8210.POLE.WOOD | 40907084 | VICTOR | STOCKTON | 2020-04-10 | 2021-08-26 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40907084 | 1971-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.0064991 | 2859.6412
118934479 | E | LC | ETL.3180.INSL.NCER | 45125840 | CONCORD | EAST BAY | 2020-04-20 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40644346 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 1.3658e-06 | 95.76 | 0.00013079
118934479 | E | LC | ETL.3180.INSL.NCER | 45125840 | CONCORD | EAST BAY | 2020-04-20 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40644346 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-03-04 | Glass Silicone Coated | Dead End |  |  |  |  | 1.3658e-06 | 95.76 | 0.00013079
118988922 | F | LC | ETL.1400.POLE.STPS | 44379642 | VICTOR | YOSEMITE | 2020-05-01 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install] |  | Tier 3 | Within Both | PEND | 44379641 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.8951e-05 | 2626.426
119023441 | E | LC | ETL.9090.INSL | 40717170 | PISMOBCH | LOS PADRES | 2020-05-06 | 2021-05-20 | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40668407 |  | Single Wood Pole | FIG4W - Wood X Arm |  | Ceramic | Other |  |  |  |  | 0.0044192 | 1728.2214
119028144 | F | LC | ETL.4220.POLE.STPS | 44388369 | TABLEMTN |  | 2020-05-11 | 2020-06-26 | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Tier 3 | Within Both | COMP | 44388368 | 2016-11-28 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00088075 | 537.9951
119037562 | E | LC | ETL.6440.POLE.WOOD | 41144209 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-08-27 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41144209 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.00019823 | 6617.2612
119051964 | E | LC | ETL.6030.TOWR | 40648048 | MIDWAY | KERN | 2020-05-21 | 2021-03-11 | ETL.6030 | MIDWAY-WHIRLWIND | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648048 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 6.2715e-06 | 5624.5342
119060260 | F | LC | ETL.8650.POLE.NWOD | 44859210 | FRESNO | YOSEMITE | 2020-05-18 | 2021-08-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44859210 | 2019-11-18 | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-11-18 | Glass | Suspension |  |  |  |  | 0.010175 | 5319.3394
119093839 | F | LC | ETL.1720.POLE.STPS | 44893479 | MOSSLNDG | SAN JOSE | 2020-05-20 | 2021-10-04 | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44893446 | 2019-11-07 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.245e-08 | 1134.4898
119100942 | E | LC | ETL.8650.TOWR | 40584433 | FRESNO | YOSEMITE | 2020-06-02 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40584433 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.016128 | 6283.7788
119108622 | B | LC | ETL.5140.POLE.WDPS | 44552281 | SACTO | SACRAMENTO | 2020-05-20 | 2020-07-29 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119113182 | B | LC | ETL.8170.INSL | 40855869 | EUREKA | HUMBOLDT | 2020-06-04 | 2020-06-29 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827993 |  | Single Wood Pole | TPSRD - Tri Post & Susp Dead End |  | Ceramic | [5 empty] | 0.040402 | 0.065148
119119059 | E | LC | ETL.6490.POLE.WOOD | 40868924 | SACTO | SIERRA | 2020-06-02 | 2021-06-02 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119119384 | F | LC | ETL.7560.POLE.NWOD | 44263385 | SACTO | SIERRA | 2020-05-29 |  | ETL.7560 | WEIMAR #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44263385 |  | Light Duty Steel Pole | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.0075317 | 6059.3994
119130526 | F | LC | ETL.7270.POLE.WOOD | 41217706 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-07-19 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41217706 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.022372 | 2804.7642
119142129 | F | LC | ETL.8365.POLE.WOOD | 40912694 | EUREKA | HUMBOLDT | 2020-06-08 | 2021-04-30 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912694 |  | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 2021-04-27 | Glass | Dead End |  |  |  |  | 0.048093 | 5040.4707
119144405 | F | LC | ETL.7300.POLE.WOOD | 40650328 | TABLEMTN | NORTH VALLEY | 2020-06-03 |  | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40650328 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.00057827 | 537.9698
119165985 | E | LC | ETL.8300.POLE.WOOD | 40769401 | TABLEMTN | NORTH VALLEY | 2020-06-11 | 2021-07-23 | ETL.8300 | VOLTA-SOUTH | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40769401 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0079096 | 6175.3105
119166488 | E | LC | ETL.8170.POLE.WOOD | 44966204 | EUREKA | HUMBOLDT | 2020-06-15 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44966204 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Unknown | Unknown |  |  |  |  | 0.010693 | 2360.6118 | 25.2419
119188623 | E | LC | ETL.6979.POLE.WOOD | 40750295 | LAKEVLLE | SONOMA | 2020-06-19 | 2021-10-07 | ETL.6979 | MONTE RIO-FORT ROSS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.18188 | 1886.6401
119195017 | F | LC | ETL.6470.POLE.WOOD | 40912099 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40912099 | 1999-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.067109 | 142.5149
119195025 | E | LC | ETL.6470.POLE.WOOD | 40874718 | SACTO | SIERRA | 2020-06-22 | 2021-08-02 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.087783 | 142.4516
119197936 | F | LC | ETL.6470.POLE.WOOD | 40766626 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40766626 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.30563 | 189.9644
119199546 | F | LC | ETL.6470.POLE.WOOD | 40760745 | SACTO | SIERRA | 2020-06-23 | 2021-07-07 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760745 |  | Single Wood Pole | T2N | 2021-07-13 | Polymer | Post |  |  |  |  | 0.20217 | 158.2723
119201066 | E | LC | ETL.9340.POLE.NWOD | 44180722 | FRESNO | FRESNO | 2020-06-23 | 2020-08-06 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44180722 | 2015-06-18 | Light Duty Steel Pole | T-1 - Tri Post | 2015-06-18 | Non Ceramic | Post |  |  |  |  | 0.00082105 | 5445.5674
119201094 | E | LC | ETL.9340.POLE.NWOD | 43680879 | FRESNO | FRESNO | 2020-06-23 | 2020-09-09 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43680879 | 2015-06-15 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2016-06-15 | Porcelain | Post |  |  |  |  | 0.00027881 | 6552.9092
119202543 | B | LC | ETL.4220.POLE.STPS | 44388410 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-07-15 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue] |  | Tier 2 | Within Both | DLFL | 44388408 | 2016-12-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.2205e-05 | 822.7042
119231180 | E | LC | ETL.8290.POLE.WOOD | 40615924 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2021-04-21 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119290526 | E | LC | ETL.1400.INSL.NCER | 44815071 | VICTOR | STOCKTON | 2020-06-30 | 2021-05-10 | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44815070 | 2019-08-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2019-08-09 | Glass | Suspension |  |  |  |  | 4.4747e-05
119290526 | E | LC | ETL.1400.INSL.NCER | 44815071 | VICTOR | STOCKTON | 2020-06-30 | 2021-05-10 | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44815070 | 2019-08-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2019-08-09 | Glass | Suspension |  |  |  |  | 4.4747e-05
119292536 | E | LC | ETL.5440.POLE.WDPS | 44558390 | TABLEMTN |  | 2020-07-01 | 2020-08-31 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119303985 | E | LC | ETL.7300.POLE.NWOD | 44837825 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-08-17 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44837825 | 2019-03-25 | Light Duty Steel Pole | T2N | 2019-03-25 | Polymer | Post |  |  |  |  | 2.7375e-07 | 443.6193
119304514 | E | LC | ETL.1450.POLE.WDPS | 44552484 | SACTO | SACRAMENTO | 2020-07-01 | 2020-08-07 | ETL.1450 | DRUM-SUMMIT #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44551582 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.015408 | 31.7066
119308115 | B | LC | ETL.7140.POLE.WOOD | 40657316 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-26 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40657316 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | [5 empty] | 0.057284 | 4211.6216
119309301 | B | LC | ETL.4393.POLE.WDPS | 44552302 | SACTO | SACRAMENTO | 2020-07-01 | 2020-09-08 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119311051 | E | LC | ETL.7780.POLE.WOOD | 40660548 | LAKEVLLE | SONOMA | 2020-07-03 | 2021-04-15 | ETL.7780 | PHILO JCT-ELK | Jumper-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660548 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.00069792 | 3750.7092
119311220 | E | LC | ETL.8170.POLE.WDPS | 44565472 | EUREKA | HUMBOLDT | 2020-07-03 | 2021-08-16 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564173 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.008738 | 2589.7983
119317129 | F | LC | ETL.8170.POLE.WOOD | 40701884 | EUREKA | HUMBOLDT | 2020-07-06 | 2021-01-25 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40701884 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.020424 | 2085.287
119317857 | F | LC | ETL.1450.POLE.STPS | 44339722 | SACTO | SIERRA | 2020-07-02 | 2020-08-10 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44339720 | 2018-12-13 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 2.083e-05 | 1260.556
119324357 | E | LC | ETL.7300.POLE.WOOD | 40676503 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2020-11-17 | ETL.7300 | KILARC-DESCHUTES | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40676503 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00088451 | 2298.2134
119327196 | E | LC | ETL.8060.POLE.WOOD | 40652035 | SACTO | SIERRA | 2020-07-07 | 2021-04-28 | ETL.8060 | SPAULDING-SUMMIT | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40652035 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0091135 | 2547.2131
119331477 | A | LC | ETL.8990.INSL.CERA | 40727628 | FRESNO | FRESNO | 2020-07-08 | 2020-07-15 | ETL.8990 | MERCED FALLS-EXCHEQUER | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119332496 | E | LC | ETL.1810.POLE.WDPS | 44322462 | EUREKA | HUMBOLDT | 2020-07-07 | 2021-07-12 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322461 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.033005
119336045 | F | LC | ETL.8060.POLE.WOOD | 40701993 | SACTO | SIERRA | 2020-07-07 | 2021-05-04 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40701993 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0067454 | 31.7066
119341403 | E | LC | ETL.1430.TOWR | 40858065 | SACTO | SACRAMENTO | 2020-07-09 | 2021-03-03 | ETL.1430 | DRUM-RIO OSO #2 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40858065 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-03-20 | Glass | Dead End |  |  |  |  | 0.00028023 | 0.065152
119341819 | E | LC | ETL.8560.POLE.WOOD | 40606214 | PISMOBCH | LOS PADRES | 2020-07-08 | 2021-08-11 | ETL.8560 | CAYUCOS-CAMBRIA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119353361 | E | LC | ETL.6280.POLE.NWOD | 44688366 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-07-07 | ETL.6280 | CARIBOU #2 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44688366 | 2018-11-24 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-24 | Polymer | Post |  |  |  |  | 4.1476e-07 | 4065.6267
119370209 | F | LC | ETL.7630.POLE.WOOD | 40770568 | LAKEVLLE | SONOMA | 2020-07-14 | 2021-01-20 | ETL.7630 | MONTE RIO-FULTON | Guy Wire Mark /Indic-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40770568 | 1952-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.047428 | 36.4511
119374129 | E | LC | ETL.6280.POLE.WOOD | 40751769 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-10-04 | ETL.6280 | CARIBOU #2 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751769 |  | Single Wood Pole | TAP - Tri Arm Post | 2021-08-29 | Glass | Double Dead End |  |  |  |  | 6.9932e-05 | 4811.106 | 0.33645
119375023 | F | LC | ETL.7170.POLE.WOOD | 44871189 | LAKEVLLE | NORTH BAY | 2020-07-14 |  | ETL.7170 | IGNACIO-ALTO-SAUSALITO #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871189 | 2019-09-19 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2019-09-19 | Glass | Suspension |  |  |  |  | 0.29938 | 158.2261
119378093 | F | LC | ETL.8060.POLE.WOOD | 44349554 | SACTO | SACRAMENTO | 2020-07-15 | 2021-05-18 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44349554 | 2018-09-06 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-09-06 | Polymer | Post |  |  |  |  | 0.0043151 | 0.065152
119381958 | F | LC | ETL.6220.POLE.WOOD | 40826263 | EUREKA | HUMBOLDT | 2020-07-15 | 2021-10-26 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40826263 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.080547
119461733 | F | LC | ETL.7030.POLE.WOOD | 40770721 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-07-07 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770721 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.024468 | 126.76
119469970 | F | LC | ETL.7030.POLE.WOOD | 40667982 | TABLEMTN | NORTH VALLEY | 2020-07-17 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40667982 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.020063 | 0.06515
119477818 | F | LC | ETL.2060.POLE.WOOD | 40669458 | LAKEVLLE | SONOMA | 2020-07-20 |  | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40669458 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.19384 | 15.8807
119477848 | E | LC | ETL.2060.INSL | 40710164 | LAKEVLLE | HUMBOLDT | 2020-07-20 | 2021-08-12 | ETL.2060 | FORT BRAGG-ELK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119488866 | F | LC | ETL.6240.POLE.WOOD | 40665103 | MOSSLNDG | CENTRAL COAST | 2020-07-22 | 2021-01-12 | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40665103 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.12667 | 63.351
119505269 | F | LC | ETL.2060.POLE.WOOD | 40768468 | LAKEVLLE | SONOMA | 2020-07-24 |  | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40768468 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.14745 | 189.852
119521712 | F | LC | ETL.7572.POLE.WOOD | 40588794 | METCALF | SAN JOSE | 2020-07-29 |  | ETL.7572 | SAN BRUNO TAP | Guy Wire Mark /Indic-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40588794 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2020-10-23 | Glass Silicone Coated | Dead End |  |  |  |  | 0.0036141 | 0.066432
119529835 | E | LC | ETL.6220.POLE.WOOD | 40862501 | EUREKA | HUMBOLDT | 2020-07-30 | 2021-02-24 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40862501 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0055536 | 452.319
119557727 | E | LC | ETL.6220.POLE.WOOD | 40698342 | EUREKA | HUMBOLDT | 2020-08-04 | 2021-02-23 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Tie Wire-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | DLFL | 40698342 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.25534
119560348 | E | LC | ETL.7180.INSL.NCER | 40778801 | LAKEVLLE | NORTH BAY | 2020-08-04 | 2021-04-20 | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator | Contaminated | [Ground Wash, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750722 |  | Single Wood Pole | TP - Tri Pin |  | Non Ceramic | Pin |  |  |  |  | 9.7939e-06 | 126.9887
119568163 | E | LC | ETL.1450.POLE.WOOD | 44155564 | SACTO | SACRAMENTO | 2020-08-06 | 2020-09-03 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 1.959e-06 | 363.9416
119592362 | E | LC | ETL.8365.POLE.WOOD | 40912669 | EUREKA | HUMBOLDT | 2020-08-10 | 2021-02-03 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | DLFL | 40912669 |  | Single Wood Pole | DV-DE - Double Vertical Dead End | 2021-01-25 | Glass | Dead End |  |  |  |  | 0.04502
119602877 | E | LC | ETL.7930.POLE.WOOD | 40768291 | MOSSLNDG | CENTRAL COAST | 2020-08-11 |  | ETL.7930 | SALINAS-LAURELES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40768291 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0079716 | 47.5096 | 0.37873
119605325 | E | LC | ETL.7490.INSL.NCER | 44950913 | EUREKA | HUMBOLDT | 2020-08-12 | 2021-08-17 | ETL.7490 | MAPLE CREEK-HOOPA | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602126 |  | Single Wood Pole | DV-DE - Double Vertical Dead End | 2020-07-11 | Glass | Dead End |  |  |  |  | 0.012418 | 0.065148
119635887 | E | LC | ETL.8365.POLE.NWOD | 40906658 | EUREKA | HUMBOLDT | 2020-08-19 | 2021-03-24 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906658 | 2011-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.03384
119658791 | A | LC | ETL.6240.POLE.WOOD | 44425201 | MOSSLNDG | CENTRAL COAST | 2020-08-22 | 2020-10-01 | ETL.6240 | BURNS-LONE STAR #2 | Emergency-Wood | Other | [Replace, Completed] | Tier3 |  |  | COMP
119668702 | E | LC | ETL.1730.POLE.WDPS | 44413431 | MOSSLNDG | CENTRAL COAST | 2020-08-25 | 2020-08-26 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Damper-Steel | Missing | [Install] | Tier3 |  |  | DLFL
119721442 | E | LC | ETL.8240.POLE.WOOD | 40599125 | VICTOR | STOCKTON | 2020-07-28 | 2020-10-26 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40599125 | 1978-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.0010629 | 902.8336
119752880 | F | LC | ETL.7030.POLE.WOOD | 40876209 | TABLEMTN | NORTH VALLEY | 2020-08-14 | 2021-09-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876209 |  | Single Wood Pole | T-1 - Tri Post | 2019-09-09 | Polymer | Post |  |  |  |  | 0.0062499 | 31.7022
119753123 | F | LC | ETL.7590.POLE.WDPS | 44944229 | MOSSLNDG | CENTRAL COAST | 2020-08-06 | 2021-01-12 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119790473 | E | LC | ETL.1240.POLE.STPS | 44960473 | TABLEMTN | NORTH VALLEY | 2020-07-30 |  | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44960356 | 2020-04-02 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.3941e-08 | 2046.0615 | 0.00011037
119804954 | F | LC | ETL.6280.POLE.NWOD | 44677444 | TABLEMTN | NORTH VALLEY | 2020-08-07 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44677444 | 2018-11-24 | Light Duty Steel Pole | T2N | 2018-11-24 | Polymer | Post |  |  |  |  | 1.9182e-07 | 63.3304
119805916 | E | LC | ETL.1073.POLE.WDPS | 44962148 | VICTOR | YOSEMITE | 2020-09-23 | 2021-08-17 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119805961 | F | LC | ETL.1073.POLE.STPS | 44962143 | VICTOR | STOCKTON | 2020-09-23 |  | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40760734 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.2415e-06 | 110.769
119816130 | F | LC | ETL.7290.POLE.WOOD | 40601998 | TABLEMTN | NORTH VALLEY | 2020-08-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40601998 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.010751 | 158.265
119818288 | F | LC | ETL.6980.POLE.NWOD | 44311165 | LAKEVLLE | HUMBOLDT | 2020-09-11 |  | ETL.6980 | FORT ROSS-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44311165 |  | Light Duty Steel Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.034856 | 110.872
119850928 | F | LC | ETL.1710.POLE | 44513696 | MOSSLNDG | CENTRAL COAST | 2020-09-17 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | PEND | 44512256 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00078134 | 63.3245
119939814 | E | LC | ETL.8060.POLE.WOOD | 44326147 | SACTO | SIERRA | 2020-10-22 | 2021-04-28 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44326147 | 2016-06-13 | Single Wood Pole | TCDE - Tap Construction Dead End | 2016-06-13 | Polymer | Dead End |  |  |  |  | 0.0099281 | 2547.2131
120011406 | E | LC | ETL.6020.TOWR | 40595123 | TABLEMTN | NORTH VALLEY | 2020-11-06 | 2021-07-26 | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40595123 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00013386 | 221.5655
120097806 | F | LC | ETL.3180.TOWR | 40594270 | CONCORD | EAST BAY | 2020-11-16 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40594270 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.5124e-05 | 416.7626 | 0.0063033
120097806 | F | LC | ETL.3180.TOWR | 40594270 | CONCORD | EAST BAY | 2020-11-16 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40594270 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-03-27 | Glass Silicone Coated | Suspension |  |  |  |  | 1.5124e-05 | 416.7626 | 0.0063033
120110303 | E | LC | ETL.5630.TOWR | 40867805 | TABLEMTN | NORTH VALLEY | 2020-11-23 |  | ETL.5630 | ROCK CREEK-POE | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40867805 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 2.4032e-09 | 63.3704 | 1.5229e-07
120110505 | E | LC | ETL.6280.POLE.WOOD | 40614758 | TABLEMTN | NORTH VALLEY | 2020-11-20 |  | ETL.6280 | CARIBOU #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40614758 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00082973 | 174.0445 | 0.14441
120133555 | F | LC | ETL.6480.POLE.WOOD | 40873636 | SACTO | NORTH VALLEY | 2020-10-23 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | PEND
120191297 | E | LC | ETL.4430.INSL | 40634238 | TABLEMTN | NORTH VALLEY | 2020-12-14 | 2021-08-22 | ETL.4430 | BUCKS CREEK-ROCK CREEK-CRESTA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120232314 | F | LC | ETL.6240.POLE.NWOD | 44802689 | MOSSLNDG | CENTRAL COAST | 2020-11-20 | 2021-09-27 | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44802689 | 2019-05-27 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-05-27 | Polymer | Dead End |  |  |  |  | 0.060472 | 294.3728
120639064 | E | LC | ETL.2660.TOWR | 40681902 | SACTO | SIERRA | 2021-03-11 | 2021-06-11 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40681902 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 1.2339e-09 | 0.066432
120639064 | E | LC | ETL.2660.TOWR | 40681902 | SACTO | SIERRA | 2021-03-11 | 2021-06-11 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40681902 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Ceramic | Suspension |  |  |  |  | 1.2339e-09 | 0.066432
120705797 | E | LC | ETL.7140.POLE.WOOD | 40770917 | LAKEVLLE | SONOMA | 2021-03-25 | 2021-09-14 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.14072 | 348.1174
120707755 | E | LC | ETL.1350.POLE.STPS | 44409305 | TABLEMTN | NORTH VALLEY | 2021-03-29 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44409303 | 2017-10-27 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0001304 | 221.5655
120712191 | A | LC | ETL.8360.POLE.NWOD | 40600468 | LAKEVLLE | SONOMA | 2021-03-30 | 2021-04-01 | ETL.8360 | LAYTONVILLE-WILLITS | Emergency | Storm Related | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600468 | 2010-01-01 | Tubular Steel Pole | DV-DE - Double Vertical Dead End |  | Non Ceramic | [5 empty] | 0.00016528 | 253.1613
120714400 | E | LC | ETL.1350.POLE.WDPS | 44513789 | TABLEMTN | NORTH VALLEY | 2021-03-30 | 2021-09-20 | ETL.1350 | CRAG VIEW-CASCADE | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44512234 |  | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.054417 | 94.9939
120717713 | E | LC | ETL.4590.INSL.CERA | 40638292 | TABLEMTN | NORTH VALLEY | 2021-03-31 |  | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40608860 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | Suspension |  |  |  |  | 7.8825e-07 | 4513.7266 | 0.0035579
120724137 | E | LC | ETL.6750.POLE.STPS | 44751949 | TABLEMTN | NORTH VALLEY | 2021-04-01 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44751908 | 2019-04-14 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 2.5101e-06 | 351.3014 | 0.0008818
120727397 | E | LC | ETL.7390.POLE.WDPS | 44412027 | LAKEVLLE | SONOMA | 2021-04-01 | 2021-06-25 | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44412025 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.022665 | 1344.7017
120734185 | E | LC | ETL.1890.INSL.CERA | 40893569 | FRESNO | FRESNO | 2021-04-01 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40870015 | 1982-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1982-01-01 | Porcelain | Suspension |  |  |  |  | 0.00011004 | 6141.7236 | 0.67586
120766477 | B | LC | ETL.3190.TOWR | 40910306 | TABLEMTN | NORTH VALLEY | 2021-04-08 | 2021-06-25 | ETL.3190 | CARIBOU-PALERMO | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910306 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2017-07-28 | Ceramic | Suspension |  |  |  |  | 0.0080089 | 1407.9186
120842390 | E | LC | ETL.5540.TOWR | 40762689 | TABLEMTN | NORTH VALLEY | 2021-04-12 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762689 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 3.1342e-06 | 552.2716 | 0.0017309
120843324 | E | LC | ETL.6500.POLE.WOOD | 40767121 | SACTO | SIERRA | 2021-04-19 | 2021-09-01 | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40767121 |  | Single Wood Pole | T2N | 2018-10-18 | Polymer | Post |  |  |  |  | 0.00347 | 350.8019
120866893 | E | LC | ETL.5510.TOWR | 40810214 | CONCORD | DIABLO | 2021-04-22 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810214 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Dead End |  |  |  |  | 2.1994e-06 | 5366.5112 | 0.011803
120873131 | B | LC | ETL.9250.POLE.NWOD | 40807902 | MIDWAY | KERN | 2021-04-23 | 2021-05-13 | ETL.9250 | TEJON-LEBEC | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40807902 | 1966-01-01 | Tubular Steel Pole | T-1 - Tri Post |  | Non Ceramic | Pin |  |  |  |  | 0.0026275 | 3471.7266
120873858 | F | LC | ETL.6470.POLE.WOOD | 40869634 | SACTO | SACRAMENTO | 2021-04-23 | 2021-08-17 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40869634 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 2021-08-07 | Polymer | Post |  |  |  |  | 0.0198 | 5778.0215
120884472 | E | LC | ETL.7270.POLE.NWOD | 44649333 | TABLEMTN | NORTH VALLEY | 2021-04-26 | 2021-07-28 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44649333 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.0019805 | 1347.3177
120903274 | F | LC | ETL.4450.TOWR | 40814656 | CONCORD | DIABLO | 2021-04-29 |  | ETL.4450 | CASTRO VALLEY-NEWARK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40814656 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.7005e-05 | 633.226 | 0.0171
120903274 | F | LC | ETL.4450.TOWR | 40814656 | CONCORD | DIABLO | 2021-04-29 |  | ETL.4450 | CASTRO VALLEY-NEWARK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40814656 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 2.7005e-05 | 633.226 | 0.0171
120904504 | E | LC | ETL.4870.TOWR | 40761930 | FRESNO | FRESNO | 2021-04-29 |  | ETL.4870 | HELMS-GREGG #1 | Road | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40761930 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 5.6918e-09 | 5176.6899
120911529 | E | LC | ETL.5930.TOWR | 40763001 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40763001 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-30 | Glass | Suspension |  |  |  |  | 8.5616e-09 | 302.6878 | 2.5915e-06
120911529 | E | LC | ETL.5930.TOWR | 40763001 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40763001 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-01 | Ceramic | Suspension |  |  |  |  | 8.5616e-09 | 302.6878 | 2.5915e-06
120918743 | E | LC | ETL.7820.POLE.WOOD | 40656746 | LAKEVLLE | SONOMA | 2021-05-02 |  | ETL.7820 | POTTER VALLEY-WILLITS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40656746 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | [5 empty] | 0.00032172 | 253.2372 | 0.081472
120919618 | E | LC | ETL.5250.TOWR | 40756557 | CONCORD | DIABLO | 2021-05-01 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40756557 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 2.7127e-07 | 506.1398 | 0.0001373
120928697 | E | LC | ETL.4340.INSL | 40726149 | LAKEVLLE | NORTH BAY | 2021-05-04 |  | ETL.4340 | BAHIA-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40683889 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.8274e-09 | 395.7004 | 1.5145e-06
120929177 | F | LC | ETL.5300.TOWR | 40592063 | PISMOBCH | LOS PADRES | 2021-05-04 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40592063 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.5307e-05 | 1915.7988 | 0.0868
120936095 | E | LC | ETL.7000.POLE.WDPS | 44410059 | TABLEMTN | NORTH VALLEY | 2021-05-05 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44410058 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0011121 | 15.8815 | 0.017662
120937501 | B | LC | ETL.4550.TOWR | 40817922 | TABLEMTN | NORTH VALLEY | 2021-05-04 | 2021-06-17 | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817922 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.3661e-07 | 6331.7764
120994788 | E | LC | ETL.1810.POLE.WDPS | 44322632 | EUREKA | HUMBOLDT | 2021-05-08 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44322631 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0020141 | 63.3274 | 0.12755
121319064 | E | LC | ETL.5540.TOWR | 40873454 | TABLEMTN | NORTH VALLEY | 2021-04-21 |  | ETL.5540 | POE-RIO OSO | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40873454 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 1.0063e-06 | 4292.0464 | 0.0043191
121322149 | E | LC | ETL.4850.INSL | 40605265 | FRESNO | FRESNO | 2021-04-21 |  | ETL.4850 | HAAS-MCCALL | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40581322 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1957-01-01 | Ceramic | Double Dead End |  |  |  |  | 7.0557e-06 | 6837.5508 | 0.048244
121336911 | F | LC | ETL.3500.TOWR | 40856706 | VICTOR | STOCKTON | 2021-04-26 | 2021-10-04 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40856706 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 4.5382e-05 | 4114.0205
121351703 | F | LC | ETL.8450.POLE.WOOD | 41148779 | MIDWAY | KERN | 2021-04-27 |  | ETL.8450 | ARCO-POLONIO PASS PP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41148779 | 1994-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1994-01-01 | Porcelain | Post |  |  |  |  | 6.7587e-05 | 7584.0327
121355122 | E | LC | ETL.1820.POLE.WDPS | 44560596 | EUREKA | HUMBOLDT | 2021-05-18 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560105 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.19497 | 0.065152 | 0.012703
121356001 | F | LC | ETL.1250.POLE.NWOD | 40748514 | FRESNO | YOSEMITE | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40748514 |  | Lattice Steel Pole | SUSP - Suspension (TWR) |  | Ceramic | [5 empty] | 3.9861e-06 | 5129.5112
121383975 | F | LC | ETL.1820.POLE.STPS | 44395396 | EUREKA | HUMBOLDT | 2021-05-22 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395395 | 2020-03-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00030068 | 237.3869
121384389 | E | LC | ETL.6760.POLE.WOOD | 40824338 | SACTO | SIERRA | 2021-05-12 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40824338 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Unknown |  |  |  |  | 0.047629 | 31.7022 | 1.5099
121385542 | E | LC | ETL.6470.POLE.WOOD | 40593287 | SACTO | SIERRA | 2021-05-14 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40593287 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.014808 | 569.5315 | 8.4335
121392068 | F | LC | ETL.1430.TOWR | 40814408 | SACTO | SIERRA | 2021-05-15 | 2021-06-14 | ETL.1430 | DRUM-RIO OSO #2 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40814408 | 1913-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-07-09 | Glass | Dead End |  |  |  |  | 0.003201 | 142.4642
121392200 | E | LC | ETL.6690.POLE.WOOD | 40814225 | SACTO | SIERRA | 2021-05-14 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40814225 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.14874 | 142.4769 | 21.1924
121398117 | E | LC | ETL.6950.POLE.NWOD | 44174902 | SACTO | SIERRA | 2021-05-19 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44174902 |  | Light Duty Steel Pole | DDE - Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.058515 | 2360.4771 | 138.1227
121409218 | E | LC | ETL.6640.POLE.WOOD | 40615977 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40615977 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.050916 | 2107.8877 | 107.3242
121419813 | E | LC | ETL.6470.INSL.CERA | 40639165 | SACTO | SACRAMENTO | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40611195 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.58599 | 110.8102 | 64.9333
121422387 | F | LC | ETL.1400.POLE.STPS | 44840547 | VICTOR | YOSEMITE | 2021-05-25 | 2021-06-11 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44840521 | 2019-09-24 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.8782e-05 | 158.2923
121437896 | E | LC | ETL.5140.POLE.WDPS | 44557707 | SACTO | SACRAMENTO | 2021-05-29 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44553947 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0061619 | 387.6186 | 2.3885
121447200 | E | LC | ETL.1820.INSL.CERA | 40679216 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562409 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.060065
121447200 | E | LC | ETL.1820.INSL.CERA | 40679216 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562409 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.060065
121449878 | B | LC | ETL.8360.POLE.NWOD | 40656795 | LAKEVLLE | SONOMA | 2021-06-03 | 2021-07-07 | ETL.8360 | LAYTONVILLE-WILLITS | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656795 | 2010-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 1.7149e-05 | 458.8272
121451838 | E | LC | ETL.5630.INSL.CERA | 40883786 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5630 | ROCK CREEK-POE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40861901 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Ceramic | Dead End |  |  |  |  | 1.1072e-05 | 5252.52 | 0.058157
121453294 | F | LC | ETL.1820.POLE.STPS | 44194941 | EUREKA | HUMBOLDT | 2021-05-28 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44194940 | 2014-09-20 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0010563 | 5288.2002
121470332 | F | LC | ETL.2710.POLE.NWOD | 45114356 | CONCORD | DIABLO | 2021-06-03 |  | ETL.2710 | MORAGA-CLAREMONT #2 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45114356 |  | Lattice Steel Pole |  |  | Ceramic | Suspension | [5 empty] | 1568.8029
121481745 | E | LC | ETL.5140.POLE.WDPS | 44552278 | SACTO | SACRAMENTO | 2021-06-07 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44551664 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00030903 | 1086.9597 | 0.3359
121482738 | E | LC | ETL.5140.POLE.STPS | 44411581 | SACTO | SACRAMENTO | 2021-05-29 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44411579 | 2016-10-24 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.273e-06 | 83.9184 | 0.00019075
121491202 | E | LC | ETL.8060.SWIT | 41158200 | SACTO | SACRAMENTO | 2021-06-07 |  | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | PEND | [8 empty] | KPF | ARCHING HORNS ONLY | Manual
121492642 | F | LC | ETL.4750.TOWR | 40761757 | LAKEVLLE | SONOMA | 2021-06-01 | 2021-08-11 | ETL.4750 | GEYSERS #12-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40761757 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 6.0933e-09 | 989.7274
121492642 | F | LC | ETL.4750.TOWR | 40761757 | LAKEVLLE | SONOMA | 2021-06-01 | 2021-08-11 | ETL.4750 | GEYSERS #12-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40761757 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-02-05 | Glass | Dead End |  |  |  |  | 6.0933e-09 | 989.7274
121496865 | F | LC | ETL.1401.POLE.STPS | 44161086 | VICTOR | STOCKTON | 2021-06-01 |  | ETL.1401 | BEARDSLEY TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44161085 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.5075e-05 | 253.2337
121498798 | E | LC | ETL.9330.TOWR | 40606321 | FRESNO | FRESNO | 2021-06-03 |  | ETL.9330 | WISHON-COPPERMINE | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40606321 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Glass | [5 empty] | 0.002407 | 6919.8752 | 16.656
121519460 | F | LC | ETL.5650.TOWR | 40864683 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40864683 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 7.3045e-06 | 375.8978 | 0.0027457
121519688 | F | LC | ETL.1440.POLE.STPS | 44338174 | SACTO | SIERRA | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44338173 | 2018-09-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.2678e-06 | 94.9894
121523655 | E | LC | ETL.1430.TOWR | 40805323 | SACTO | SIERRA | 2021-06-07 |  | ETL.1430 | DRUM-RIO OSO #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40805323 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical |  | Ceramic | Post |  |  |  |  | 0.025679 | 3797.0496 | 97.5063
121524143 | F | LC | ETL.4040.POLE.WDPS | 44561371 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44552624 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.006359 | 4481.9893
121530910 | F | LC | ETL.4780.POLE.NWOD | 44386966 | LAKEVLLE | SONOMA | 2021-06-09 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44386966 | 2020-07-05 | Tubular Steel Pole | DDE - Double Dead End | 2020-07-05 | Ceramic | Dead End |  |  |  |  | 0.00049578 | 190.1994
121533394 | B | LC | ETL.5390.INSL.NCER | 45113191 | TABLEMTN | NORTH VALLEY | 2021-06-13 | 2021-08-17 | ETL.5390 | PIT #1-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40816150 | 1924-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-01-13 | Glass | Dead End |  |  |  |  | 7.8535e-08 | 3531.9717
121534285 | E | LC | ETL.6480.POLE.WOOD | 40598490 | SACTO | SIERRA | 2021-06-09 | 2021-09-01 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40598490 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | Suspension |  |  |  |  | 0.063158 | 113.9584
121535846 | E | LC | ETL.7550.POLE.WOOD | 40600354 | LAKEVLLE | HUMBOLDT | 2021-06-10 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40600354 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-06-14 | Polymer | Dead End |  |  |  |  | 0.00012125 | 15.8807 | 0.0019255
121536575 | E | LC | ETL.5650.TOWR | 40608939 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40608939 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-09-19 | Ceramic | Suspension |  |  |  |  | 6.3678e-08 | 4785.1641 | 0.00030471
121542077 | E | LC | ETL.6220.POLE.WOOD | 40586730 | EUREKA | HUMBOLDT | 2021-06-15 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40586730 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.26093 | 1028.302 | 268.3136
121544203 | F | LC | ETL.1820.POLE.STPS | 44395539 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395538 | 2020-03-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0082312 | 656.6579
121547743 | F | LC | ETL.1820.POLE.NWOD | 45009258 | EUREKA | HUMBOLDT | 2021-06-13 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45009258 | 2020-11-18 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2020-06-02 | Glass | Suspension |  |  |  |  | 0.016224 | 94.9756
121554099 | E | LC | ETL.6750.INSL.CERA | 40893124 | TABLEMTN |  | 2021-06-17 |  | ETL.6750 | DELTA-MTN GATE JCT | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564331 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.017053
121554099 | E | LC | ETL.6750.INSL.CERA | 40893124 | TABLEMTN |  | 2021-06-17 |  | ETL.6750 | DELTA-MTN GATE JCT | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564331 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.017053
121556535 | F | LC | ETL.6750.POLE.WDPS | 44374912 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44374911 | 2012-08-04 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014268 | 31.7081
121560463 | E | LC | ETL.4392.TOWR | 41129315 | LAKEVLLE | SONOMA | 2021-06-14 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129315 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-03-04 | Glass | Dead End |  |  |  |  | 0.0017387 | 2235.5632 | 3.887
121560463 | E | LC | ETL.4392.TOWR | 41129315 | LAKEVLLE | SONOMA | 2021-06-14 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129315 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.0017387 | 2235.5632 | 3.887
121562216 | F | LC | ETL.7550.POLE.WDPS | 44211135 | LAKEVLLE |  | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44211134 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00062638 | 110.7947 | 0.069399
121564078 | E | LC | ETL.8250.POLE.WOOD | 40908876 | VICTOR | STOCKTON | 2021-06-17 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40908876 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.0016396 | 2614.054 | 4.2859
121565519 | E | LC | ETL.6020.TOWR | 40870732 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40870732 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.9526e-07 | 775.7971 | 0.00015148
121568388 | E | LC | ETL.6720.POLE.WDPS | 44949092 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 42578815 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0022315 | 174.0849 | 0.38846
121584286 | E | LC | ETL.4050.POLE.WDPS | 44558327 | LAKEVLLE | SONOMA | 2021-06-22 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44557855 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 2.6031e-05 | 1614.755 | 0.042034
121587271 | E | LC | ETL.1372.POLE.WDPS | 44726496 | PISMOBCH | LOS PADRES | 2021-06-23 |  | ETL.1372 | MANVILLE TAP | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44283672 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00032699 | 4036.8325 | 1.32
121591550 | F | LC | ETL.6650.POLE.WDPS | 44386946 | TABLEMTN | NORTH VALLEY | 2021-06-23 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44386944 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0012209 | 0.065157 | 7.9549e-05
121655253 | A | LC | ETL.6750.POLE.WDPS | 44561324 | TABLEMTN |  | 2021-07-01 | 2021-07-29 | ETL.6750 | DELTA-MTN GATE JCT | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
121659365 | B | LC | ETL.8264.POLE.WDPS | 44255307 | VICTOR | STOCKTON | 2021-07-02 | 2021-09-07 | ETL.8264 | VALLEY SPRINGS-CLAY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP | [12 empty] | 6185.1016
121662828 | F | LC | ETL.6230.POLE.WOOD | 40876706 | MOSSLNDG | CENTRAL COAST | 2021-07-01 |  | ETL.6230 | BURNS-LONE STAR #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40876706 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Ceramic | Post |  |  |  |  | 0.1655 | 31.7081
121684463 | F | LC | ETL.9040.POLE.WOOD | 40690997 | MIDWAY | KERN | 2021-07-08 |  | ETL.9040 | TULE-SPRINGVILLE | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 |  |  | PEND | [11 empty] | 7.5644e-05 | 1301.3602
121705242 | E | LC | ETL.1710.POLE.WDPS | 44510587 | MOSSLNDG | CENTRAL COAST | 2021-07-01 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44509645 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0006406 | 83.2264 | 0.053315
121741746 | F | LC | ETL.9250.POLE.NWOD | 44359325 | MIDWAY | KERN | 2021-07-14 | 2021-08-17 | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44359325 | 2016-11-20 | Light Duty Steel Pole | T-1 - Tri Post | 2016-11-20 | Polymer | Post |  |  |  |  | 0.0016618 | 5387.1509
121741914 | E | LC | ETL.7060.POLE.WDPS | 45099478 | METCALF | PENINSULA | 2021-07-14 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42564724 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0023905 | 412.0099 | 0.9849
121742008 | F | LC | ETL.9340.POLE.NWOD | 45078773 | FRESNO | YOSEMITE | 2021-07-12 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45078773 | 2021-04-12 | Light Duty Steel Pole | T-1 - Tri Post | 2021-04-21 | Polymer | Post |  |  |  |  | 0.0012283 | 6923.0002
121781444 | E | LC | ETL.8360.INSL.CERA | 40779315 | LAKEVLLE |  | 2021-07-20 |  | ETL.8360 | LAYTONVILLE-WILLITS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44412052 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 0.0069193
121781444 | E | LC | ETL.8360.INSL.CERA | 40779315 | LAKEVLLE |  | 2021-07-20 |  | ETL.8360 | LAYTONVILLE-WILLITS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44412052 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 0.0069193
121781444 | E | LC | ETL.8360.INSL.CERA | 40779315 | LAKEVLLE |  | 2021-07-20 |  | ETL.8360 | LAYTONVILLE-WILLITS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44412052 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Suspension |  |  |  |  | 0.0069193
121786257 | E | LC | ETL.7390.POLE.WOOD | 40861064 | LAKEVLLE | HUMBOLDT | 2021-07-23 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40861064 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.095711 | 2515.2839 | 240.7396
121815724 | E | LC | ETL.7060.POLE.WOOD | 40612338 | METCALF | PENINSULA | 2021-07-28 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40612338 |  | Single Wood Pole | 3P DV - 3 Pole Double Vertical |  | Non Ceramic | Other |  |  |  |  | 0.00023691 | 1060.2281 | 0.25118
121821006 | B | LC | ETL.6290.POLE.WOOD | 40666904 | TABLEMTN | NORTH VALLEY | 2021-07-30 | 2021-09-21 | ETL.6290 | CARIBOU-PLUMAS JCT | Emergency | Fire | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.092518 | 1376.0835
121823826 | E | LC | ETL.1350.INSL | 40850633 | TABLEMTN |  | 2021-07-30 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40821763 |  | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.023299
121823826 | E | LC | ETL.1350.INSL | 40850633 | TABLEMTN |  | 2021-07-30 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40821763 |  | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.023299
122014634 | E | LC | ETL.6750.INSL.CERA | 44245093 | TABLEMTN | NORTH VALLEY | 2021-09-08 |  | ETL.6750 | DELTA-MTN GATE JCT | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44245087 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 3.7661e-05
122014634 | E | LC | ETL.6750.INSL.CERA | 44245093 | TABLEMTN | NORTH VALLEY | 2021-09-08 |  | ETL.6750 | DELTA-MTN GATE JCT | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44245087 | 2017-06-16 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 3.7661e-05
122033661 | F | LC | ETL.4440.POLE.NWOD | 44190873 | TABLEMTN | NORTH VALLEY | 2021-09-03 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44190873 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 4.623e-05 | 1804.4395
122058171 | E | LC | ETL.4780.INSL.NCER | 45129014 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129358 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 1.8675e-05 | 3897.7966 | 0.07279
122058171 | E | LC | ETL.4780.INSL.NCER | 45129014 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129358 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 1.8675e-05 | 3897.7966 | 0.07279
122063956 | E | LC | ETL.4780.INSL | 40790607 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40760444 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.0038669 | 348.2342 | 1.3466
122432120 | E | LC | ETL.2740.TOWR | 40687327 | CONCORD | DIABLO | 2021-12-01 |  | ETL.2740 | MORAGA-OAKLAND #3 | Non-Routine Patrol | Investigate | [Ground Patrol] | Tier2 | Tier 2 | HFRA Removal | PEND | 40687327 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1960-01-01 | Polymer | Suspension |  |  |  |  | 2.5235e-05 | 0.065147
118428033 | A | LC | ETL.6979.POLE.WOOD | 40769836 | LAKEVLLE | SONOMA | 2020-01-10 | 2020-02-05 | ETL.6979 | MONTE RIO-FORT ROSS | SCADA-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40769836 | 1984-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 2010-01-01 | Polymer | Suspension |  |  |  |  | 0.018051 | 921.0253
118441833 | A | LC | ETL.1110.TOWR | 40759205 | EUREKA | HUMBOLDT | 2020-01-17 | 2020-02-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759205 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-08-29 | Ceramic | Suspension |  |  |  |  | 0.00028317 | 79.1724
118441833 | A | LC | ETL.1110.TOWR | 40759205 | EUREKA | HUMBOLDT | 2020-01-17 | 2020-02-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759205 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-07-20 | Ceramic | Suspension |  |  |  |  | 0.00028317 | 79.1724
118473404 | E | LC | ETL.4750.INSL.CERA | 40612434 | LAKEVLLE |  | 2020-01-21 | 2020-04-03 | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 41129211 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-12-16 | Glass | Suspension |  |  |  |  | 0.0020124 | 5004.0796
118473404 | E | LC | ETL.4750.INSL.CERA | 40612434 | LAKEVLLE |  | 2020-01-21 | 2020-04-03 | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 41129211 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.0020124 | 5004.0796
118576591 | B | LC | ETL.5930.INSL.NCER | 44806741 | CONCORD |  | 2020-02-25 | 2020-04-01 | ETL.5930 | PARKWAY-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873496 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-30 | Glass | Suspension |  |  |  |  | 4.3582e-09 | 1692.6119
118576591 | B | LC | ETL.5930.INSL.NCER | 44806741 | CONCORD |  | 2020-02-25 | 2020-04-01 | ETL.5930 | PARKWAY-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873496 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 4.3582e-09 | 1692.6119
118591890 | E | LC | ETL.3180.TOWR | 40644346 | CONCORD | DIABLO | 2020-02-27 | 2020-05-21 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40644346 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 1.3658e-06 | 95.76
118591890 | E | LC | ETL.3180.TOWR | 40644346 | CONCORD | DIABLO | 2020-02-27 | 2020-05-21 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40644346 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-03-04 | Glass Silicone Coated | Dead End |  |  |  |  | 1.3658e-06 | 95.76
118957086 | F | LC | ETL.4750.TOWR | 40814642 | LAKEVLLE | SONOMA | 2020-04-28 | 2021-09-02 | ETL.4750 | GEYSERS #12-FULTON | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40814642 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-05-14 | Glass | Dead End |  |  |  |  | 3.2565e-06 | 2470.457
118957086 | F | LC | ETL.4750.TOWR | 40814642 | LAKEVLLE | SONOMA | 2020-04-28 | 2021-09-02 | ETL.4750 | GEYSERS #12-FULTON | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40814642 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2020-02-13 | Glass | Dead End |  |  |  |  | 3.2565e-06 | 2470.457
118958803 | E | LC | ETL.5430.POLE.WDPS | 44561261 | TABLEMTN | NORTH VALLEY | 2020-04-28 | 2020-07-08 | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118992051 | F | LC | ETL.5790.TOWR | 40811205 | VICTOR | STOCKTON | 2020-04-27 | 2021-06-01 | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40811205 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 2.548e-06 | 237.591
119030586 | E | LC | ETL.6980.POLE.WOOD | 40821495 | LAKEVLLE | HUMBOLDT | 2020-05-07 | 2021-06-22 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40821495 | 1986-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2010-01-01 | Polymer | Suspension |  |  |  |  | 0.21831 | 15.8873
119042209 | E | LC | ETL.6950.POLE.NWOD | 44922626 | SACTO | SIERRA | 2020-05-12 |  | ETL.6950 | GOLD HILL #1 | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44922626 | 2020-05-08 | Light Duty Steel Pole | SV-1B - Single Vertical Light Angle BR | 2020-05-08 | Glass | Suspension |  |  |  |  | 0.0037811 | 1313.0015 | 4.9646
119043143 | E | LC | ETL.6440.POLE.WOOD | 40875733 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-06-03 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40875733 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.006138 | 3534.6604
119044624 | A | LC | ETL.1420.TOWR | 40865482 | SACTO | SACRAMENTO | 2020-05-19 | 2020-06-25 | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40865482 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-05-20 | Glass | Suspension |  |  |  |  | 0.00056839 | 15.8837
119044624 | A | LC | ETL.1420.TOWR | 40865482 | SACTO | SACRAMENTO | 2020-05-19 | 2020-06-25 | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40865482 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.00056839 | 15.8837
119101701 | F | LC | ETL.7560.POLE.WOOD | 40693659 | SACTO | SIERRA | 2020-05-20 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40693659 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.01386 | 3306.2222
119108727 | E | LC | ETL.2540.POLE.WDPS | 44401547 | MOSSLNDG | CENTRAL COAST | 2020-05-20 | 2021-01-25 | ETL.2540 | METCALF-GREEN VALLEY | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44401546 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.019632 | 158.2797
119110334 | F | LC | ETL.2540.POLE.WDPS | 44401541 | MOSSLNDG | CENTRAL COAST | 2020-05-21 | 2021-10-06 | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44401540 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.009301 | 1927.4977
119113803 | E | LC | ETL.6760.POLE.WOOD | 40766643 | SACTO | SIERRA | 2020-05-28 | 2021-03-17 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40766643 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.054974 | 949.3081
119115581 | F | LC | ETL.6320.POLE.WOOD | 40598447 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40598447 | 1999-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Pin |  |  |  |  | 0.0029737 | 271.6997
119117153 | E | LC | ETL.7290.POLE.WOOD | 40771266 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-02-26 | ETL.7290 | KILARC-CEDAR CREEK | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40771266 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0028951 | 1744.4635
119117387 | F | LC | ETL.1400.POLE.NWOD | 44384140 | VICTOR | YOSEMITE | 2020-05-27 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44384140 | 2017-08-17 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 4.7361e-05 | 965.199
119118071 | F | LC | ETL.5640.TOWR | 40591305 | TABLEMTN | NORTH VALLEY | 2020-05-28 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40591305 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 8.3718e-09 | 570.8813 | 4.7793e-06
119118871 | F | LC | ETL.6720.POLE.WOOD | 40675469 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40675469 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 2.4906e-05 | 237.6179
119119534 | E | LC | ETL.8650.TOWR | 40859252 | FRESNO | YOSEMITE | 2020-06-02 | 2021-06-29 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40859252 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0078722 | 4649.6255
119125888 | F | LC | ETL.6280.POLE.WOOD | 40751732 | TABLEMTN | NORTH VALLEY | 2020-06-03 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40751732 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 3.099e-06 | 15.8815
119127328 | E | LC | ETL.1050.INSL.CERA | 40831207 | FRESNO | FRESNO | 2020-05-27 | 2021-08-02 | ETL.1050 | BALCH-SANGER | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40806885 | 1923-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1923-01-01 | Porcelain | Dead End |  |  |  |  | 0.001214 | 6331.5771
119144650 | E | LC | ETL.6520.POLE.WOOD | 40770756 | SACTO | SIERRA | 2020-06-03 | 2021-06-23 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770756 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0050688 | 5004.7632
119166508 | B | LC | ETL.6280.POLE.WOOD | 44217540 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2020-06-24 | ETL.6280 | CARIBOU #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44217540 | 2014-11-25 | Single Wood Pole | T2N | 2014-11-25 | Non Ceramic | Post |  |  |  |  | 7.5925e-05 | 5950.0312
119172589 | E | LC | ETL.8170.POLE.WDPS | 44565511 | EUREKA | HUMBOLDT | 2020-06-12 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564266 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.079393 | 1174.8506 | 93.275
119176695 | E | LC | ETL.1680.TOWR | 40818237 | LAKEVLLE | SONOMA | 2020-06-16 | 2021-04-19 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818237 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1978-01-01 | Glass | Other |  |  |  |  | 1.744e-06 | 5274.8779
119176695 | E | LC | ETL.1680.TOWR | 40818237 | LAKEVLLE | SONOMA | 2020-06-16 | 2021-04-19 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818237 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1978-01-01 | Glass | Dead End |  |  |  |  | 1.744e-06 | 5274.8779
119181545 | F | LC | ETL.6280.POLE.WOOD | 40591750 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40591750 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 6.0205e-06 | 1775.8434
119182464 | E | LC | ETL.8170.POLE.WDPS | 44564200 | EUREKA | HUMBOLDT | 2020-06-12 | 2021-06-08 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564200 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.01394
119182464 | E | LC | ETL.8170.POLE.WDPS | 44564200 | EUREKA | HUMBOLDT | 2020-06-12 | 2021-06-08 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564200 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.01394
119182464 | E | LC | ETL.8170.POLE.WDPS | 44564200 | EUREKA | HUMBOLDT | 2020-06-12 | 2021-06-08 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564200 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.01394
119194652 | F | LC | ETL.1240.POLE.STPS | 44200946 | TABLEMTN | NORTH VALLEY | 2020-06-22 | 2020-07-30 | ETL.1240 | CASCADE-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Tier 2 | Within Both | COMP | 44200944 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 3.2742e-09 | 5687.9312
119197868 | F | LC | ETL.6470.POLE.WOOD | 40868966 | SACTO | SIERRA | 2020-06-22 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40868966 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.043534 | 727.8687
119199323 | F | LC | ETL.6470.POLE.WOOD | 40611344 | SACTO | SIERRA | 2020-06-22 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611344 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.30511 | 189.9644
119199888 | F | LC | ETL.6470.POLE.WOOD | 40693300 | SACTO | SIERRA | 2020-06-23 | 2021-07-08 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693300 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.087167 | 31.7066
119201067 | E | LC | ETL.9340.POLE.NWOD | 44663904 | FRESNO | FRESNO | 2020-06-23 | 2020-08-06 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44663904 | 2018-10-03 | Light Duty Steel Pole | T-1 - Tri Post | 2018-10-03 | Polymer | Post |  |  |  |  | 0.00062538 | 5445.5674
119201068 | E | LC | ETL.9340.POLE.NWOD | 44663905 | FRESNO | FRESNO | 2020-06-23 | 2020-08-06 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44663905 | 2018-10-03 | Light Duty Steel Pole | T-1 - Tri Post | 2018-10-03 | Polymer | Post |  |  |  |  | 0.00060543 | 5445.5674
119221486 | E | LC | ETL.4440.INSL.CERA | 40788532 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2021-06-01 | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119222762 | E | LC | ETL.8290.POLE.WOOD | 40825122 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2021-04-26 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40825122 |  | Single Wood Pole | T2N | 2021-04-19 | Polymer | Post |  |  |  |  | 0.012772 | 3057.9141
119232537 | F | LC | ETL.6020.TOWR | 40647532 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2021-06-04 | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40647532 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 4.1464e-06 | 2616.3878
119289822 | F | LC | ETL.5140.POLE.WDPS | 44552336 | SACTO | SACRAMENTO | 2020-06-30 | 2021-01-25 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44551593 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.010976 | 189.9644
119294282 | F | LC | ETL.7160.TOWR | 44340984 | LAKEVLLE | SONOMA | 2020-07-01 |  | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 44340984 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 0.31154 | 174.0409 | 54.2212
119295774 | F | LC | ETL.7030.POLE.WOOD | 40701311 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2021-01-25 | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40701311 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0078929 | 2778.8323
119295805 | E | LC | ETL.9330.TOWR | 40872019 | FRESNO | FRESNO | 2020-06-29 |  | ETL.9330 | WISHON-COPPERMINE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40872019 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 5.0349e-05
119295832 | F | LC | ETL.6900.POLE.WOOD | 40667813 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 2 | Within Both | PEND | 40667813 | 1986-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 2.0568e-06 | 95.2109
119318196 | E | LC | ETL.4393.POLE.WDPS | 44172274 | SACTO | SACRAMENTO | 2020-07-01 | 2021-04-05 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119324832 | E | LC | ETL.7180.POLE.WOOD | 44281905 | LAKEVLLE | SONOMA | 2020-07-07 | 2020-07-21 | ETL.7180 | IGNACIO-BOLINAS #2 | Vegetation | Overgrown | [Trim, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44281905 | 2015-10-19 | Single Wood Pole | TH - TriAngle Post 70 | 2015-10-19 | Polymer | Post |  |  |  |  | 1.6646e-05 | 94.9794
119327939 | F | LC | ETL.1420.POLE.STPS | 44415583 | SACTO | SACRAMENTO | 2020-07-06 |  | ETL.1420 | DRUM-RIO OSO #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44415582 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.276e-08 | 1977.4294
119330886 | E | LC | ETL.7300.POLE.WOOD | 40876526 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-03-11 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119333688 | E | LC | ETL.2060.POLE.WOOD | 40586995 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-08-12 | ETL.2060 | FORT BRAGG-ELK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586995 | 1961-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2021-08-02 | Glass | Suspension |  |  |  |  | 0.096795 | 0.066432
119338527 | E | LC | ETL.7030.POLE.WOOD | 40759224 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-07 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119339312 | E | LC | ETL.7300.POLE.WOOD | 40668064 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-03-29 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
119341390 | E | LC | ETL.8560.INSL.NCER | 40793377 | PISMOBCH | LOS PADRES | 2020-07-08 | 2021-08-19 | ETL.8560 | CAYUCOS-CAMBRIA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119356659 | F | LC | ETL.6380.POLE.WOOD | 44141955 | LAKEVLLE | SONOMA | 2020-07-10 | 2021-02-16 | ETL.6380 | KONOCTI-MIDDLETOWN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44141955 | 2013-04-29 | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | Suspension |  |  |  |  | 6.2758e-07 | 7445.5029
119357091 | F | LC | ETL.7030.POLE.WOOD | 40759214 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-07-19 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759214 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.011289 | 808.4792
119357141 | E | LC | ETL.1422.TOWR | 40645086 | SACTO | SACRAMENTO | 2020-07-10 | 2021-03-03 | ETL.1422 | BRUNSWICK #1 TAP | Foundation/Concrete-Tower | Earth Covered Tower | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40645086 | 1975-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 9.2946e-07 | 31.7148
119357592 | F | LC | ETL.2395.POLE.WDPS | 44550035 | TABLEMTN |  | 2020-07-01 |  | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | PEND
119359961 | F | LC | ETL.7270.POLE.NWOD | 44856189 | TABLEMTN | NORTH VALLEY | 2020-07-13 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44856189 | 2019-04-20 | Light Duty Steel Pole | T-1 - Tri Post | 2019-04-20 | Polymer | Post |  |  |  |  | 0.00096744 | 2583.7695
119370263 | E | LC | ETL.1110.POLE.WDPS | 44423963 | EUREKA | HUMBOLDT | 2020-07-13 | 2021-07-12 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119379258 | F | LC | ETL.7030.POLE.WOOD | 40676324 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40676324 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0051631 | 664.4426
119474206 | E | LC | ETL.1450.POLE.WDPS | 44766899 | SACTO | SACRAMENTO | 2020-07-16 | 2021-11-08 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870149 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0020974 | 15.8859 | 0.033319
119475061 | E | LC | ETL.6280.INSL.NCER | 44259799 | TABLEMTN | NORTH VALLEY | 2020-07-20 | 2021-07-08 | ETL.6280 | CARIBOU #2 | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44259039 | 2020-07-16 | Light Duty Steel Pole | T2N | 2020-07-16 | Polymer | Post |  |  |  |  | 5.6365e-08 | 158.2282
119477903 | F | LC | ETL.1110.POLE.STPS | 44862874 | TABLEMTN | NORTH VALLEY | 2020-07-20 | 2021-04-21 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Steel | Missing | [Install, Completed] |  | Tier 2 | Within Both | COMP | 44862871 | 2019-12-23 | 2-Pole Non Wood | FSS - Field Switch Structure | [7 empty] | 2.5659e-05 | 332.3156
119498899 | E | LC | ETL.7030.POLE.WOOD | 40675716 | TABLEMTN | NORTH VALLEY | 2020-07-24 | 2021-06-14 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40675716 |  | Single Wood Pole | T-1 - Tri Post | 2020-06-30 | Polymer | Post |  |  |  |  | 0.0055817 | 31.7022
119509416 | F | LC | ETL.1350.POLE.WDPS | 44549876 | TABLEMTN |  | 2020-07-23 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44549445 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 0.037047 | 94.9939
119514905 | B | LC | ETL.1110.POLE.WDPS | 44424470 | TABLEMTN | HUMBOLDT | 2020-07-06 | 2020-08-14 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44424467 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00077317 | 2837.7712
119530825 | E | LC | ETL.7510.POLE.WOOD | 40862666 | LAKEVLLE | SONOMA | 2020-07-30 | 2020-08-31 | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119561920 | E | LC | ETL.6290.INSL.NCER | 42721991 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-11-18 | ETL.6290 | CARIBOU-PLUMAS JCT | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 42721892 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | Dead End |  |  |  |  | 0.15224 | 5538.7192
119576099 | F | LC | ETL.1480.TOWR | 40648890 | LAKEVLLE | HUMBOLDT | 2020-08-07 | 2021-07-06 | ETL.1480 | EAGLE ROCK-REDBUD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40648890 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1978-01-01 | Glass | Dead End |  |  |  |  | 0.0081755 | 4728.469
119578120 | E | LC | ETL.7490.POLE.WDPS | 44743798 | EUREKA | HUMBOLDT | 2020-08-07 | 2021-10-20 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [12 empty] | 0.065148
119597688 | F | LC | ETL.9061.POLE.WOOD | 40595665 | FRESNO | FRESNO | 2020-08-11 |  | ETL.9061 | DUNLAP TAP | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40595665 | 1964-01-01 | Tubular Steel Pole | DV-DE - Double Vertical Dead End | 1964-01-01 | Non Ceramic | Other |  |  |  |  | 5.8913e-08
119598306 | F | LC | ETL.7380.POLE.WOOD | 40697477 | MOSSLNDG | CENTRAL COAST | 2020-08-11 | 2021-03-10 | ETL.7380 | LAURELES-OTTER | Road | Grade Change | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40697477 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.017521 | 0.065148
119629282 | E | LC | ETL.8365.POLE.NWOD | 45002585 | EUREKA | HUMBOLDT | 2020-08-17 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | PEND | 45002585 | 2020-03-26 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-03-26 | Glass | Dead End |  |  |  |  | 0.00041566
119630360 | B | LC | ETL.7140.POLE.WOOD | 40750602 | LAKEVLLE | NORTH BAY | 2020-08-17 | 2020-11-18 | ETL.7140 | IGNACIO-BOLINAS #1 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750602 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0047317 | 720.4106
119637862 | E | LC | ETL.1450.POLE.WDPS | 44553710 | SACTO | SACRAMENTO | 2020-08-18 | 2021-07-06 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44553189 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0023818 | 174.093
119648016 | E | LC | ETL.7180.POLE.STPS | 44924647 | LAKEVLLE | SONOMA | 2020-08-21 | 2021-04-14 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44924572 | 2020-01-30 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.8737e-07 | 411.7471
119658112 | E | LC | ETL.1420.TOWR | 40589599 | SACTO | SACRAMENTO | 2020-08-22 | 2021-01-21 | ETL.1420 | DRUM-RIO OSO #1 | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40589599 | 1965-01-01 | LATTICE STEEL TOWER | FDDE - Flat Dead End Construction | 1965-01-01 | Porcelain | Dead End |  |  |  |  | 1.9676e-07 | 237.3428
119664153 | E | LC | ETL.3190.TOWR | 40913193 | TABLEMTN | NORTH VALLEY | 2020-08-24 |  | ETL.3190 | CARIBOU-PALERMO | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40913193 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | [7 empty] | 0.00096687 | 15.8851 | 0.015359
119697923 | B | LC | ETL.6380.INSL.CERA | 40902262 | LAKEVLLE |  | 2020-08-31 | 2020-10-28 | ETL.6380 | KONOCTI-MIDDLETOWN | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876736 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 1.2209e-05 | 5019.3472
119718967 | B | LC | ETL.1680.INSL.CERA | 40741361 | LAKEVLLE |  | 2020-07-30 | 2020-11-18 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119750324 | E | LC | ETL.7270.POLE.WOOD | 40591296 | TABLEMTN | NORTH VALLEY | 2020-08-13 | 2021-09-14 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591296 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0071467 | 477.4416
119753379 | E | LC | ETL.6280.POLE.WOOD | 45121205 | TABLEMTN | NORTH VALLEY | 2020-08-13 | 2021-08-19 | ETL.6280 | CARIBOU #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45121205 | 2020-03-09 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-03-09 | Glass | Dead End | [5 empty] | 2404.1431
119765713 | E | LC | ETL.9000.POLE.WOOD | 40650233 | FRESNO | YOSEMITE | 2020-09-08 | 2020-11-04 | ETL.9000 | MERCED #1 | Vegetation | Overgrown | [Trim, Completed] | Tier3 | Non-HFTD | Non-HFRA | COMP | 40650233 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00011806
119769271 | B | LC | ETL.7180.POLE.WOOD | 40617175 | LAKEVLLE | NORTH BAY | 2020-09-09 | 2020-12-07 | ETL.7180 | IGNACIO-BOLINAS #2 | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40617175 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | Dead End |  |  |  |  | 7.1676e-05 | 253.1975
119771792 | B | LC | ETL.6852.POLE.WOOD | 40648315 | LAKEVLLE | SONOMA | 2020-09-16 | 2021-07-07 | ETL.6852 | CLEAR LAKE-KONOCTI | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648315 | 2011-01-01 | Single Wood Pole | FSS - Field Switch Structure |  | Porcelain | Pin |  |  |  |  | 0.01526 | 4447.7559
119773523 | F | LC | ETL.6690.POLE.WOOD | 40873872 | SACTO | SIERRA | 2020-09-09 | 2021-03-08 | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119775952 | F | LC | ETL.2395.POLE.WDPS | 44550743 | TABLEMTN |  | 2020-09-08 |  | ETL.2395 | GRIZZLY TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44550102 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.023607 | 189.8861
119783547 | A | LC | ETL.4220.POLE.WDPS | 44561454 | TABLEMTN |  | 2020-09-18 | 2020-10-19 | ETL.4220 | WOODLEAF-PALERMO | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119790989 | E | LC | ETL.6440.POLE.WOOD | 40770035 | TABLEMTN | NORTH VALLEY | 2020-09-17 | 2021-04-15 | ETL.6440 | COLEMAN-RED BLUFF | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40770035 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0016601 | 4284.2378
119810036 | F | LC | ETL.4040.POLE.STPS | 44647068 | TABLEMTN | NORTH VALLEY | 2020-08-25 |  | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44646904 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00038013 | 427.7504
119821959 | F | LC | ETL.1450.POLE.NWOD | 44963450 | SACTO | SIERRA | 2020-09-25 | 2021-04-22 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44963450 | 2020-06-16 | Light Duty Steel Pole | SVDE - Single Vertical Dead End | 2020-06-16 | Glass | Dead End |  |  |  |  | 1.3744e-06 | 765.7878
119829191 | E | LC | ETL.8580.TOWR | 40690782 | FRESNO | FRESNO | 2020-09-29 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40690782 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Glass | [5 empty] | 9.9064e-06
119838046 | B | LC | ETL.6880.POLE.WOOD | 44677458 | LAKEVLLE | SONOMA | 2020-09-30 | 2020-10-20 | ETL.6880 | FULTON-CALISTOGA | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119839429 | E | LC | ETL.7490.POLE.WOOD | 40811061 | EUREKA | HUMBOLDT | 2020-07-30 | 2021-10-04 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.0057489 | 126.5956
119927570 | E | LC | ETL.6880.POLE.WOOD | 40588914 | LAKEVLLE | NORTH BAY | 2020-10-19 | 2021-07-22 | ETL.6880 | FULTON-CALISTOGA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40588914 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0024277 | 3387.7546
119995012 | F | LC | ETL.6280.POLE.NWOD | 40769473 | TABLEMTN | NORTH VALLEY | 2020-11-04 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40769473 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 2.1727e-05 | 2072.0388
120000347 | B | LC | ETL.8580.TOWR | 40651070 | FRESNO | FRESNO | 2020-11-06 | 2020-11-16 | ETL.8580 | COALINGA #1-SAN MIGUEL | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40651070 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-11-10 | Glass | Suspension |  |  |  |  | 1.6541e-05
120018020 | F | LC | ETL.1721.TOWR | 44181044 | MOSSLNDG | SAN JOSE | 2020-11-10 | 2021-01-20 | ETL.1721 | METCALF-SALINAS #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44181044 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | [5 empty] | 3.7342e-07 | 0.13001
120018020 | F | LC | ETL.1721.TOWR | 44181044 | MOSSLNDG | SAN JOSE | 2020-11-10 | 2021-01-20 | ETL.1721 | METCALF-SALINAS #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44181044 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 3.7342e-07 | 0.13001
120018020 | F | LC | ETL.1721.TOWR | 44181044 | MOSSLNDG | SAN JOSE | 2020-11-10 | 2021-01-20 | ETL.1721 | METCALF-SALINAS #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44181044 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Non Ceramic | Suspension |  |  |  |  | 3.7342e-07 | 0.13001
120044973 | F | LC | ETL.6280.POLE.WOOD | 40653383 | TABLEMTN | NORTH VALLEY | 2020-11-13 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40653383 |  | Single Wood Pole | FSS - Field Switch Structure |  | Unknown | Unknown |  |  |  |  | 0.00025372 | 2404.1431
120076626 | E | LC | ETL.1440.POLE.WOOD | 40597485 | SACTO | SIERRA | 2020-09-11 | 2020-11-20 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Rotten | [Replace] | Tier2 |  |  | DLFL | [11 empty] | 0.022792 | 0.065152
120133387 | F | LC | ETL.7780.POLE.WOOD | 40762805 | LAKEVLLE | HUMBOLDT | 2020-10-27 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40762805 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 3.2574e-05 | 31.6963
120161387 | F | LC | ETL.1050.TOWR | 40608217 | FRESNO | FRESNO | 2020-12-08 | 2021-04-19 | ETL.1050 | BALCH-SANGER | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | DLFL | 40608217 | 1927-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-04-14 | Porcelain | Suspension |  |  |  |  | 0.024063 | 253.126
120161387 | F | LC | ETL.1050.TOWR | 40608217 | FRESNO | FRESNO | 2020-12-08 | 2021-04-19 | ETL.1050 | BALCH-SANGER | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | DLFL | 40608217 | 1927-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-04-14 | Porcelain | Suspension |  |  |  |  | 0.024063 | 253.126
120475980 | A | LC | ETL.7490.POLE.STPS | 44960394 | EUREKA | HUMBOLDT | 2021-01-28 | 2021-02-02 | ETL.7490 | MAPLE CREEK-HOOPA | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44960394 | 2020-08-14 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-08-14 | Glass | Dead End |  |  |  |  | 0.0052424
120475980 | A | LC | ETL.7490.POLE.STPS | 44960394 | EUREKA | HUMBOLDT | 2021-01-28 | 2021-02-02 | ETL.7490 | MAPLE CREEK-HOOPA | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44960394 | 2020-08-14 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-08-14 | Glass | Dead End |  |  |  |  | 0.0052424
120475980 | A | LC | ETL.7490.POLE.STPS | 44960394 | EUREKA | HUMBOLDT | 2021-01-28 | 2021-02-02 | ETL.7490 | MAPLE CREEK-HOOPA | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44960394 | 2020-08-14 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-08-14 | Glass | Dead End |  |  |  |  | 0.0052424
120689491 | E | LC | ETL.4040.POLE.WDPS | 44565761 | TABLEMTN | NORTH VALLEY | 2021-03-24 | 2021-10-11 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 865.5564
120690744 | F | LC | ETL.6760.POLE.WOOD | 40913013 | SACTO | SACRAMENTO | 2021-03-25 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40913013 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0035536 | 4399.0391
120691164 | E | LC | ETL.3700.POLE.WOOD | 41147623 | PISMOBCH | LOS PADRES | 2021-03-25 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41147623 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | [5 empty] | 3.8842e-05 | 3453.2021 | 0.13413
120697312 | B | LC | ETL.5960.TOWR | 40651916 | PISMOBCH | LOS PADRES | 2021-03-26 | 2021-06-11 | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40651916 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 3.3239e-08 | 3710.9561
120697369 | F | LC | ETL.6720.POLE.WDPS | 44974728 | TABLEMTN | NORTH VALLEY | 2021-03-26 | 2021-09-08 | ETL.6720 | DESABLA-CENTERVILLE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 42578845 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.01641 | 47.5251
120706738 | E | LC | ETL.1530.TOWR | 40751968 | SACTO | SACRAMENTO | 2021-03-29 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40751968 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 0.00020018 | 237.4567 | 0.047534
120706765 | F | LC | ETL.7380.POLE.WOOD | 44974707 | MOSSLNDG | CENTRAL COAST | 2021-03-29 | 2021-07-28 | ETL.7380 | LAURELES-OTTER | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44974707 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.14335 | 31.6978
120718010 | E | LC | ETL.2900.TOWR | 40595227 | MOSSLNDG | CENTRAL COAST | 2021-03-31 | 2021-04-07 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40595227 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0011156 | 860.535
120737116 | F | LC | ETL.3820.TOWR | 40803365 | VICTOR | STOCKTON | 2021-04-01 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40803365 | 1970-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1989-01-01 | Porcelain | Dead End |  |  |  |  | 3.6157e-08 | 3833.2197 | 0.0001386
120750209 | E | LC | ETL.8405.POLE.WOOD | 40589948 | SACTO | SACRAMENTO | 2021-04-06 | 2021-09-28 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.16122 | 4160.9766
120757026 | E | LC | ETL.1070.POLE.WOOD | 40587321 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40587321 | 1957-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1957-01-01 | Polymer | Suspension |  |  |  |  | 3.2011e-05 | 3279.5457 | 0.10498
120765139 | B | LC | ETL.5090.INSL | 40622801 | MOSSLNDG | CENTRAL COAST | 2021-04-08 | 2021-07-08 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40582103 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.0071317 | 79.1724
120766622 | E | LC | ETL.7380.POLE.WDPS | 44563008 | MOSSLNDG | CENTRAL COAST | 2021-04-08 |  | ETL.7380 | LAURELES-OTTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44562410 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.62913 | 0.065148 | 0.040987
120787934 | E | LC | ETL.6880.POLE.WOOD | 40911336 | LAKEVLLE | SONOMA | 2021-04-10 | 2021-07-12 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120788101 | E | LC | ETL.6870.POLE.WOOD | 40589928 | SACTO | SACRAMENTO | 2021-04-10 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40589928 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.28022 | 79.2067 | 22.1954
120796204 | B | LC | ETL.3830.TOWR | 40803310 | VICTOR | STOCKTON | 2021-04-09 | 2021-05-26 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803310 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 9.9564e-05 | 4067.2603
120800141 | E | LC | ETL.8250.POLE.WOOD | 40904148 | VICTOR | STOCKTON | 2021-04-12 | 2021-08-31 | ETL.8250 | CLAY-MARTEL | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40904148 |  | Single Wood Pole | T1DE - Tri Post Dead End 115 |  | Glass | Dead End |  |  |  |  | 0.022834 | 1362.709
120800180 | E | LC | ETL.1070.POLE.NWOD | 44928859 | VICTOR | YOSEMITE | 2021-04-12 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44928859 | 2020-04-20 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-04-20 | Polymer | Post |  |  |  |  | 2.0538e-11 | 3378.8298 | 6.9393e-08
120805174 | E | LC | ETL.8650.POLE.NWOD | 44420152 | FRESNO | YOSEMITE | 2021-04-07 |  | ETL.8650 | EXCHEQUER-INDIAN FLAT | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44420152 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0028592 | 4117.0835 | 11.7714
120813263 | E | LC | ETL.7290.POLE.WOOD | 40771230 | TABLEMTN | NORTH VALLEY | 2021-04-14 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40771230 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Ceramic | Unknown |  |  |  |  | 0.11642 | 2262.72 | 263.4302
120813577 | F | LC | ETL.9100.POLE.WOOD | 44191936 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-31 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 1.4353e-05 | 2732.2681
120813600 | E | LC | ETL.8060.POLE.WOOD | 40650039 | SACTO | SACRAMENTO | 2021-04-14 | 2021-10-04 | ETL.8060 | SPAULDING-SUMMIT | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650039 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.026849 | 95.0274
120819392 | E | LC | ETL.2720.INSL | 40773202 | CONCORD | DIABLO | 2021-04-14 |  | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40745884 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 0.00083106 | 0.065158 | 5.415e-05
120830454 | F | LC | ETL.5300.TOWR | 40870859 | PISMOBCH | LOS PADRES | 2021-04-09 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40870859 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 4.3685e-06 | 952.4091 | 0.0041606
120839583 | F | LC | ETL.6500.POLE.WOOD | 40610968 | SACTO | SACRAMENTO | 2021-04-17 | 2021-05-05 | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40610968 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0044991 | 6284.8086
120839583 | F | LC | ETL.6500.POLE.WOOD | 40610968 | SACTO | SACRAMENTO | 2021-04-17 | 2021-05-05 | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40610968 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0044991 | 6284.8086
120839583 | F | LC | ETL.6500.POLE.WOOD | 40610968 | SACTO | SACRAMENTO | 2021-04-17 | 2021-05-05 | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40610968 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0044991 | 6284.8086
120841457 | E | LC | ETL.5980.TOWR | 40863923 | PISMOBCH | LOS PADRES | 2021-04-19 |  | ETL.5980 | DIABLO-MIDWAY #3 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40863923 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-10-07 | Glass Silicone Coated | Suspension |  |  |  |  | 2.1406e-10 | 2203.3623 | 4.7165e-07
120850456 | E | LC | ETL.3740.INSL.NCER | 42582031 | CONCORD | EAST BAY | 2021-04-20 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44188772 | 2008-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Polymer | Dead End |  |  |  |  | 0.076314 | 398.0443 | 30.3762
120874200 | E | LC | ETL.3830.TOWR | 40594278 | VICTOR | STOCKTON | 2021-04-23 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40594278 | 1910-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1989-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.6767e-06 | 5476.1846 | 0.020134
120888702 | E | LC | ETL.1820.POLE.WOOD | 44553993 | EUREKA | HUMBOLDT | 2021-04-27 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553993 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.36519 | 790.9056 | 288.8278
120901561 | E | LC | ETL.4870.TOWR | 40582537 | FRESNO | FRESNO | 2021-04-29 |  | ETL.4870 | HELMS-GREGG #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40582537 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 2.3016e-08 | 6197.0627 | 0.00014263
120924345 | E | LC | ETL.1820.POLE.NWOD | 45105736 | EUREKA | HUMBOLDT | 2021-05-03 |  | ETL.1820 | HUMBOLDT-TRINITY | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45105736 | 2020-03-04 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-03-04 | Ceramic | Suspension | [5 empty] | 0.065152
120943094 | E | LC | ETL.3830.TOWR | 40681759 | VICTOR | STOCKTON | 2021-05-06 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40681759 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.0111e-06 | 3360.5701 | 0.003398
120944083 | E | LC | ETL.1810.POLE.STPS | 45105809 | EUREKA | HUMBOLDT | 2021-05-05 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45105764 | 2020-12-03 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [8 empty] | 0.065148
121013852 | E | LC | ETL.7610.POLE.WOOD | 40824938 | METCALF | SAN JOSE | 2021-05-10 |  | ETL.7610 | MONTA VISTA-LOS GATOS | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40824938 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0010216 | 0.066432 | 6.787e-05
121086680 | F | LC | ETL.6500.POLE.WOOD | 40757118 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40757118 |  | Single Wood Pole | T2N | 2018-06-29 | Polymer | Post |  |  |  |  | 0.008974 | 6284.8086
121191294 | F | LC | ETL.1820.POLE.WOOD | 44553505 | EUREKA | HUMBOLDT | 2021-05-11 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44553505 |  | Single Wood Pole | SV-1B - Single Vertical Light Angle BR |  | Glass | Suspension |  |  |  |  | 0.24831 | 2753.0989
121328808 | E | LC | ETL.7380.POLE.WOOD | 40668271 | MOSSLNDG | CENTRAL COAST | 2021-04-23 |  | ETL.7380 | LAURELES-OTTER | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40668271 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 0.28442 | 0.065148 | 0.01853
121336986 | F | LC | ETL.2395.POLE.WOOD | 44549430 | TABLEMTN | NORTH VALLEY | 2021-05-14 |  | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44549430 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.00039855 | 79.172
121348810 | F | LC | ETL.5300.TOWR | 40762076 | PISMOBCH | LOS PADRES | 2021-04-26 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762076 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 1.2931e-06 | 5604.0952 | 0.0072467
121356973 | E | LC | ETL.4870.TOWR | 40576742 | FRESNO | FRESNO | 2021-05-18 |  | ETL.4870 | HELMS-GREGG #1 | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier2 | Tier 2 | Within Both | PEND | 40576742 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 7.3905e-07 | 5867.9263 | 0.0043367
121377564 | E | LC | ETL.1600.TOWR | 40594502 | LAKEVLLE | SONOMA | 2021-05-21 |  | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40594502 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 1.7768e-05 | 158.4545 | 0.0028154
121377564 | E | LC | ETL.1600.TOWR | 40594502 | LAKEVLLE | SONOMA | 2021-05-21 |  | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40594502 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 1.7768e-05 | 158.4545 | 0.0028154
121379676 | B | LC | ETL.4440.TOWR | 40603330 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-29 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40603330 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 3.0367e-05 | 4683.9302
121381238 | F | LC | ETL.8250.POLE.WOOD | 40908832 | VICTOR | STOCKTON | 2021-05-10 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908832 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.001062 | 1664.5133
121382809 | E | LC | ETL.8250.POLE.WOOD | 40912850 | VICTOR | STOCKTON | 2021-05-11 | 2021-08-26 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40912850 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00086865 | 2931.7273
121384868 | E | LC | ETL.7000.INSL.NCER | 40852932 | TABLEMTN |  | 2021-05-22 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40825643 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0025468 | 0.065148 | 0.00016592
121390969 | B | LC | ETL.5630.INSL | 40892283 | TABLEMTN | NORTH VALLEY | 2021-05-24 | 2021-06-16 | ETL.5630 | ROCK CREEK-POE | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
121392147 | E | LC | ETL.6291.POLE.WOOD | 40876676 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6291 | PLUMAS-SIERRA TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40876676 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | [5 empty] | 0.00010527 | 1118.6899 | 0.11776
121394409 | F | LC | ETL.6760.POLE.WOOD | 40591317 | SACTO | SIERRA | 2021-05-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40591317 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.038008 | 126.6638
121397106 | B | LC | ETL.8250.POLE.WOOD | 40663970 | VICTOR | STOCKTON | 2021-05-25 | 2021-06-24 | ETL.8250 | CLAY-MARTEL | Switch-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
121404706 | F | LC | ETL.8290.POLE.WOOD | 40875831 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40875831 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.00019898 | 4041.0511
121409441 | F | LC | ETL.6660.POLE.NWOD | 45087095 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45087095 | 2021-03-04 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-04 | Polymer | Post |  |  |  |  | 1.2198e-08 | 1560.4213
121427402 | F | LC | ETL.6470.POLE.WOOD | 40693296 | SACTO | SIERRA | 2021-05-27 | 2021-06-24 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40693296 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.25085 | 158.2723
121428197 | F | LC | ETL.5140.POLE.STPS | 44993384 | SACTO | SIERRA | 2021-05-26 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44993380 | 2020-10-28 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.2026e-07 | 205.7817
121431032 | E | LC | ETL.6880.POLE.WOOD | 40649312 | LAKEVLLE | SONOMA | 2021-05-26 | 2021-08-12 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40649312 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 0.028818 | 522.4158
121434887 | E | LC | ETL.1450.INSL.CERA | 40630552 | SACTO | SACRAMENTO | 2021-05-31 | 2021-06-15 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44553957 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064757
121434887 | E | LC | ETL.1450.INSL.CERA | 40630552 | SACTO | SACRAMENTO | 2021-05-31 | 2021-06-15 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44553957 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064757
121434887 | E | LC | ETL.1450.INSL.CERA | 40630552 | SACTO | SACRAMENTO | 2021-05-31 | 2021-06-15 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44553957 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064757
121443971 | E | LC | ETL.6220.POLE.WOOD | 40810923 | EUREKA | HUMBOLDT | 2021-06-01 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40810923 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Pin |  |  |  |  | 0.041428 | 901.8474 | 37.3616
121481100 | F | LC | ETL.6320.POLE.NWOD | 44416324 | TABLEMTN | NORTH VALLEY | 2021-06-04 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44416324 | 2018-10-09 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2018-10-09 | Polymer | Suspension |  |  |  |  | 0.0007167 | 2156.25
121485045 | F | LC | ETL.5140.POLE.STPS | 44690717 | SACTO | SIERRA | 2021-05-29 | 2021-11-08 | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44141458 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.926e-07 | 5269.8428
121489010 | E | LC | ETL.1380.POLE.WDPS | 44283830 | PISMOBCH | LOS PADRES | 2021-06-08 |  | ETL.1380 | DIVIDE-CABRILLO #1 | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44283829 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.014465 | 2011.5979 | 29.0981
121492694 | F | LC | ETL.6110.TOWR | 40753703 | METCALF | SAN JOSE | 2021-06-01 |  | ETL.6110 | TESLA-METCALF | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40753703 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.8276e-08 | 1365.5936
121493269 | F | LC | ETL.5630.TOWR | 40869366 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5630 | ROCK CREEK-POE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40869366 | 1968-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1968-01-01 | Ceramic | Suspension |  |  |  |  | 5.4888e-06 | 6641.8135
121499685 | F | LC | ETL.1073.POLE.WOOD | 44948164 | VICTOR | YOSEMITE | 2021-06-04 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40872955 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00070476 | 31.7081
121516854 | F | LC | ETL.1600.TOWR | 40810971 | LAKEVLLE | NORTH BAY | 2021-06-05 |  | ETL.1600 | FULTON-PUEBLO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40810971 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-06-20 | Glass | Suspension |  |  |  |  | 7.049e-09 | 31.7184
121516854 | F | LC | ETL.1600.TOWR | 40810971 | LAKEVLLE | NORTH BAY | 2021-06-05 |  | ETL.1600 | FULTON-PUEBLO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40810971 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-10-27 | Glass | Suspension |  |  |  |  | 7.049e-09 | 31.7184
121524067 | F | LC | ETL.5650.TOWR | 40605780 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40605780 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-17 | Glass | Suspension |  |  |  |  | 5.5665e-06 | 350.2999 | 0.00195
121525439 | E | LC | ETL.2390.INSL.NCER | 40827975 | VICTOR | STOCKTON | 2021-06-12 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391208 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 0.00013765
121525439 | E | LC | ETL.2390.INSL.NCER | 40827975 | VICTOR | STOCKTON | 2021-06-12 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391208 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 0.00013765
121545308 | E | LC | ETL.4550.INSL | 40637015 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40605626 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 0.00017603 | 4056.6345 | 0.71409
121548855 | F | LC | ETL.3830.POLE.NWOD | 45089100 | VICTOR | STOCKTON | 2021-06-16 | 2021-07-26 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 |  |  | DLFL
121549910 | E | LC | ETL.5970.INSL | 40782672 | PISMOBCH | LOS PADRES | 2021-06-16 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40753815 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 6.7631e-07 | 5982.9551 | 0.0040463
121550192 | F | LC | ETL.1820.POLE.STPS | 44395554 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395553 | 2017-10-27 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0027589 | 253.2084
121555810 | E | LC | ETL.9340.POLE.WOOD | 40584832 | FRESNO | YOSEMITE | 2021-06-16 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40584832 |  | Single Wood Pole | TCDE - Tap Construction Dead End | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.099813 | 5176.5 | 516.6797
121557606 | F | LC | ETL.5640.TOWR | 40820415 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40820415 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 2.2721e-07 | 4421.1143 | 0.0010045
121560023 | E | LC | ETL.6050.INSL | 40680697 | MOSSLNDG | CENTRAL COAST | 2021-06-16 |  | ETL.6050 | MOSS LANDING-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40651804 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.3716e-07 | 1250.099 | 0.00017146
121562691 | E | LC | ETL.6750.POLE.WDPS | 44374919 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44374918 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0003691 | 205.744 | 0.07594
121562760 | F | LC | ETL.6750.POLE.WDPS | 44374920 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44374918 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0003691 | 205.744
121573517 | E | LC | ETL.7550.POLE.WOOD | 40585233 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40585233 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0017661 | 110.7947 | 0.19568
121578087 | E | LC | ETL.1440.POLE.WDPS | 44765653 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40865987 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0018212 | 648.7145 | 1.1815
121578341 | F | LC | ETL.6020.TOWR | 41162775 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6020 | MALIN-ROUND MTN #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41162775 |  | LATTICE STEEL TOWER | Unknown | [7 empty] | 4.6399e-09 | 1380.2244
121580215 | B | LC | ETL.6060.INSL | 40722382 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-09-20 | ETL.6060 | ROUND MTN-TABLE MTN #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40677947 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00054771 | 397.6502
121594264 | A | LC | ETL.3190.INSL.CERA | 40920058 | TABLEMTN | NORTH VALLEY | 2021-06-24 | 2021-06-29 | ETL.3190 | CARIBOU-PALERMO | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910319 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.030544 | 3875.0593
121596571 | E | LC | ETL.1440.POLE.WDPS | 44180216 | SACTO | SIERRA | 2021-06-17 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44180214 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.010399 | 713.184 | 7.4162
121601285 | E | LC | ETL.6040.TOWR | 40603258 | MOSSLNDG | CENTRAL COAST | 2021-06-24 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40603258 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.1657e-06 | 190.4757 | 0.00041251
121617733 | B | LC | ETL.6060.INSL | 40635070 | TABLEMTN | NORTH VALLEY | 2021-06-27 | 2021-09-16 | ETL.6060 | ROUND MTN-TABLE MTN #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40601329 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 3.2388e-06 | 462.5264
121620637 | F | LC | ETL.1350.POLE.WDPS | 44552364 | TABLEMTN |  | 2021-06-18 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44551668 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.029775 | 386.5805
121624004 | B | LC | ETL.6020.TOWR | 40601190 | TABLEMTN | NORTH VALLEY | 2021-06-26 | 2021-07-21 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601190 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 3.2211e-10 | 63.351
121629590 | F | LC | ETL.1820.POLE.NWOD | 44395467 | EUREKA | HUMBOLDT | 2021-06-12 | 2021-07-12 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44395467 |  | Light Duty Steel Pole | DDE - Double Dead End | 2020-03-10 | Glass | Dead End |  |  |  |  | 0.0010799 | 5637.4995
121641938 | E | LC | ETL.1650.POLE.WOOD | 40577418 | LAKEVLLE | SONOMA | 2021-06-26 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40577418 | 1991-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1966-01-01 | Polymer | Suspension |  |  |  |  | 0.00012687 | 2393.1714 | 0.30363
121651681 | F | LC | ETL.7060.POLE.WOOD | 40653281 | METCALF | PENINSULA | 2021-06-27 | 2021-11-08 | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40653281 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.0022556 | 0.066432 | 0.00014984
121673745 | E | LC | ETL.6020.TOWR | 40816580 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40816580 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 7.4217e-06 | 79.2104 | 0.00058788
121726527 | B | LC | ETL.5430.INSL.NCER | 44562621 | TABLEMTN | NORTH VALLEY | 2021-07-09 | 2021-07-29 | ETL.5430 | PIT #5-ROUND MTN #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562330 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.0087001
121726527 | B | LC | ETL.5430.INSL.NCER | 44562621 | TABLEMTN | NORTH VALLEY | 2021-07-09 | 2021-07-29 | ETL.5430 | PIT #5-ROUND MTN #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562330 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.0087001
121736533 | F | LC | ETL.1820.POLE.STPS | 44395400 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-09 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44395398 | 2020-03-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00028685 | 237.3869
121737222 | E | LC | ETL.7030.POLE.NWOD | 45140008 | TABLEMTN | NORTH VALLEY | 2021-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45140008 | 2021-06-17 | Light Duty Steel Pole | T2N | 2021-06-17 | Polymer | Post | [5 empty] | 0.06515
121741854 | F | LC | ETL.8350.POLE.NWOD | 45015280 | VICTOR | STOCKTON | 2021-07-14 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45015280 | 2020-03-31 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-03-31 | Polymer | Dead End |  |  |  |  | 3.5581e-07 | 553.7256
121744639 | E | LC | ETL.2390.POLE.WDPS | 44195263 | VICTOR | STOCKTON | 2021-07-14 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44195261 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.073e-05 | 1550.6018 | 0.10967
121750734 | F | LC | ETL.6760.POLE.WOOD | 44178361 | SACTO | SIERRA | 2021-07-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44178361 | 2015-03-25 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2015-03-25 | Porcelain | Dead End |  |  |  |  | 0.03397 | 126.6688
121761949 | E | LC | ETL.5430.POLE.WDPS | 44561263 | TABLEMTN | NORTH VALLEY | 2021-07-13 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560778 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.01706 | 490.5428 | 8.3688
121762703 | E | LC | ETL.6020.TOWR | 40821636 | TABLEMTN | NORTH VALLEY | 2021-07-19 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40821636 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.333e-07 | 791.1378 | 0.00018457
121764655 | B | LC | ETL.6280.POLE.WOOD | 40591751 | TABLEMTN | NORTH VALLEY | 2021-07-20 | 2021-10-06 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40591751 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 5.968e-06 | 6157.4399
121807226 | F | LC | ETL.7040.POLE.WOOD | 40591241 | TABLEMTN | NORTH VALLEY | 2021-07-26 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40591241 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.04927 | 1380.2334
121816505 | F | LC | ETL.8405.POLE.WOOD | 40874900 | SACTO | SIERRA | 2021-07-27 | 2021-10-08 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40874900 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0031317 | 2610.7236
121824569 | B | LC | ETL.7390.INSL.CERA | 40627158 | LAKEVLLE | HUMBOLDT | 2021-07-30 | 2021-08-09 | ETL.7390 | LAYTONVILLE-COVELO | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40600465 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.40389 | 1059.9053
121860175 | B | LC | ETL.6300.POLE.WOOD | 44642286 | TABLEMTN | NORTH VALLEY | 2021-08-07 | 2021-09-14 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.2787e-05 | 221.7338
122011832 | E | LC | ETL.4430.INSL.NCER | 45062985 | TABLEMTN | NORTH VALLEY | 2021-09-03 |  | ETL.4430 | BUCKS CREEK-ROCK CREEK-CRESTA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 45062983 |  | 2-Pole Non Wood | DDE - Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.00058104
122011832 | E | LC | ETL.4430.INSL.NCER | 45062985 | TABLEMTN | NORTH VALLEY | 2021-09-03 |  | ETL.4430 | BUCKS CREEK-ROCK CREEK-CRESTA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 45062983 |  | 2-Pole Non Wood | DDE - Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.00058104
118472892 | B | LC | ETL.8250.POLE.NWOD | 44841538 | VICTOR | STOCKTON | 2020-01-27 | 2020-02-10 | ETL.8250 | CLAY-MARTEL | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44841538 | 2019-09-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-09-11 | Polymer | Dead End |  |  |  |  | 4.3804e-07 | 954.3378
118601786 | E | LC | ETL.7820.POLE.WOOD | 40577245 | LAKEVLLE | SONOMA | 2020-03-03 | 2020-04-28 | ETL.7820 | POTTER VALLEY-WILLITS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118682727 | E | LC | ETL.7850.POLE.WOOD | 40808358 | EUREKA | HUMBOLDT | 2020-03-12 | 2021-03-10 | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40808358 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 2020-02-19 | Glass | Suspension |  |  |  |  | 0.00029232 | 1028.0897
118744131 | E | LC | ETL.4316.POLE.STPS | 44383192 | TABLEMTN | NORTH VALLEY | 2020-03-25 | 2021-04-28 | ETL.4316 | PARADISE-TABLE MTN | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] |  | Tier 3 | Within Both | DLFL | 44383189 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00034535 | 238.4023
118786798 | E | LC | ETL.2760.INSL | 40671361 | CONCORD | EAST BAY | 2020-04-07 | 2021-03-31 | ETL.2760 | MORAGA-OAKLAND J | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118926860 | E | LC | ETL.5290.INSL | 40895393 | PISMOBCH | LOS PADRES | 2020-04-16 | 2021-01-20 | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
118942850 | F | LC | ETL.4440.TOWR | 40867849 | TABLEMTN | NORTH VALLEY | 2020-04-23 | 2020-04-23 | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40867849 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 1.8925e-06 | 807.4282
118948053 | B | LC | ETL.8253.POLE.WOOD | 40804110 | VICTOR | STOCKTON | 2020-04-23 | 2020-07-22 | ETL.8253 | IONE TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40804110 | 1987-01-01 | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00053021 | 1595.6494
118965098 | E | LC | ETL.7490.POLE.WOOD | 40662197 | EUREKA | HUMBOLDT | 2020-04-30 | 2020-11-10 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40662197 | 2010-01-01 | Single Wood Pole | T-1 - Tri Post | 2019-03-13 | Polymer | Post |  |  |  |  | 0.0071902 | 1455.165
118988217 | E | LC | ETL.1650.POLE.WOOD | 44298419 | LAKEVLLE | SONOMA | 2020-04-23 | 2021-03-16 | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44298419 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | [5 empty] | 0.00031378 | 4022.6609
119001369 | B | LC | ETL.1110.POLE.WDPS | 44515775 | TABLEMTN | HUMBOLDT | 2020-05-08 | 2020-05-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44515184 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0041594 | 4892.3394
119016683 | B | LC | ETL.8410.INSL.NCER | 40637130 | LAKEVLLE | HUMBOLDT | 2020-05-07 | 2020-06-11 | ETL.8410 | ELK-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40605895 | 2009-01-01 | Single Wood Pole | 3P DV - 3 Pole Double Vertical | 2009-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.079516 | 714.3839
119017123 | F | LC | ETL.1330.TOWR | 40657082 | LAKEVLLE | HUMBOLDT | 2020-04-24 |  | ETL.1330 | CORTINA-MENDOCINO #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40657082 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 3.435e-05 | 5613.8252
119023445 | B | LC | ETL.6440.POLE.WOOD | 44191510 | TABLEMTN | NORTH VALLEY | 2020-05-08 | 2020-07-09 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
119046634 | E | LC | ETL.1330.TOWR | 40672386 | SACTO | SACRAMENTO | 2020-05-13 | 2021-03-17 | ETL.1330 | CORTINA-MENDOCINO #1 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40672386 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.00045787 | 6270.522
119046634 | E | LC | ETL.1330.TOWR | 40672386 | SACTO | SACRAMENTO | 2020-05-13 | 2021-03-17 | ETL.1330 | CORTINA-MENDOCINO #1 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40672386 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-05-09 | Glass | Suspension |  |  |  |  | 0.00045787 | 6270.522
119083161 | E | LC | ETL.7290.INSL.NCER | 40845369 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-03-02 | ETL.7290 | KILARC-CEDAR CREEK | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40817416 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.0032429 | 556.7504
119096694 | E | LC | ETL.8240.POLE.WOOD | 40599122 | VICTOR | STOCKTON | 2020-06-02 | 2021-03-29 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119104204 | F | LC | ETL.1110.POLE.WDPS | 44423266 | TABLEMTN | HUMBOLDT | 2020-05-19 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44423265 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.001288 | 3455.426
119116746 | E | LC | ETL.5490.TOWR | 40581140 | CONCORD | DIABLO | 2020-05-22 | 2021-02-23 | ETL.5490 | PITTSBURG-SAN RAMON | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581140 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 0.00030112 | 4357.1626
119118966 | E | LC | ETL.8650.POLE.NWOD | 44420176 | FRESNO | YOSEMITE | 2020-06-03 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44420176 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0025978 | 3305.365
119132014 | E | LC | ETL.1073.POLE.WDPS | 44774786 | VICTOR | YOSEMITE | 2020-06-09 | 2021-08-16 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119152845 | B | LC | ETL.1810.INSL.CERA | 40720033 | EUREKA | HUMBOLDT | 2020-06-11 | 2020-09-17 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322437 |  | 2-Pole Wood | 2P DDE-A - 2 Pole Double Dead End Angle |  | Porcelain | Suspension |  |  |  |  | 0.0056486
119152845 | B | LC | ETL.1810.INSL.CERA | 40720033 | EUREKA | HUMBOLDT | 2020-06-11 | 2020-09-17 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322437 |  | 2-Pole Wood | 2P DDE-A - 2 Pole Double Dead End Angle |  | Porcelain | Suspension |  |  |  |  | 0.0056486
119158865 | E | LC | ETL.4590.TOWR | 40910142 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-07-08 | ETL.4590 | CRESTA-RIO OSO | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910142 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-14 | Glass | Suspension |  |  |  |  | 0.00028729 | 254.0199
119162632 | E | LC | ETL.1810.POLE.WDPS | 44322336 | EUREKA | HUMBOLDT | 2020-06-11 | 2021-05-03 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322334 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0022299
119162894 | F | LC | ETL.1400.POLE.WDPS | 44239782 | VICTOR | STOCKTON | 2020-06-12 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44239781 | 2016-03-22 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00026352 | 965.199
119172194 | E | LC | ETL.1400.POLE.WDPS | 44770774 | VICTOR | STOCKTON | 2020-06-12 | 2021-11-08 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Tier 3 | Within Both | COMP | 40860860 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0026299 | 2246.7366 | 5.9088
119176141 | E | LC | ETL.6280.POLE.WOOD | 40769638 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2021-09-01 | ETL.6280 | CARIBOU #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40769638 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 5.5024e-05 | 4878.0016
119180907 | F | LC | ETL.7300.POLE.WOOD | 40816238 | TABLEMTN |  | 2020-06-16 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40816238 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00042219 | 5760.6406
119195356 | E | LC | ETL.6470.POLE.WOOD | 40824282 | SACTO | SIERRA | 2020-06-22 | 2021-06-08 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40824282 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.58415 | 221.5931
119196218 | F | LC | ETL.6470.POLE.WOOD | 40817363 | SACTO | SIERRA | 2020-06-22 | 2021-07-13 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.059999 | 110.8608
119222766 | F | LC | ETL.7290.POLE.WOOD | 42615555 | TABLEMTN | NORTH VALLEY | 2020-06-26 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 42615555 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.015134 | 31.7051
119233412 | E | LC | ETL.7140.POLE.WOOD | 40584912 | LAKEVLLE | SONOMA | 2020-06-29 | 2021-05-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119235194 | F | LC | ETL.7160.POLE.WOOD | 44871204 | LAKEVLLE | SONOMA | 2020-06-30 |  | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871204 | 2019-09-19 | Single Wood Pole | 3HP - 3 Horizontal Post | 2019-09-19 | Polymer | Post |  |  |  |  | 0.21406 | 580.7642
119238425 | E | LC | ETL.4050.POLE.STPS | 44838824 | LAKEVLLE | SONOMA | 2020-06-30 | 2021-04-15 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44339697 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 5.6616e-07 | 2375.632
119290875 | E | LC | ETL.1370.POLE.WOOD | 40828424 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-06-23 | ETL.1370 | DIVIDE-CABRILLO #2 | Conductor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40828424 | 1960-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 2021-06-15 | Glass | Double Dead End |  |  |  |  | 0.0017689 | 3042.0652
119295348 | F | LC | ETL.8170.POLE.WDPS | 44565336 | EUREKA | HUMBOLDT | 2020-07-01 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44564309 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.04202 | 553.6737
119299456 | E | LC | ETL.1450.INSL.CERA | 40690175 | SACTO | SACRAMENTO | 2020-07-01 | 2021-10-04 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44551595 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0033471
119299456 | E | LC | ETL.1450.INSL.CERA | 40690175 | SACTO | SACRAMENTO | 2020-07-01 | 2021-10-04 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44551595 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0033471
119315100 | B | LC | ETL.4221.INSL.CERA | 44621397 | TABLEMTN |  | 2020-07-02 | 2020-08-20 | ETL.4221 | SLY CREEK TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119315451 | B | LC | ETL.7270.POLE.WOOD | 40909542 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2020-07-31 | ETL.7270 | KESWICK-TRINITY | Tie Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40909542 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0043396 | 933.5561
119328676 | F | LC | ETL.7270.POLE.WOOD | 40906071 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906071 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0015448 | 4993.7136
119329601 | F | LC | ETL.7270.POLE.WOOD | 40906068 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40906068 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0091086 | 4936.5352
119335894 | F | LC | ETL.1440.POLE.WOOD | 40756806 | SACTO | SIERRA | 2020-07-08 | 2021-05-17 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756806 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00092482
119335894 | F | LC | ETL.1440.POLE.WOOD | 40756806 | SACTO | SIERRA | 2020-07-08 | 2021-05-17 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756806 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00092482
119340996 | F | LC | ETL.6720.POLE.WOOD | 40751700 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40751700 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Pin |  |  |  |  | 0.0020702 | 15.8851
119341068 | F | LC | ETL.7030.POLE.WOOD | 40825592 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Other | Other | [Other, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825592 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.014221 | 698.4329
119341936 | E | LC | ETL.7140.POLE.WOOD | 41111824 | LAKEVLLE | NORTH BAY | 2020-07-08 | 2021-05-03 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41111824 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.021637
119341936 | E | LC | ETL.7140.POLE.WOOD | 41111824 | LAKEVLLE | NORTH BAY | 2020-07-08 | 2021-05-03 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41111824 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.021637
119341936 | E | LC | ETL.7140.POLE.WOOD | 41111824 | LAKEVLLE | NORTH BAY | 2020-07-08 | 2021-05-03 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41111824 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.021637
119341977 | F | LC | ETL.8060.POLE.WOOD | 40660099 | SACTO | SIERRA | 2020-07-07 | 2021-04-28 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660099 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0090224 | 2547.2131
119355242 | F | LC | ETL.6300.POLE.WOOD | 44191130 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-09-14 | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 3.6221e-06 | 15.8815
119357451 | F | LC | ETL.5140.POLE.WDPS | 44337488 | SACTO | SACRAMENTO | 2020-07-01 | 2021-07-06 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44337486 | 2017-03-15 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0028046 | 316.5174
119359491 | E | LC | ETL.7030.POLE.WOOD | 40600143 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-05-19 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600143 |  | Single Wood Pole | T2N | 2021-05-04 | Polymer | Post |  |  |  |  | 0.014081 | 4481.1777
119359675 | E | LC | ETL.7030.POLE.WOOD | 40827469 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-06-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827469 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.024309 | 444.4778
119361378 | E | LC | ETL.1110.POLE.WDPS | 44424382 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-07-12 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119362703 | E | LC | ETL.6290.POLE.WOOD | 40595031 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-08-30 | ETL.6290 | CARIBOU-PLUMAS JCT | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40595031 | 1958-01-01 | Single Wood Pole | T2N | 2021-08-22 | Polymer | Post |  |  |  |  | 0.031253 | 0.066432
119369388 | B | LC | ETL.7130.POLE.WOOD | 40751084 | EUREKA | HUMBOLDT | 2020-07-14 | 2020-11-02 | ETL.7130 | HUMBOLDT-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40751084 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Non Ceramic | Suspension |  |  |  |  | 0.1917 | 71.3456
119377708 | E | LC | ETL.8060.POLE.WOOD | 40878088 | SACTO | SACRAMENTO | 2020-07-15 | 2021-07-23 | ETL.8060 | SPAULDING-SUMMIT | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40878088 |  | Single Wood Pole | T2N | 2021-05-03 | Polymer | Post |  |  |  |  | 0.012108 | 95.1488
119461780 | E | LC | ETL.8170.POLE.WOOD | 40752256 | EUREKA | HUMBOLDT | 2020-07-16 | 2021-08-17 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40752256 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.013685 | 6206.8564
119468834 | F | LC | ETL.6290.POLE.WOOD | 40769623 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-01-25 | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40769623 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.28783 | 1043.9412
119471378 | F | LC | ETL.7030.POLE.WOOD | 40617101 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40617101 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.003637
119480938 | E | LC | ETL.5970.INSL | 40896518 | PISMOBCH | LOS PADRES | 2020-07-21 | 2021-08-31 | ETL.5970 | DIABLO-MIDWAY #2 | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40871221 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 8.8151e-09 | 1456.3075
119488258 | E | LC | ETL.6880.POLE.NWOD | 44916824 | LAKEVLLE | SONOMA | 2020-07-22 | 2020-09-14 | ETL.6880 | FULTON-CALISTOGA | Vegetation | Overgrown | [Trim, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44916824 | 2020-05-14 | Light Duty Steel Pole | T2N | 2020-05-14 | Polymer | Post |  |  |  |  | 0.00016953 | 63.3804
119488867 | F | LC | ETL.6240.POLE.WOOD | 40612373 | MOSSLNDG | CENTRAL COAST | 2020-07-22 | 2020-10-12 | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40612373 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.12626 | 110.8153
119495699 | E | LC | ETL.7490.POLE.NWOD | 44145876 | EUREKA | HUMBOLDT | 2020-07-23 | 2021-08-04 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44145876 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | Suspension |  |  |  |  | 0.0013356 | 126.5956
119498342 | F | LC | ETL.5250.TOWR | 40819147 | CONCORD | DIABLO | 2020-07-24 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40819147 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.2414e-06 | 379.7729
119498342 | F | LC | ETL.5250.TOWR | 40819147 | CONCORD | DIABLO | 2020-07-24 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40819147 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 1.2414e-06 | 379.7729
119511146 | F | LC | ETL.6110.TOWR | 40863781 | METCALF | SAN JOSE | 2020-07-27 | 2020-10-22 | ETL.6110 | TESLA-METCALF | Marker (i.e. signs)-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863781 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.0618e-08 | 3423.8503
119516522 | E | LC | ETL.8060.POLE.WOOD | 40602277 | SACTO | SACRAMENTO | 2020-07-28 | 2021-09-14 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602277 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | [5 empty] | 0.006871 | 541.3708
119528687 | E | LC | ETL.1440.POLE.WDPS | 44762486 | SACTO | SACRAMENTO | 2020-07-30 | 2021-09-16 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 0.065152
119536599 | E | LC | ETL.6480.POLE.WOOD | 40815345 | SACTO | SACRAMENTO | 2020-07-31 | 2021-06-14 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119560438 | E | LC | ETL.7780.INSL.NCER | 40640240 | LAKEVLLE | HUMBOLDT | 2020-08-04 | 2021-05-12 | ETL.7780 | PHILO JCT-ELK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119569709 | F | LC | ETL.6880.POLE.WOOD | 40827213 | LAKEVLLE | NORTH BAY | 2020-08-06 | 2021-02-10 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119575297 | B | LC | ETL.7780.POLE.WOOD | 40871814 | LAKEVLLE | SONOMA | 2020-08-07 | 2020-10-19 | ETL.7780 | PHILO JCT-ELK | Other | Customer Issue | [Access Issue] | Tier2 | Tier 2 | Within Both | COMP | 40871814 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 3.3398e-05 | 63.3274
119577646 | E | LC | ETL.6220.POLE.WOOD | 40586763 | EUREKA | HUMBOLDT | 2020-08-06 | 2021-02-08 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40586763 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.21515
119615156 | F | LC | ETL.1110.TOWR | 40592233 | TABLEMTN | HUMBOLDT | 2020-08-13 | 2021-07-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592233 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.7661e-05 | 63.351
119615156 | F | LC | ETL.1110.TOWR | 40592233 | TABLEMTN | HUMBOLDT | 2020-08-13 | 2021-07-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592233 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 2.7661e-05 | 63.351
119616395 | B | LC | ETL.8650.POLE.NWOD | 44420210 | FRESNO | FRESNO | 2020-08-14 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420210 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.013591 | 369.2492
119665296 | E | LC | ETL.7030.POLE.WOOD | 40656692 | TABLEMTN | NORTH VALLEY | 2020-08-20 | 2021-06-14 | ETL.7030 | HAT CREEK #1-WESTWOOD | Hardware-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656692 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2017-09-26 | Ceramic | Suspension |  |  |  |  | 0.02944 | 55.5438
119700082 | B | LC | ETL.5440.POLE.STPS | 44968886 | TABLEMTN | NORTH VALLEY | 2020-09-01 | 2020-09-30 | ETL.5440 | PIT #6 JCT-ROUND MTN | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44968845 | 2020-08-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0015933 | 1028.4974
119703537 | E | LC | ETL.7140.POLE.WOOD | 40825695 | LAKEVLLE | SONOMA | 2020-09-01 | 2021-05-13 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Stub-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825695 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.013601 | 47.5251
119721004 | A | LC | ETL.6230.POLE.WOOD | 40664555 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-09-19 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119721514 | E | LC | ETL.6861.POLE.WOOD | 40750921 | LAKEVLLE | HUMBOLDT | 2020-07-29 | 2021-09-13 | ETL.6861 | KONOCTI-EAGLE ROCK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750921 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2018-11-06 | Polymer | Dead End |  |  |  |  | 5.4048e-05 | 1518.7485
119727713 | E | LC | ETL.2740.INSL.NCER | 40704848 | CONCORD | EAST BAY | 2020-09-04 | 2021-06-14 | ETL.2740 | MORAGA-OAKLAND #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44367707 |  | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 4.6782e-05 | 0.065156
119741275 | B | LC | ETL.8170.POLE.WOOD | 40906262 | EUREKA | HUMBOLDT | 2020-07-21 | 2020-10-22 | ETL.8170 | TRINITY-MAPLE CREEK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906262 |  | Single Wood Pole | T2N | 2020-10-17 | Polymer | Post |  |  |  |  | 0.063367 | 1025.3294
119757676 | F | LC | ETL.8410.POLE.WOOD | 40601547 | LAKEVLLE | HUMBOLDT | 2020-09-02 |  | ETL.8410 | ELK-GUALALA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40601547 | 1960-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1960-01-01 | Polymer | Dead End |  |  |  |  | 0.32267 | 170.8733
119762114 | F | LC | ETL.7490.POLE.NWOD | 40650887 | EUREKA | HUMBOLDT | 2020-09-14 | 2021-10-06 | ETL.7490 | MAPLE CREEK-HOOPA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40650887 | 2011-01-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Ceramic | [5 empty] | 0.00018177 | 189.8608
119771127 | B | LC | ETL.7030.POLE.WOOD | 40701256 | TABLEMTN | NORTH VALLEY | 2020-08-19 | 2020-09-28 | ETL.7030 | HAT CREEK #1-WESTWOOD | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40701256 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.016049 | 0.066432
119788996 | F | LC | ETL.7030.POLE.WOOD | 40667948 | TABLEMTN | NORTH VALLEY | 2020-09-18 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40667948 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0062415 | 5587.7441
119790495 | F | LC | ETL.1710.POLE.WDPS | 44513681 | MOSSLNDG | CENTRAL COAST | 2020-07-31 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44512253 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00029236 | 63.3245
119803706 | F | LC | ETL.6310.POLE.WOOD | 40592304 | TABLEMTN | NORTH VALLEY | 2020-09-22 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40592304 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.151e-05 | 2218.8638
119809782 | F | LC | ETL.6470.POLE.WOOD | 44918012 | SACTO | SIERRA | 2020-08-18 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44918012 | 2019-08-11 | Light Duty Steel Pole | T-1 - Tri Post | 2019-08-16 | Polymer | Post |  |  |  |  | 0.0081942 | 142.4516
119816578 | F | LC | ETL.6480.POLE.WOOD | 42549815 | SACTO | NORTH VALLEY | 2020-09-08 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
119818188 | F | LC | ETL.8240.POLE.WOOD | 40825811 | VICTOR | STOCKTON | 2020-09-11 |  | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40825811 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.025563 | 3815.678
119865532 | B | LC | ETL.7630.INSL | 40778255 | LAKEVLLE |  | 2020-10-06 | 2020-12-02 | ETL.7630 | MONTE RIO-FULTON | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119909255 | E | LC | ETL.1400.POLE.WDPS | 44770790 | VICTOR | STOCKTON | 2020-10-13 | 2021-05-17 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 40584549 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.030606 | 2436.5813
119924955 | E | LC | ETL.7030.POLE.WOOD | 40868237 | TABLEMTN | NORTH VALLEY | 2020-10-19 | 2021-07-09 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40868237 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2020-06-29 | Glass | Pin |  |  |  |  | 0.00065315 | 110.7947
119995356 | F | LC | ETL.7030.POLE.WOOD | 40676283 | TABLEMTN | NORTH VALLEY | 2020-10-05 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40676283 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.047037 | 0.065151
120042122 | E | LC | ETL.1890.TOWR | 40682157 | FRESNO | FRESNO | 2020-11-10 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40682157 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1986-01-01 | Porcelain | Suspension |  |  |  |  | 5.6541e-07
120076252 | E | LC | ETL.8651.POLE.WOOD | 40859272 | FRESNO | FRESNO | 2020-11-19 |  | ETL.8651 | BRICEBURG JCT-MARIPOSA TAP | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40859272 | 1986-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 1986-01-01 | Porcelain | Suspension |  |  |  |  | 6.5158e-05 | 5931.6899 | 0.3865
120085287 | F | LC | ETL.8365.POLE.WOOD | 40912604 | EUREKA | HUMBOLDT | 2020-11-20 | 2021-02-01 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40912604 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-04-22 | Glass | Double Dead End |  |  |  |  | 0.19011
120097180 | E | LC | ETL.3180.INSL.NCER | 44190119 | CONCORD | EAST BAY | 2020-11-16 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44231991 | 2014-10-23 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees |  | Non Ceramic | Suspension |  |  |  |  | 7.9211e-07 | 16.3369 | 1.2941e-05
120097180 | E | LC | ETL.3180.INSL.NCER | 44190119 | CONCORD | EAST BAY | 2020-11-16 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44231991 | 2014-10-23 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees |  | Non Ceramic | Suspension |  |  |  |  | 7.9211e-07 | 16.3369 | 1.2941e-05
120124547 | F | LC | ETL.1450.POLE.NWOD | 44868833 | SACTO | SIERRA | 2020-12-01 | 2021-06-28 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44868833 | 2019-08-16 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-08-16 | Glass | Dead End |  |  |  |  | 1.9513e-06 | 2056.7583
120126071 | E | LC | ETL.1180.POLE.WOOD | 44879462 | TABLEMTN | NORTH VALLEY | 2020-12-02 |  | ETL.1180 | BUTTE VALLEY-CARIBOU | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44879462 |  | Single Wood Pole | SV-DE-90 - Single Vertical Dead End 90 |  | Unknown | Unknown |  |  |  |  | 0.050008 | 5538.7192 | 276.981
120133639 | E | LC | ETL.1050.INSL.CERA | 40626202 | FRESNO | FRESNO | 2020-12-04 | 2021-08-09 | ETL.1050 | BALCH-SANGER | Connector | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585033 | 1923-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2019-04-02 | Ceramic | Dead End |  |  |  |  | 0.0027094 | 6295.1361
120133639 | E | LC | ETL.1050.INSL.CERA | 40626202 | FRESNO | FRESNO | 2020-12-04 | 2021-08-09 | ETL.1050 | BALCH-SANGER | Connector | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585033 | 1923-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1923-01-01 | Porcelain | Dead End |  |  |  |  | 0.0027094 | 6295.1361
120134111 | F | LC | ETL.6520.POLE.WOOD | 42562712 | SACTO | SIERRA | 2020-10-23 |  | ETL.6520 | COLGATE-SMARTVILLE #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 42562712 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.034993 | 428.1771
120150014 | F | LC | ETL.6280.POLE.WOOD | 40656539 | TABLEMTN | NORTH VALLEY | 2020-12-09 | 2020-12-10 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40656539 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Pin |  |  |  |  | 0.00011361 | 1739.9091
120220690 | F | LC | ETL.6300.POLE.NWOD | 44775180 | TABLEMTN | NORTH VALLEY | 2020-11-25 |  | ETL.6300 | CARIBOU-WESTWOOD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44775180 | 2019-05-19 | Light Duty Steel Pole | 3P DDE-A - 3 Pole Double Dead End Angle | 2019-05-19 | Polymer | Post |  |  |  |  | 1.4498e-07 | 1597.5244
120243404 | E | LC | ETL.4393.POLE.WDPS | 44172277 | SACTO | SACRAMENTO | 2020-12-31 | 2021-04-06 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120427295 | B | LC | ETL.7930.SWIT | 40744051 | MOSSLNDG | CENTRAL COAST | 2021-01-13 | 2021-01-14 | ETL.7930 | SALINAS-LAURELES | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 |  |  | COMP | [9 empty] | HIGH VELOCITY INTERRUPTER | Manual
120527356 | E | LC | ETL.1450.POLE.WDPS | 44553509 | SACTO | SACRAMENTO | 2020-07-20 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 44553185 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0015315 | 31.7066 | 0.048559
120627203 | B | LC | ETL.7390.POLE.WOOD | 40861062 | LAKEVLLE | SONOMA | 2021-03-10 | 2021-06-28 | ETL.7390 | LAYTONVILLE-COVELO | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40861062 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.65611 | 3280.324
120646974 | F | LC | ETL.5290.TOWR | 40668104 | PISMOBCH | LOS PADRES | 2021-03-12 |  | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40668104 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-19 | Glass | Suspension |  |  |  |  | 5.9251e-09 | 2090.6594 | 1.2387e-05
120646974 | F | LC | ETL.5290.TOWR | 40668104 | PISMOBCH | LOS PADRES | 2021-03-12 |  | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40668104 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-23 | Glass | Suspension |  |  |  |  | 5.9251e-09 | 2090.6594 | 1.2387e-05
120708530 | E | LC | ETL.6979.POLE.NWOD | 45121212 | LAKEVLLE | SONOMA | 2021-03-29 |  | ETL.6979 | MONTE RIO-FORT ROSS | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45121212 | 2021-07-13 | Light Duty Steel Pole | T-1 - Tri Post | 2021-07-13 | Polymer | Post | [5 empty] | 31.7242
120712647 | E | LC | ETL.5390.TOWR | 40863438 | TABLEMTN | NORTH VALLEY | 2021-03-30 | 2021-06-07 | ETL.5390 | PIT #1-COTTONWOOD | Conductor-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863438 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.0142e-08 | 4326.0913
120717361 | E | LC | ETL.5540.TOWR | 40815737 | TABLEMTN | NORTH VALLEY | 2021-03-31 |  | ETL.5540 | POE-RIO OSO | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40815737 | 1950-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | Double Dead End |  |  |  |  | 4.5173e-07 | 5787.9745 | 0.0026146
120738898 | E | LC | ETL.5330.TOWR | 40810759 | MOSSLNDG | CENTRAL COAST | 2021-04-02 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810759 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 2.3331e-05 | 208.6439 | 0.004868
120744810 | F | LC | ETL.4750.TOWR | 40605182 | LAKEVLLE | SONOMA | 2021-04-05 |  | ETL.4750 | GEYSERS #12-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40605182 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Porcelain | Suspension |  |  |  |  | 3.3641e-05 | 3246.7576 | 0.10922
120750436 | F | LC | ETL.2900.TOWR | 40762246 | MOSSLNDG | CENTRAL COAST | 2021-04-06 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762246 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0088299 | 1156.762 | 10.2141
120758357 | B | LC | ETL.7040.INSL.NCER | 40788330 | TABLEMTN | NORTH VALLEY | 2021-04-07 | 2021-05-21 | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758221 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.040993 | 969.5029
120797867 | E | LC | ETL.2720.INSL | 40851155 | CONCORD | DIABLO | 2021-04-07 |  | ETL.2720 | MORAGA-OAKLAND #1 | Splice-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40822215 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 0.00016476 | 0.065158 | 1.0735e-05
120805147 | F | LC | ETL.5780.TOWR | 40822946 | VICTOR | STOCKTON | 2021-04-13 |  | ETL.5780 | TIGER CREEK-ELECTRA | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40822946 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 1.6413e-06 | 1075.7365
120815419 | E | LC | ETL.7851.POLE.WOOD | 40824578 | EUREKA | HUMBOLDT | 2021-04-14 |  | ETL.7851 | RIO DELL TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40824578 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Non Ceramic | [5 empty] | 0.85569 | 221.4831 | 189.5211
120815523 | E | LC | ETL.2870.POLE.WOOD | 43203522 | MOSSLNDG | CENTRAL COAST | 2021-04-14 |  | ETL.2870 | SARGENT SW STA-HOLLISTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 43203522 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | [5 empty] | 5.0556e-05
120826871 | B | LC | ETL.6880.POLE.NWOD | 45071346 | LAKEVLLE | SONOMA | 2021-04-16 | 2021-05-04 | ETL.6880 | FULTON-CALISTOGA | Other | Customer Issue | [Access Issue] | Tier3 | Tier 3 | Within Both | COMP | 45071346 | 2020-03-05 | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 2020-03-05 | Glass | Suspension |  |  |  |  | 0.00066771 | 110.894
120828333 | E | LC | ETL.6470.POLE.WOOD | 40873652 | SACTO | SACRAMENTO | 2021-04-16 | 2021-08-30 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873652 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0090452 | 6094.7842
120829022 | E | LC | ETL.1073.POLE.WDPS | 44948167 | VICTOR | STOCKTON | 2021-04-16 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40860734 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00087186 | 17.4687 | 0.01523
120835045 | F | LC | ETL.4392.TOWR | 40756575 | LAKEVLLE | SONOMA | 2021-04-17 | 2021-05-03 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40756575 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-05-12 | Porcelain | Suspension |  |  |  |  | 1.1142e-06 | 2789.2666
120835045 | F | LC | ETL.4392.TOWR | 40756575 | LAKEVLLE | SONOMA | 2021-04-17 | 2021-05-03 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40756575 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-03-10 | Porcelain | Suspension |  |  |  |  | 1.1142e-06 | 2789.2666
120859169 | E | LC | ETL.6470.INSL.CERA | 40922958 | SACTO | SACRAMENTO | 2021-04-21 | 2021-08-11 | ETL.6470 | COLGATE-ALLEGHANY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120859613 | F | LC | ETL.1600.TOWR | 40810963 | LAKEVLLE | NORTH BAY | 2021-04-13 |  | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810963 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 2.4063e-06 | 2049.1519 | 0.004931
120860044 | E | LC | ETL.2400.INSL.NCER | 44670981 | VICTOR | STOCKTON | 2021-04-13 |  | ETL.2400 | MELONES-RACETRACK | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44268636 | 2018-10-24 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-10-24 | Polymer | Dead End - Suspension |  |  |  |  | 5.2e-10 | 6851.2905 | 3.5627e-06
120866832 | F | LC | ETL.3960.TOWR | 40809772 | PISMOBCH | LOS PADRES | 2021-04-14 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40809772 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 5.8911e-09 | 4654.7246
120904913 | E | LC | ETL.7055.POLE.WOOD | 40768311 | CONCORD | DIABLO | 2021-04-29 |  | ETL.7055 | BRIONES TAP | Structure-Wood | Rotten | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40768311 | 1982-01-01 | Single Wood Pole | T-1 - Tri Post | 1982-01-01 | Ceramic | Post |  |  |  |  | 0.013055 | 5022.7134 | 65.571
120944342 | E | LC | ETL.4521.POLE.NWOD | 40593224 | CONCORD | DIABLO | 2021-05-06 | 2021-09-29 | ETL.4521 | US WINDPOWER #3 TAP | Switch | Out of Adjustment | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593224 | 2012-01-01 | Tubular Steel Pole | DV-DE - Double Vertical Dead End | 1984-01-01 | Ceramic | Other |  |  |  |  | 2.7713e-07 | 5466.0889
120947392 | F | LC | ETL.7550.POLE.WOOD | 40750965 | LAKEVLLE | SONOMA | 2021-05-06 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40750965 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 1.3978e-06 | 79.143
121190108 | F | LC | ETL.7550.POLE.WOOD | 40861435 | LAKEVLLE | SONOMA | 2021-05-11 | 2021-07-12 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40861435 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.00137 | 15.8807
121328919 | E | LC | ETL.2720.TOWR | 40857639 | CONCORD | DIABLO | 2021-04-21 |  | ETL.2720 | MORAGA-OAKLAND #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40857639 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1931-01-01 | Non Ceramic | Dead End |  |  |  |  | 7.7847e-06 | 0.065147 | 5.0715e-07
121328919 | E | LC | ETL.2720.TOWR | 40857639 | CONCORD | DIABLO | 2021-04-21 |  | ETL.2720 | MORAGA-OAKLAND #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40857639 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1931-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 7.7847e-06 | 0.065147 | 5.0715e-07
121333610 | E | LC | ETL.6470.POLE.WOOD | 40874698 | SACTO | SIERRA | 2021-05-14 | 2021-07-29 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40874698 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Post |  |  |  |  | 0.0029667 | 237.3428
121339315 | E | LC | ETL.1420.INSL.NCER | 44984461 | SACTO | SIERRA | 2021-04-26 |  | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40866026 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.0078808 | 3865.0645 | 30.4598
121339315 | E | LC | ETL.1420.INSL.NCER | 44984461 | SACTO | SIERRA | 2021-04-26 |  | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40866026 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-09-07 | Glass | Suspension |  |  |  |  | 0.0078808 | 3865.0645 | 30.4598
121360333 | E | LC | ETL.4870.TOWR | 40576615 | FRESNO | FRESNO | 2021-05-19 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576615 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 3.4639e-06 | 2957.7136 | 0.010245
121363621 | F | LC | ETL.1820.POLE.STPS | 44395440 | EUREKA | HUMBOLDT | 2021-05-19 |  | ETL.1820 | HUMBOLDT-TRINITY | Conductor-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395438 | 2020-03-04 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.009475 | 6300.0015
121365112 | F | LC | ETL.1820.POLE.STPS | 44260987 | EUREKA | HUMBOLDT | 2021-05-19 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44260986 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.027186 | 94.963
121370068 | E | LC | ETL.1820.POLE.WDPS | 44560670 | EUREKA | HUMBOLDT | 2021-05-20 | 2021-08-30 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [12 empty] | 6300.0015
121371201 | E | LC | ETL.6880.POLE.WOOD | 40912473 | LAKEVLLE | NORTH BAY | 2021-05-01 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40912473 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.01018 | 476.0715 | 4.8463
121372695 | F | LC | ETL.8290.POLE.WOOD | 40600274 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40600274 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.0048702 | 3232.478
121373400 | F | LC | ETL.4550.TOWR | 40601457 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40601457 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.251e-06 | 4579.355 | 0.010308
121378120 | B | LC | ETL.7820.POLE.WOOD | 40768611 | LAKEVLLE | SONOMA | 2021-05-21 | 2021-07-07 | ETL.7820 | POTTER VALLEY-WILLITS | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40768611 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 7.05e-05 | 2024.8344
121378820 | F | LC | ETL.6760.POLE.WOOD | 40693382 | SACTO | SIERRA | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40693382 |  | Single Wood Pole | T-1 - Tri Post | 2019-08-13 | Polymer | Post |  |  |  |  | 0.0058464 | 0.066432
121381184 | F | LC | ETL.8350.POLE.NWOD | 44359637 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44359637 | 2016-12-09 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2016-12-09 | Polymer | [5 empty] | 4.1479e-09 | 31.7022
121382056 | F | LC | ETL.8250.POLE.WOOD | 40908836 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908836 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00053222 | 1664.5133
121382102 | F | LC | ETL.6500.POLE.NWOD | 40597460 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40597460 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.00021124 | 3888.6564
121384564 | E | LC | ETL.6500.POLE.WOOD | 40757112 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40757112 |  | Single Wood Pole | T2N | 2018-06-29 | Polymer | Post |  |  |  |  | 0.0025158 | 1064.2323 | 2.6774
121384662 | F | LC | ETL.4393.TOWR | 40814105 | SACTO | SIERRA | 2021-05-12 |  | ETL.4393 | DRUM-HIGGINS | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40814105 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 7.7031e-08 | 3071.4875
121397958 | F | LC | ETL.7212.POLE.WOOD | 40867883 | METCALF | PENINSULA | 2021-05-19 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40867883 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 2018-07-24 | Glass | Suspension |  |  |  |  | 0.43403 | 966.1616
121404708 | E | LC | ETL.8290.POLE.WOOD | 40875831 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.8290 | VOLTA-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40875831 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.00019898 | 4041.0511 | 0.8041
121404973 | E | LC | ETL.2710.INSL.CERA | 43203363 | CONCORD | EAST BAY | 2021-05-19 |  | ETL.2710 | MORAGA-CLAREMONT #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44188844 | 2008-01-01 | LATTICE STEEL TOWER | Unknown |  | Ceramic | Unknown |  |  |  |  | 4.3482e-06 | 445.731 | 0.0019381
121405061 | E | LC | ETL.3840.INSL.NCER | 40829052 | VICTOR | STOCKTON | 2021-05-21 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40803360 | 1927-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 1.0098e-06 | 1633.3451 | 0.0016493
121405623 | F | LC | ETL.7000.POLE.WOOD | 40656640 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-10 | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40656640 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0021886 | 458.7379
121408275 | F | LC | ETL.7560.POLE.NWOD | 44923845 | SACTO | SIERRA | 2021-05-20 |  | ETL.7560 | WEIMAR #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | HFRA Removal | PEND | 44923845 | 2019-06-23 | Light Duty Steel Pole | T2N | 2019-06-23 | Polymer | Post |  |  |  |  | 0.050049 | 2768.4309 | 138.5583
121417717 | F | LC | ETL.7040.POLE.WOOD | 40758240 | TABLEMTN | NORTH VALLEY | 2021-05-24 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758240 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0087841 | 1664.4871
121452318 | E | LC | ETL.8365.POLE.WOOD | 40768633 | EUREKA | HUMBOLDT | 2021-05-28 | 2021-06-28 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40768633 | 2010-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0037405 | 1359.6121
121454241 | E | LC | ETL.1401.POLE.WDPS | 44390909 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1401 | BEARDSLEY TAP | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44390907 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00034063 | 47.5548 | 0.016198
121474598 | E | LC | ETL.1440.INSL | 40669774 | SACTO | SIERRA | 2021-06-05 |  | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40642863 |  | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 1.426e-06 | 2056.7583 | 0.002933
121488603 | E | LC | ETL.5140.INSL | 40895362 | SACTO | SIERRA | 2021-06-07 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40870401 | 1965-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1965-01-01 | Ceramic | Dead End |  |  |  |  | 1.097e-06 | 6874.0736 | 0.0075411
121493094 | E | LC | ETL.6890.POLE.WOOD | 40648296 | LAKEVLLE | HUMBOLDT | 2021-06-02 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40648296 | 1932-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0031401 | 2053.5329 | 6.4483
121496065 | E | LC | ETL.7040.INSL.NCER | 40788344 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758235 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.4127 | 398.0284 | 164.2657
121498227 | B | LC | ETL.1450.POLE.WDPS | 44420819 | SACTO | SACRAMENTO | 2021-06-08 | 2021-08-05 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420818 |  | 2-Pole Wood | THDE - Tri Post Dead End 60 | [7 empty] | 0.0024883 | 3765.6233
121514015 | E | LC | ETL.6890.INSL.CERA | 44713099 | LAKEVLLE |  | 2021-05-11 |  | ETL.6890 | FULTON-HOPLAND | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44713031 | 2019-02-16 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-02-06 | Ceramic | Suspension |  |  |  |  | 1.3676e-07 | 791.7091 | 0.00010828
121518448 | E | LC | ETL.6720.POLE.WOOD | 40649880 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40649880 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 7.874e-05 | 0.065151 | 5.13e-06
121522035 | E | LC | ETL.4450.INSL | 40690785 | CONCORD | MISSION | 2021-06-05 |  | ETL.4450 | CASTRO VALLEY-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40660135 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.095e-05 | 2231.1023 | 0.02443
121522035 | E | LC | ETL.4450.INSL | 40690785 | CONCORD | MISSION | 2021-06-05 |  | ETL.4450 | CASTRO VALLEY-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40660135 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 1.095e-05 | 2231.1023 | 0.02443
121525073 | E | LC | ETL.8650.TOWR | 40859245 | FRESNO | FRESNO | 2021-06-12 | 2021-08-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40859245 | 1929-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0044388 | 5662.9517
121527528 | E | LC | ETL.1600.TOWR | 40870233 | LAKEVLLE | SONOMA | 2021-06-11 |  | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40870233 | 1955-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1946-01-01 | Polymer | Dead End |  |  |  |  | 3.2954e-05 | 1567.5188 | 0.051656
121535938 | F | LC | ETL.6760.POLE.WOOD | 40767269 | SACTO | SIERRA | 2021-06-09 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40767269 | 1999-01-01 | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | Dead End |  |  |  |  | 0.034224 | 649.2313
121538949 | E | LC | ETL.4770.INSL | 40785646 | LAKEVLLE |  | 2021-06-14 |  | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40756490 | 1971-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 9.2298e-06 | 950.5959 | 0.0087739
121539983 | F | LC | ETL.6510.POLE.WOOD | 44399419 | SACTO | SACRAMENTO | 2021-06-15 | 2021-08-09 | ETL.6510 | COLGATE-SMARTVILLE #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44399416 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 4.5629e-07 | 1092.7948
121554022 | E | LC | ETL.6050.TOWR | 40753741 | MOSSLNDG | SAN JOSE | 2021-06-16 |  | ETL.6050 | MOSS LANDING-METCALF | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753741 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 2019-08-29 | Glass | Suspension |  |  |  |  | 2.2772e-08 | 2643.032 | 6.0187e-05
121564736 | F | LC | ETL.1820.POLE.STPS | 44395502 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395500 | 2020-03-03 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017115 | 5095.5723
121568892 | E | LC | ETL.4950.TOWR | 40864245 | LAKEVLLE | SONOMA | 2021-06-16 |  | ETL.4950 | FULTON-LAKEVILLE | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier2 | Tier 2 | Within Both | PEND | 40864245 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.012287 | 732.0612 | 8.9947
121568892 | E | LC | ETL.4950.TOWR | 40864245 | LAKEVLLE | SONOMA | 2021-06-16 |  | ETL.4950 | FULTON-LAKEVILLE | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier2 | Tier 2 | Within Both | PEND | 40864245 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.012287 | 732.0612 | 8.9947
121573469 | E | LC | ETL.6852.POLE.WOOD | 41134785 | LAKEVLLE | HUMBOLDT | 2021-06-10 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 41134785 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-11-01 | Ceramic | Suspension |  |  |  |  | 0.021243 | 6506.4966 | 138.2155
121630008 | E | LC | ETL.1070.INSL.NCER | 45073124 | VICTOR | STOCKTON | 2021-06-22 | 2021-10-12 | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 45073099 | 2021-03-05 | Light Duty Steel Pole | TPS1D - Tri Post & Susp DDE 115 KV | 2021-03-05 | Glass | Dead End - Suspension |  |  |  |  | 4.8291e-10 | 2633.8957
121649541 | E | LC | ETL.6470.POLE.WOOD | 40822642 | SACTO | SIERRA | 2021-06-26 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40822642 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 0.10043 | 253.2093 | 25.4305
121659068 | B | LC | ETL.3730.INSL | 40830924 | CONCORD | EAST BAY | 2021-07-01 | 2021-08-16 | ETL.3730 | SOBRANTE-G #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40804933 | 1968-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1968-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.4665e-06 | 356.4935
121659256 | E | LC | ETL.2540.POLE.WDPS | 44401535 | MOSSLNDG | CENTRAL COAST | 2021-06-29 |  | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44401534 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.009099 | 385.9546 | 3.5118
121679351 | E | LC | ETL.6650.POLE.WDPS | 44386808 | TABLEMTN | NORTH VALLEY | 2021-07-01 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44386807 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.014681 | 2441.9417 | 35.85
121687929 | E | LC | ETL.3700.POLE.WDPS | 44296815 | PISMOBCH | LOS PADRES | 2021-07-09 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44296813 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.9923e-05 | 3642.803 | 0.109
121713219 | F | LC | ETL.1073.POLE.NWOD | 45083297 | VICTOR | YOSEMITE | 2021-07-08 | 2021-08-16 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL | [11 empty] | 1.5603e-05 | 31.7081
121722364 | F | LC | ETL.5140.POLE.NWOD | 45146233 | SACTO | SIERRA | 2021-07-08 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45146233 | 2020-07-25 | Light Duty Steel Pole | DDE - Double Dead End | 2020-07-25 | Glass | Dead End
121732143 | E | LC | ETL.5400.INSL | 40726224 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.5400 | PIT #3-PIT #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40684015 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 0.058619 | 4935.4473 | 289.3102
121738158 | F | LC | ETL.1820.POLE.STPS | 44395293 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395292 | 2017-11-29 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00048623 | 2360.6118
121738884 | E | LC | ETL.6450.POLE.WOOD | 40655910 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.6450 | COLEMAN-SOUTH | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40655910 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.00030411 | 6175.3105 | 1.878
121741699 | E | LC | ETL.7850.POLE.WOOD | 40826290 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40826290 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 9.61e-05 | 641.5788 | 0.061656
121800252 | F | LC | ETL.9240.TOWR | 43249621 | PISMOBCH | LOS PADRES | 2021-07-26 | 2021-09-27 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249621 |  | LATTICE STEEL TOWER | [9 empty] | 1871.2655
121810085 | E | LC | ETL.8365.POLE.WOOD | 45009255 | EUREKA | HUMBOLDT | 2021-07-27 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 45009255 | 2020-11-09 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-11-09 | Glass | Dead End |  |  |  |  | 0.057127
121816111 | E | LC | ETL.7390.POLE.WOOD | 40808392 | LAKEVLLE | HUMBOLDT | 2021-07-29 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40808392 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.10403 | 696.1808 | 72.426
121820983 | B | LC | ETL.6290.POLE.WOOD | 40815674 | TABLEMTN | NORTH VALLEY | 2021-07-30 | 2021-10-05 | ETL.6290 | CARIBOU-PLUMAS JCT | Emergency | Fire | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.092505 | 126.5956
122007347 | E | LC | ETL.6310.POLE.WOOD | 40600656 | TABLEMTN | NORTH VALLEY | 2021-09-07 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40600656 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.6827e-05 | 3390.7913 | 0.057057
122058346 | E | LC | ETL.4780.INSL.NCER | 45129022 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129366 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 6.7769e-05 | 1160.0938 | 0.078619
122058346 | E | LC | ETL.4780.INSL.NCER | 45129022 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129366 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 6.7769e-05 | 1160.0938 | 0.078619
118718211 | A | LC | ETL.6690.POLE.WOOD | 42568597 | SACTO | SACRAMENTO | 2020-03-18 | 2020-04-27 | ETL.6690 | DEER CREEK-DRUM | Conductor-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
118771545 | E | LC | ETL.7212.INSL.NCER | 44913384 | METCALF | PENINSULA | 2020-04-02 | 2021-08-12 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Damper-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768024 |  | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2019-11-06 | Glass | Suspension |  |  |  |  | 0.011369 | 412.0099
118771545 | E | LC | ETL.7212.INSL.NCER | 44913384 | METCALF | PENINSULA | 2020-04-02 | 2021-08-12 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Damper-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768024 |  | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2019-02-01 | Ceramic | Suspension |  |  |  |  | 0.011369 | 412.0099
118778932 | E | LC | ETL.5780.TOWR | 40752893 | VICTOR | STOCKTON | 2020-04-06 | 2021-06-07 | ETL.5780 | TIGER CREEK-ELECTRA | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40752893 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 1.6585e-07 | 1075.7365
118898238 | E | LC | ETL.4392.TOWR | 40596513 | LAKEVLLE | SONOMA | 2020-04-08 | 2020-05-13 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40596513 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2020-03-14 | Porcelain | Dead End |  |  |  |  | 2.7013e-06 | 1680.3796
118898238 | E | LC | ETL.4392.TOWR | 40596513 | LAKEVLLE | SONOMA | 2020-04-08 | 2020-05-13 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40596513 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 2.7013e-06 | 1680.3796
118899344 | E | LC | ETL.4750.INSL.CERA | 40792278 | LAKEVLLE |  | 2020-04-09 | 2021-03-15 | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118934184 | E | LC | ETL.1600.TOWR | 40862873 | LAKEVLLE | SONOMA | 2020-04-20 |  | ETL.1600 | FULTON-PUEBLO | Right of Way | Encroachment | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40862873 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2019-12-16 | Glass | Dead End |  |  |  |  | 2.3549e-07 | 775.2442
118955192 | F | LC | ETL.4392.TOWR | 41129323 | LAKEVLLE | SONOMA | 2020-04-28 | 2020-06-18 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129323 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.00016787 | 2470.457
118955192 | F | LC | ETL.4392.TOWR | 41129323 | LAKEVLLE | SONOMA | 2020-04-28 | 2020-06-18 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129323 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.00016787 | 2470.457
118979901 | F | LC | ETL.4220.POLE.WOOD | 40598532 | TABLEMTN | NORTH VALLEY | 2020-04-29 | 2020-06-02 | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 |  |  | COMP
118987807 | F | LC | ETL.1073.POLE.WOOD | 40744858 | VICTOR | YOSEMITE | 2020-04-23 | 2020-06-10 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40744858 | 1956-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00027269
118987807 | F | LC | ETL.1073.POLE.WOOD | 40744858 | VICTOR | YOSEMITE | 2020-04-23 | 2020-06-10 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40744858 | 1956-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00027269
118987807 | F | LC | ETL.1073.POLE.WOOD | 40744858 | VICTOR | YOSEMITE | 2020-04-23 | 2020-06-10 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40744858 | 1956-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00027269
119013305 | A | LC | ETL.7510.POLE.WOOD | 40752839 | LAKEVLLE | SONOMA | 2020-05-10 | 2020-05-12 | ETL.7510 | MENDOCINO-HARTLEY | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752839 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 4.7053e-05 | 2171.0598
119015404 | B | LC | ETL.4220.POLE.WOOD | 40758033 | TABLEMTN | NORTH VALLEY | 2020-05-11 | 2020-06-09 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119016737 | E | LC | ETL.8410.INSL.CERA | 40793176 | LAKEVLLE | HUMBOLDT | 2020-05-06 | 2021-02-09 | ETL.8410 | ELK-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119026673 | E | LC | ETL.1600.TOWR | 40586782 | LAKEVLLE | NORTH BAY | 2020-05-12 | 2021-03-02 | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40586782 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 1.3756e-06 | 110.8668
119026673 | E | LC | ETL.1600.TOWR | 40586782 | LAKEVLLE | NORTH BAY | 2020-05-12 | 2021-03-02 | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40586782 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 1.3756e-06 | 110.8668
119036668 | B | LC | ETL.6810.POLE.WOOD | 40588607 | EUREKA | HUMBOLDT | 2020-05-07 | 2021-03-18 | ETL.6810 | ESSEX JCT-ORICK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Zone 1 | HFRA Removal | COMP | 40588607 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.41842
119060809 | F | LC | ETL.5780.POLE.STPS | 44373671 | VICTOR | STOCKTON | 2020-05-20 | 2021-09-28 | ETL.5780 | TIGER CREEK-ELECTRA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44373670 | 2016-10-20 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.1624e-06 | 47.5207
119074148 | F | LC | ETL.1400.POLE.NWOD | 44804158 | VICTOR | YOSEMITE | 2020-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44804158 | 2019-08-06 | Light Duty Steel Pole | DDE - Double Dead End | 2019-08-06 | Glass | Double Dead End |  |  |  |  | 2.0639e-05 | 4176.9663
119076444 | E | LC | ETL.1050.INSL.CERA | 40708331 | FRESNO | FRESNO | 2020-05-27 | 2021-07-22 | ETL.1050 | BALCH-SANGER | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119099671 | E | LC | ETL.6330.POLE.NWOD | 40824067 | TABLEMTN | NORTH VALLEY | 2020-06-02 | 2021-04-19 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40824067 | 1998-01-01 | Tubular Steel Pole | TH - TriAngle Post 70 |  | Non Ceramic | Pin |  |  |  |  | 9.0602e-06 | 4782.7798
119103513 | F | LC | ETL.5290.TOWR | 40753055 | PISMOBCH | LOS PADRES | 2020-05-18 |  | ETL.5290 | MORRO BAY-MESA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40753055 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-01 | Glass | Suspension |  |  |  |  | 1.7087e-09 | 2312.019
119103513 | F | LC | ETL.5290.TOWR | 40753055 | PISMOBCH | LOS PADRES | 2020-05-18 |  | ETL.5290 | MORRO BAY-MESA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40753055 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.7087e-09 | 2312.019
119110330 | F | LC | ETL.1710.POLE.WDPS | 44512082 | MOSSLNDG | CENTRAL COAST | 2020-05-20 | 2021-04-01 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44510831 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0022426 | 15.88
119118450 | E | LC | ETL.6490.INSL | 40851085 | SACTO | SACRAMENTO | 2020-05-28 | 2021-09-23 | ETL.6490 | COLGATE-GRASS VALLEY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119118614 | E | LC | ETL.6490.POLE.WOOD | 40767582 | SACTO | SIERRA | 2020-06-02 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40767582 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.020438 | 569.5441 | 11.6404
119119225 | F | LC | ETL.8240.POLE.WOOD | 40816461 | VICTOR | STOCKTON | 2020-06-01 |  | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40816461 | 1993-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0040071 | 2804.8376
119119437 | F | LC | ETL.6470.POLE.WOOD | 40602502 | SACTO | SIERRA | 2020-06-01 | 2021-02-10 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40602502 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.040234 | 1439.967
119120136 | E | LC | ETL.7300.POLE.WOOD | 40676474 | TABLEMTN |  | 2020-06-03 | 2021-03-15 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676474 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00063244 | 1229.7022
119131933 | F | LC | ETL.8220.POLE.WOOD | 40658510 | VICTOR | STOCKTON | 2020-06-09 | 2021-04-07 | ETL.8220 | VALLEY SPRINGS-CALAVERAS CEMENT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40658510 | 1963-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 4.8333e-05 | 2122.9976
119140063 | F | LC | ETL.6320.POLE.NWOD | 44384845 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44384845 | 2018-10-04 | Light Duty Steel Pole | T-1 - Tri Post | 2018-10-04 | Polymer | Post |  |  |  |  | 2.6083e-07 | 622.0948
119148396 | E | LC | ETL.7300.POLE.WOOD | 40817236 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-03-26 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119161784 | F | LC | ETL.7260.POLE.WOOD | 40867907 | TABLEMTN | NORTH VALLEY | 2020-06-09 | 2021-04-29 | ETL.7260 | KESWICK-CASCADE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40867907 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00014403 | 3564.7319
119162966 | E | LC | ETL.4040.POLE.STPS | 44923037 | TABLEMTN | NORTH VALLEY | 2020-06-13 | 2021-08-23 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44922941 | 2020-03-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.4403e-05 | 2077.158
119165684 | F | LC | ETL.6480.POLE.WOOD | 40611341 | SACTO | NORTH VALLEY | 2020-06-15 | 2021-06-21 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119166337 | F | LC | ETL.6480.POLE.WOOD | 40598651 | SACTO | NORTH VALLEY | 2020-06-15 | 2020-11-12 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40598651 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.15123 | 63.3392
119169924 | F | LC | ETL.1810.POLE.STPS | 44950918 | EUREKA | HUMBOLDT | 2020-06-12 | 2021-04-20 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | DLFL | 44950899 | 2020-04-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.9248e-05
119181860 | E | LC | ETL.6980.POLE.WOOD | 40750297 | LAKEVLLE | SONOMA | 2020-04-24 | 2021-06-22 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750297 | 1985-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1953-01-01 | Polymer | Dead End |  |  |  |  | 0.44233 | 205.8492
119184574 | E | LC | ETL.2760.INSL | 40676704 | CONCORD | EAST BAY | 2020-06-17 | 2021-03-31 | ETL.2760 | MORAGA-OAKLAND J | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119185872 | F | LC | ETL.8210.POLE.WOOD | 40908256 | VICTOR | STOCKTON | 2020-04-07 |  | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908256 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.001979 | 523.1114
119188070 | F | LC | ETL.7300.POLE.WOOD | 40676511 | TABLEMTN |  | 2020-06-18 | 2020-07-28 | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | DLFL
119194834 | F | LC | ETL.6470.POLE.WOOD | 40760458 | SACTO | SIERRA | 2020-06-19 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760458 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.091084 | 174.1689
119196216 | F | LC | ETL.6470.POLE.WOOD | 40868969 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40868969 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Other |  |  |  |  | 0.078797 | 269.0426
119196216 | F | LC | ETL.6470.POLE.WOOD | 40868969 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40868969 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Post |  |  |  |  | 0.078797 | 269.0426
119197603 | F | LC | ETL.6470.POLE.WOOD | 40760447 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40760447 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.033165 | 269.0553
119199043 | F | LC | ETL.6480.POLE.WOOD | 40598489 | SACTO | SIERRA | 2020-06-22 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40598489 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.18722 | 316.5113
119199326 | E | LC | ETL.6470.POLE.WOOD | 40817348 | SACTO | SIERRA | 2020-06-23 | 2021-08-03 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | DLFL | [11 empty] | 0.033268 | 120.3368
119219172 | E | LC | ETL.5140.POLE.NWOD | 41195908 | SACTO | SACRAMENTO | 2020-06-26 | 2020-10-28 | ETL.5140 | MIDDLE FORK-GOLD HILL | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 41195908 |  | Lattice Steel Pole | Unknown |  | Non Ceramic | [5 empty] | 0.00035205 | 186.7919
119238049 | E | LC | ETL.5420.INSL.NCER | 44931523 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44931501 | 2020-06-16 | 2-Pole Wood | 2PS TRP - 2 Pole SUSP. Transposition | 2020-06-16 | Glass | Suspension |  |  |  |  | 6.2649e-05
119238049 | E | LC | ETL.5420.INSL.NCER | 44931523 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44931501 | 2020-06-16 | 2-Pole Wood | 2PS TRP - 2 Pole SUSP. Transposition | 2020-06-16 | Glass | Suspension |  |  |  |  | 6.2649e-05
119289792 | E | LC | ETL.6690.POLE.WOOD | 40822856 | SACTO | SACRAMENTO | 2020-06-30 | 2021-03-22 | ETL.6690 | DEER CREEK-DRUM | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822856 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | [5 empty] | 0.053636 | 142.4642
119293505 | E | LC | ETL.1370.INSL | 40641779 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-08-23 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119293825 | F | LC | ETL.6690.POLE.WOOD | 40822852 | SACTO | SACRAMENTO | 2020-07-01 |  | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40822852 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.044909 | 63.348
119294574 | E | LC | ETL.3540.INSL.CERA | 40711700 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-06-07 | ETL.3540 | SAN LUIS OBISPO-SANTA MARIA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40658759 | 1952-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2021-06-09 | Glass | Dead End |  |  |  |  | 1.2651e-06 | 807.7476
119294574 | E | LC | ETL.3540.INSL.CERA | 40711700 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-06-07 | ETL.3540 | SAN LUIS OBISPO-SANTA MARIA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40658759 | 1952-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1952-01-01 | Porcelain | Dead End |  |  |  |  | 1.2651e-06 | 807.7476
119310159 | E | LC | ETL.1450.INSL.CERA | 40633501 | SACTO | SACRAMENTO | 2020-07-01 | 2020-08-24 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119311103 | F | LC | ETL.2660.TOWR | 40651647 | SACTO | SIERRA | 2020-07-01 | 2021-02-11 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40651647 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Ceramic | Suspension |  |  |  |  | 1.0273e-08 | 3436.4141
119311103 | F | LC | ETL.2660.TOWR | 40651647 | SACTO | SIERRA | 2020-07-01 | 2021-02-11 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40651647 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-12 | Glass | Suspension |  |  |  |  | 1.0273e-08 | 3436.4141
119317006 | F | LC | ETL.7630.POLE.WOOD | 40597977 | LAKEVLLE | SONOMA | 2020-07-06 | 2020-12-31 | ETL.7630 | MONTE RIO-FULTON | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40597977 | 1995-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.040449 | 94.985
119317279 | E | LC | ETL.1110.POLE.WDPS | 44424422 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-04-12 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424420 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0017394 | 3040.7186
119323345 | B | LC | ETL.5970.TOWR | 40871721 | PISMOBCH | LOS PADRES | 2020-07-07 | 2020-08-03 | ETL.5970 | DIABLO-MIDWAY #2 | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40871721 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-30 | Glass Silicone Coated | Suspension |  |  |  |  | 8.6427e-10 | 3657.9473
119324154 | F | LC | ETL.7980.POLE.WOOD | 40760394 | SACTO | SIERRA | 2020-07-07 |  | ETL.7980 | SMARTVILLE-MARYSVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40760394 |  | Single Wood Pole | T-1 - Tri Post | 2021-01-15 | Polymer | Post |  |  |  |  | 0.0010462 | 2346.4021
119325600 | B | LC | ETL.7780.POLE.NWOD | 40666543 | LAKEVLLE | SONOMA | 2020-07-07 | 2020-10-27 | ETL.7780 | PHILO JCT-ELK | Other | Customer Issue | [Access Issue, Completed] |  | Tier 2 | Within Both | COMP | 40666543 |  | Light Duty Steel Pole | FSS - Field Switch Structure | [7 empty] | 7.3549e-07 | 316.4353
119325633 | B | LC | ETL.4393.POLE.WDPS | 44202756 | SACTO | SACRAMENTO | 2020-07-07 | 2020-09-15 | ETL.4393 | DRUM-HIGGINS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44202754 | 2015-03-27 | 3-Pole Wood | DV - Double Vertical | [7 empty] | 1.3763e-05 | 300.8319
119325901 | F | LC | ETL.8060.POLE.WOOD | 40862199 | SACTO | SIERRA | 2020-07-07 | 2021-05-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862199 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0068206 | 1819.4475
119330621 | F | LC | ETL.8060.POLE.WOOD | 40590001 | SACTO | SIERRA | 2020-07-07 | 2021-05-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119330900 | F | LC | ETL.6300.POLE.WOOD | 40615009 | TABLEMTN |  | 2020-07-07 | 2021-10-04 | ETL.6300 | CARIBOU-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | DLFL | 40615009 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 6.4523e-07 | 0.065148
119335946 | E | LC | ETL.6900.POLE.WOOD | 40580910 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-03-03 | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Insulator | Contaminated | [Ground Wash] |  | Tier 2 | Within Both | DLFL | 40580910 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post |  | Porcelain | Post |  |  |  |  | 1.184e-06 | 0.065158
119339861 | B | LC | ETL.1110.TOWR | 40592233 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2020-10-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Other | Customer Issue | [Customer Refusal, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592233 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.7661e-05 | 63.351
119339861 | B | LC | ETL.1110.TOWR | 40592233 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2020-10-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Other | Customer Issue | [Customer Refusal, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592233 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 2.7661e-05 | 63.351
119340512 | E | LC | ETL.7300.POLE.WOOD | 40827912 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-03-08 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827912 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00022295 | 5356.6348
119341018 | E | LC | ETL.3190.TOWR | 40668944 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.3190 | CARIBOU-PALERMO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40668944 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.060927 | 537.9698 | 32.777
119341396 | F | LC | ETL.1430.TOWR | 40858065 | SACTO | SACRAMENTO | 2020-07-09 | 2021-07-22 | ETL.1430 | DRUM-RIO OSO #2 | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40858065 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-03-20 | Glass | Dead End |  |  |  |  | 0.00028023 | 0.065152
119341399 | E | LC | ETL.1430.TOWR | 40746580 | SACTO | SACRAMENTO | 2020-07-09 | 2020-12-04 | ETL.1430 | DRUM-RIO OSO #2 | Vegetation-Tower | Overgrown | [Cage Clearing, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40746580 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2016-11-14 | Ceramic | Suspension |  |  |  |  | 0.0010538 | 15.9216
119367913 | E | LC | ETL.6280.POLE.WOOD | 40768854 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-08-17 | ETL.6280 | CARIBOU #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768854 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 2.6629e-05 | 5124.6736
119369679 | E | LC | ETL.5970.TOWR | 40871219 | PISMOBCH | LOS PADRES | 2020-07-14 | 2021-05-17 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871219 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-04-22 | Glass | Suspension |  |  |  |  | 1.8417e-07 | 2991.8135
119462197 | F | LC | ETL.1810.TOWR | 40598282 | EUREKA | HUMBOLDT | 2020-07-15 | 2021-02-09 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40598282 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Polymer | Suspension |  |  |  |  | 0.0045066
119475353 | E | LC | ETL.3180.INSL | 40775617 | CONCORD | DIABLO | 2020-07-20 | 2021-08-12 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40747004 | 1921-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1963-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.9055e-06 | 207.208
119475353 | E | LC | ETL.3180.INSL | 40775617 | CONCORD | DIABLO | 2020-07-20 | 2021-08-12 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40747004 | 1921-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-04-08 | Glass Silicone Coated | Dead End |  |  |  |  | 3.9055e-06 | 207.208
119483147 | F | LC | ETL.7540.POLE.WOOD | 41113147 | LAKEVLLE | HUMBOLDT | 2020-07-21 | 2021-04-10 | ETL.7540 | MENDOCINO-WILLITS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41113147 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00074997 | 1105.778
119486481 | E | LC | ETL.2470.POLE.WOOD | 40861589 | MOSSLNDG | CENTRAL COAST | 2020-07-22 |  | ETL.2470 | METCALF-COYOTE PUMPING PLANT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40861589 | 1986-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1986-01-01 | Ceramic | Suspension |  |  |  |  | 1.7283e-05
119488535 | F | LC | ETL.8170.POLE.WOOD | 40906305 | EUREKA | HUMBOLDT | 2020-07-21 | 2020-08-14 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40906305 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.019156 | 5491.4502
119492760 | B | LC | ETL.1440.INSL | 40615563 | SACTO | SIERRA | 2020-07-22 | 2020-09-22 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119495909 | F | LC | ETL.6280.POLE.NWOD | 44258993 | TABLEMTN | NORTH VALLEY | 2020-07-23 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44258993 | 2020-07-21 | Light Duty Steel Pole | T2N | 2020-07-21 | Polymer | Post |  |  |  |  | 4.8058e-10 | 0.065148
119500449 | E | LC | ETL.4393.POLE.WDPS | 44172222 | SACTO | SACRAMENTO | 2020-07-23 | 2021-01-25 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44172220 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 8.6873e-06 | 1360.4569
119522657 | F | LC | ETL.6890.POLE.WOOD | 40587771 | LAKEVLLE | SONOMA | 2020-07-29 | 2021-02-12 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40587771 | 1948-01-01 | Single Wood Pole | DV - Double Vertical | 2021-03-12 | Glass | Double Dead End |  |  |  |  | 0.00057675 | 745.8444
119523555 | E | LC | ETL.7510.POLE.WOOD | 40826586 | LAKEVLLE | SONOMA | 2020-07-29 | 2020-09-02 | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119528677 | E | LC | ETL.6480.INSL.NCER | 40787321 | SACTO | SACRAMENTO | 2020-07-30 | 2021-06-17 | ETL.6480 | COLGATE-CHALLENGE | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40757260 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | Post |  |  |  |  | 0.40174 | 189.8873
119549979 | E | LC | ETL.7780.POLE.WOOD | 40595267 | LAKEVLLE | SONOMA | 2020-08-03 | 2021-04-08 | ETL.7780 | PHILO JCT-ELK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40595267 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Non Ceramic | Pin |  |  |  |  | 0.00011877 | 3862.9951
119556384 | E | LC | ETL.7360.INSL.NCER | 44137073 | LAKEVLLE |  | 2020-08-04 | 2021-01-14 | ETL.7360 | LAKEVILLE #1 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44137070 | 2013-12-05 | Light Duty Steel Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 1.4341e-05 | 221.6582
119557732 | E | LC | ETL.6220.POLE.WOOD | 40824457 | EUREKA | HUMBOLDT | 2020-08-04 | 2021-02-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40824457 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.25822
119560176 | E | LC | ETL.6300.POLE.WOOD | 40769695 | TABLEMTN |  | 2020-08-04 | 2021-07-21 | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119578409 | E | LC | ETL.6490.POLE.WOOD | 40874472 | SACTO | SACRAMENTO | 2020-08-07 | 2021-09-01 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40874472 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Post |  |  |  |  | 0.0043231 | 4144.5146
119578523 | F | LC | ETL.7340.POLE.WOOD | 43219776 | LAKEVLLE | SONOMA | 2020-08-07 |  | ETL.7340 | LAKEVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 43219776 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Other |  |  |  |  | 0.0026904 | 891.0143
119600387 | E | LC | ETL.7930.POLE.WOOD | 40812867 | MOSSLNDG | CENTRAL COAST | 2020-08-11 | 2021-07-26 | ETL.7930 | SALINAS-LAURELES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40812867 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0016779 | 0.066432
119600584 | F | LC | ETL.9210.POLE.WOOD | 40662106 | MIDWAY | KERN | 2020-08-11 |  | ETL.9210 | TAFT-CUYAMA #2 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40662106 | 1946-01-01 | Single Wood Pole | 2PS - 2 Pole SUSP | 1946-01-01 | Ceramic | Pin |  |  |  |  | 0.084192
119600746 | E | LC | ETL.6330.POLE.WOOD | 40767075 | TABLEMTN | NORTH VALLEY | 2020-08-11 | 2021-09-14 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40767075 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0025214 | 3343.2844
119602896 | E | LC | ETL.1110.TOWR | 40604126 | TABLEMTN | HUMBOLDT | 2020-08-11 | 2021-03-31 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40604126 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.0349e-05 | 807.3893
119608856 | B | LC | ETL.8650.POLE.NWOD | 44859208 | FRESNO | FRESNO | 2020-08-13 | 2020-12-08 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44859208 | 2019-11-18 | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-11-18 | Glass | Suspension |  |  |  |  | 0.0063222 | 7011.6025
119630481 | E | LC | ETL.9200.POLE.WOOD | 40647858 | MIDWAY | KERN | 2020-08-18 |  | ETL.9200 | TAFT-CUYAMA #1 | Anchor-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40647858 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Ceramic | Pin |  |  |  |  | 0.0033902
119633104 | F | LC | ETL.1610.POLE.NWOD | 44866808 | LAKEVLLE | NORTH BAY | 2020-08-18 |  | ETL.1610 | SILVERADO-FULTON JCT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44866808 | 2019-10-05 | Light Duty Steel Pole | SV-PJ - Single Vertical Post Jumper | 2019-10-05 | Glass | Suspension |  |  |  |  | 3.6887e-07 | 2406.1555
119635878 | E | LC | ETL.7140.POLE.WOOD | 40809042 | LAKEVLLE | NORTH BAY | 2020-08-18 | 2021-05-07 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119648861 | E | LC | ETL.7030.POLE.NWOD | 44311024 | TABLEMTN | NORTH VALLEY | 2020-08-20 | 2021-06-22 | ETL.7030 | HAT CREEK #1-WESTWOOD | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44311024 | 2014-07-24 | Fiberglass | T2N | 2014-07-24 | Polymer | Post |  |  |  |  | 0.0066681 | 15.8837
119699024 | E | LC | ETL.6890.POLE.WOOD | 40808468 | LAKEVLLE | SONOMA | 2020-09-01 | 2021-03-24 | ETL.6890 | FULTON-HOPLAND | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40808468 | 1948-01-01 | Single Wood Pole | DV - Double Vertical | 2021-03-10 | Glass | Double Dead End |  |  |  |  | 0.00031831 | 126.6897
119704534 | F | LC | ETL.6880.POLE.WOOD | 40585444 | LAKEVLLE | SONOMA | 2020-09-02 | 2020-10-14 | ETL.6880 | FULTON-CALISTOGA | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119719175 | B | LC | ETL.1651.INSL.NCER | 44144201 | LAKEVLLE |  | 2020-08-05 | 2020-09-21 | ETL.1651 | MISSION POWER TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44144187 |  | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper |  | Polymer | Dead End |  |  |  |  | 9.3271e-07 | 2992.874
119721598 | F | LC | ETL.1710.POLE.WDPS | 44510521 | MOSSLNDG | CENTRAL COAST | 2020-07-30 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44509644 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0021389 | 63.3245
119722963 | F | LC | ETL.6760.POLE.WOOD | 40824403 | SACTO | SIERRA | 2020-08-04 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40824403 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.22316 | 47.5526
119728064 | E | LC | ETL.6520.POLE.WOOD | 40594294 | SACTO | SIERRA | 2020-09-08 | 2021-06-07 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40594294 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.002435 | 1092.7948
119766238 | E | LC | ETL.6760.POLE.WOOD | 40873733 | SACTO | SIERRA | 2020-09-08 | 2021-03-29 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40873733 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0016769 | 629.9716
119772791 | F | LC | ETL.6330.POLE.NWOD | 40692690 | TABLEMTN | NORTH VALLEY | 2020-09-09 | 2021-07-19 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40692690 | 1998-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Non Ceramic | Post |  |  |  |  | 1.1085e-06 | 474.6646
119774776 | B | LC | ETL.5933.TOWR | 40821794 | PISMOBCH | LOS PADRES | 2020-09-16 | 2020-11-07 | ETL.5933 | MORRO BAY-TEMPLETON | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40821794 | 1954-01-01 | LATTICE STEEL TOWER | TRP DE - Tramp Dead End | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.7626e-07 | 522.0685
119780873 | F | LC | ETL.1730.POLE.NWOD | 44601338 | MOSSLNDG | CENTRAL COAST | 2020-07-27 | 2020-10-21 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44601338 | 2017-09-25 | Light Duty Steel Pole | SVDE - Single Vertical Dead End | 2017-09-25 | Polymer | Dead End - Suspension |  |  |  |  | 6.5856e-09 | 15.88
119786452 | E | LC | ETL.8170.POLE.WOOD | 40906420 | EUREKA | HUMBOLDT | 2020-09-14 | 2021-06-09 | ETL.8170 | TRINITY-MAPLE CREEK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906420 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-06-04 | Glass | Dead End |  |  |  |  | 0.0055919 | 348.1371
119790378 | F | LC | ETL.6810.POLE.WOOD | 40667585 | EUREKA | HUMBOLDT | 2020-07-30 |  | ETL.6810 | ESSEX JCT-ORICK | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Zone 1 | HFRA Removal | PEND | 40667585 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.018446
119799451 | E | LC | ETL.6950.INSL.NCER | 40918440 | SACTO | SACRAMENTO | 2020-09-19 | 2020-10-12 | ETL.6950 | GOLD HILL #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40908721 | 2013-10-17 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2013-10-17 | Non Ceramic | Post |  |  |  |  | 0.0017441 | 1697.6278
119801116 | F | LC | ETL.1073.POLE.WDPS | 44963368 | VICTOR | STOCKTON | 2020-09-22 | 2021-07-30 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40744523 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00027239 | 1298.4628
119805030 | F | LC | ETL.6470.POLE.WOOD | 40868975 | SACTO | SIERRA | 2020-08-07 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40868975 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.1227 | 221.5931
119816856 | F | LC | ETL.7390.POLE.WOOD | 40740733 | LAKEVLLE | HUMBOLDT | 2020-09-10 | 2021-09-28 | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40740733 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.037328
119873464 | E | LC | ETL.8170.POLE.WOOD | 40906451 | EUREKA | HUMBOLDT | 2020-10-07 | 2021-06-14 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906451 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.080432 | 94.9939
119965222 | E | LC | ETL.1420.INSL.CERA | 44337147 | SACTO | SACRAMENTO | 2020-08-25 |  | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44337064 | 2016-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2016-08-08 | Porcelain | Suspension |  |  |  |  | 1.2054e-07
119965222 | E | LC | ETL.1420.INSL.CERA | 44337147 | SACTO | SACRAMENTO | 2020-08-25 |  | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44337064 | 2016-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2016-08-08 | Porcelain | Suspension |  |  |  |  | 1.2054e-07
119978706 | E | LC | ETL.8960.POLE.WDPS | 44236927 | FRESNO | FRESNO | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44236926 |  | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 7.4751e-05
120011410 | E | LC | ETL.6020.TOWR | 40595123 | TABLEMTN | NORTH VALLEY | 2020-11-06 | 2021-07-01 | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40595123 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00013386 | 221.5655
120044512 | E | LC | ETL.6240.POLE.WOOD | 40823332 | MOSSLNDG | CENTRAL COAST | 2020-11-13 |  | ETL.6240 | BURNS-LONE STAR #2 | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40823332 |  | Single Wood Pole | TPAF - Flat Pin Arm | 2021-08-01 | Polymer | Post |  |  |  |  | 0.60757 | 0.065152 | 0.039585
120084174 | E | LC | ETL.6060.TOWR | 40592685 | TABLEMTN | NORTH VALLEY | 2020-11-21 |  | ETL.6060 | ROUND MTN-TABLE MTN #1 | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier3 | Tier 3 | Within Both | PEND | 40592685 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 4.5011e-08 | 1432.0019 | 6.4456e-05
120226678 | E | LC | ETL.5080.TOWR | 40753220 | VICTOR | YOSEMITE | 2020-12-18 |  | ETL.5080 | MELONES-WILSON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753220 | 1979-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1979-01-01 | Porcelain | Dead End |  |  |  |  | 1.953e-07 | 2439.7625 | 0.00047648
120226678 | E | LC | ETL.5080.TOWR | 40753220 | VICTOR | YOSEMITE | 2020-12-18 |  | ETL.5080 | MELONES-WILSON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753220 | 1979-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 1.953e-07 | 2439.7625 | 0.00047648
120253052 | F | LC | ETL.9340.POLE.NWOD | 44663898 | FRESNO | YOSEMITE | 2020-12-16 | 2021-07-20 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44663898 | 2018-10-03 | Light Duty Steel Pole | T-1 - Tri Post | 2018-10-03 | Polymer | Post |  |  |  |  | 0.0027143 | 5176.5
120471005 | A | LC | ETL.7820.POLE.WOOD | 40860907 | LAKEVLLE | SONOMA | 2021-01-27 | 2021-02-02 | ETL.7820 | POTTER VALLEY-WILLITS | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40860907 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.0011534 | 3785.6865
120594373 | E | LC | ETL.1440.POLE.WOOD | 40814984 | SACTO | SIERRA | 2020-09-17 | 2021-06-28 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0042981 | 458.8659
120599209 | E | LC | ETL.6490.POLE.WOOD | 40665757 | SACTO | SACRAMENTO | 2021-03-03 |  | ETL.6490 | COLGATE-GRASS VALLEY | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40665757 |  | Single Wood Pole | T2N | 2021-02-16 | Polymer | Post |  |  |  |  | 0.0082514 | 2815.7598 | 23.2338
120613586 | F | LC | ETL.8170.POLE.WOOD | 40861531 | EUREKA | HUMBOLDT | 2021-03-08 |  | ETL.8170 | TRINITY-MAPLE CREEK | Road | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40861531 |  | Single Wood Pole | DDE - Double Dead End | 2019-02-09 | Ceramic | Double Dead End |  |  |  |  | 0.0095887 | 110.7793
120656640 | F | LC | ETL.4223.POLE.WDPS | 44565776 | TABLEMTN |  | 2021-03-17 |  | ETL.4223 | KANAKA TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44560112 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0019668 | 822.8433
120672061 | E | LC | ETL.4040.POLE.WDPS | 44552582 | TABLEMTN | NORTH VALLEY | 2021-03-22 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 44551548 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.066798 | 2155.7598 | 143.9997
120673385 | F | LC | ETL.1710.TOWR | 40605354 | MOSSLNDG | CENTRAL COAST | 2021-03-22 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40605354 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-06 | Glass | Dead End |  |  |  |  | 6.9828e-08 | 0.065147 | 4.5491e-09
120673385 | F | LC | ETL.1710.TOWR | 40605354 | MOSSLNDG | CENTRAL COAST | 2021-03-22 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40605354 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147 | 4.5491e-09
120681883 | E | LC | ETL.6050.TOWR | 40587619 | MOSSLNDG | CENTRAL COAST | 2021-03-23 | 2021-08-02 | ETL.6050 | MOSS LANDING-METCALF | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587619 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 2011-12-12 | Ceramic | Suspension |  |  |  |  | 2.1885e-05 | 174.1138
120717476 | F | LC | ETL.4000.POLE.WOOD | 44253831 | VICTOR | YOSEMITE | 2021-03-31 | 2021-10-06 | ETL.4000 | TESLA-SALADO-MANTECA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44253831 | 2013-04-22 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2013-04-22 | Porcelain | Suspension |  |  |  |  | 0.0012716 | 1254.9044
120737274 | E | LC | ETL.3820.TOWR | 43249454 | VICTOR | STOCKTON | 2021-03-31 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 43249454 | 1963-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post |  | Glass | [5 empty] | 3.4673e-09 | 2282.6465 | 7.9147e-06
120745364 | E | LC | ETL.1730.POLE.WDPS | 44413235 | MOSSLNDG | CENTRAL COAST | 2021-04-05 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44413234 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.3474e-05 | 38.0207 | 0.0024133
120750216 | E | LC | ETL.8365.POLE.WOOD | 40769341 | EUREKA | HUMBOLDT | 2021-04-06 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40769341 | 2010-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0037405 | 1350.2804 | 5.0507
120761605 | E | LC | ETL.6720.INSL | 40712274 | TABLEMTN | NORTH VALLEY | 2021-04-07 |  | ETL.6720 | DESABLA-CENTERVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40659712 | 1998-01-01 | Tubular Steel Pole | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 7.0006e-05 | 23.7951 | 0.0016658
120769938 | F | LC | ETL.3830.TOWR | 40745910 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40745910 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.8803e-07 | 569.3991 | 0.000164
120771665 | F | LC | ETL.4750.TOWR | 40813800 | LAKEVLLE | SONOMA | 2021-04-09 |  | ETL.4750 | GEYSERS #12-FULTON | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40813800 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Porcelain | Suspension |  |  |  |  | 7.9187e-10 | 348.2954
120793162 | B | LC | ETL.3840.INSL.CERA | 40771614 | VICTOR | STOCKTON | 2021-04-09 | 2021-05-24 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40744465 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 8.3055e-07 | 6204.2363
120795031 | E | LC | ETL.6030.INSL | 40777723 | MIDWAY | KERN | 2021-04-12 |  | ETL.6030 | MIDWAY-WHIRLWIND | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40749810 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 5.4989e-05 | 6700.9697 | 0.36848
120805737 | F | LC | ETL.4316.TOWR | 40589080 | TABLEMTN | NORTH VALLEY | 2021-04-07 | 2021-06-17 | ETL.4316 | PARADISE-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40589080 |  | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2021-08-02 | Polymer | Double Dead End |  |  |  |  | 0.0021771 | 3832.9919
120823487 | B | LC | ETL.8490.TOWR | 40667112 | PISMOBCH | LOS PADRES | 2021-04-15 | 2021-05-03 | ETL.8490 | ATASCADERO-SAN LUIS OBISPO | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40667112 | 1932-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0012442 | 2389.5793
120826864 | B | LC | ETL.6880.POLE.NWOD | 45071347 | LAKEVLLE | SONOMA | 2021-04-16 | 2021-05-04 | ETL.6880 | FULTON-CALISTOGA | Other | Customer Issue | [Access Issue] | Tier3 | Tier 3 | Within Both | COMP | 45071347 | 2020-03-05 | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 2020-03-05 | Glass | Suspension |  |  |  |  | 6.0341e-05 | 110.894
120827556 | F | LC | ETL.2900.TOWR | 40765679 | MOSSLNDG | CENTRAL COAST | 2021-04-16 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40765679 | 1970-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1970-01-01 | Porcelain | Dead End |  |  |  |  | 0.0051297 | 555.1911 | 2.8479
120827766 | E | LC | ETL.7290.POLE.WOOD | 40868727 | TABLEMTN | NORTH VALLEY | 2021-04-16 | 2021-06-17 | ETL.7290 | KILARC-CEDAR CREEK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40868727 |  | Single Wood Pole | T2N | 2021-06-10 | Polymer | Post |  |  |  |  | 0.016471 | 443.7837
120833015 | E | LC | ETL.3830.TOWR | 40642778 | VICTOR | STOCKTON | 2021-04-16 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40642778 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 7.3198e-06 | 130.1517 | 0.00095268
120839581 | E | LC | ETL.6500.POLE.WOOD | 40610968 | SACTO | SACRAMENTO | 2021-04-17 | 2021-08-19 | ETL.6500 | COLGATE-PALERMO | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40610968 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0044991 | 6284.8086
120839581 | E | LC | ETL.6500.POLE.WOOD | 40610968 | SACTO | SACRAMENTO | 2021-04-17 | 2021-08-19 | ETL.6500 | COLGATE-PALERMO | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40610968 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0044991 | 6284.8086
120839581 | E | LC | ETL.6500.POLE.WOOD | 40610968 | SACTO | SACRAMENTO | 2021-04-17 | 2021-08-19 | ETL.6500 | COLGATE-PALERMO | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40610968 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0044991 | 6284.8086
120842796 | E | LC | ETL.1070.POLE.WOOD | 40580424 | VICTOR | YOSEMITE | 2021-04-12 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40580424 | 1973-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1957-01-01 | Polymer | Dead End |  |  |  |  | 5.283e-06 | 4947.8276 | 0.026139
120854184 | E | LC | ETL.6470.POLE.WOOD | 40760406 | SACTO | SACRAMENTO | 2021-04-20 | 2021-08-18 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760406 |  | Single Wood Pole | T2N | 2021-08-09 | Polymer | Post |  |  |  |  | 0.0053827 | 419.3189
120855839 | F | LC | ETL.6480.POLE.NWOD | 45122797 | SACTO | NORTH VALLEY | 2021-04-20 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45122797 | 2021-06-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-06-18 | Polymer | Post | [5 empty] | 253.3131
120860501 | F | LC | ETL.3740.TOWR | 40746112 | CONCORD | DIABLO | 2021-04-21 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40746112 | 1961-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1966-01-01 | Porcelain | Dead End |  |  |  |  | 0.061529 | 0.065158 | 0.0040091
120860995 | E | LC | ETL.4880.INSL | 40881222 | FRESNO | FRESNO | 2021-04-20 |  | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40858327 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 7.7361e-09 | 4812.7461 | 3.7232e-05
120860995 | E | LC | ETL.4880.INSL | 40881222 | FRESNO | FRESNO | 2021-04-20 |  | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40858327 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-31 | Glass | Dead End |  |  |  |  | 7.7361e-09 | 4812.7461 | 3.7232e-05
120876826 | E | LC | ETL.4040.POLE.WDPS | 44557607 | TABLEMTN | NORTH VALLEY | 2021-04-22 | 2021-09-14 | ETL.4040 | TRINITY-COTTONWOOD | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553912 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.043652 | 0.49026
120880250 | E | LC | ETL.6762.POLE.WOOD | 40650077 | SACTO | SACRAMENTO | 2021-04-22 | 2021-10-11 | ETL.6762 | ROLLINS TAP | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40650077 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.00035691 | 110.7947 | 0.039544
120880280 | F | LC | ETL.1810.TOWR | 44321393 | EUREKA | HUMBOLDT | 2021-04-24 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44321393 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | [5 empty] | 3.5126e-05
120889183 | E | LC | ETL.3960.INSL.CERA | 40879193 | PISMOBCH | LOS PADRES | 2021-04-27 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40856740 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 2.7574e-09 | 1249.7175 | 3.446e-06
120889833 | E | LC | ETL.4460.INSL | 40885091 | MOSSLNDG | CENTRAL COAST | 2021-04-23 | 2021-11-29 | ETL.4460 | COBURN-LAS AGUILAS SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862917 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 5.1728e-07 | 47.5223 | 2.4582e-05
120889833 | E | LC | ETL.4460.INSL | 40885091 | MOSSLNDG | CENTRAL COAST | 2021-04-23 | 2021-11-29 | ETL.4460 | COBURN-LAS AGUILAS SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862917 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 5.1728e-07 | 47.5223 | 2.4582e-05
120892584 | E | LC | ETL.1250.POLE.WOOD | 40761741 | FRESNO | YOSEMITE | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761741 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 1.5099e-05 | 5920.3032 | 0.089393
120893783 | F | LC | ETL.1250.POLE.WOOD | 40748523 | FRESNO | YOSEMITE | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40748523 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Double Dead End |  |  |  |  | 0.00014483 | 6379.0093
120906680 | B | LC | ETL.5933.INSL.CERA | 44358896 | PISMOBCH | LOS PADRES | 2021-04-29 | 2021-05-24 | ETL.5933 | MORRO BAY-TEMPLETON | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40863323 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2016-08-27 | Ceramic | Suspension |  |  |  |  | 1.4488e-08 | 2882.8154
120928545 | F | LC | ETL.6890.POLE.NWOD | 44963407 | LAKEVLLE | SONOMA | 2021-05-04 | 2021-05-23 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44963407 | 2019-12-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-12-18 | Glass | Dead End |  |  |  |  | 0.00010922 | 451.9435
120947668 | B | LC | ETL.4920.INSL.CERA | 40789738 | CONCORD | EAST BAY | 2021-05-06 | 2021-07-26 | ETL.4920 | IGNACIO-SOBRANTE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760274 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.00077772 | 127.6204
121045778 | F | LC | ETL.1820.POLE.STPS | 44395508 | EUREKA | HUMBOLDT | 2021-05-10 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395506 | 2020-03-03 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.011298 | 4462.79
121318840 | E | LC | ETL.5290.INSL | 40835755 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810723 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-08 | Glass | Suspension |  |  |  |  | 1.642e-06 | 650.8898 | 0.0010687
121318840 | E | LC | ETL.5290.INSL | 40835755 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810723 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.642e-06 | 650.8898 | 0.0010687
121320127 | E | LC | ETL.1820.POLE.WDPS | 44562713 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Hardware-Wood | Missing | [Install] | Tier2 |  |  | PEND
121322340 | E | LC | ETL.1820.POLE.WDPS | 44770814 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40771946 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.058543 | 5842.8242 | 342.0551
121322343 | E | LC | ETL.1820.POLE.WDPS | 44770815 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40771946 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.058543 | 5842.8242 | 342.0551
121329262 | F | LC | ETL.4850.TOWR | 40865880 | FRESNO | FRESNO | 2021-04-22 |  | ETL.4850 | HAAS-MCCALL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40865880 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1957-01-01 | Ceramic | Dead End |  |  |  |  | 1.5353e-08 | 6632.3721 | 0.00010182
121329262 | F | LC | ETL.4850.TOWR | 40865880 | FRESNO | FRESNO | 2021-04-22 |  | ETL.4850 | HAAS-MCCALL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40865880 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2016-02-20 | Ceramic | Dead End |  |  |  |  | 1.5353e-08 | 6632.3721 | 0.00010182
121332191 | E | LC | ETL.7890.INSL.NCER | 40733312 | MOSSLNDG | CENTRAL COAST | 2021-04-21 |  | ETL.7890 | SALINAS-FORT ORD #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40697711 |  | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 1.5661e-06 | 0.065148 | 1.0203e-07
121334450 | E | LC | ETL.6470.POLE.WOOD | 40822600 | SACTO | SIERRA | 2021-05-13 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40822600 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.19115 | 522.076 | 99.7972
121335812 | F | LC | ETL.8480.POLE.WOOD | 40760573 | PISMOBCH | LOS PADRES | 2021-04-23 |  | ETL.8480 | ATASCADERO-CAYUCOS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40760573 | 1954-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2007-01-01 | Polymer | Post |  |  |  |  | 0.000331 | 2199.9841
121364980 | E | LC | ETL.7820.INSL.CERA | 40799399 | LAKEVLLE | HUMBOLDT | 2021-05-19 |  | ETL.7820 | POTTER VALLEY-WILLITS | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40768596 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0019656 | 650.3827 | 1.2784
121364980 | E | LC | ETL.7820.INSL.CERA | 40799399 | LAKEVLLE | HUMBOLDT | 2021-05-19 |  | ETL.7820 | POTTER VALLEY-WILLITS | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40768596 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0019656 | 650.3827 | 1.2784
121369786 | B | LC | ETL.7930.SWIT | 40744050 | MOSSLNDG | CENTRAL COAST | 2021-05-20 | 2021-05-25 | ETL.7930 | SALINAS-LAURELES | Switch | Out of Adjustment | [Repair, Completed, Completed] | Tier2 |  |  | COMP | [9 empty] | NO ATTACHMENTS | Manual
121370846 | F | LC | ETL.9340.POLE.NWOD | 44663900 | FRESNO | YOSEMITE | 2021-05-03 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44663900 | 2018-10-03 | Light Duty Steel Pole | T-1 - Tri Post | 2018-10-03 | Polymer | Post |  |  |  |  | 0.0021838 | 3246.6982
121380143 | F | LC | ETL.8350.POLE.WOOD | 40803747 | VICTOR | STOCKTON | 2021-05-06 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40803747 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.00060654 | 379.722
121380365 | B | LC | ETL.4440.POLE.STPS | 44392376 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-29 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44392373 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 6.8182e-06 | 5879.0113
121384200 | F | LC | ETL.8250.POLE.WOOD | 40908801 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908801 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.00067148 | 5094.106
121392203 | F | LC | ETL.6660.POLE.NWOD | 40738445 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40738445 | 1998-01-01 | Light Duty Steel Pole | T-1 - Tri Post | 2021-02-11 | Polymer | Post |  |  |  |  | 4.3374e-08 | 3819.6531 | 0.00016568
121394918 | E | LC | ETL.2394.POLE.WOOD | 40593085 | PISMOBCH | LOS PADRES | 2021-05-25 |  | ETL.2394 | OCEANO-CALLENDER SW STA | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40593085 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2018-06-08 | Glass | Suspension |  |  |  |  | 0.00061033 | 356.4771 | 0.21757
121394918 | E | LC | ETL.2394.POLE.WOOD | 40593085 | PISMOBCH | LOS PADRES | 2021-05-25 |  | ETL.2394 | OCEANO-CALLENDER SW STA | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40593085 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2018-06-08 | Glass | Suspension |  |  |  |  | 0.00061033 | 356.4771 | 0.21757
121402272 | F | LC | ETL.6470.POLE.WOOD | 40611162 | SACTO | SIERRA | 2021-05-19 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40611162 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.084026 | 142.5149
121404246 | E | LC | ETL.6870.POLE.WOOD | 40870170 | SACTO | SIERRA | 2021-05-19 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40870170 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post | 2020-05-14 | Polymer | Post |  |  |  |  | 0.053167 | 126.6309 | 6.7325
121420210 | F | LC | ETL.1420.POLE.STPS | 44415621 | SACTO | SACRAMENTO | 2021-05-25 | 2021-08-03 | ETL.1420 | DRUM-RIO OSO #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44415620 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [8 empty] | 1338.3376
121425530 | F | LC | ETL.6470.POLE.WOOD | 40760751 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40760751 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.25187 | 221.5931
121447308 | B | LC | ETL.5640.TOWR | 40656016 | TABLEMTN | NORTH VALLEY | 2021-06-02 | 2021-07-01 | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656016 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.9682e-08 | 2077.4675
121447308 | B | LC | ETL.5640.TOWR | 40656016 | TABLEMTN | NORTH VALLEY | 2021-06-02 | 2021-07-01 | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656016 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 9.9682e-08 | 2077.4675
121447494 | B | LC | ETL.1600.TOWR | 40821158 | LAKEVLLE | SONOMA | 2021-06-02 | 2021-06-08 | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40821158 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2019-12-16 | Glass | Dead End |  |  |  |  | 5.8591e-07 | 2645.7832
121466648 | F | LC | ETL.6020.TOWR | 40817695 | TABLEMTN | NORTH VALLEY | 2021-06-03 | 2021-10-01 | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40817695 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 6.1863e-06 | 1487.7782
121467284 | B | LC | ETL.9330.INSL.NCER | 44859276 | FRESNO | FRESNO | 2021-06-03 | 2021-06-17 | ETL.9330 | WISHON-COPPERMINE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40872016 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-09-30 | Glass | Suspension |  |  |  |  | 0.001583 | 6734.7707
121475212 | E | LC | ETL.7180.INSL.NCER | 40800916 | LAKEVLLE | NORTH BAY | 2021-06-03 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40770104 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 8.4796e-07 | 253.482 | 0.00021494
121482324 | F | LC | ETL.6900.POLE.WOOD | 40825348 | LAKEVLLE | SONOMA | 2021-06-04 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40825348 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0010286 | 3332.2297 | 3.4274
121484036 | B | LC | ETL.5640.TOWR | 40674243 | TABLEMTN | NORTH VALLEY | 2021-06-07 | 2021-06-21 | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40674243 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 5.493e-06 | 556.1051
121485425 | E | LC | ETL.4392.INSL.NCER | 42642977 | LAKEVLLE | SONOMA | 2021-06-01 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44191983 |  | Tubular Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.00019597 | 3726.486 | 0.73027
121486020 | E | LC | ETL.7550.POLE.WOOD | 40808815 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40808815 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00012709 | 4148.8545 | 0.52726
121489030 | E | LC | ETL.7550.POLE.WOOD | 40861413 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40861413 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0017614 | 1838.0487 | 3.2374
121492654 | F | LC | ETL.7575.POLE.WOOD | 40755181 | METCALF | PENINSULA | 2021-06-01 |  | ETL.7575 | SNEATH LANE-PACIFICA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40755181 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | Post |  |  |  |  | 0.37175 | 316.4883 | 117.6539
121493445 | E | LC | ETL.6890.POLE.WOOD | 40616427 | LAKEVLLE | SONOMA | 2021-06-01 |  | ETL.6890 | FULTON-HOPLAND | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40616427 | 1994-01-01 | Single Wood Pole | T-1 - Tri Post | 2014-06-03 | Polymer | Post |  |  |  |  | 0.00017642 | 2089.8596 | 0.3687
121516691 | E | LC | ETL.1400.INSL | 40829524 | VICTOR | YOSEMITE | 2021-06-04 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40803723 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00033217
121516691 | E | LC | ETL.1400.INSL | 40829524 | VICTOR | YOSEMITE | 2021-06-04 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40803723 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00033217
121523410 | E | LC | ETL.7212.POLE.WDPS | 44779577 | METCALF | PENINSULA | 2021-06-04 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40867264 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.5781 | 79.2658 | 45.8235
121525442 | F | LC | ETL.2390.POLE.WDPS | 44391209 | VICTOR | STOCKTON | 2021-06-12 |  | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391208 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00013765 | 63.3245 | 0.0087164
121526921 | F | LC | ETL.4040.POLE.WOOD | 44552572 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44551523 |  | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00027214 | 1645.5847
121533561 | E | LC | ETL.1350.POLE.WDPS | 44512178 | TABLEMTN |  | 2021-06-08 | 2021-07-12 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40677247 | 1993-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.074495 | 490.5302
121535911 | E | LC | ETL.5970.INSL | 40839491 | PISMOBCH | LOS PADRES | 2021-06-10 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40812075 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 8.6542e-10 | 951.6246 | 8.2355e-07
121540153 | E | LC | ETL.4440.TOWR | 40595027 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40595027 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 0.0002025 | 5999.3906 | 1.2149
121543640 | F | LC | ETL.1450.POLE.NWOD | 44270075 | SACTO | SIERRA | 2021-06-12 |  | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44270075 |  | Light Duty Steel Pole | Other |  | Ceramic | Suspension |  |  |  |  | 3.0451e-06 | 348.1462 | 0.0010602
121543754 | F | LC | ETL.7100.POLE.WOOD | 40860846 | EUREKA | HUMBOLDT | 2021-06-11 |  | ETL.7100 | HUMBOLDT BAY-RIO DELL JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40860846 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.39666 | 205.6675
121544697 | F | LC | ETL.1820.POLE.STPS | 44396308 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44396307 | 2020-03-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0027072 | 363.9585
121549597 | E | LC | ETL.6750.POLE.WDPS | 44562125 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44561574 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00047763 | 79.1724 | 0.037815
121550728 | F | LC | ETL.7390.POLE.NWOD | 44412206 | LAKEVLLE | HUMBOLDT | 2021-06-13 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44412206 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0020171 | 143.1723
121553577 | E | LC | ETL.7640.POLE.WDPS | 44565370 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564268 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.001496 | 506.6299 | 0.75792
121565270 | E | LC | ETL.5650.INSL | 40617513 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591938 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 0.00067714 | 5133.3115 | 3.476
121565681 | E | LC | ETL.2395.POLE.WOOD | 45001466 | TABLEMTN | NORTH VALLEY | 2021-06-15 | 2021-09-14 | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45001466 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | Dead End |  |  |  |  | 0.00026142 | 3021.0042
121573572 | F | LC | ETL.4040.POLE.STPS | 44783291 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44783240 | 2019-07-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00026062 | 3218.0649
121588151 | F | LC | ETL.1400.POLE.WDPS | 45095797 | VICTOR | STOCKTON | 2021-06-23 | 2021-07-08 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | DLFL | 40579912 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0099386 | 2246.7366
121596705 | F | LC | ETL.5390.TOWR | 40657397 | TABLEMTN | NORTH VALLEY | 2021-06-22 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40657397 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.1119e-05 | 648.6474 | 0.013699
121602766 | E | LC | ETL.6650.POLE.NWOD | 44926533 | TABLEMTN | NORTH VALLEY | 2021-06-22 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44926533 | 2020-04-08 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2020-04-08 | Glass | Dead End |  |  |  |  | 0.00016494 | 363.0611 | 0.059884
121603125 | F | LC | ETL.6020.TOWR | 40592584 | TABLEMTN | NORTH VALLEY | 2021-06-24 |  | ETL.6020 | MALIN-ROUND MTN #2 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40592584 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.4976e-05 | 681.0834
121603344 | F | LC | ETL.1350.POLE.STPS | 44994020 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44993916 | 2020-06-05 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.8159e-05 | 269.0425
121608254 | F | LC | ETL.1070.POLE.WOOD | 40804191 | VICTOR | YOSEMITE | 2021-06-22 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40804191 | 1957-01-01 | Single Wood Pole | T-1 - Tri Post | 1957-01-01 | Polymer | Suspension |  |  |  |  | 2.0311e-05 | 2376.3638 | 0.048266
121623561 | E | LC | ETL.4770.INSL | 40791767 | LAKEVLLE | SONOMA | 2021-06-16 |  | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40761390 | 1971-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.8952e-08 | 408.8128 | 1.1836e-05
121631344 | E | LC | ETL.5420.POLE.WDPS | 44562724 | TABLEMTN | NORTH VALLEY | 2021-06-26 | 2021-07-12 | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44562415 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0094612 | 2361.4426
121648427 | E | LC | ETL.2395.INSL.CERA | 45019138 | TABLEMTN | NORTH VALLEY | 2021-06-30 |  | ETL.2395 | GRIZZLY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45019108 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.11128 | 300.6002 | 33.4522
121683996 | E | LC | ETL.9240.TOWR | 43249745 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249745 |  | LATTICE STEEL TOWER | [9 empty] | 1473.9071
121684355 | E | LC | ETL.1110.TOWR | 40605509 | TABLEMTN | NORTH VALLEY | 2021-07-08 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40605509 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 7.1159e-05 | 6600.2397 | 0.46967
121684707 | A | LC | ETL.1710.INSL | 40788248 | MOSSLNDG | CENTRAL COAST | 2021-07-08 | 2021-07-20 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
121685240 | E | LC | ETL.2395.INSL.CERA | 44950313 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.2395 | GRIZZLY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44950303 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.039554 | 121.876 | 4.8207
121690499 | F | LC | ETL.5420.POLE.STPS | 44400048 | TABLEMTN |  | 2021-07-06 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44400047 | 2017-11-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.7279e-07 | 2217.3672
121707512 | E | LC | ETL.7640.POLE.WDPS | 44565575 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.7640 | MTN GATE JCT-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44564245 |  | 2-Pole Wood | TH - TriAngle Post 70 | [7 empty] | 6.7495e-05 | 3880.9729 | 0.26195
121714926 | B | LC | ETL.1820.POLE.NWOD | 44934863 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-09-29 | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44934863 | 2020-03-09 | Light Duty Steel Pole | DDE - Double Dead End | 2020-03-09 | Glass | Dead End |  |  |  |  | 0.058111 | 31.7081
121730345 | E | LC | ETL.1720.POLE.WDPS | 44400970 | MOSSLNDG | CENTRAL COAST | 2021-07-14 | 2021-07-28 | ETL.1720 | GREEN VALLEY-LLAGAS | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44400969 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.3246e-05 | 15.8866
121732190 | E | LC | ETL.1400.POLE.WDPS | 45087025 | VICTOR | YOSEMITE | 2021-07-07 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40579644 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0085281 | 31.7207 | 0.27052
121732307 | F | LC | ETL.8405.POLE.WOOD | 40650001 | SACTO | SIERRA | 2021-07-12 |  | ETL.8405 | MIDDLE FORK #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40650001 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.12518 | 1186.6189 | 148.5379
121745445 | E | LC | ETL.6760.POLE.WOOD | 40873721 | SACTO | SIERRA | 2021-07-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40873721 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.032117 | 174.0688 | 5.5905
121746509 | F | LC | ETL.6480.POLE.NWOD | 44695496 | SACTO | SIERRA | 2021-07-15 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44695496 | 2018-12-10 | Light Duty Steel Pole | T2N | 2018-12-10 | Polymer | Post |  |  |  |  | 0.021949 | 348.1483
121776546 | F | LC | ETL.8360.POLE.WDPS | 44412051 | LAKEVLLE |  | 2021-07-20 |  | ETL.8360 | LAYTONVILLE-WILLITS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44412048 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0035111 | 2913.8086 | 10.2308
121781195 | B | LC | ETL.1810.TOWR | 40598279 | EUREKA | HUMBOLDT | 2021-07-22 | 2021-10-19 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40598279 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Porcelain | Suspension |  |  |  |  | 9.7335e-05
121786749 | F | LC | ETL.6280.POLE.NWOD | 40666797 | TABLEMTN | NORTH VALLEY | 2021-07-21 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40666797 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 4.661e-06 | 0.065148
121788079 | B | LC | ETL.6280.POLE.WOOD | 44722636 | TABLEMTN | NORTH VALLEY | 2021-07-23 | 2021-09-16 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.3904e-05 | 680.1661
121797001 | B | LC | ETL.9240.TOWR | 43249717 | PISMOBCH | LOS PADRES | 2021-07-26 | 2021-10-06 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249717 |  | LATTICE STEEL TOWER | [9 empty] | 2470.1736
121882790 | B | LC | ETL.6300.POLE.WDPS | 44976227 | TABLEMTN | NORTH VALLEY | 2021-08-10 | 2021-09-23 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 174.1204
121911024 | E | LC | ETL.7630.POLE.NWOD | 45137059 | LAKEVLLE | SONOMA | 2021-08-17 |  | ETL.7630 | MONTE RIO-FULTON | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45137059 | 2021-07-22 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-07-22 | Glass | Dead End | [5 empty] | 69.6731
121957250 | E | LC | ETL.1440.POLE.STPS | 44963254 | SACTO | SIERRA | 2021-03-24 | 2021-09-09 | ETL.1440 | DRUM-SUMMIT #1 | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44961228 | 2020-06-03 | 3-Pole Non Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 1.4832e-06 | 58.6018
122379414 | E | LC | ETL.6470.INSL.NCER | 45144327 | SACTO | SIERRA | 2021-11-15 |  | ETL.6470 | COLGATE-ALLEGHANY | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40873654 |  | Single Wood Pole | TCDE - Tap Construction Dead End | 2021-07-25 | Glass | Dead End |  |  |  |  | 0.0067473 | 3211.3491 | 21.6679
118442076 | A | LC | ETL.6222.POLE.WOOD | 40825299 | EUREKA | HUMBOLDT | 2020-01-17 | 2020-02-07 | ETL.6222 | FORT SEWARD TAP | Vegetation | Overgrown | [Remove, No Action Taken] |  | Non-HFTD | HFRA Addition | CNCL | 40825299 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0013193
118491760 | F | LC | ETL.4590.TOWR | 40907015 | TABLEMTN | NORTH VALLEY | 2020-02-03 | 2020-02-18 | ETL.4590 | CRESTA-RIO OSO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40907015 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.1964e-05 | 218.3706
118677899 | E | LC | ETL.6640.INSL.CERA | 42579398 | TABLEMTN | NORTH VALLEY | 2020-03-10 | 2021-08-05 | ETL.6640 | COTTONWOOD-BENTON #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
118718177 | A | LC | ETL.1420.INSL.NCER | 40718151 | SACTO | SACRAMENTO | 2020-03-18 | 2020-05-27 | ETL.1420 | DRUM-RIO OSO #1 | Emergency-Steel | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40670118 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm |  | Polymer | [5 empty] | 1.6854e-05 | 158.3103
118782761 | E | LC | ETL.7590.POLE.WOOD | 40767943 | MOSSLNDG | CENTRAL COAST | 2020-04-06 | 2020-04-22 | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
118954422 | E | LC | ETL.8351.POLE.WOOD | 40863882 | VICTOR | STOCKTON | 2020-03-18 | 2020-08-10 | ETL.8351 | PINE GROVE TAP | Structure-Wood | Rotten | [Replace] | Tier2 |  |  | DLFL | [11 empty] | 9.3295e-05 | 47.5207
118981723 | F | LC | ETL.5463.TOWR | 40581163 | CONCORD | MISSION | 2020-04-20 | 2021-02-10 | ETL.5463 | PITTSBURG-SAN MATEO | Marker (i.e. signs)-Steel | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581163 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 7.5377e-09 | 3043.1921
118997052 | E | LC | ETL.1530.POLE.NWOD | 44722642 | SACTO | SIERRA | 2020-05-01 | 2021-04-27 | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44722642 | 2018-11-10 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2018-11-10 | Ceramic | Suspension |  |  |  |  | 1.4741e-07 | 1344.6511
119003303 | E | LC | ETL.8410.POLE.WOOD | 40763065 | LAKEVLLE | HUMBOLDT | 2020-05-05 | 2021-05-26 | ETL.8410 | ELK-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40763065 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 2021-05-18 | Glass | Suspension |  |  |  |  | 0.31438 | 348.0076
119026759 | F | LC | ETL.5220.TOWR | 40760553 | METCALF | PENINSULA | 2020-05-11 | 2021-03-04 | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760553 | 1963-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1963-01-01 | Ceramic | Suspension |  |  |  |  | 0.023779 | 332.3283
119049135 | E | LC | ETL.6950.POLE.WOOD | 40661281 | SACTO | SIERRA | 2020-05-12 |  | ETL.6950 | GOLD HILL #1 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40661281 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.013406 | 1534.4731 | 20.5708
119056651 | F | LC | ETL.4220.POLE.WOOD | 40866892 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-06-30 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40866892 | 1962-01-01 | Single Wood Pole | T-1 - Tri Post | 1962-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.012068 | 2787.6616
119063552 | F | LC | ETL.1730.POLE.WDPS | 44281048 | MOSSLNDG | CENTRAL COAST | 2020-05-26 | 2020-07-01 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] |  | Tier 2 | Within Both | COMP | 44281047 | 2016-04-07 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.7854e-05 | 0.065147
119070724 | E | LC | ETL.5420.POLE.WDPS | 44562861 | TABLEMTN | NORTH VALLEY | 2020-05-27 | 2020-06-18 | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119103164 | F | LC | ETL.7140.POLE.WOOD | 41118222 | LAKEVLLE | NORTH BAY | 2020-05-29 | 2021-01-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41118222 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.054361
119103164 | F | LC | ETL.7140.POLE.WOOD | 41118222 | LAKEVLLE | NORTH BAY | 2020-05-29 | 2021-01-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41118222 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.054361
119103164 | F | LC | ETL.7140.POLE.WOOD | 41118222 | LAKEVLLE | NORTH BAY | 2020-05-29 | 2021-01-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41118222 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.054361
119103436 | F | LC | ETL.2790.TOWR | 40745916 | CONCORD | EAST BAY | 2020-05-15 | 2021-03-23 | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40745916 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 3.9559e-06 | 0.065147
119111110 | E | LC | ETL.5290.INSL | 40774719 | PISMOBCH | LOS PADRES | 2020-05-26 | 2021-01-07 | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40746359 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Other |  |  |  |  | 6.3577e-07 | 619.4626
119111110 | E | LC | ETL.5290.INSL | 40774719 | PISMOBCH | LOS PADRES | 2020-05-26 | 2021-01-07 | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40746359 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 6.3577e-07 | 619.4626
119114612 | F | LC | ETL.6690.POLE.WOOD | 40664854 | SACTO | SIERRA | 2020-05-29 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40664854 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.14874 | 110.8102
119117533 | E | LC | ETL.6760.POLE.WOOD | 40654093 | SACTO | SIERRA | 2020-05-28 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40654093 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.025467 | 110.8102 | 2.822
119118720 | F | LC | ETL.8170.POLE.WOOD | 40906286 | EUREKA | HUMBOLDT | 2020-06-02 | 2020-06-25 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40906286 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.031461 | 405.5042
119119425 | E | LC | ETL.6950.POLE.NWOD | 44997983 | SACTO | SIERRA | 2020-06-02 | 2021-10-27 | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44997983 | 2020-05-05 | Light Duty Steel Pole | T-1 - Tri Post | 2020-05-05 | Polymer | Post |  |  |  |  | 0.001673 | 2978.5881 | 4.9832
119119474 | F | LC | ETL.6470.POLE.NWOD | 44398588 | SACTO | SIERRA | 2020-06-01 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44398588 | 2017-05-18 | Light Duty Steel Pole | T2N | 2017-05-18 | Polymer | Post |  |  |  |  | 7.3252e-05 | 253.174
119123299 | F | LC | ETL.1422.TOWR | 40761884 | SACTO | SIERRA | 2020-06-04 | 2020-11-12 | ETL.1422 | BRUNSWICK #1 TAP | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40761884 | 1975-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.1632e-06 | 71.2674
119127990 | F | LC | ETL.1422.TOWR | 40651683 | SACTO | SIERRA | 2020-06-04 | 2021-02-17 | ETL.1422 | BRUNSWICK #1 TAP | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40651683 | 1975-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.0024e-06 | 306.9531
119128042 | F | LC | ETL.8365.POLE.NWOD | 40912689 | EUREKA | HUMBOLDT | 2020-06-08 | 2020-10-06 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912689 | 2010-01-01 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 0.056089 | 4492.853
119172357 | E | LC | ETL.6440.POLE.WOOD | 40816963 | TABLEMTN | NORTH VALLEY | 2020-06-16 | 2020-08-31 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119173831 | E | LC | ETL.1820.INSL.CERA | 40635182 | EUREKA | HUMBOLDT | 2020-06-16 | 2021-03-24 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed, Completed] | Tier2 |  |  | COMP
119176412 | F | LC | ETL.9250.POLE.WOOD | 44799542 | MIDWAY | KERN | 2020-06-15 |  | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44799542 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.042031 | 5418.7817
119177089 | F | LC | ETL.6280.POLE.WOOD | 40664906 | TABLEMTN | NORTH VALLEY | 2020-06-16 | 2021-08-11 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 1.5033e-05 | 205.6771
119183104 | F | LC | ETL.6310.POLE.WOOD | 40817320 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40817320 |  | Single Wood Pole | T-1 - Tri Post | 2019-04-29 | Polymer | Post |  |  |  |  | 1.1335e-06 | 4154.5377
119184255 | F | LC | ETL.6280.POLE.WOOD | 40876579 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-09-10 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40876579 |  | Single Wood Pole | T-1 - Tri Post | 2018-10-30 | Polymer | Post |  |  |  |  | 1.1768e-05 | 6616.2266
119194767 | E | LC | ETL.6470.POLE.WOOD | 40693271 | SACTO | SIERRA | 2020-06-22 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693271 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.17399 | 269.0426
119201102 | F | LC | ETL.6310.POLE.WOOD | 41177775 | TABLEMTN | NORTH VALLEY | 2020-06-23 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41177775 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 2.4315e-05 | 1663.1614
119207571 | E | LC | ETL.8351.POLE.WOOD | 40811754 | VICTOR | STOCKTON | 2020-03-18 | 2020-11-13 | ETL.8351 | PINE GROVE TAP | Structure-Wood | Rotten | [Stub, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40811754 | 1977-01-01 | Single Wood Pole | 1VP - 1 Vertical |  | Porcelain | [5 empty] | 0.70064 | 63.3392
119290832 | E | LC | ETL.1650.POLE.WOOD | 44613035 | LAKEVLLE | SONOMA | 2020-07-01 | 2021-03-16 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44613035 | 2018-05-18 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-05-18 | Ceramic | Suspension |  |  |  |  | 1.9917e-05 | 3024.8135
119291718 | E | LC | ETL.6900.POLE.WOOD | 40823370 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | PEND | 40823370 | 1986-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Polymer | Suspension |  |  |  |  | 1.2496e-06 | 1613.9003 | 0.0020167
119294013 | E | LC | ETL.6890.POLE.WOOD | 40610846 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6890 | FULTON-HOPLAND | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40610846 | 1954-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Other |  |  |  |  | 0.0002968 | 126.6897 | 0.037602
119295340 | E | LC | ETL.8170.POLE.WDPS | 44565516 | EUREKA | HUMBOLDT | 2020-07-01 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564177 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.028619 | 553.6737 | 15.8455
119295345 | E | LC | ETL.8170.POLE.WOOD | 40662724 | EUREKA | HUMBOLDT | 2020-07-01 | 2021-10-14 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.011249 | 3688.5637
119296313 | F | LC | ETL.6890.POLE.WOOD | 40601385 | LAKEVLLE | SONOMA | 2020-06-29 | 2021-03-11 | ETL.6890 | FULTON-HOPLAND | Guy Wire Mark /Indic-Wood | Missing | [Install, Completed] |  | Tier 2 | Within Both | COMP | 40601385 | 1993-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Other |  |  |  |  | 0.00015222 | 126.6897
119302890 | F | LC | ETL.1450.POLE.STPS | 44945965 | SACTO | SIERRA | 2020-06-30 | 2020-11-05 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44945895 | 2020-07-24 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00031328 | 617.0731
119302995 | E | LC | ETL.1110.POLE.WDPS | 44423223 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-04-12 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423222 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00083679 | 3930.0344
119305161 | E | LC | ETL.7270.POLE.WOOD | 40909435 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-08-17 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40909435 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0021511 | 142.6986
119313491 | E | LC | ETL.1110.POLE.WDPS | 44424030 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424029 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0011115 | 7021.2925
119314698 | F | LC | ETL.6280.POLE.NWOD | 40675398 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40675398 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 2.0885e-05 | 2072.0388
119317186 | F | LC | ETL.1110.POLE.WDPS | 44424421 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-07-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] |  | Tier 2 | Within Both | COMP | 44424420 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0017394 | 3040.7186
119325286 | E | LC | ETL.1110.POLE.WDPS | 44424365 | EUREKA | NORTH VALLEY | 2020-07-07 | 2021-06-25 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424363 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00088649 | 174.0445
119330910 | E | LC | ETL.7850.POLE.WOOD | 40860859 | EUREKA | HUMBOLDT | 2020-07-08 | 2021-07-29 | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40860859 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 1.9399e-05 | 411.2699
119336057 | B | LC | ETL.7560.INSL.NCER | 40841285 | SACTO | SIERRA | 2020-07-08 | 2020-08-17 | ETL.7560 | WEIMAR #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44662500 | 2018-09-29 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End - Suspension |  |  |  |  | 0.0068614 | 3116.3115
119354090 | E | LC | ETL.6300.POLE.WOOD | 40698938 | TABLEMTN |  | 2020-07-07 | 2021-07-15 | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119359549 | E | LC | ETL.7030.POLE.WOOD | 40617095 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-06-08 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40617095 |  | Single Wood Pole | T2N | 2018-11-30 | Polymer | Post |  |  |  |  | 0.017961 | 94.9762
119359751 | E | LC | ETL.7490.INSL | 40884631 | EUREKA | HUMBOLDT | 2020-07-10 | 2021-09-16 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119375422 | E | LC | ETL.6220.POLE.WOOD | 40586733 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40586733 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | Dead End |  |  |  |  | 0.042684 | 2372.7383 | 101.2775
119467153 | E | LC | ETL.7780.POLE.NWOD | 44784134 | LAKEVLLE | SONOMA | 2020-07-17 | 2021-03-15 | ETL.7780 | PHILO JCT-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44784134 | 2019-06-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-06-03 | Polymer | Dead End |  |  |  |  | 1.5216e-07 | 2345.1394
119476395 | F | LC | ETL.2870.POLE.WOOD | 43203518 | MOSSLNDG | CENTRAL COAST | 2020-07-20 | 2021-04-07 | ETL.2870 | SARGENT SW STA-HOLLISTER | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 43203518 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | [5 empty] | 0.00026417
119483689 | E | LC | ETL.2060.POLE.NWOD | 44141376 | LAKEVLLE | SONOMA | 2020-07-21 |  | ETL.2060 | FORT BRAGG-ELK | Vegetation | Overgrown | [Remove] | Tier2 |  |  | PEND
119485962 | E | LC | ETL.4050.POLE.WOOD | 44846556 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-04-15 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44846556 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Dead End |  |  |  |  | 0.00060246 | 3389.4077
119485962 | E | LC | ETL.4050.POLE.WOOD | 44846556 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-04-15 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44846556 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Dead End |  |  |  |  | 0.00060246 | 3389.4077
119488282 | E | LC | ETL.7160.TOWR | 40601775 | LAKEVLLE | NORTH BAY | 2020-07-20 |  | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40601775 |  | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Polymer | [5 empty] | 0.057406 | 237.5913 | 13.6392
119490850 | F | LC | ETL.8170.POLE.WOOD | 40752182 | EUREKA | HUMBOLDT | 2020-07-21 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40752182 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.010734 | 0.065152
119512792 | F | LC | ETL.3190.POLE.NWOD | 44191909 | TABLEMTN | NORTH VALLEY | 2020-07-27 |  | ETL.3190 | CARIBOU-PALERMO | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44191909 |  | Lattice Steel Pole | Unknown | [7 empty] | 0.016411 | 6284.0591
119515075 | F | LC | ETL.9210.POLE.WOOD | 40586287 | MIDWAY | KERN | 2020-07-23 | 2020-10-06 | ETL.9210 | TAFT-CUYAMA #2 | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | DLFL | 40586287 | 1946-01-01 | Single Wood Pole | 2P DDE - 2 Pole Double Dead End | 1946-01-01 | Ceramic | Pin |  |  |  |  | 0.01085
119529674 | E | LC | ETL.6480.INSL.NCER | 40891309 | SACTO | SACRAMENTO | 2020-07-30 | 2021-06-30 | ETL.6480 | COLGATE-CHALLENGE | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40866891 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.043095 | 94.9762
119536305 | E | LC | ETL.5650.INSL | 40729447 | TABLEMTN | NORTH VALLEY | 2020-07-31 | 2021-03-03 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119552925 | E | LC | ETL.5390.TOWR | 40762579 | TABLEMTN | NORTH VALLEY | 2020-08-03 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40762579 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 7.9821e-06 | 475.7527 | 0.0037975
119571633 | F | LC | ETL.6980.POLE.WOOD | 40769848 | LAKEVLLE | HUMBOLDT | 2020-08-06 |  | ETL.6980 | FORT ROSS-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40769848 | 1986-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.027627 | 300.8518
119574061 | E | LC | ETL.6980.POLE.WOOD | 40584661 | LAKEVLLE | HUMBOLDT | 2020-08-06 | 2021-01-14 | ETL.6980 | FORT ROSS-GUALALA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40584661 | 1986-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.16186 | 7.9762
119591019 | F | LC | ETL.8210.POLE.WOOD | 40908251 | VICTOR | STOCKTON | 2020-08-07 |  | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908251 | 1974-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0033477 | 1015.9799
119592696 | F | LC | ETL.6880.POLE.WOOD | 44677461 | LAKEVLLE | SONOMA | 2020-08-10 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44677461 | 2017-10-21 | Single Wood Pole | T-1 - Tri Post | 2017-10-21 | Polymer | Post |  |  |  |  | 0.0076773 | 1250.5789
119592758 | F | LC | ETL.6220.POLE.WOOD | 40810347 | EUREKA | HUMBOLDT | 2020-08-10 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40810347 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.28002
119605595 | E | LC | ETL.6220.POLE.WOOD | 40810905 | EUREKA | HUMBOLDT | 2020-08-12 | 2021-02-24 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40810905 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Polymer | [5 empty] | 0.0051198 | 499.5363
119608829 | B | LC | ETL.8650.TOWR | 40582624 | FRESNO | FRESNO | 2020-08-13 | 2020-12-08 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Customer Refusal, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40582624 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1929-01-01 | Ceramic | Suspension |  |  |  |  | 0.013197 | 937.1003
119608890 | E | LC | ETL.5934.TOWR | 40858178 | FRESNO | FRESNO | 2020-08-12 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40858178 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00015184
119617996 | F | LC | ETL.1450.POLE.NWOD | 44766885 | SACTO | SACRAMENTO | 2020-08-14 | 2021-07-13 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44766885 | 2019-05-07 | Light Duty Steel Pole | DDE - Double Dead End | 2019-05-07 | Glass | Suspension |  |  |  |  | 2.3254e-07 | 443.0452
119629192 | F | LC | ETL.6870.POLE.WOOD | 40586036 | SACTO | SIERRA | 2020-08-17 | 2021-04-12 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40586036 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.08445 | 0.065152
119636577 | B | LC | ETL.5440.POLE.WDPS | 44557953 | TABLEMTN | NORTH VALLEY | 2020-08-19 | 2020-09-08 | ETL.5440 | PIT #6 JCT-ROUND MTN | Damper-Steel | Missing | [Install, Completed] | Tier2 |  |  | COMP
119649040 | E | LC | ETL.1420.TOWR | 40866005 | SACTO | SACRAMENTO | 2020-08-21 | 2021-03-01 | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40866005 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-05-03 | Glass | Suspension |  |  |  |  | 1.067e-05 | 158.3103
119650013 | E | LC | ETL.1240.POLE.WDPS | 44386360 | TABLEMTN | NORTH VALLEY | 2020-08-21 | 2020-09-01 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119662671 | E | LC | ETL.1680.POLE.WOOD | 40741737 | LAKEVLLE | SONOMA | 2020-08-24 | 2021-01-26 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40741737 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | Dead End |  |  |  |  | 0.001782 | 2708.3875
119662671 | E | LC | ETL.1680.POLE.WOOD | 40741737 | LAKEVLLE | SONOMA | 2020-08-24 | 2021-01-26 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40741737 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | Dead End |  |  |  |  | 0.001782 | 2708.3875
119688046 | F | LC | ETL.8060.POLE.WOOD | 40876713 | SACTO | SIERRA | 2020-08-26 | 2020-11-12 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40876713 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Polymer | [5 empty] | 0.0067894 | 63.348
119695973 | E | LC | ETL.1650.POLE.WOOD | 40669104 | LAKEVLLE | SONOMA | 2020-08-31 | 2021-04-08 | ETL.1650 | GEYSERS #3-CLOVERDALE | Vegetation | Overgrown | [Trim, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40669104 | 1966-01-01 | Single Wood Pole | WB - Wishbone | 2021-03-10 | Glass | Suspension |  |  |  |  | 4.1817e-05 | 3875.5634
119711602 | E | LC | ETL.7180.POLE.WOOD | 40617163 | LAKEVLLE | NORTH BAY | 2020-09-01 | 2021-04-05 | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40617163 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Glass | [5 empty] | 7.2628e-06 | 1919.4884
119720541 | A | LC | ETL.6240.POLE.WOOD | 40695110 | MOSSLNDG | CENTRAL COAST | 2020-09-05 | 2020-09-08 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace] | Tier2 |  |  | DLFL
119723082 | E | LC | ETL.6950.POLE.NWOD | 44186626 | SACTO | SIERRA | 2020-08-05 | 2021-10-20 | ETL.6950 | GOLD HILL #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44186626 | 2017-04-10 | Fiberglass | SVDE - Single Vertical Dead End | 2017-04-10 | Polymer | Dead End - Suspension |  |  |  |  | 4.209e-06 | 481.7272 | 0.0020276
119723085 | E | LC | ETL.8405.POLE.WOOD | 40755573 | SACTO | SIERRA | 2020-08-05 | 2021-10-20 | ETL.8405 | MIDDLE FORK #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40755573 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.038421 | 6723.8696 | 258.3388
119742104 | F | LC | ETL.1400.POLE.STPS | 44381758 | VICTOR | YOSEMITE | 2020-08-18 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44381757 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00020168 | 158.2923
119752285 | E | LC | ETL.6770.POLE.WOOD | 40751833 | SACTO | SIERRA | 2020-08-13 | 2021-04-22 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119760252 | E | LC | ETL.3740.TOWR | 40752436 | CONCORD | EAST BAY | 2020-09-04 | 2021-06-01 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40752436 | 1922-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1991-01-01 | Porcelain | Suspension |  |  |  |  | 0.044312 | 11.1359
119791236 | E | LC | ETL.1073.POLE.WDPS | 44962131 | VICTOR | STOCKTON | 2020-09-18 | 2021-09-07 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | DLFL | 40580228 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0016085 | 0.065147
119803159 | F | LC | ETL.6760.POLE.WOOD | 40767247 | SACTO | SIERRA | 2020-08-07 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40767247 |  | Single Wood Pole | T2N | 2020-03-02 | Polymer | Post |  |  |  |  | 0.03683 | 110.8453
119807705 | E | LC | ETL.6650.POLE.STPS | 44916447 | TABLEMTN | NORTH VALLEY | 2020-09-23 | 2021-06-01 | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44916371 | 2020-04-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0002465 | 1250.7715
119808517 | F | LC | ETL.1400.POLE.STPS | 44384134 | VICTOR | YOSEMITE | 2020-08-13 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 3 | Within Both | PEND | 44384132 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.7304e-05 | 31.7081
119815111 | B | LC | ETL.6240.POLE.WOOD | 40652077 | MOSSLNDG | CENTRAL COAST | 2020-09-25 | 2020-12-07 | ETL.6240 | BURNS-LONE STAR #2 | Damper-Wood | Missing | [Install, Completed] | Tier3 |  |  | COMP
119819830 | E | LC | ETL.8650.TOWR | 40660816 | FRESNO | YOSEMITE | 2020-08-31 | 2021-08-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40660816 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.018242 | 5840.8999
119829711 | E | LC | ETL.4590.INSL | 40919874 | TABLEMTN | NORTH VALLEY | 2020-09-28 | 2021-09-11 | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119835389 | F | LC | ETL.6480.POLE.WOOD | 40767129 | SACTO | SIERRA | 2020-09-04 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40767129 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.073691 | 316.448
119838770 | F | LC | ETL.8060.POLE.WOOD | 40618256 | SACTO | SIERRA | 2020-10-01 | 2021-05-24 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40618256 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Polymer | Dead End - Pin |  |  |  |  | 0.0046114 | 63.348
119863655 | B | LC | ETL.7180.INSL.CERA | 40882809 | LAKEVLLE | NORTH BAY | 2020-10-06 | 2020-11-02 | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40861079 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 8.448e-06 | 190.8427
119900329 | E | LC | ETL.8580.TOWR | 40597698 | PISMOBCH | LOS PADRES | 2020-10-14 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Road | Brush Fuel | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40597698 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-12-13 | Glass | Dead End |  |  |  |  | 1.3514e-06 | 2071.0579
119907581 | E | LC | ETL.1650.POLE.WOOD | 40808982 | LAKEVLLE | SONOMA | 2020-10-07 | 2021-04-26 | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808982 | 1993-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1966-01-01 | Ceramic | Other |  |  |  |  | 3.5006e-05 | 4970.959
119920437 | E | LC | ETL.5980.TOWR | 40753903 | PISMOBCH | LOS PADRES | 2020-10-19 | 2021-05-13 | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40753903 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-11-17 | Glass Silicone Coated | Suspension |  |  |  |  | 1.696e-06 | 948.955
120128738 | F | LC | ETL.6710.POLE.WOOD | 40824145 | MOSSLNDG | CENTRAL COAST | 2020-10-13 |  | ETL.6710 | DEL MONTE-VIEJO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40824145 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.17277 | 0.065148
120201319 | F | LC | ETL.1440.POLE.STPS | 40590089 | SACTO | SIERRA | 2020-12-11 | 2021-07-01 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40590089 |  | 3-Pole Non Wood | FSS - Field Switch Structure | [7 empty] | 4.4004e-07
120201319 | F | LC | ETL.1440.POLE.STPS | 40590089 | SACTO | SIERRA | 2020-12-11 | 2021-07-01 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40590089 |  | 3-Pole Non Wood | FSS - Field Switch Structure | [7 empty] | 4.4004e-07
120201319 | F | LC | ETL.1440.POLE.STPS | 40590089 | SACTO | SIERRA | 2020-12-11 | 2021-07-01 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40590089 |  | 3-Pole Non Wood | FSS - Field Switch Structure | [7 empty] | 4.4004e-07
120229461 | F | LC | ETL.6280.POLE.WOOD | 40867515 | TABLEMTN | NORTH VALLEY | 2020-11-20 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40867515 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00077897 | 47.5141
120552778 | E | LC | ETL.6320.INSL.NCER | 45040205 | TABLEMTN | NORTH VALLEY | 2021-02-18 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45040199 | 2021-02-09 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2021-02-09 | Polymer | Suspension |  |  |  |  | 0.0095181 | 2314.1787 | 22.0265
120653241 | F | LC | ETL.6950.POLE.NWOD | 44192356 | SACTO | SACRAMENTO | 2021-03-17 |  | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44192356 | 2017-04-09 | Light Duty Steel Pole | T-1 - Tri Post | 2017-04-09 | Polymer | Post |  |  |  |  | 3.1655e-05 | 1600.5433
120653241 | F | LC | ETL.6950.POLE.NWOD | 44192356 | SACTO | SACRAMENTO | 2021-03-17 |  | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44192356 | 2017-04-09 | Light Duty Steel Pole | T-1 - Tri Post | 2017-04-09 | Polymer | Post |  |  |  |  | 3.1655e-05 | 1600.5433
120657377 | F | LC | ETL.4590.TOWR | 40910157 | TABLEMTN | NORTH VALLEY | 2021-03-18 | 2021-05-31 | ETL.4590 | CRESTA-RIO OSO | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910157 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.9521e-05 | 0.065151
120674004 | F | LC | ETL.5140.POLE.STPS | 44690697 | SACTO | SACRAMENTO | 2021-03-22 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44141448 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.2059e-08 | 411.6627
120690458 | E | LC | ETL.1680.POLE.WOOD | 40740491 | LAKEVLLE | SONOMA | 2021-03-25 | 2021-06-25 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40740491 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2020-11-13 | Glass | Dead End |  |  |  |  | 0.0013891 | 5129.7943
120699312 | F | LC | ETL.2170.TOWR | 40579947 | SACTO | SACRAMENTO | 2021-03-26 |  | ETL.2170 | MADISON-VACA | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40579947 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-04-30 | Glass | Suspension |  |  |  |  | 8.1473e-07 | 9772.6035 | 0.007962
120710333 | F | LC | ETL.2170.TOWR | 40815794 | SACTO | SACRAMENTO | 2021-03-29 |  | ETL.2170 | MADISON-VACA | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40815794 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-04-30 | Glass | Suspension |  |  |  |  | 4.411e-08 | 9178.4814 | 0.00040487
120714406 | E | LC | ETL.5630.POLE.NWOD | 40862392 | TABLEMTN | NORTH VALLEY | 2021-03-30 |  | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40862392 |  | Lattice Steel Pole | DDE - Double Dead End | 1958-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.0023809 | 6046.7764 | 14.397
120726467 | E | LC | ETL.4040.POLE.STPS | 44647509 | TABLEMTN | NORTH VALLEY | 2021-04-01 | 2021-09-15 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44646912 | 2018-08-17 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00021353 | 205.7554
120726525 | B | LC | ETL.3830.INSL | 40877380 | VICTOR | STOCKTON | 2021-03-31 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40856461 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.3158e-08 | 1839.7756
120737270 | E | LC | ETL.3960.INSL.CERA | 40630215 | PISMOBCH | LOS PADRES | 2021-04-02 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40589300 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 3.1014e-07 | 1328.7231 | 0.00041209
120747853 | E | LC | ETL.1890.TOWR | 40659543 | FRESNO | FRESNO | 2021-03-29 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40659543 | 1982-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 6.9707e-06 | 5324.1222 | 0.037113
120753077 | B | LC | ETL.3830.INSL | 40774214 | VICTOR | STOCKTON | 2021-03-26 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40746012 | 1910-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1989-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.8526e-06 | 2454.5776
120765600 | E | LC | ETL.6050.TOWR | 40811342 | MOSSLNDG | CENTRAL COAST | 2021-04-08 | 2021-07-27 | ETL.6050 | MOSS LANDING-METCALF | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40811342 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.5761e-09 | 3024.1367
120808821 | E | LC | ETL.5310.TOWR | 40740585 | PISMOBCH | LOS PADRES | 2021-04-13 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40740585 | 1960-01-01 | LATTICE STEEL TOWER | TRP SUSP - Tramp Susp | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 9.9183e-07 | 714.9968 | 0.00070915
120811451 | F | LC | ETL.9100.POLE.WOOD | 44191303 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191303 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.4654e-05 | 1440.5813
120811556 | F | LC | ETL.9100.POLE.WOOD | 44191217 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191217 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.9945e-05 | 1523.1348
120815971 | E | LC | ETL.4316.INSL.CERA | 40632689 | TABLEMTN | NORTH VALLEY | 2021-04-14 | 2021-08-02 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120819622 | E | LC | ETL.1530.INSL | 40604881 | SACTO | SIERRA | 2021-04-14 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40581059 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 7.5402e-06 | 3701.6848 | 0.027911
120819890 | B | LC | ETL.1530.POLE.NWOD | 43704866 | SACTO | SIERRA | 2021-04-14 | 2021-05-17 | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43704866 | 2018-11-10 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2018-11-10 | Ceramic | Suspension |  |  |  |  | 6.5703e-06 | 1249.74
120821705 | F | LC | ETL.3960.TOWR | 40870130 | PISMOBCH | LOS PADRES | 2021-04-08 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40870130 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 5.8047e-09 | 4369.6021
120828495 | B | LC | ETL.6500.INSL.NCER | 42564769 | TABLEMTN | SACRAMENTO | 2021-04-15 | 2021-06-01 | ETL.6500 | COLGATE-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42564762 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.0010936 | 3374.0149
120835785 | F | LC | ETL.1400.POLE.WOOD | 40643201 | VICTOR | STOCKTON | 2021-04-17 | 2021-06-23 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40643201 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010247
120835785 | F | LC | ETL.1400.POLE.WOOD | 40643201 | VICTOR | STOCKTON | 2021-04-17 | 2021-06-23 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40643201 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010247
120841408 | E | LC | ETL.1810.INSL.CERA | 44395998 | EUREKA | HUMBOLDT | 2021-04-19 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Conductor-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44395981 | 2019-06-15 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-06-15 | Ceramic | Suspension |  |  |  |  | 5.5926e-06
120841408 | E | LC | ETL.1810.INSL.CERA | 44395998 | EUREKA | HUMBOLDT | 2021-04-19 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Conductor-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44395981 | 2017-06-15 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-06-15 | Ceramic | Suspension |  |  |  |  | 5.5926e-06
120843329 | E | LC | ETL.7890.INSL.CERA | 40716189 | MOSSLNDG | CENTRAL COAST | 2021-04-19 |  | ETL.7890 | SALINAS-FORT ORD #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40666589 |  | Lattice Steel Pole | DCPOST - Double Circuit Post |  | Porcelain | [5 empty] | 4.5487e-06 | 474.5322 | 0.0021585
120853516 | E | LC | ETL.4393.POLE.NWOD | 45078753 | SACTO | SIERRA | 2021-04-20 |  | ETL.4393 | DRUM-HIGGINS | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45078753 | 2020-09-02 | Light Duty Steel Pole | DDE - Double Dead End | 2020-09-02 | Glass | Double Dead End |  |  |  |  | 0.00032628 | 2056.7583 | 0.67107
120854981 | F | LC | ETL.6230.POLE.WOOD | 40826873 | MOSSLNDG | CENTRAL COAST | 2021-04-19 | 2021-06-08 | ETL.6230 | BURNS-LONE STAR #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40826873 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.14152 | 15.8866
120859102 | E | LC | ETL.4090.INSL.CERA | 40792410 | SACTO | SACRAMENTO | 2021-04-13 |  | ETL.4090 | VACA-VACAVILLE-CORDELIA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40813738 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2021-05-23 | Glass | Double Dead End |  |  |  |  | 2.3322e-06 | 5498.8643 | 0.012824
120859102 | E | LC | ETL.4090.INSL.CERA | 40792410 | SACTO | SACRAMENTO | 2021-04-13 |  | ETL.4090 | VACA-VACAVILLE-CORDELIA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40813738 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 2.3322e-06 | 5498.8643 | 0.012824
120859997 | F | LC | ETL.5330.TOWR | 40587018 | MOSSLNDG | CENTRAL COAST | 2021-04-13 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587018 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 6.2455e-08 | 1299.1967 | 8.1141e-05
120859997 | F | LC | ETL.5330.TOWR | 40587018 | MOSSLNDG | CENTRAL COAST | 2021-04-13 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587018 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 6.2455e-08 | 1299.1967 | 8.1141e-05
120865545 | F | LC | ETL.4850.TOWR | 40644847 | FRESNO | FRESNO | 2021-04-21 |  | ETL.4850 | HAAS-MCCALL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40644847 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1957-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.8694e-08 | 6933.1348 | 0.00026827
120865545 | F | LC | ETL.4850.TOWR | 40644847 | FRESNO | FRESNO | 2021-04-21 |  | ETL.4850 | HAAS-MCCALL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40644847 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-28 | Glass | Dead End |  |  |  |  | 3.8694e-08 | 6933.1348 | 0.00026827
120871952 | F | LC | ETL.5790.TOWR | 40587515 | VICTOR | STOCKTON | 2021-04-22 |  | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40587515 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 2.3703e-05 | 175.6506
120875990 | E | LC | ETL.7630.INSL.CERA | 40902583 | LAKEVLLE |  | 2021-04-23 |  | ETL.7630 | MONTE RIO-FULTON | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40877373 | 1990-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.11092 | 31.7051 | 3.5168
120878551 | E | LC | ETL.3830.TOWR | 40856458 | VICTOR | STOCKTON | 2021-04-24 | 2021-08-05 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40856458 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.07e-06 | 469.1458
120884177 | F | LC | ETL.1252.POLE.NWOD | 40601676 | FRESNO | FRESNO | 2021-04-26 |  | ETL.1252 | OAKHURST TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40601676 | 1997-01-01 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 1996-01-01 | Polymer | Post |  |  |  |  | 0.00015871 | 6568.6606
120886000 | E | LC | ETL.1250.INSL.NCER | 40777161 | FRESNO | FRESNO | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40748526 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 4.5878e-06 | 4946.1465 | 0.022692
120886794 | F | LC | ETL.5463.TOWR | 40582079 | CONCORD | DIABLO | 2021-04-26 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40582079 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 6.2953e-06 | 3992.2439 | 0.025132
120892166 | E | LC | ETL.7550.POLE.WOOD | 40750931 | LAKEVLLE | SONOMA | 2021-04-27 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40750931 |  | Single Wood Pole | SV-1B - Single Vertical Light Angle BR |  | Porcelain | [5 empty] | 3.695e-06 | 2974.7925 | 0.010992
120911641 | E | LC | ETL.5930.TOWR | 40816049 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40816049 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 8.6556e-07 | 1553.9977 | 0.0013451
120923238 | E | LC | ETL.8650.POLE.NWOD | 44420156 | FRESNO | YOSEMITE | 2021-04-14 |  | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44420156 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0056224 | 207.8215 | 1.1685
120930059 | E | LC | ETL.7000.POLE.WOOD | 40758913 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40758913 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-09-24 | Ceramic | Dead End |  |  |  |  | 0.00010719 | 31.6978 | 0.0033978
120932377 | B | LC | ETL.6500.POLE.WOOD | 40766507 | SACTO | SACRAMENTO | 2021-05-04 | 2021-05-13 | ETL.6500 | COLGATE-PALERMO | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40766507 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00052562 | 2214.9285
120938830 | E | LC | ETL.7490.POLE.WOOD | 40602136 | EUREKA | HUMBOLDT | 2021-05-05 |  | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40602136 |  | Single Wood Pole | T-1 - Tri Post | 2019-09-26 | Polymer | Post |  |  |  |  | 0.0078143 | 63.3304 | 0.49488
121112837 | E | LC | ETL.1540.INSL | 40780222 | SACTO | SIERRA | 2021-04-19 |  | ETL.1540 | EL DORADO-MISSOURI FLAT #2 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40751970 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 5.5537e-06 | 332.6081 | 0.0018472
121324890 | B | LC | ETL.7550.POLE.WOOD | 40809289 | LAKEVLLE | SONOMA | 2021-05-13 | 2021-06-17 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809289 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 7.1038e-06 | 110.7947
121328364 | E | LC | ETL.8290.POLE.WOOD | 40700143 | TABLEMTN | NORTH VALLEY | 2021-05-13 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40700143 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.0018048 | 795.2646 | 1.4353
121337846 | E | LC | ETL.5330.TOWR | 40591776 | MOSSLNDG | CENTRAL COAST | 2021-04-26 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40591776 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 2.9225e-08 | 0.077799 | 2.2737e-09
121337846 | E | LC | ETL.5330.TOWR | 40591776 | MOSSLNDG | CENTRAL COAST | 2021-04-26 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40591776 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 2.9225e-08 | 0.077799 | 2.2737e-09
121339308 | E | LC | ETL.5510.TOWR | 40819252 | CONCORD | DIABLO | 2021-04-26 | 2021-10-04 | ETL.5510 | PITTSBURG-TESLA #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40819252 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Dead End |  |  |  |  | 5.7411e-08 | 4101.8267 | 0.00023549
121353056 | B | LC | ETL.6020.TOWR | 40576226 | TABLEMTN | NORTH VALLEY | 2021-05-18 | 2021-06-07 | ETL.6020 | MALIN-ROUND MTN #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40576226 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 6.7738e-07 | 237.3869
121356742 | E | LC | ETL.1350.POLE.STPS | 45065785 | TABLEMTN | NORTH VALLEY | 2021-05-18 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40759609 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.1582e-05 | 3216.0659 | 0.069408
121356744 | E | LC | ETL.5630.INSL | 40896997 | TABLEMTN | NORTH VALLEY | 2021-04-23 |  | ETL.5630 | ROCK CREEK-POE | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40871540 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 1.4205e-07 | 1171.7432 | 0.00016645
121370121 | E | LC | ETL.1820.INSL.CERA | 44324200 | EUREKA | HUMBOLDT | 2021-05-20 | 2021-08-17 | ETL.1820 | HUMBOLDT-TRINITY | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
121370310 | E | LC | ETL.6950.POLE.WOOD | 40824099 | SACTO | SIERRA | 2021-05-01 | 2021-06-23 | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40824099 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00335 | 5283.5483
121370390 | F | LC | ETL.6880.POLE.WOOD | 44677461 | LAKEVLLE | SONOMA | 2021-05-01 | 2021-09-27 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44677461 | 2017-10-21 | Single Wood Pole | T-1 - Tri Post | 2017-10-21 | Polymer | Post |  |  |  |  | 0.0076773 | 1250.5789
121370419 | F | LC | ETL.1250.POLE.NWOD | 40870856 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40870856 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.3144e-06 | 4148.9409
121388675 | E | LC | ETL.8250.POLE.WOOD | 45096574 | VICTOR | STOCKTON | 2021-05-10 | 2021-08-31 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45096574 | 2020-06-23 | Single Wood Pole | T-1 - Tri Post | 2020-06-23 | Polymer | Post |  |  |  |  | 4.367e-05 | 2471.0422
121388931 | E | LC | ETL.1651.POLE.NWOD | 44915839 | LAKEVLLE | SONOMA | 2021-05-12 |  | ETL.1651 | MISSION POWER TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44915839 | 2020-05-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2020-05-01 | Glass | Dead End |  |  |  |  | 0.000167 | 5211.9639 | 0.87038
121389495 | E | LC | ETL.7380.POLE.WOOD | 40701565 | MOSSLNDG | CENTRAL COAST | 2021-05-12 | 2021-10-18 | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40701565 |  | Single Wood Pole | T1DE - Tri Post Dead End 115 |  | Polymer | Post |  |  |  |  | 0.11539 | 63.6087
121391769 | E | LC | ETL.6470.POLE.WOOD | 40874826 | SACTO | SACRAMENTO | 2021-05-24 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40874826 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.014536 | 1598.1093 | 23.2302
121395051 | F | LC | ETL.8060.POLE.WOOD | 40751899 | SACTO | SIERRA | 2021-05-18 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40751899 |  | Single Wood Pole | T2N | 2020-10-28 | Polymer | Post |  |  |  |  | 0.015888 | 95.0274
121401850 | F | LC | ETL.1073.POLE.NWOD | 44384836 | VICTOR | YOSEMITE | 2021-05-19 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44384836 | 2017-08-17 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 1.4819e-05 | 31.7081
121404196 | E | LC | ETL.8405.POLE.WOOD | 40586050 | SACTO | SIERRA | 2021-05-20 |  | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40586050 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.54856 | 4160.9766 | 2282.529
121405299 | E | LC | ETL.8250.POLE.WOOD | 40904101 | VICTOR | STOCKTON | 2021-05-21 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40904101 |  | Single Wood Pole | TPSRD - Tri Post & Susp Dead End |  | Porcelain | [5 empty] | 0.00011128 | 3548.5354 | 0.39487
121417876 | F | LC | ETL.8405.POLE.WOOD | 40751860 | SACTO | SIERRA | 2021-05-20 |  | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40751860 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.018114 | 981.1266
121418235 | E | LC | ETL.1070.POLE.WOOD | 40818424 | VICTOR | STOCKTON | 2021-05-20 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40818424 | 1998-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1957-01-01 | Polymer | Dead End |  |  |  |  | 9.9639e-05 | 2377.5283 | 0.2369
121427924 | E | LC | ETL.4316.INSL.CERA | 44681916 | TABLEMTN | NORTH VALLEY | 2021-05-26 |  | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44383161 | 2015-09-22 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2015-09-22 | Ceramic | Suspension |  |  |  |  | 0.0021824
121427924 | E | LC | ETL.4316.INSL.CERA | 44681916 | TABLEMTN | NORTH VALLEY | 2021-05-26 |  | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44383161 | 2015-09-22 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2015-09-22 | Ceramic | Suspension |  |  |  |  | 0.0021824
121476463 | E | LC | ETL.1440.INSL | 40615537 | SACTO | SIERRA | 2021-06-05 |  | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40590098 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00037523
121476463 | E | LC | ETL.1440.INSL | 40615537 | SACTO | SIERRA | 2021-06-05 |  | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40590098 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00037523
121493460 | F | LC | ETL.1402.POLE.WDPS | 44550822 | VICTOR | STOCKTON | 2021-06-02 |  | ETL.1402 | SPRING GAP TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44550061 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0019296 | 1329.0924
121496119 | E | LC | ETL.8630.INSL.CERA | 40632370 | PISMOBCH | LOS PADRES | 2021-06-09 |  | ETL.8630 | DIVIDE-VANDENBERG #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564299 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00032026
121496119 | E | LC | ETL.8630.INSL.CERA | 40632370 | PISMOBCH | LOS PADRES | 2021-06-09 |  | ETL.8630 | DIVIDE-VANDENBERG #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564299 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00032026
121496119 | E | LC | ETL.8630.INSL.CERA | 40632370 | PISMOBCH | LOS PADRES | 2021-06-09 |  | ETL.8630 | DIVIDE-VANDENBERG #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564299 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00032026
121497387 | E | LC | ETL.1450.POLE.WDPS | 44557780 | SACTO | SACRAMENTO | 2021-06-08 | 2021-07-01 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | DLFL | 44554054 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.05406 | 1123.6396
121499631 | E | LC | ETL.7212.POLE.WOOD | 40874256 | METCALF | PENINSULA | 2021-06-03 | 2021-08-17 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40874256 |  | Single Wood Pole | BDE - Buck Dead End |  | Polymer | [5 empty] | 0.23369 | 950.0938
121513053 | E | LC | ETL.6240.POLE.WOOD | 44991779 | MOSSLNDG | CENTRAL COAST | 2021-06-05 |  | ETL.6240 | BURNS-LONE STAR #2 | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44991779 | 2020-09-18 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-09-18 | Polymer | Post |  |  |  |  | 0.52236 | 15.8866 | 8.2986
121513301 | F | LC | ETL.6500.POLE.WOOD | 40757199 | SACTO | NORTH VALLEY | 2021-06-09 |  | ETL.6500 | COLGATE-PALERMO | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40757199 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.00053883 | 2353.5344
121516224 | E | LC | ETL.6690.POLE.WOOD | 40822856 | SACTO | SIERRA | 2021-06-05 | 2021-07-20 | ETL.6690 | DEER CREEK-DRUM | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40822856 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | [5 empty] | 0.053636 | 142.4642
121518238 | E | LC | ETL.6890.POLE.WOOD | 40825408 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40825408 | 1973-01-01 | Single Wood Pole | DV - Double Vertical |  | Ceramic | Other |  |  |  |  | 0.013492 | 1393.6937 | 18.8034
121518324 | E | LC | ETL.4440.INSL | 40791019 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761230 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 0.00029556 | 6600.7266 | 1.9509
121519830 | E | LC | ETL.8630.POLE.WDPS | 44565452 | PISMOBCH | LOS PADRES | 2021-06-11 | 2021-08-10 | ETL.8630 | DIVIDE-VANDENBERG #2 | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | DLFL | 44564228 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.712e-05 | 4322.2461
121522250 | E | LC | ETL.1350.INSL.CERA | 40897082 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40871613 | 1943-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.013068
121522250 | E | LC | ETL.1350.INSL.CERA | 40897082 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40871613 | 1943-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.013068
121523067 | F | LC | ETL.6760.POLE.WOOD | 40824302 | SACTO | SIERRA | 2021-06-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40824302 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | [5 empty] | 0.11358 | 110.8228
121524238 | F | LC | ETL.4040.POLE.WDPS | 44553733 | TABLEMTN |  | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44553119 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.039476 | 4481.9893
121525146 | E | LC | ETL.6640.POLE.WOOD | 40825172 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40825172 |  | Single Wood Pole | SUSP-V - Suspension Vertical (TWR) |  | Ceramic | [5 empty] | 0.017851 | 7691.732 | 137.3042
121525839 | E | LC | ETL.4550.INSL | 40845901 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40817930 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.8499e-05 | 2963.4478 | 0.17336
121536502 | E | LC | ETL.1440.POLE.WDPS | 44837707 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40618829 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0039142 | 31.7066 | 0.12411
121539243 | E | LC | ETL.2390.POLE.WDPS | 44391015 | VICTOR | STOCKTON | 2021-06-15 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391013 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 5.7132e-05 | 4273.2705 | 0.24414
121543835 | E | LC | ETL.4550.TOWR | 40592762 | TABLEMTN | NORTH VALLEY | 2021-06-12 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40592762 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 9.3107e-06 | 3151.3353 | 0.029341
121551881 | E | LC | ETL.5980.INSL | 40782699 | PISMOBCH | LOS PADRES | 2021-06-10 |  | ETL.5980 | DIABLO-MIDWAY #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40753843 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 8.8324e-07 | 5982.9551 | 0.0052844
121590828 | F | LC | ETL.4040.POLE.STPS | 44784256 | TABLEMTN |  | 2021-06-18 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44784114 | 2019-07-14 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 9.5511e-05 | 142.5046
121591200 | E | LC | ETL.6500.POLE.WOOD | 40757203 | SACTO | NORTH VALLEY | 2021-06-22 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40757203 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.032448 | 554.0433 | 17.9779
121596810 | E | LC | ETL.7610.POLE.WOOD | 40824938 | METCALF | DE ANZA | 2021-06-22 |  | ETL.7610 | MONTA VISTA-LOS GATOS | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40824938 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0010216 | 0.066432 | 6.787e-05
121598729 | F | LC | ETL.7000.POLE.NWOD | 45092625 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45092625 | 2019-08-05 | Light Duty Steel Pole | T2N | 2019-08-05 | Polymer | Post |  |  |  |  | 0.001194 | 47.5141
121606123 | F | LC | ETL.1440.POLE.STPS | 44966930 | SACTO | SIERRA | 2021-06-18 |  | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44966895 | 2020-07-21 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.8782e-07 | 0.065152
121607602 | F | LC | ETL.7550.POLE.WOOD | 40702876 | LAKEVLLE | HUMBOLDT | 2021-06-18 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40702876 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00019171 | 110.7947 | 0.02124
121610867 | E | LC | ETL.5452.INSL.CERA | 44291691 | CONCORD | DIABLO | 2021-06-27 | 2021-11-17 | ETL.5452 | CONTRA COSTA-MORAGA #1 | Insulator | Contaminated | [Ground Wash, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818035 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2013-01-01 | Ceramic | Dead End |  |  |  |  | 5.7697e-09 | 1537.8524 | 8.8729e-06
121620433 | F | LC | ETL.4780.POLE.NWOD | 44469284 | LAKEVLLE | SONOMA | 2021-06-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44469284 | 2018-01-31 | Tubular Steel Pole | SVDE - Single Vertical Dead End | 2018-01-31 | Ceramic | Post |  |  |  |  | 0.00057081 | 1188.9327
121624191 | F | LC | ETL.6060.TOWR | 40805131 | TABLEMTN | NORTH VALLEY | 2021-06-27 | 2021-10-14 | ETL.6060 | ROUND MTN-TABLE MTN #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40805131 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 3.2388e-06 | 3658.251
121629223 | E | LC | ETL.8423.INSL.CERA | 40851482 | MOSSLNDG | CENTRAL COAST | 2021-06-23 |  | ETL.8423 | SALINAS-FORT ORD #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40824208 |  | Lattice Steel Pole | DCPOST - Double Circuit Post |  | Porcelain | [5 empty] | 1.1307e-07 | 697.5886 | 7.888e-05
121629616 | B | LC | ETL.5420.INSL.CERA | 40849323 | TABLEMTN | NORTH VALLEY | 2021-06-28 | 2021-08-02 | ETL.5420 | PIT #5-ROUND MTN #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562454 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0014049
121629616 | B | LC | ETL.5420.INSL.CERA | 40849323 | TABLEMTN | NORTH VALLEY | 2021-06-28 | 2021-08-02 | ETL.5420 | PIT #5-ROUND MTN #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562454 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0014049
121648826 | E | LC | ETL.6760.POLE.WOOD | 40597226 | SACTO | SIERRA | 2021-06-28 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40597226 |  | Single Wood Pole | LB - Line and Buck | 2020-02-27 | Glass | Dead End |  |  |  |  | 0.07294 | 0.066432 | 0.0048455
121660928 | F | LC | ETL.7550.POLE.NWOD | 45012927 | LAKEVLLE | HUMBOLDT | 2021-07-01 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45012927 | 2020-06-01 | Light Duty Steel Pole | T-1 - Tri Post | 2020-06-01 | Polymer | Post |  |  |  |  | 8.3667e-06 | 79.143
121662714 | E | LC | ETL.4316.INSL.NCER | 44674863 | TABLEMTN |  | 2021-06-30 |  | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44674848 | 2018-11-16 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2018-11-16 | Glass | Suspension |  |  |  |  | 0.0023729
121662714 | E | LC | ETL.4316.INSL.NCER | 44674863 | TABLEMTN |  | 2021-06-30 |  | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44674848 | 2018-11-16 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2018-11-16 | Glass | Suspension |  |  |  |  | 0.0023729
121684260 | F | LC | ETL.7030.POLE.WOOD | 40868486 | TABLEMTN | NORTH VALLEY | 2021-07-08 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40868486 |  | Single Wood Pole | T2N | 2021-06-04 | Polymer | Post |  |  |  |  | 0.01045 | 159.5787
121690626 | E | LC | ETL.8180.POLE.NWOD | 45112913 | LAKEVLLE | SACRAMENTO | 2021-07-09 |  | ETL.8180 | TULUCAY-NAPA #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45112913 | 2021-06-16 | Light Duty Steel Pole | 3WV-T - Three Way Vertical Tap | 2021-06-16 | Glass | Dead End | [5 empty] | 4036.2856
121732178 | F | LC | ETL.4440.POLE.NWOD | 40819007 | TABLEMTN | NORTH VALLEY | 2021-07-12 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40819007 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.00089585 | 2721.3928
121736447 | F | LC | ETL.1820.POLE.NWOD | 44789679 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44789679 | 2019-04-29 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-04-29 | Glass | Suspension |  |  |  |  | 0.19564 | 189.8987
121738243 | E | LC | ETL.1820.POLE.WDPS | 44562879 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562485 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.089103 | 142.4582 | 12.6934
121742391 | E | LC | ETL.1820.POLE.STPS | 44395493 | EUREKA | HUMBOLDT | 2021-07-13 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395491 | 2020-03-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0059245 | 2753.0989 | 16.3108
121745535 | E | LC | ETL.1252.INSL.NCER | 40708300 | FRESNO | FRESNO | 2021-07-14 |  | ETL.1252 | OAKHURST TAP | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44319950 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 3.1141e-05
121745535 | E | LC | ETL.1252.INSL.NCER | 40708300 | FRESNO | FRESNO | 2021-07-14 |  | ETL.1252 | OAKHURST TAP | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44319950 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 3.1141e-05
121745535 | E | LC | ETL.1252.INSL.NCER | 40708300 | FRESNO | FRESNO | 2021-07-14 |  | ETL.1252 | OAKHURST TAP | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44319950 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 3.1141e-05
121747005 | E | LC | ETL.1810.TOWR | 44321408 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44321408 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-08-28 | Glass | Suspension |  |  |  |  | 2.6261e-06
121748223 | F | LC | ETL.1820.POLE.WOOD | 45102072 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45102072 |  | Single Wood Pole | 3P DDE - 3 Pole Double Dead End |  | Polymer | Double Dead End |  |  |  |  | 0.061564 | 79.2483 | 4.8788
121748348 | E | LC | ETL.8365.POLE.WOOD | 40912514 | EUREKA | HUMBOLDT | 2021-07-16 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40912514 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.16635
121749101 | E | LC | ETL.1820.POLE.NWOD | 44194982 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44194982 | 2014-09-20 | Light Duty Steel Pole | 3P SV - 3 Pole Single Vertical | 2014-09-20 | Ceramic | Suspension |  |  |  |  | 0.15399 | 47.5118 | 7.3163
121750699 | E | LC | ETL.1810.POLE.STPS | 45087855 | EUREKA | HUMBOLDT | 2021-07-16 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 45087783 | 2021-05-11 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.263e-06
121762474 | F | LC | ETL.7490.POLE.WOOD | 40586852 | EUREKA | HUMBOLDT | 2021-07-19 |  | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40586852 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Double Dead End |  |  |  |  | 0.0066547 | 63.3304 | 0.42145
121784504 | E | LC | ETL.9240.TOWR | 43249647 | PISMOBCH | LOS PADRES | 2021-07-22 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 43249647 |  | LATTICE STEEL TOWER | [9 empty] | 446.1609
121800774 | B | LC | ETL.6280.POLE.WOOD | 44259125 | TABLEMTN | NORTH VALLEY | 2021-07-26 | 2021-09-22 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 4.1639e-06 | 695.9825
121810922 | B | LC | ETL.8365.INSL.NCER | 40916352 | EUREKA | HUMBOLDT | 2021-07-27 | 2021-08-18 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906680 | 2010-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.055565
121810928 | E | LC | ETL.6690.POLE.NWOD | 42568602 | SACTO | SIERRA | 2021-07-27 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 42568602 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Dead End |  |  |  |  | 0.050625 | 886.0379 | 44.8556
121815407 | E | LC | ETL.8620.POLE.WDPS | 44564950 | PISMOBCH | LOS PADRES | 2021-07-28 |  | ETL.8620 | DIVIDE-VANDENBERG #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564340 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0015731 | 3024.9492 | 4.7586
122021239 | F | LC | ETL.6330.POLE.STPS | 45147673 | TABLEMTN | NORTH VALLEY | 2021-09-09 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45147552 | 2021-08-31 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End
122043572 | E | LC | ETL.7490.INSL.NCER | 45164023 | EUREKA | HUMBOLDT | 2021-09-13 |  | ETL.7490 | MAPLE CREEK-HOOPA | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45163991 | 2021-08-31 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2021-08-31 | Glass Silicone Coated | Suspension
122043572 | E | LC | ETL.7490.INSL.NCER | 45164023 | EUREKA | HUMBOLDT | 2021-09-13 |  | ETL.7490 | MAPLE CREEK-HOOPA | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45163991 | 2021-08-31 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2021-08-31 | Glass Silicone Coated | Suspension
122057765 | E | LC | ETL.4780.INSL.NCER | 45128975 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 41129340 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.00010865 | 3423.9121 | 0.37202
122057765 | E | LC | ETL.4780.INSL.NCER | 45128975 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 41129340 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.00010865 | 3423.9121 | 0.37202
122113022 | E | LC | ETL.8650.TOWR | 40873714 | FRESNO | STOCKTON | 2021-09-28 | 2021-11-16 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Anode-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40873714 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-11-18 | Glass | Suspension |  |  |  |  | 0.015352 | 15.88 | 0.24379
122361352 | E | LC | ETL.8620.POLE.WDPS | 44564941 | PISMOBCH | LOS PADRES | 2021-11-01 |  | ETL.8620 | DIVIDE-VANDENBERG #1 | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564336 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.567e-05 | 4195.7021 | 0.35945
118423692 | E | LC | ETL.1240.POLE.WDPS | 44386178 | TABLEMTN | NORTH VALLEY | 2020-01-11 | 2020-04-28 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118684508 | E | LC | ETL.7060.POLE.WOOD | 40653281 | METCALF | SAN JOSE | 2020-03-12 | 2021-06-29 | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Vegetation | Overgrown | [Trim] | Tier3 | Tier 3 | Within Both | DLFL | 40653281 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.0022556 | 0.066432
118776264 | E | LC | ETL.5090.TOWR | 40863204 | MOSSLNDG | DE ANZA | 2020-04-03 | 2020-06-01 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40863204 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.053345 | 189.9226
118943695 | F | LC | ETL.1250.POLE.NWOD | 40590407 | FRESNO | FRESNO | 2020-04-23 | 2021-05-10 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40590407 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 7.9337e-05 | 5619.8403
118949310 | E | LC | ETL.6470.POLE.WOOD | 40693197 | SACTO | SACRAMENTO | 2020-04-23 | 2020-07-01 | ETL.6470 | COLGATE-ALLEGHANY | Connector | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693197 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0092407 | 202.5446
118950982 | E | LC | ETL.5440.INSL.NCER | 44878264 | TABLEMTN | NORTH VALLEY | 2020-04-27 | 2020-06-09 | ETL.5440 | PIT #6 JCT-ROUND MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118966448 | B | LC | ETL.7820.POLE.WOOD | 40750471 | LAKEVLLE | HUMBOLDT | 2020-04-29 | 2020-08-03 | ETL.7820 | POTTER VALLEY-WILLITS | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118982785 | E | LC | ETL.4220.POLE.WOOD | 40866897 | TABLEMTN | NORTH VALLEY | 2020-04-29 | 2020-06-08 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40866897 | 1962-01-01 | Single Wood Pole | WB - Wishbone | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.026104 | 1076.7538
119003188 | B | LC | ETL.8410.POLE.WDPS | 44312675 | LAKEVLLE |  | 2020-05-06 | 2020-08-05 | ETL.8410 | ELK-GUALALA | Jumper-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44312674 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.087588 | 332.192
119016223 | E | LC | ETL.4220.POLE.WOOD | 40753961 | TABLEMTN | NORTH VALLEY | 2020-05-06 | 2020-05-29 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40753961 | 1962-01-01 | Single Wood Pole | WB - Wishbone | 1962-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0084974 | 4187.606
119044733 | E | LC | ETL.5920.INSL | 40773792 | CONCORD | EAST BAY | 2020-05-13 | 2021-08-31 | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746287 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Dead End |  |  |  |  | 1.5384e-07 | 442.8804
119044733 | E | LC | ETL.5920.INSL | 40773792 | CONCORD | EAST BAY | 2020-05-13 | 2021-08-31 | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746287 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 1.5384e-07 | 442.8804
119044733 | E | LC | ETL.5920.INSL | 40773792 | CONCORD | EAST BAY | 2020-05-13 | 2021-08-31 | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746287 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.5384e-07 | 442.8804
119049748 | E | LC | ETL.1240.POLE.WDPS | 44386162 | TABLEMTN | NORTH VALLEY | 2020-05-13 | 2020-06-10 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Tier 2 | Within Both | COMP | 44386161 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.9993e-05 | 2441.9417
119052199 | B | LC | ETL.7270.INSL.NCER | 40699771 | TABLEMTN |  | 2020-05-19 | 2020-06-24 | ETL.7270 | KESWICK-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40668358 | 2011-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.00071222 | 1567.3287
119062396 | E | LC | ETL.1240.POLE.WDPS | 44386135 | TABLEMTN | NORTH VALLEY | 2020-05-13 | 2020-06-08 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119084463 | F | LC | ETL.6490.POLE.WOOD | 40593269 | SACTO | SIERRA | 2020-05-28 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40593269 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.018806 | 4628.7279
119084463 | F | LC | ETL.6490.POLE.WOOD | 40593269 | SACTO | SIERRA | 2020-05-28 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40593269 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.018806 | 4628.7279
119088712 | E | LC | ETL.8410.INSL.NCER | 40894863 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-06-01 | ETL.8410 | ELK-GUALALA | Insulator | Contaminated | [Ground Wash, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870904 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Polymer | Suspension |  |  |  |  | 0.22772 | 348.0076
119100763 | E | LC | ETL.5540.TOWR | 40757242 | TABLEMTN | NORTH VALLEY | 2020-06-02 | 2021-03-25 | ETL.5540 | POE-RIO OSO | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40757242 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 5.6351e-05 | 94.985
119111577 | F | LC | ETL.1050.TOWR | 40819798 | FRESNO | FRESNO | 2020-05-26 |  | ETL.1050 | BALCH-SANGER | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40819798 | 1961-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1923-01-01 | Porcelain | Suspension |  |  |  |  | 0.0013205 | 8178.4194 | 10.7996
119114895 | E | LC | ETL.1600.TOWR | 40818829 | LAKEVLLE | NORTH BAY | 2020-05-26 | 2021-03-10 | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818829 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Polymer | Suspension |  |  |  |  | 6.6276e-07 | 3691.0676
119117671 | F | LC | ETL.6720.POLE.WOOD | 40862027 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-09-01 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40862027 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00012163 | 0.065151
119118953 | F | LC | ETL.6490.POLE.WOOD | 40768368 | SACTO | SIERRA | 2020-06-02 | 2021-02-18 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768368 |  | Single Wood Pole | T2N | 2021-02-14 | Polymer | Post |  |  |  |  | 0.0047253 | 419.3189
119127187 | F | LC | ETL.7300.POLE.WOOD | 40600381 | TABLEMTN |  | 2020-06-03 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600381 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0058201 | 285.7737
119162899 | F | LC | ETL.1400.POLE.WDPS | 44776441 | VICTOR | STOCKTON | 2020-06-12 | 2021-05-17 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40580204 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.0043374 | 31.7334
119163504 | E | LC | ETL.6710.INSL | 40901965 | MOSSLNDG | CENTRAL COAST | 2020-06-13 |  | ETL.6710 | DEL MONTE-VIEJO | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40876140 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | [5 empty] | 0.039624 | 0.065148 | 0.0025814
119164332 | E | LC | ETL.8170.POLE.WOOD | 40617861 | EUREKA | HUMBOLDT | 2020-06-14 |  | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40617861 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.15515 | 158.2408 | 24.5515
119167285 | F | LC | ETL.6280.POLE.NWOD | 44414597 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 3 | Within Both | PEND | 44414597 | 2014-08-27 | Light Duty Steel Pole | T-1 - Tri Post | 2014-08-27 | Polymer | Post |  |  |  |  | 1.1729e-05 | 5950.0312
119174917 | F | LC | ETL.6280.POLE.WOOD | 40826432 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2021-08-11 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 1.5033e-05 | 632.7172
119190471 | E | LC | ETL.3740.INSL.CERA | 40638423 | CONCORD | EAST BAY | 2020-06-19 | 2021-08-23 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Insulator | Contaminated | [Ground Wash, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40609143 | 1922-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1991-01-01 | Porcelain | Suspension |  |  |  |  | 0.10218 | 0.065158
119194045 | F | LC | ETL.8210.POLE.WOOD | 40903826 | VICTOR | STOCKTON | 2020-06-18 |  | ETL.8210 | VALLEY SPRINGS #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40903826 | 1985-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0022987 | 1359.403
119194753 | F | LC | ETL.1240.POLE.STPS | 44200945 | TABLEMTN | NORTH VALLEY | 2020-06-22 | 2020-07-30 | ETL.1240 | CASCADE-COTTONWOOD | Guy Wire Mark /Indic-Wood | Missing | [Install, Completed] |  | Tier 2 | Within Both | COMP | 44200944 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 3.2742e-09 | 5687.9312
119196152 | F | LC | ETL.6470.POLE.WOOD | 40760451 | SACTO | SIERRA | 2020-06-22 | 2021-07-13 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.047175 | 79.2067
119197835 | B | LC | ETL.6470.POLE.WOOD | 40693251 | SACTO | SIERRA | 2020-06-22 | 2020-07-08 | ETL.6470 | COLGATE-ALLEGHANY | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693251 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.035174 | 95.0148
119219057 | E | LC | ETL.3840.TOWR | 41196637 | VICTOR | STOCKTON | 2020-06-26 | 2020-08-25 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41196637 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | [5 empty] | 8.5708e-08 | 1028.0419
119236872 | F | LC | ETL.7270.POLE.NWOD | 44649359 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44649359 | 2018-08-17 | Light Duty Steel Pole | T2N | 2018-08-17 | Polymer | Post |  |  |  |  | 0.00028952 | 0.065152
119238216 | E | LC | ETL.8170.POLE.WOOD | 40877943 | EUREKA | HUMBOLDT | 2020-06-30 | 2021-06-08 | ETL.8170 | TRINITY-MAPLE CREEK | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877943 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-05-29 | Glass | Double Dead End |  |  |  |  | 0.0026496 | 1822.1172
119238751 | E | LC | ETL.7300.POLE.WOOD | 40770448 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2021-03-18 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119238869 | E | LC | ETL.4392.INSL.CERA | 44388723 | LAKEVLLE |  | 2020-06-30 | 2020-12-31 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119290786 | F | LC | ETL.6690.POLE.WOOD | 40866662 | SACTO | SACRAMENTO | 2020-07-01 |  | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40866662 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.018201 | 142.4642
119291675 | E | LC | ETL.7490.POLE.WDPS | 44223072 | EUREKA | HUMBOLDT | 2020-06-30 |  | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
119310904 | F | LC | ETL.8060.POLE.WOOD | 40602280 | SACTO | SIERRA | 2020-07-02 | 2020-11-12 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40602280 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.086421 | 617.0731
119316988 | E | LC | ETL.1820.POLE.NWOD | 44789694 | EUREKA | HUMBOLDT | 2020-07-06 | 2021-01-19 | ETL.1820 | HUMBOLDT-TRINITY | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44789694 | 2019-04-29 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-04-29 | Glass | Suspension |  |  |  |  | 0.19564 | 189.8987
119334163 | E | LC | ETL.7030.POLE.WOOD | 40659938 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-06-18 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40659938 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.00038624 | 110.7947
119341650 | B | LC | ETL.6280.POLE.WOOD | 40826373 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2020-11-17 | ETL.6280 | CARIBOU #2 | Other | Customer Issue | [Access Issue, Completed] | Tier2 |  |  | COMP
119353997 | E | LC | ETL.8560.INSL.NCER | 40632358 | PISMOBCH | LOS PADRES | 2020-07-08 | 2021-04-19 | ETL.8560 | CAYUCOS-CAMBRIA | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | DLFL | 40594504 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | [5 empty] | 0.00022886 | 667.6282
119355703 | E | LC | ETL.5430.INSL | 40722179 | TABLEMTN |  | 2020-07-10 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Damper-Steel | Missing | [Install] | Tier2 |  |  | PEND
119356774 | E | LC | ETL.8170.POLE.WDPS | 44769654 | EUREKA | HUMBOLDT | 2020-07-10 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Rotten | [Replace] |  | Tier 2 | Within Both | PEND | 40660539 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.011375 | 1028.5986 | 11.7006
119357677 | F | LC | ETL.6280.POLE.WOOD | 40768850 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-07-06 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768850 |  | Single Wood Pole | LB - Line and Buck |  | Ceramic | Other |  |  |  |  | 4.8615e-05 | 490.3705
119358145 | F | LC | ETL.8170.POLE.WOOD | 40862474 | EUREKA | HUMBOLDT | 2020-07-10 | 2021-06-14 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862474 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.023322 | 363.9585
119359773 | F | LC | ETL.7270.POLE.WOOD | 40877846 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40877846 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0035153 | 493.2504
119360111 | F | LC | ETL.7270.POLE.WOOD | 40617617 | TABLEMTN | NORTH VALLEY | 2020-07-13 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40617617 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0057501 | 2932.1831
119378297 | F | LC | ETL.7030.POLE.WOOD | 40757857 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40757857 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0039981 | 6268.4326
119466588 | F | LC | ETL.6220.POLE.WOOD | 44210152 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44210152 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.068305 | 1486.7976
119469336 | F | LC | ETL.7030.POLE.WOOD | 40815890 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2020-10-28 | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40815890 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0063696
119482325 | E | LC | ETL.7490.POLE.WDPS | 45089746 | EUREKA | HUMBOLDT | 2020-07-21 | 2021-10-11 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40662150 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.20352 | 79.1467
119495076 | F | LC | ETL.3190.TOWR | 40870660 | TABLEMTN | NORTH VALLEY | 2020-07-23 |  | ETL.3190 | CARIBOU-PALERMO | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40870660 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.00037536 | 2092.6382
119495315 | F | LC | ETL.6230.POLE.WOOD | 40771529 | MOSSLNDG | CENTRAL COAST | 2020-07-23 | 2021-06-24 | ETL.6230 | BURNS-LONE STAR #1 | Animal Guard-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771529 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Pin |  |  |  |  | 0.073811 | 1028.9148
119496357 | E | LC | ETL.7380.POLE.WOOD | 40771077 | MOSSLNDG | CENTRAL COAST | 2020-07-23 | 2021-04-01 | ETL.7380 | LAURELES-OTTER | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40771077 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.43683 | 174.3987
119498965 | E | LC | ETL.5250.INSL | 40844892 | CONCORD | EAST BAY | 2020-07-24 | 2021-06-14 | ETL.5250 | MORAGA-CASTRO VALLEY | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119508803 | E | LC | ETL.3190.TOWR | 40599260 | TABLEMTN | NORTH VALLEY | 2020-07-24 |  | ETL.3190 | CARIBOU-PALERMO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40599260 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.011357 | 5329.2935 | 60.5262
119529833 | E | LC | ETL.6220.POLE.WOOD | 40810318 | EUREKA | HUMBOLDT | 2020-07-30 | 2021-03-08 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40810318 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.055889 | 499.5363
119534065 | E | LC | ETL.7850.POLE.WOOD | 40861026 | EUREKA | HUMBOLDT | 2020-07-31 | 2021-02-22 | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40861026 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 5.9754e-06 | 452.319
119562550 | E | LC | ETL.8350.POLE.WOOD | 40697098 | VICTOR | STOCKTON | 2020-08-05 | 2021-03-29 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40697098 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0055542 | 1556.7621
119563764 | F | LC | ETL.7780.POLE.WOOD | 40600333 | LAKEVLLE | HUMBOLDT | 2020-08-05 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40600333 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 4.6832e-05 | 110.7741
119578475 | F | LC | ETL.7180.POLE.WOOD | 40827654 | LAKEVLLE | NORTH BAY | 2020-08-07 | 2021-02-10 | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40827654 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 5.3178e-06 | 3027.2869
119638293 | F | LC | ETL.8365.POLE.NWOD | 40906670 | EUREKA | HUMBOLDT | 2020-08-19 | 2021-07-19 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40906670 | 2011-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0020282
119645002 | B | LC | ETL.8650.TOWR | 40684998 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40684998 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0060733 | 79.1393
119649324 | F | LC | ETL.2660.TOWR | 40651647 | SACTO | SACRAMENTO | 2020-08-21 | 2021-02-12 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40651647 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Ceramic | Suspension |  |  |  |  | 1.0273e-08 | 3436.4141
119649324 | F | LC | ETL.2660.TOWR | 40651647 | SACTO | SACRAMENTO | 2020-08-21 | 2021-02-12 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40651647 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-12 | Glass | Suspension |  |  |  |  | 1.0273e-08 | 3436.4141
119665295 | E | LC | ETL.8300.POLE.WOOD | 40770185 | TABLEMTN | NORTH VALLEY | 2020-08-24 | 2020-09-17 | ETL.8300 | VOLTA-SOUTH | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119719918 | F | LC | ETL.5452.TOWR | 40804947 | CONCORD | DIABLO | 2020-06-22 | 2021-01-20 | ETL.5452 | CONTRA COSTA-MORAGA #1 | Structure-Tower | Anti-Climbing Guard | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40804947 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-01-01 | Ceramic | Suspension |  |  |  |  | 2.076e-07 | 31.7066
119723202 | E | LC | ETL.8060.POLE.WOOD | 40826229 | SACTO | SIERRA | 2020-06-29 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826229 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.059897 | 31.7066
119769277 | E | LC | ETL.4220.POLE.NWOD | 44923828 | TABLEMTN | NORTH VALLEY | 2020-08-17 | 2021-04-19 | ETL.4220 | WOODLEAF-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44923828 | 2019-09-23 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2019-09-23 | Glass | Dead End |  |  |  |  | 0.0010346
119769277 | E | LC | ETL.4220.POLE.NWOD | 44923828 | TABLEMTN | NORTH VALLEY | 2020-08-17 | 2021-04-19 | ETL.4220 | WOODLEAF-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44923828 | 2019-09-23 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2019-09-23 | Glass | Dead End |  |  |  |  | 0.0010346
119769277 | E | LC | ETL.4220.POLE.NWOD | 44923828 | TABLEMTN | NORTH VALLEY | 2020-08-17 | 2021-04-19 | ETL.4220 | WOODLEAF-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44923828 | 2019-09-23 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2019-09-23 | Glass | Dead End |  |  |  |  | 0.0010346
119776033 | E | LC | ETL.5540.INSL.CERA | 40786454 | TABLEMTN | NORTH VALLEY | 2020-09-09 | 2021-06-29 | ETL.5540 | POE-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119781261 | E | LC | ETL.8240.POLE.WOOD | 40863729 | VICTOR | STOCKTON | 2020-09-12 |  | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40863729 | 1995-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2021-01-27 | Polymer | Post |  |  |  |  | 0.0036047 | 2425.3579 | 8.7426
119784100 | E | LC | ETL.8490.TOWR | 40594469 | PISMOBCH | LOS PADRES | 2020-09-14 | 2021-01-07 | ETL.8490 | ATASCADERO-SAN LUIS OBISPO | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594469 | 1932-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0012442 | 142.4119
119789424 | F | LC | ETL.1073.POLE.WOOD | 40643749 | VICTOR | YOSEMITE | 2020-07-29 | 2021-02-09 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40643749 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00060567
119789424 | F | LC | ETL.1073.POLE.WOOD | 40643749 | VICTOR | YOSEMITE | 2020-07-29 | 2021-02-09 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40643749 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00060567
119794777 | E | LC | ETL.1880.INSL.CERA | 40791657 | FRESNO | FRESNO | 2020-09-18 |  | ETL.1880 | KERCKHOFF #1-KERCKHOFF #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761729 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 3.2657e-07 | 4069.8035 | 0.0013291
119794777 | E | LC | ETL.1880.INSL.CERA | 40791657 | FRESNO | FRESNO | 2020-09-18 |  | ETL.1880 | KERCKHOFF #1-KERCKHOFF #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761729 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2002-01-01 | Porcelain | Suspension |  |  |  |  | 3.2657e-07 | 4069.8035 | 0.0013291
119801107 | F | LC | ETL.1073.POLE.WDPS | 44963368 | VICTOR | STOCKTON | 2020-09-22 | 2021-07-30 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40744523 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00027239 | 1298.4628
119907453 | E | LC | ETL.7620.POLE.WOOD | 40612258 | METCALF | DE ANZA | 2020-10-08 |  | ETL.7620 | MONTA VISTA-PERMANENTE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40612258 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Non Ceramic | Other | [5 empty] | 1140.4965
119917422 | F | LC | ETL.5140.POLE.STPS | 44411043 | SACTO | SIERRA | 2020-09-21 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44411042 | 2018-12-01 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.4685e-06 | 3733.8787
119951402 | B | LC | ETL.7780.POLE.WOOD | 40819507 | LAKEVLLE | HUMBOLDT | 2020-10-27 | 2020-11-06 | ETL.7780 | PHILO JCT-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40819507 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Dead End |  |  |  |  | 9.1175e-06 | 3862.9951
119953409 | E | LC | ETL.9340.POLE.NWOD | 40765856 | FRESNO | YOSEMITE | 2020-10-20 | 2021-10-23 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40765856 | 2013-01-01 | Fiberglass | TH - TriAngle Post 70 | 1984-01-01 | Polymer | Post |  |  |  |  | 0.037667 | 4686.4556 | 176.5251
119974716 | F | LC | ETL.8580.TOWR | 40584322 | FRESNO | FRESNO | 2020-11-02 | 2020-12-21 | ETL.8580 | COALINGA #1-SAN MIGUEL | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40584322 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Porcelain | [5 empty] | 6.0314e-07
119985654 | F | LC | ETL.8365.POLE.WOOD | 40912554 | EUREKA | HUMBOLDT | 2020-11-02 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40912554 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.020297
119992892 | E | LC | ETL.8580.TOWR | 40652833 | PISMOBCH | CENTRAL COAST | 2020-11-04 | 2021-07-08 | ETL.8580 | COALINGA #1-SAN MIGUEL | Foundation/Concrete-Tower | Earth Covered Tower | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40652833 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 3.192e-07 | 7679.498
120013120 | E | LC | ETL.5934.TOWR | 40805214 | FRESNO | FRESNO | 2020-11-09 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40805214 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00020514
120013122 | F | LC | ETL.5934.TOWR | 40805214 | FRESNO | FRESNO | 2020-11-09 | 2021-07-19 | ETL.5934 | TEMPLETON-GATES | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40805214 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00020514
120108649 | E | LC | ETL.6280.POLE.WOOD | 40649910 | TABLEMTN | NORTH VALLEY | 2020-11-20 | 2021-05-11 | ETL.6280 | CARIBOU #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40649910 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-02-11 | Polymer | Dead End |  |  |  |  | 4.6361e-06 | 15.8815
120134320 | F | LC | ETL.6979.POLE.WOOD | 40656314 | LAKEVLLE | SONOMA | 2020-10-21 | 2021-07-19 | ETL.6979 | MONTE RIO-FORT ROSS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40656314 | 1985-01-01 | Single Wood Pole | T-1 - Tri Post | 2010-01-01 | Non Ceramic | Post |  |  |  |  | 0.0070401 | 31.7051
120162027 | F | LC | ETL.6770.POLE.NWOD | 44166986 | VICTOR | SIERRA | 2020-11-03 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44166986 | 2013-09-24 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2013-09-24 | Non Ceramic | Dead End |  |  |  |  | 0.00019115 | 2259.2634
120190469 | B | LC | ETL.1110.TOWR | 40761532 | TABLEMTN | HUMBOLDT | 2020-12-11 | 2021-01-13 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761532 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 0.00016185 | 379.78
120222648 | B | LC | ETL.1470.POLE.NWOD | 44921286 | LAKEVLLE | SONOMA | 2020-12-18 | 2021-07-07 | ETL.1470 | EAGLE ROCK-CORTINA | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44921286 | 2020-05-10 | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 1.0193e-05 | 5079.5444
120243213 | E | LC | ETL.1440.POLE.WDPS | 44765650 | SACTO | SACRAMENTO | 2020-12-31 | 2021-07-27 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 680.4761
120243328 | E | LC | ETL.4393.POLE.WDPS | 44172123 | SACTO | SACRAMENTO | 2020-12-31 | 2021-03-31 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120482040 | A | LC | ETL.1402.TOWR | 40803738 | VICTOR | STOCKTON | 2021-01-30 | 2021-02-04 | ETL.1402 | SPRING GAP TAP | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40803738 | 1956-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | [7 empty] | 2.2206e-05 | 1659.7658
120572091 | E | LC | ETL.6710.POLE.WOOD | 40613852 | MOSSLNDG | CENTRAL COAST | 2021-02-24 |  | ETL.6710 | DEL MONTE-VIEJO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40613852 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.047119 | 0.066432 | 0.0031302
120635637 | B | LC | ETL.8250.POLE.NWOD | 40912846 | VICTOR | STOCKTON | 2021-03-11 | 2021-05-17 | ETL.8250 | CLAY-MARTEL | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40912846 | 2011-01-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 3.6634e-07 | 2888.8808
120639066 | E | LC | ETL.5100.TOWR | 40810615 | MOSSLNDG | SAN JOSE | 2021-03-11 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40810615 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2005-01-01 | Non Ceramic | Dead End |  |  |  |  | 9.7934e-08 | 1772.1183 | 0.00017355
120639066 | E | LC | ETL.5100.TOWR | 40810615 | MOSSLNDG | SAN JOSE | 2021-03-11 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40810615 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2005-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 9.7934e-08 | 1772.1183 | 0.00017355
120679785 | B | LC | ETL.5140.POLE.WDPS | 44558251 | SACTO | SACRAMENTO | 2021-03-23 | 2021-04-01 | ETL.5140 | MIDDLE FORK-GOLD HILL | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120710899 | A | LC | ETL.6220.POLE.WOOD | 40586743 | EUREKA | HUMBOLDT | 2021-03-30 | 2021-04-05 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Emergency | Storm Related | [Repair, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40586743 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.068216
120718257 | E | LC | ETL.1730.INSL.NCER | 40903025 | MOSSLNDG | CENTRAL COAST | 2021-03-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40878200 | 1972-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1972-01-01 | Polymer | Dead End |  |  |  |  | 0.00055002 | 126.5838 | 0.069624
120734813 | E | LC | ETL.3840.INSL.CERA | 40885080 | VICTOR | STOCKTON | 2021-03-31 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40861750 | 1970-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1989-01-01 | Porcelain | Suspension |  |  |  |  | 8.493e-08 | 3833.2197 | 0.00032556
120739361 | F | LC | ETL.5650.TOWR | 40762577 | TABLEMTN | NORTH VALLEY | 2021-04-03 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40762577 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 3.2187e-06 | 4689.9517 | 0.015096
120743463 | E | LC | ETL.1350.POLE.STPS | 44990449 | TABLEMTN | NORTH VALLEY | 2021-04-05 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44990395 | 2020-06-10 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.2081e-05 | 269.0551
120756560 | E | LC | ETL.1350.POLE.WDPS | 44552543 | TABLEMTN | NORTH VALLEY | 2021-04-07 | 2021-06-22 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44551558 |  | 2-Pole Wood | TRP SUSP - Tramp Susp | [7 empty] | 0.0087384 | 0.065152
120758375 | B | LC | ETL.8365.POLE.WOOD | 40768635 | EUREKA | HUMBOLDT | 2021-04-07 | 2021-04-20 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768635 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.015223 | 1966.5326
120763548 | E | LC | ETL.4391.INSL.NCER | 41178904 | LAKEVLLE |  | 2021-04-08 |  | ETL.4391 | GEYSERS #11-EAGLE ROCK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41102744 | 1999-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 7.1735e-05 | 4395.2046 | 0.31529
120772741 | B | LC | ETL.4050.POLE.WOOD | 40750653 | LAKEVLLE | SONOMA | 2021-04-09 | 2021-04-17 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750653 | 1970-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-04-14 | Glass | Dead End |  |  |  |  | 0.0010647 | 5287.5088
120773828 | E | LC | ETL.8250.POLE.WOOD | 40607081 | VICTOR | STOCKTON | 2021-04-09 | 2021-08-11 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120786946 | E | LC | ETL.8250.POLE.WOOD | 40588354 | VICTOR | STOCKTON | 2021-04-10 | 2021-08-12 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 2235.5154
120788759 | E | LC | ETL.8250.POLE.WOOD | 40904169 | VICTOR | STOCKTON | 2021-04-10 | 2021-07-22 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40904169 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0048513 | 3357.1318
120795723 | E | LC | ETL.4316.INSL.CERA | 44652085 | TABLEMTN |  | 2021-04-12 | 2021-07-29 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40755640 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-05-07 | Ceramic | Suspension |  |  |  |  | 0.065122 | 4481.9458
120798524 | F | LC | ETL.6880.POLE.WDPS | 44286447 | LAKEVLLE |  | 2021-04-12 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44286446 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0022828 | 1219.0785
120801581 | E | LC | ETL.3830.TOWR | 40579571 | VICTOR | STOCKTON | 2021-04-12 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40579571 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 6.2559e-07 | 4843.4395 | 0.00303
120804986 | F | LC | ETL.5540.TOWR | 40598069 | TABLEMTN | NORTH VALLEY | 2021-03-29 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40598069 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 1.3993e-07 | 2916.0366 | 0.00040805
120812832 | E | LC | ETL.1710.INSL | 40792707 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40762461 | 1970-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 3.0697e-06 | 0.065147 | 1.9998e-07
120823539 | F | LC | ETL.1073.POLE.WDPS | 44974306 | VICTOR | STOCKTON | 2021-04-15 | 2021-04-22 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40643749 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00060567 | 31.7081
120831205 | E | LC | ETL.2870.POLE.WOOD | 43203521 | MOSSLNDG | CENTRAL COAST | 2021-04-16 |  | ETL.2870 | SARGENT SW STA-HOLLISTER | Crossarm-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 43203521 |  | Single Wood Pole | WB - Wishbone |  | Porcelain | [5 empty] | 0.00050871
120843323 | E | LC | ETL.6500.POLE.WOOD | 42564738 | SACTO | SACRAMENTO | 2021-04-19 | 2021-08-17 | ETL.6500 | COLGATE-PALERMO | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42564738 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0016212 | 94.9762
120847293 | F | LC | ETL.8365.POLE.WOOD | 40912515 | EUREKA | HUMBOLDT | 2021-04-19 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Right of Way | Encroachment | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40912515 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.023413
120850397 | E | LC | ETL.5540.INSL | 40694138 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.5540 | POE-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40663013 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 4.8781e-06 | 2883.9575 | 0.014068
120859276 | F | LC | ETL.5540.TOWR | 40814837 | TABLEMTN | NORTH VALLEY | 2021-04-13 | 2021-05-05 | ETL.5540 | POE-RIO OSO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40814837 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 1.3e-06 | 4386.7925
120859481 | F | LC | ETL.4440.TOWR | 40591414 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40591414 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 2.7749e-06 | 1632.2432 | 0.0045292
120865060 | F | LC | ETL.1820.POLE.STPS | 44395186 | EUREKA | HUMBOLDT | 2021-04-22 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395185 | 2017-10-03 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.057528 | 142.4559
120865060 | F | LC | ETL.1820.POLE.STPS | 44395186 | EUREKA | HUMBOLDT | 2021-04-22 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395185 | 2017-10-03 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.057528 | 142.4559
120866100 | E | LC | ETL.1600.INSL.NCER | 40835240 | LAKEVLLE | SONOMA | 2021-04-13 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810364 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Polymer | Suspension |  |  |  |  | 7.4515e-08 | 269.18 | 2.0058e-05
120877928 | E | LC | ETL.5463.TOWR | 40680792 | CONCORD | DIABLO | 2021-04-23 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40680792 | 1964-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-05-10 | Glass | Suspension |  |  |  |  | 5.1509e-08 | 5196.8096 | 0.00026768
120877928 | E | LC | ETL.5463.TOWR | 40680792 | CONCORD | DIABLO | 2021-04-23 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40680792 | 1964-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 5.1509e-08 | 5196.8096 | 0.00026768
120878295 | E | LC | ETL.3741.INSL | 41111103 | CONCORD | EAST BAY | 2021-04-23 | 2021-08-10 | ETL.3741 | MORAGA-LAKEWOOD | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 41111102 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 1.402e-05 | 458.8659
120880219 | F | LC | ETL.1252.POLE.STPS | 44319943 | FRESNO | FRESNO | 2021-04-24 | 2021-07-30 | ETL.1252 | OAKHURST TAP | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44319942 | 2000-03-30 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.8778e-06 | 3515.5505
120914688 | E | LC | ETL.5930.INSL | 40726151 | LAKEVLLE |  | 2021-05-01 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40683889 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.8274e-09 | 395.7004 | 1.5145e-06
120914751 | E | LC | ETL.1440.POLE.WDPS | 44162399 | SACTO | SACRAMENTO | 2021-05-01 | 2021-06-11 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44162396 | 2013-09-10 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00018379 | 79.1687
120934689 | F | LC | ETL.3500.TOWR | 40744664 | VICTOR | STOCKTON | 2021-04-16 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40744664 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 3.4735e-05 | 94.9894 | 0.0032994
120936479 | F | LC | ETL.1600.TOWR | 40648685 | LAKEVLLE | SONOMA | 2021-05-05 |  | ETL.1600 | FULTON-PUEBLO | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40648685 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-03-29 | Glass Silicone Coated | Suspension |  |  |  |  | 1.8098e-07 | 31.7331
120936479 | F | LC | ETL.1600.TOWR | 40648685 | LAKEVLLE | SONOMA | 2021-05-05 |  | ETL.1600 | FULTON-PUEBLO | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40648685 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-03-23 | Glass | Suspension |  |  |  |  | 1.8098e-07 | 31.7331
121192051 | F | LC | ETL.7560.POLE.WOOD | 40668866 | SACTO | SIERRA | 2021-04-19 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40668866 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-06-30 | Glass | Dead End |  |  |  |  | 0.015161 | 3116.3115
121330762 | E | LC | ETL.5330.TOWR | 40591782 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.5330 | MOSS LANDING-COBURN | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40591782 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 2.2461e-05 | 871.2979 | 0.01957
121330762 | E | LC | ETL.5330.TOWR | 40591782 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.5330 | MOSS LANDING-COBURN | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40591782 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 2.2461e-05 | 871.2979 | 0.01957
121356847 | E | LC | ETL.1420.TOWR | 40762307 | SACTO | SIERRA | 2021-04-28 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40762307 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.0022604 | 3564.2905 | 8.0568
121381565 | E | LC | ETL.6500.POLE.WOOD | 40873546 | SACTO | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40873546 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | Pin |  |  |  |  | 0.0077246 | 917.0279 | 7.0837
121383587 | E | LC | ETL.6320.POLE.WOOD | 40873575 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40873575 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0026328 | 1523.649 | 4.0114
121384936 | F | LC | ETL.1430.TOWR | 40597639 | SACTO | SIERRA | 2021-05-12 |  | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40597639 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.001164 | 1360.4569 | 1.5836
121392202 | E | LC | ETL.6660.POLE.NWOD | 40738445 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40738445 | 1998-01-01 | Light Duty Steel Pole | T-1 - Tri Post | 2021-02-11 | Polymer | Post |  |  |  |  | 4.3374e-08 | 3819.6531 | 0.00016568
121397535 | F | LC | ETL.6050.TOWR | 40812002 | MOSSLNDG | SAN JOSE | 2021-05-18 | 2021-10-04 | ETL.6050 | MOSS LANDING-METCALF | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40812002 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.6548e-07 | 1536.8715
121402980 | E | LC | ETL.6870.POLE.NWOD | 44340602 | SACTO | SIERRA | 2021-05-19 | 2021-06-30 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44340602 | 2014-10-01 | Light Duty Steel Pole | T-1 - Tri Post | 2014-10-01 | Non Ceramic | Post |  |  |  |  | 0.020724 | 94.9894
121409448 | E | LC | ETL.6280.POLE.NWOD | 44259059 | TABLEMTN | NORTH VALLEY | 2021-05-21 | 2021-08-13 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44259059 | 2020-07-16 | Light Duty Steel Pole | T2N | 2020-07-16 | Polymer | Post |  |  |  |  | 1.7956e-10 | 300.5749
121424590 | E | LC | ETL.4220.POLE.WDPS | 44557515 | TABLEMTN |  | 2021-05-26 |  | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44553930 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.085564 | 205.7755 | 17.607
121434916 | B | LC | ETL.1450.INSL.CERA | 40630552 | SACTO | SACRAMENTO | 2021-05-25 | 2021-09-01 | ETL.1450 | DRUM-SUMMIT #2 | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553957 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064757
121434916 | B | LC | ETL.1450.INSL.CERA | 40630552 | SACTO | SACRAMENTO | 2021-05-25 | 2021-09-01 | ETL.1450 | DRUM-SUMMIT #2 | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553957 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064757
121434916 | B | LC | ETL.1450.INSL.CERA | 40630552 | SACTO | SACRAMENTO | 2021-05-25 | 2021-09-01 | ETL.1450 | DRUM-SUMMIT #2 | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553957 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064757
121469754 | B | LC | ETL.5640.TOWR | 40756677 | TABLEMTN | NORTH VALLEY | 2021-06-03 | 2021-06-29 | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756677 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 1.4387e-06 | 3962.0544
121473364 | F | LC | ETL.1440.POLE.WDPS | 44761207 | SACTO | SACRAMENTO | 2021-06-04 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40683594 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00058853 | 47.5526 | 0.027986
121474638 | E | LC | ETL.6750.POLE.WDPS | 44562147 | TABLEMTN | NORTH VALLEY | 2021-06-05 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44561577 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00033586 | 411.4229 | 0.13818
121476466 | A | LC | ETL.4781.INSL | 40895526 | LAKEVLLE |  | 2021-06-05 | 2021-06-08 | ETL.4781 | GEYSERS #13 TAP | Emergency-Steel | Other | [Replace, Completed] | Tier3 |  |  | COMP
121481747 | E | LC | ETL.5140.POLE.WDPS | 44552538 | SACTO | SACRAMENTO | 2021-06-07 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44551664 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00030903 | 1086.9597 | 0.3359
121489559 | F | LC | ETL.6890.POLE.WOOD | 40656897 | LAKEVLLE | SONOMA | 2021-06-02 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40656897 | 1993-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Other |  |  |  |  | 6.3388e-05 | 1884.812
121493332 | F | LC | ETL.5640.TOWR | 40873681 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40873681 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 1.1007e-09 | 4658.4756 | 5.1278e-06
121495920 | F | LC | ETL.5640.TOWR | 40805321 | TABLEMTN | NORTH VALLEY | 2021-06-03 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40805321 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 6.2458e-10 | 4571.4038 | 2.8552e-06
121500210 | F | LC | ETL.5650.TOWR | 40819717 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40819717 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 7.7059e-08 | 2806.333 | 0.00021625
121523466 | E | LC | ETL.1350.POLE.WDPS | 44201742 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44201741 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.14209 | 490.5302 | 69.6996
121526201 | E | LC | ETL.5650.TOWR | 40675860 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Structure-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40675860 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.5197e-05 | 4674.3652 | 0.071034
121527149 | E | LC | ETL.5650.TOWR | 40762510 | TABLEMTN | NORTH VALLEY | 2021-06-03 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier2 | Tier 2 | Within Both | PEND | 40762510 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 6.6806e-08 | 2806.333 | 0.00018748
121538386 | B | LC | ETL.1470.INSL.CERA | 40779415 | LAKEVLLE | HUMBOLDT | 2021-06-14 | 2021-08-23 | ETL.1470 | EAGLE ROCK-CORTINA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121540115 | E | LC | ETL.2390.INSL.NCER | 40895715 | VICTOR | STOCKTON | 2021-06-15 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391279 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 7.1585e-05
121540115 | E | LC | ETL.2390.INSL.NCER | 40895715 | VICTOR | STOCKTON | 2021-06-15 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391279 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 7.1585e-05
121540115 | E | LC | ETL.2390.INSL.NCER | 40895715 | VICTOR | STOCKTON | 2021-06-15 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391279 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 7.1585e-05
121540468 | B | LC | ETL.7290.INSL.NCER | 45059684 | TABLEMTN | NORTH VALLEY | 2021-06-15 | 2021-09-04 | ETL.7290 | KILARC-CEDAR CREEK | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 45059640 | 2020-03-03 | Light Duty Steel Pole | T2N | 2020-03-03 | Polymer | Post |  |  |  |  | 0.0039113 | 364.8483
121541865 | E | LC | ETL.5390.TOWR | 41107603 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 41107603 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.1355e-06 | 4610.73 | 0.0098463
121543009 | F | LC | ETL.1820.POLE.STPS | 44921409 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44921326 | 2020-03-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00079264 | 363.9585
121551199 | F | LC | ETL.1350.POLE.NWOD | 44993094 | TABLEMTN | NORTH VALLEY | 2021-06-12 | 2021-06-30 | ETL.1350 | CRAG VIEW-CASCADE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44993094 | 2020-06-11 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-11 | Glass | Dead End |  |  |  |  | 6.2682e-05 | 79.1724
121552371 | F | LC | ETL.5980.TOWR | 40863923 | PISMOBCH | LOS PADRES | 2021-06-17 |  | ETL.5980 | DIABLO-MIDWAY #3 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40863923 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-10-07 | Glass Silicone Coated | Suspension |  |  |  |  | 2.1406e-10 | 2203.3623
121557745 | F | LC | ETL.5400.TOWR | 40657312 | TABLEMTN | NORTH VALLEY | 2021-06-13 | 2021-07-01 | ETL.5400 | PIT #3-PIT #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40657312 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 0.025506 | 1428.0112
121562258 | F | LC | ETL.7550.POLE.WDPS | 44211135 | LAKEVLLE |  | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44211134 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00062638 | 110.7947 | 0.069399
121568319 | F | LC | ETL.8350.POLE.NWOD | 45015285 | VICTOR | STOCKTON | 2021-06-15 | 2021-07-01 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 45015285 | 2020-05-07 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-07 | Glass | Dead End |  |  |  |  | 7.9582e-05 | 537.8945
121568790 | E | LC | ETL.6720.POLE.WDPS | 44950333 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.6720 | DESABLA-CENTERVILLE | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 42578839 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0026034 | 1406.4614 | 3.6615
121572469 | B | LC | ETL.7300.POLE.WOOD | 40668429 | TABLEMTN | NORTH VALLEY | 2021-06-21 | 2021-07-06 | ETL.7300 | KILARC-DESCHUTES | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40668429 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.00012121 | 4088.6799
121578023 | E | LC | ETL.1810.POLE.WDPS | 44322680 | EUREKA | HUMBOLDT | 2021-06-08 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44322677 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00012758 | 94.9585 | 0.012115
121579352 | E | LC | ETL.6060.INSL | 40847628 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6060 | ROUND MTN-TABLE MTN #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40820727 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.2846e-05 | 174.1355 | 0.0022369
121607575 | E | LC | ETL.4440.INSL | 40844347 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40816413 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 2.0438e-05 | 6363.4189 | 0.13006
121620588 | F | LC | ETL.7130.POLE.WDPS | 44837653 | EUREKA | HUMBOLDT | 2021-06-27 | 2021-08-02 | ETL.7130 | HUMBOLDT-MAPLE CREEK | Vegetation | Overgrown | [Remove] |  | Tier 2 | Within Both | DLFL | 40601317 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.46935 | 94.9585
121628012 | F | LC | ETL.5640.POLE.WDPS | 44741490 | TABLEMTN |  | 2021-06-18 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44741475 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.01129 | 2947.0984
121641651 | F | LC | ETL.4620.TOWR | 40863066 | PISMOBCH | LOS PADRES | 2021-06-26 | 2021-09-28 | ETL.4620 | DIABLO-MESA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40863066 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 2.2789e-06 | 537.9971
121641651 | F | LC | ETL.4620.TOWR | 40863066 | PISMOBCH | LOS PADRES | 2021-06-26 | 2021-09-28 | ETL.4620 | DIABLO-MESA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40863066 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-03 | Glass | Suspension |  |  |  |  | 2.2789e-06 | 537.9971
121643749 | F | LC | ETL.1730.POLE.WDPS | 44413352 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44413351 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00021179 | 31.6948
121660943 | E | LC | ETL.5934.TOWR | 40822264 | PISMOBCH | FRESNO | 2021-06-28 |  | ETL.5934 | TEMPLETON-GATES | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40822264 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.3435e-05
121660943 | E | LC | ETL.5934.TOWR | 40822264 | PISMOBCH | FRESNO | 2021-06-28 |  | ETL.5934 | TEMPLETON-GATES | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40822264 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 9.3435e-05
121663448 | A | LC | ETL.6760.POLE.WOOD | 40824375 | SACTO | SACRAMENTO | 2021-07-04 | 2021-07-07 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Emergency | Storm Related | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824375 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.009064 | 34.8659
121667423 | E | LC | ETL.6650.POLE.WDPS | 44386805 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44386804 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.021861 | 3249.6929 | 71.041
121675200 | F | LC | ETL.1730.POLE.WDPS | 44413437 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44413434 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.9788e-05 | 0.066432 | 3.3075e-06
121679390 | F | LC | ETL.4440.POLE.NWOD | 40580972 | TABLEMTN | NORTH VALLEY | 2021-06-27 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40580972 |  | Lattice Steel Pole | DV-DE - Double Vertical Dead End | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 3.2885e-13 | 1069.7238
121690943 | E | LC | ETL.6750.POLE.WDPS | 44561421 | TABLEMTN |  | 2021-07-06 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560770 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00025751 | 205.744 | 0.052982
121691868 | E | LC | ETL.6375.INSL.CERA | 43226078 | SACTO | SACRAMENTO | 2021-06-12 |  | ETL.6375 | DRUM PH #2 TAP | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 43196982 |  | Lattice Steel Pole | DE - Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00020427 | 2056.7583 | 0.42014
121707822 | E | LC | ETL.4040.POLE.WDPS | 44557777 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44554004 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.023479 | 2391.1541 | 56.1414
121717920 | F | LC | ETL.8350.POLE.WOOD | 44974712 | VICTOR | STOCKTON | 2021-07-03 | 2021-10-08 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44974712 | 2019-04-25 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2019-04-25 | Glass | Suspension |  |  |  |  | 0.00046143 | 537.8945
121727840 | E | LC | ETL.1162.TOWR | 45070081 | CONCORD | EAST BAY | 2021-07-01 | 2021-11-29 | ETL.1162 | BRIGHTON-OLEUM JCT | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL | [12 empty] | 0.1031
121738985 | F | LC | ETL.1820.POLE.WDPS | 44565494 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564302 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.083929 | 0.15372
121749042 | E | LC | ETL.1820.POLE.WOOD | 44562364 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562364 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Ceramic | Suspension |  |  |  |  | 0.2276 | 5637.5752 | 1283.1201
121771968 | B | LC | ETL.1440.POLE.STPS | 45110003 | SACTO | SIERRA | 2021-07-19 | 2021-09-16 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45109910 | 2019-12-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [8 empty] | 118.9194
121772110 | F | LC | ETL.2141.POLE.WDPS | 44264817 | MIDWAY | KERN | 2021-07-20 | 2021-09-03 | ETL.2141 | VEDDER TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44264816 |  | 3-Pole Wood | DDE - Double Dead End | [7 empty] | 6.4734e-05 | 5461.5088
121808164 | E | LC | ETL.2390.POLE.WDPS | 44391068 | VICTOR | STOCKTON | 2021-07-26 |  | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391067 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.3706e-05 | 3847.2571 | 0.091203
121815131 | B | LC | ETL.1110.TOWR | 40676706 | EUREKA | NORTH VALLEY | 2021-07-29 | 2021-08-03 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676706 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00030038 | 94.9939
121815131 | B | LC | ETL.1110.TOWR | 40676706 | EUREKA | NORTH VALLEY | 2021-07-29 | 2021-08-03 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676706 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.00030038 | 94.9939
121820052 | F | LC | ETL.4050.POLE.STPS | 45055856 | LAKEVLLE | SONOMA | 2021-07-29 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45055810 | 2020-10-24 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.6367e-08 | 2628.4556
121841063 | E | LC | ETL.8170.POLE.WDPS | 44771072 | EUREKA | HUMBOLDT | 2021-08-04 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40752192 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.016313 | 142.4582 | 2.3239
122065865 | E | LC | ETL.4780.INSL | 40791343 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761500 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.0023978 | 1630.5667 | 3.9098
118423618 | E | LC | ETL.1240.POLE.WDPS | 44386219 | TABLEMTN | NORTH VALLEY | 2020-01-11 | 2020-05-19 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118910288 | E | LC | ETL.5452.TOWR | 40662395 | CONCORD | DIABLO | 2020-04-10 | 2021-01-19 | ETL.5452 | CONTRA COSTA-MORAGA #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40662395 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-01-01 | Ceramic | Suspension |  |  |  |  | 1.0571e-06 | 4322.9263
118913849 | E | LC | ETL.4750.TOWR | 40756490 | LAKEVLLE | SONOMA | 2020-04-13 | 2020-05-07 | ETL.4750 | GEYSERS #12-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756490 | 1971-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 9.2298e-06 | 950.5959
118916982 | E | LC | ETL.2770.TOWR | 40644214 | CONCORD | DIABLO | 2020-04-14 | 2020-07-13 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40644214 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 1.5065e-07 | 0.066432
118954685 | F | LC | ETL.9341.POLE.WOOD | 40646693 | FRESNO | FRESNO | 2020-04-28 | 2021-02-09 | ETL.9341 | YANKE (NORTH FORK) TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
118966681 | E | LC | ETL.7590.POLE.WOOD | 41124293 | MOSSLNDG | CENTRAL COAST | 2020-05-01 | 2020-12-02 | ETL.7590 | MONTA VISTA-BURNS | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
118975653 | F | LC | ETL.2060.POLE.WOOD | 40586945 | LAKEVLLE | HUMBOLDT | 2020-05-01 | 2020-11-10 | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40586945 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.30441 | 284.7454
119002584 | E | LC | ETL.5660.INSL | 40605001 | CONCORD | EAST BAY | 2020-05-05 | 2021-04-04 | ETL.5660 | SAN RAMON-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119049746 | E | LC | ETL.1240.POLE.WDPS | 44386162 | TABLEMTN | NORTH VALLEY | 2020-05-13 | 2020-06-10 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44386161 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.9993e-05 | 2441.9417
119075842 | F | LC | ETL.6440.POLE.WOOD | 44191491 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2020-06-16 | ETL.6440 | COLEMAN-RED BLUFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191491 |  | Single Wood Pole | TP - Tri Pin | [7 empty] | 0.0037529 | 3740.6338
119082971 | E | LC | ETL.4590.TOWR | 40910169 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2021-04-19 | ETL.4590 | CRESTA-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40910169 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.5777e-06 | 111.7982
119099938 | E | LC | ETL.1110.TOWR | 40657032 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2021-06-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40657032 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Polymer | [5 empty] | 0.00010089 | 6600.2778
119100437 | E | LC | ETL.6490.POLE.WOOD | 40665613 | SACTO | SIERRA | 2020-06-02 | 2020-06-29 | ETL.6490 | COLGATE-GRASS VALLEY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40665613 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.015343 | 113.9589
119103953 | E | LC | ETL.1600.INSL.NCER | 40835394 | LAKEVLLE | SONOMA | 2020-05-27 | 2021-04-08 | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119106538 | E | LC | ETL.6520.POLE.WOOD | 40702105 | SACTO | SIERRA | 2020-06-03 | 2021-01-25 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119111345 | E | LC | ETL.3190.TOWR | 40910324 | TABLEMTN | NORTH VALLEY | 2020-06-04 |  | ETL.3190 | CARIBOU-PALERMO | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40910324 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 0.19393 | 1554.8076 | 301.5251
119118865 | F | LC | ETL.6770.POLE.WOOD | 40770260 | SACTO | SIERRA | 2020-05-29 | 2021-04-27 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40770260 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.02095 | 1344.8513
119120433 | E | LC | ETL.6280.POLE.WOOD | 40666801 | TABLEMTN | NORTH VALLEY | 2020-06-03 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40666801 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00039277 | 4683.9302 | 1.8397
119126199 | F | LC | ETL.8170.POLE.WOOD | 40660845 | EUREKA | HUMBOLDT | 2020-06-04 | 2021-08-23 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660845 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.01274 | 79.1724
119132079 | F | LC | ETL.8290.POLE.WOOD | 40877079 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-07-01 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40877079 |  | Single Wood Pole | T2N | 2021-04-19 | Polymer | Post |  |  |  |  | 0.00021405 | 5431.645
119161456 | E | LC | ETL.1450.POLE.WDPS | 44550017 | SACTO | SACRAMENTO | 2020-05-16 | 2020-08-31 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119180908 | E | LC | ETL.7300.POLE.WOOD | 40770411 | TABLEMTN |  | 2020-06-16 | 2021-03-05 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770411 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00021809 | 4088.6799
119183100 | E | LC | ETL.6310.POLE.WOOD | 40817340 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-09-01 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817340 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.4827e-05 | 5607.8438
119196213 | E | LC | ETL.6470.POLE.WOOD | 40874720 | SACTO | SIERRA | 2020-06-22 | 2021-08-09 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40874720 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.078782 | 110.8608
119196246 | B | LC | ETL.3540.INSL.CERA | 40780243 | PISMOBCH | LOS PADRES | 2020-06-16 | 2020-09-17 | ETL.3540 | SAN LUIS OBISPO-SANTA MARIA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751316 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1952-01-01 | Porcelain | Suspension |  |  |  |  | 4.9093e-06 | 1745.2675
119200815 | E | LC | ETL.4220.POLE.STPS | 44387625 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-08-03 | ETL.4220 | WOODLEAF-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44387622 | 2017-09-24 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 8.2104e-05 | 537.9951
119202541 | B | LC | ETL.4220.POLE.WOOD | 42568043 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-10-26 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue, Completed] | Tier2 |  |  | COMP
119209223 | E | LC | ETL.4950.TOWR | 40658046 | LAKEVLLE | SONOMA | 2020-06-25 | 2021-04-08 | ETL.4950 | FULTON-LAKEVILLE | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40658046 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.00028487 | 411.786
119213231 | E | LC | ETL.4392.INSL.CERA | 40620217 | LAKEVLLE |  | 2020-06-25 | 2021-03-15 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119231229 | F | LC | ETL.9330.TOWR | 40820990 | FRESNO | FRESNO | 2020-06-25 | 2021-04-07 | ETL.9330 | WISHON-COPPERMINE | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40820990 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Polymer | [5 empty] | 0.00031797
119238963 | F | LC | ETL.4430.POLE.NWOD | 40740410 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.4430 | BUCKS CREEK-ROCK CREEK-CRESTA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40740410 |  | Lattice Steel Pole | Unknown |  | Ceramic | Dead End - Suspension |  |  |  |  | 5.882e-05 | 6806.3008
119293432 | F | LC | ETL.8170.POLE.WOOD | 40602083 | EUREKA | HUMBOLDT | 2020-07-01 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40602083 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.19844 | 15.8815
119293620 | E | LC | ETL.5933.INSL.CERA | 44358894 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-06-21 | ETL.5933 | MORRO BAY-TEMPLETON | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40810829 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2016-08-27 | Ceramic | Dead End |  |  |  |  | 3.543e-08 | 2881.3301
119295339 | F | LC | ETL.8170.POLE.WDPS | 44565350 | EUREKA | HUMBOLDT | 2020-07-01 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44564309 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.04202 | 553.6737
119295861 | F | LC | ETL.1400.POLE.WDPS | 44776434 | VICTOR | STOCKTON | 2020-07-01 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40643191 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.0049883 | 3654.8457
119307986 | B | LC | ETL.7140.POLE.NWOD | 44396969 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44396969 | 2016-10-13 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2016-10-13 | Ceramic | Dead End |  |  |  |  | 0.0040829 | 553.9316
119308117 | B | LC | ETL.7140.POLE.WOOD | 40750698 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-26 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750698 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | [5 empty] | 0.072149 | 3832.687
119308946 | E | LC | ETL.1440.POLE.WOOD | 40590122 | SACTO | SIERRA | 2020-07-01 | 2020-09-17 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40590122 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0042156
119308946 | E | LC | ETL.1440.POLE.WOOD | 40590122 | SACTO | SIERRA | 2020-07-01 | 2020-09-17 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40590122 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0042156
119309780 | F | LC | ETL.4040.POLE.NWOD | 44874788 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2020-11-19 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44874788 | 2020-01-24 | Light Duty Steel Pole | DDE - Double Dead End | 2020-01-24 | Glass | Double Dead End |  |  |  |  | 2.6312e-05 | 0.066431
119326413 | F | LC | ETL.6300.POLE.WOOD | 42624172 | TABLEMTN | NORTH VALLEY | 2020-07-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
119329280 | E | LC | ETL.7300.POLE.WOOD | 40770435 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-03-11 | ETL.7300 | KILARC-DESCHUTES | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770435 |  | Single Wood Pole | DDE - Double Dead End | 2016-05-16 | Polymer | Post |  |  |  |  | 0.0077257 | 3833.8523
119336059 | E | LC | ETL.6470.POLE.WOOD | 40824266 | SACTO | SIERRA | 2020-07-08 | 2021-08-30 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40824266 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.059896 | 348.1462
119338445 | B | LC | ETL.1110.TOWR | 40756708 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2020-10-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756708 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 4.0394e-05 | 221.5655
119341368 | F | LC | ETL.1430.TOWR | 40866979 | SACTO | SACRAMENTO | 2020-07-09 | 2021-05-31 | ETL.1430 | DRUM-RIO OSO #2 | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40866979 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical | 2016-11-14 | Non Ceramic | Post |  |  |  |  | 0.00071044 | 775.2733
119356700 | F | LC | ETL.6380.POLE.WOOD | 40615101 | LAKEVLLE | SONOMA | 2020-07-10 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40615101 |  | Single Wood Pole | T-1 - Tri Post | 2018-10-31 | Polymer | Post |  |  |  |  | 3.7013e-06 | 7195.814
119357443 | F | LC | ETL.7270.POLE.WOOD | 40906082 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-02-10 | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40906082 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.0038017 | 724.7053
119357669 | F | LC | ETL.4040.POLE.STPS | 44647122 | TABLEMTN | NORTH VALLEY | 2020-07-07 |  | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44646902 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0003614 | 824.4197
119361249 | F | LC | ETL.1422.TOWR | 40751881 | SACTO | SACRAMENTO | 2020-07-13 | 2021-03-01 | ETL.1422 | BRUNSWICK #1 TAP | Structure-Tower | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751881 | 1975-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2021-03-16 | Glass | Dead End |  |  |  |  | 2.5117e-06 | 31.7148
119361249 | F | LC | ETL.1422.TOWR | 40751881 | SACTO | SACRAMENTO | 2020-07-13 | 2021-03-01 | ETL.1422 | BRUNSWICK #1 TAP | Structure-Tower | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751881 | 1975-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1975-01-01 | Ceramic | Dead End |  |  |  |  | 2.5117e-06 | 31.7148
119371580 | E | LC | ETL.1430.TOWR | 40597536 | SACTO | SACRAMENTO | 2020-07-14 | 2021-02-01 | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40597536 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical | 1989-01-01 | Ceramic | Post |  |  |  |  | 0.0063315 | 205.7345
119371673 | E | LC | ETL.6280.POLE.WOOD | 40826432 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-08-05 | ETL.6280 | CARIBOU #2 | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL | [11 empty] | 1.5033e-05 | 632.7172
119378804 | E | LC | ETL.8170.POLE.NWOD | 44891805 | EUREKA | HUMBOLDT | 2020-07-15 | 2021-01-15 | ETL.8170 | TRINITY-MAPLE CREEK | Splice-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44891805 | 2020-03-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-03-18 | Glass | Dead End |  |  |  |  | 0.00071252 | 110.8153
119379887 | E | LC | ETL.6220.POLE.WOOD | 40591106 | EUREKA | HUMBOLDT | 2020-07-15 | 2021-10-26 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40591106 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.055338 | 166.3953 | 9.208
119466682 | B | LC | ETL.6220.POLE.WOOD | 44210152 | EUREKA | HUMBOLDT | 2020-07-15 | 2020-09-10 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44210152 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.068305 | 1486.7976
119475343 | E | LC | ETL.3742.TOWR | 41135456 | CONCORD | DIABLO | 2020-07-20 |  | ETL.3742 | SOBRANTE-MORAGA | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41135456 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 6.341e-07 | 23.8277 | 1.5109e-05
119477817 | F | LC | ETL.2060.POLE.WOOD | 40875137 | LAKEVLLE | SONOMA | 2020-07-20 | 2021-02-23 | ETL.2060 | FORT BRAGG-ELK | Road | Grade Change | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40875137 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.43145 | 23.8261
119478822 | F | LC | ETL.7030.POLE.WOOD | 40770841 | TABLEMTN | NORTH VALLEY | 2020-07-20 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40770841 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.014534 | 6221.1479
119485480 | F | LC | ETL.8650.POLE.NWOD | 44420192 | FRESNO | YOSEMITE | 2020-07-21 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44420192 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0037238 | 79.1393
119487314 | E | LC | ETL.6290.INSL.NCER | 40720971 | TABLEMTN | NORTH VALLEY | 2020-07-22 | 2021-10-04 | ETL.6290 | CARIBOU-PLUMAS JCT | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40675189 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.3274 | 1043.9412
119488437 | E | LC | ETL.1440.POLE.WDPS | 44823750 | SACTO | SACRAMENTO | 2020-07-22 | 2021-02-18 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119494952 | E | LC | ETL.1350.POLE.WDPS | 44549848 | TABLEMTN |  | 2020-07-22 | 2021-06-24 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119509034 | E | LC | ETL.6760.POLE.WOOD | 40815108 | SACTO | SACRAMENTO | 2020-07-24 | 2021-04-07 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40815108 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.009556 | 31.7022
119552065 | E | LC | ETL.1430.TOWR | 40590432 | SACTO | SIERRA | 2020-08-03 |  | ETL.1430 | DRUM-RIO OSO #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40590432 | 1913-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-07-13 | Glass | Suspension |  |  |  |  | 0.011364 | 2056.7583 | 23.3736
119557780 | E | LC | ETL.3960.TOWR | 40643114 | PISMOBCH | LOS PADRES | 2020-08-04 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40643114 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2019-09-03 | Glass | Suspension |  |  |  |  | 3.8886e-06 | 953.6552 | 0.0037084
119595364 | E | LC | ETL.4309.INSL.CERA | 44189072 | LAKEVLLE |  | 2020-08-10 | 2021-03-12 | ETL.4309 | SANTA ROSA-CORONA | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | DLFL | 41104283 | 1978-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1978-01-01 | Porcelain | Post |  |  |  |  | 0.026144 | 206.0578
119600157 | E | LC | ETL.6710.POLE.WOOD | 40666316 | MOSSLNDG | CENTRAL COAST | 2020-08-11 |  | ETL.6710 | DEL MONTE-VIEJO | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40666316 |  | Single Wood Pole | 3HP - 3 Horizontal Post |  | Ceramic | [5 empty] | 0.1149 | 0.065148 | 0.0074853
119603962 | E | LC | ETL.6222.POLE.WOOD | 40861033 | EUREKA | HUMBOLDT | 2020-08-10 |  | ETL.6222 | FORT SEWARD TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40861033 | 1952-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0083883
119632481 | B | LC | ETL.1110.INSL.CERA | 44744830 | TABLEMTN | HUMBOLDT | 2020-08-17 | 2020-10-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119649110 | F | LC | ETL.8365.POLE.WOOD | 40912512 | EUREKA | HUMBOLDT | 2020-08-21 | 2021-02-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40912512 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Porcelain | [5 empty] | 0.14436
119663043 | F | LC | ETL.1110.POLE.STPS | 44860152 | TABLEMTN | NORTH VALLEY | 2020-08-20 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44860082 | 2019-12-19 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.7332e-06 | 2894.5761
119670500 | B | LC | ETL.8650.POLE.WDPS | 44245517 | FRESNO | FRESNO | 2020-08-25 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] |  | Tier 2 | Within Both | COMP | 44245516 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.054091 | 5503.6265
119706275 | F | LC | ETL.4510.TOWR | 40752336 | CONCORD | EAST BAY | 2020-08-29 | 2021-09-13 | ETL.4510 | CONTRA COSTA-LAS POSITAS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40752336 | 1939-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2009-01-01 | Ceramic | Suspension |  |  |  |  | 9.9798e-06 | 5383.7945
119706275 | F | LC | ETL.4510.TOWR | 40752336 | CONCORD | EAST BAY | 2020-08-29 | 2021-09-13 | ETL.4510 | CONTRA COSTA-LAS POSITAS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40752336 | 1939-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-09-06 | Glass | Suspension |  |  |  |  | 9.9798e-06 | 5383.7945
119717208 | E | LC | ETL.7490.POLE.WOOD | 40602062 | EUREKA | HUMBOLDT | 2020-09-02 | 2021-09-14 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.74544 | 222.8978
119721446 | E | LC | ETL.8650.TOWR | 40859249 | FRESNO | YOSEMITE | 2020-07-28 | 2021-08-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40859249 | 1929-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0034863 | 1249.5254
119754067 | E | LC | ETL.8170.INSL.CERA | 40619833 | EUREKA | HUMBOLDT | 2020-07-16 | 2021-07-07 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40579721 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0035084
119754067 | E | LC | ETL.8170.INSL.CERA | 40619833 | EUREKA | HUMBOLDT | 2020-07-16 | 2021-07-07 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40579721 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0035084
119754067 | E | LC | ETL.8170.INSL.CERA | 40619833 | EUREKA | HUMBOLDT | 2020-07-16 | 2021-07-07 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40579721 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0035084
119754076 | E | LC | ETL.7300.POLE.WOOD | 40877880 | TABLEMTN |  | 2020-08-13 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | PEND
119763095 | F | LC | ETL.6760.POLE.WOOD | 40671693 | SACTO | SIERRA | 2020-09-08 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40671693 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.012306 | 15.8837
119768240 | F | LC | ETL.6760.POLE.WOOD | 40654903 | SACTO | SIERRA | 2020-09-08 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40654903 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.015611 | 63.3392
119812783 | F | LC | ETL.6280.POLE.NWOD | 44259154 | TABLEMTN | NORTH VALLEY | 2020-09-25 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44259154 | 2018-11-07 | Light Duty Steel Pole | DDE - Double Dead End | 2018-11-07 | Ceramic | Post | [5 empty] | 1581.6954
119840061 | F | LC | ETL.6480.POLE.WOOD | 40597557 | SACTO | NORTH VALLEY | 2020-09-08 | 2021-05-23 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
119964589 | E | LC | ETL.8060.POLE.WOOD | 40771511 | SACTO | SIERRA | 2020-10-28 | 2021-08-18 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 427.2245
119978784 | F | LC | ETL.8960.POLE.WDPS | 44236939 | FRESNO | FRESNO | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44236936 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 6.8261e-05
119983840 | F | LC | ETL.8365.POLE.WOOD | 40912673 | EUREKA | HUMBOLDT | 2020-10-30 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40912673 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.057781
119988056 | E | LC | ETL.8960.POLE.WOOD | 40596617 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40596617 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 1925-01-01 | Polymer | Suspension |  |  |  |  | 9.6826e-05
120089391 | B | LC | ETL.3180.INSL | 40705064 | CONCORD | EAST BAY | 2020-11-18 | 2021-02-09 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40646332 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.0723e-06 | 16.3369
120114281 | E | LC | ETL.6220.POLE.WOOD | 40862534 | EUREKA | HUMBOLDT | 2020-12-01 | 2021-02-04 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40862534 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.25534
120135356 | E | LC | ETL.5431.TOWR | 44188817 | TABLEMTN | NORTH VALLEY | 2020-12-04 |  | ETL.5431 | BLACK TAP | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44188817 | 1964-01-01 | LATTICE STEEL TOWER | Unknown | [7 empty] | 4.5371e-07 | 253.2463 | 0.0001149
120142748 | E | LC | ETL.7490.POLE.WDPS | 44769632 | EUREKA | HUMBOLDT | 2020-12-08 | 2021-09-08 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120204605 | E | LC | ETL.1110.POLE.STPS | 44425577 | TABLEMTN | NORTH VALLEY | 2020-12-15 | 2021-04-16 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
120252719 | F | LC | ETL.7300.POLE.NWOD | 44872433 | TABLEMTN | NORTH VALLEY | 2020-12-14 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44872433 | 2019-05-08 | Light Duty Steel Pole | T2N | 2019-05-08 | Polymer | Post |  |  |  |  | 8.0469e-08 | 2024.9202
120632750 | E | LC | ETL.5960.TOWR | 40812106 | PISMOBCH | LOS PADRES | 2021-03-09 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40812106 | 1973-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 5.3332e-07 | 618.0835 | 0.00032964
120690640 | E | LC | ETL.4040.INSL.NCER | 42622747 | TABLEMTN |  | 2021-03-25 | 2021-10-14 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42622316 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Non Ceramic | Suspension |  |  |  |  | 0.068279 | 443.6022 | 30.2885
120711622 | F | LC | ETL.4440.TOWR | 41162679 | TABLEMTN | NORTH VALLEY | 2021-03-29 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41162679 | 1965-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post |  | Ceramic | [5 empty] | 6.0083e-05 | 1982.3486
120712054 | E | LC | ETL.4440.INSL.CERA | 40885382 | TABLEMTN | NORTH VALLEY | 2021-03-23 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40861999 | 1958-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 7.3115e-07 | 0.33085 | 2.419e-07
120717616 | F | LC | ETL.5540.TOWR | 40871487 | TABLEMTN | NORTH VALLEY | 2021-03-29 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40871487 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-11-20 | Glass | Suspension |  |  |  |  | 2.8874e-06 | 5573.8408 | 0.016094
120725433 | E | LC | ETL.1530.TOWR | 40861980 | SACTO | SACRAMENTO | 2021-04-01 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40861980 | 1923-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 2.1467e-05 | 727.8181 | 0.015624
120736813 | E | LC | ETL.3960.INSL.CERA | 40792782 | PISMOBCH | LOS PADRES | 2021-03-22 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40762119 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Dead End |  |  |  |  | 9.3173e-05 | 953.6552 | 0.088855
120741208 | F | LC | ETL.8350.POLE.WOOD | 40876051 | VICTOR | STOCKTON | 2021-04-03 | 2021-07-26 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40876051 | 1994-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 1.3714e-05 | 110.82
120743098 | E | LC | ETL.8250.POLE.WOOD | 40904143 | VICTOR | STOCKTON | 2021-04-05 | 2021-08-09 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40904143 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 9.9725e-05 | 1080.3165
120747455 | E | LC | ETL.3820.TOWR | 40744463 | VICTOR | STOCKTON | 2021-04-05 | 2021-04-15 | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40744463 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 5.0878e-06 | 3195.5342
120749265 | E | LC | ETL.3810.POLE.WOOD | 40750873 | LAKEVLLE | SONOMA | 2021-04-06 | 2021-08-04 | ETL.3810 | SONOMA-PUEBLO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750873 |  | Single Wood Pole | T2N | 2020-05-30 | Polymer | Post |  |  |  |  | 0.002953 | 2251.2722
120750207 | E | LC | ETL.1350.POLE.NWOD | 44993094 | TABLEMTN | NORTH VALLEY | 2021-04-06 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993094 | 2020-06-11 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-11 | Glass | Dead End |  |  |  |  | 6.2682e-05 | 79.1724
120760006 | E | LC | ETL.8350.POLE.NWOD | 44918816 | VICTOR | STOCKTON | 2021-04-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44918816 | 2020-03-03 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-03 | Polymer | Post |  |  |  |  | 1.1853e-06 | 1665.2784 | 0.0019739
120787249 | F | LC | ETL.2540.TOWR | 40585522 | MOSSLNDG | CENTRAL COAST | 2021-04-10 | 2021-04-26 | ETL.2540 | METCALF-GREEN VALLEY | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | DLFL | 40585522 | 1928-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1986-01-01 | Porcelain | Suspension |  |  |  |  | 3.4775e-05 | 2578.8315
120793024 | B | LC | ETL.3840.INSL | 40680633 | VICTOR | STOCKTON | 2021-04-09 | 2021-05-24 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40651746 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.7119e-06 | 5333.8435
120794801 | F | LC | ETL.3830.TOWR | 40861800 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40861800 | 1989-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 3.7342e-05 | 5823.2505 | 0.21745
120804619 | F | LC | ETL.3830.TOWR | 40803328 | VICTOR | STOCKTON | 2021-04-12 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40803328 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.1958e-05 | 2156.2512
120829000 | F | LC | ETL.5300.TOWR | 40810946 | PISMOBCH | LOS PADRES | 2021-04-08 | 2021-07-19 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40810946 | 1960-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 4.7297e-07 | 3863.8943
120833079 | B | LC | ETL.1530.INSL.CERA | 44647986 | SACTO | SACRAMENTO | 2021-04-16 | 2021-07-19 | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870993 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-05-07 | Ceramic | Suspension |  |  |  |  | 1.5194e-05 | 316.5366
120843619 | F | LC | ETL.8365.POLE.NWOD | 40906660 | EUREKA | HUMBOLDT | 2021-04-19 | 2021-06-04 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40906660 | 2011-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.00083882
120851080 | E | LC | ETL.7020.POLE.WOOD | 40601702 | TABLEMTN | NORTH VALLEY | 2021-04-20 | 2021-07-01 | ETL.7020 | HAT CREEK #1-PIT #1 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601702 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.25984 | 2613.3103
120854570 | E | LC | ETL.3500.TOWR | 40579956 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40579956 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.00025118 | 6665.3057 | 1.6742
120860347 | E | LC | ETL.3820.TOWR | 40642815 | VICTOR | STOCKTON | 2021-04-21 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40642815 | 1910-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post | 1989-01-01 | Polymer | Post |  |  |  |  | 1.2114e-06 | 5967.0518 | 0.0072287
120860347 | E | LC | ETL.3820.TOWR | 40642815 | VICTOR | STOCKTON | 2021-04-21 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40642815 | 1910-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post | 1989-01-01 | Polymer | Suspension |  |  |  |  | 1.2114e-06 | 5967.0518 | 0.0072287
120879346 | E | LC | ETL.1810.POLE.WDPS | 44322501 | EUREKA | HUMBOLDT | 2021-04-22 | 2021-05-10 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 44322500 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.013663
120879453 | E | LC | ETL.4040.POLE.STPS | 44647075 | TABLEMTN | NORTH VALLEY | 2021-04-24 |  | ETL.4040 | TRINITY-COTTONWOOD | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44646838 | 2018-08-17 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00066038 | 206.9966 | 0.1367
120883354 | E | LC | ETL.2780.INSL | 40604491 | CONCORD | DIABLO | 2021-04-26 | 2021-09-01 | ETL.2780 | MORAGA-SAN LEANDRO #2 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40580808 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 3.1885e-08 | 332.4702
120883974 | E | LC | ETL.7270.POLE.NWOD | 44649382 | TABLEMTN | NORTH VALLEY | 2021-04-26 |  | ETL.7270 | KESWICK-TRINITY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44649382 | 2018-08-17 | Light Duty Steel Pole | T2N | 2018-08-17 | Polymer | Post |  |  |  |  | 0.0014903 | 1861.3817 | 2.7739
120887196 | F | LC | ETL.5410.TOWR | 40661613 | TABLEMTN | NORTH VALLEY | 2021-04-26 | 2021-06-14 | ETL.5410 | CARBERRY SW STA-ROUND MTN | Structure-Steel | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40661613 | 1942-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Ceramic | Dead End |  |  |  |  | 3.6264e-07 | 1982.3832
120894084 | E | LC | ETL.3820.TOWR | 40587578 | VICTOR | STOCKTON | 2021-04-28 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587578 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 8.5967e-07 | 1962.8882 | 0.0016874
120894153 | F | LC | ETL.3830.TOWR | 40642825 | VICTOR | STOCKTON | 2021-04-28 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40642825 | 1963-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 5.0262e-07 | 1962.8882 | 0.00098658
120907413 | E | LC | ETL.5660.INSL.NCER | 45060897 | CONCORD | MISSION | 2021-04-29 |  | ETL.5660 | SAN RAMON-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40762046 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-03-22 | Glass Silicone Coated | Suspension |  |  |  |  | 0.0022858 | 2709.8901 | 6.1942
120907413 | E | LC | ETL.5660.INSL.NCER | 45060897 | CONCORD | MISSION | 2021-04-29 |  | ETL.5660 | SAN RAMON-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40762046 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0022858 | 2709.8901 | 6.1942
120909048 | E | LC | ETL.1820.POLE.NWOD | 44976957 | EUREKA | HUMBOLDT | 2021-04-30 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44976957 | 2020-03-10 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-03-10 | Glass | Suspension |  |  |  |  | 0.017204 | 648.7573 | 11.1613
120911647 | E | LC | ETL.5930.TOWR | 40605466 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40605466 | 1946-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.1846e-08 | 1380.069 | 3.0148e-05
120920323 | F | LC | ETL.6890.POLE.WOOD | 40584864 | LAKEVLLE | SONOMA | 2021-05-03 | 2021-08-10 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40584864 | 1967-01-01 | Single Wood Pole | TPSR - Tri Post & Susp Light |  | Ceramic | Suspension - Post |  |  |  |  | 0.0019398 | 2801.8037
120921107 | B | LC | ETL.6110.INSL.NCER | 45000090 | METCALF | MISSION | 2021-05-03 | 2021-06-04 | ETL.6110 | TESLA-METCALF | Splice-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40764874 | 1978-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-10-14 | Glass Silicone Coated | Suspension |  |  |  |  | 4.6766e-08 | 4690.2227
120924223 | F | LC | ETL.6890.POLE.NWOD | 44963422 | LAKEVLLE | SONOMA | 2021-05-03 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44963422 | 2019-11-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-11-11 | Glass | Dead End |  |  |  |  | 1.2305e-06 | 3896.4603
121191927 | E | LC | ETL.4870.INSL | 40578758 | FRESNO | FRESNO | 2021-04-20 |  | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40576770 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.5868e-07 | 731.474 | 0.00011607
121192006 | E | LC | ETL.9100.POLE.WOOD | 44191890 | PISMOBCH | LOS PADRES | 2021-04-19 | 2021-06-11 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Hardware-Wood | Missing | [Install] | Tier3 |  |  | DLFL | [11 empty] | 0.00020437 | 2704.2016
121338243 | E | LC | ETL.3500.TOWR | 40872938 | VICTOR | STOCKTON | 2021-04-26 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40872938 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 0.00068769 | 284.8886 | 0.19592
121338244 | E | LC | ETL.5310.INSL | 40680126 | PISMOBCH | LOS PADRES | 2021-04-26 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40651387 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 2.536e-05 | 4323.1064 | 0.10963
121358296 | E | LC | ETL.4870.INSL | 40578726 | FRESNO | FRESNO | 2021-04-21 |  | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40576740 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 2.0332e-05 | 2957.7136 | 0.060135
121364866 | F | LC | ETL.6880.POLE.WOOD | 40905745 | LAKEVLLE | HUMBOLDT | 2021-05-01 | 2021-06-23 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40905745 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00071534 | 2486.5969
121370742 | F | LC | ETL.1250.POLE.WOOD | 41109530 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41109530 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 9.4525e-06 | 5287.748
121373442 | E | LC | ETL.5070.TOWR | 40591725 | FRESNO | YOSEMITE | 2021-05-04 |  | ETL.5070 | QUINTO SW STA-WESTLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40591725 | 1947-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1947-01-01 | Ceramic | Suspension |  |  |  |  | 1.6523e-06 | 765.584 | 0.001265
121378077 | F | LC | ETL.1820.POLE.WDPS | 44565330 | EUREKA | HUMBOLDT | 2021-05-21 | 2021-07-20 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44564305 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.2634 | 5399.9375
121380363 | B | LC | ETL.4440.TOWR | 40815421 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-29 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40815421 | 1968-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1968-01-01 | Porcelain | Dead End |  |  |  |  | 0.0016539 | 1804.4395
121383567 | F | LC | ETL.6500.POLE.WOOD | 40590392 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40590392 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0020353 | 935.866
121384175 | F | LC | ETL.6760.POLE.NWOD | 40873709 | SACTO | SIERRA | 2021-05-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40873709 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.021872 | 110.8327 | 2.4242
121384412 | F | LC | ETL.6760.POLE.NWOD | 45096588 | SACTO | SIERRA | 2021-05-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45096588 | 2021-03-08 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-08 | Polymer | Post |  |  |  |  | 0.028515 | 94.9894
121388319 | F | LC | ETL.6220.POLE.WOOD | 40614599 | EUREKA | HUMBOLDT | 2021-05-24 | 2021-08-17 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40614599 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.2171 | 585.9515
121393944 | E | LC | ETL.8060.POLE.WOOD | 40602263 | SACTO | SIERRA | 2021-05-18 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40602263 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.49458 | 110.8102 | 54.8049
121395151 | E | LC | ETL.3750.TOWR | 40870754 | CONCORD | DIABLO | 2021-05-15 | 2021-07-12 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40870754 | 1922-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.1843e-08 | 0.066432
121404827 | F | LC | ETL.6110.TOWR | 40646892 | METCALF | MISSION | 2021-05-21 |  | ETL.6110 | TESLA-METCALF | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40646892 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-10-14 | Glass Silicone Coated | Suspension |  |  |  |  | 7.7129e-06 | 4389.5649 | 0.033856
121419925 | E | LC | ETL.7390.POLE.NWOD | 40750431 | LAKEVLLE | HUMBOLDT | 2021-05-27 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40750431 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.16286 | 474.6711 | 77.3037
121425003 | E | LC | ETL.8290.POLE.WOOD | 40826988 | TABLEMTN | NORTH VALLEY | 2021-05-27 | 2021-06-11 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40826988 |  | Single Wood Pole | T-1 - Tri Post | 2016-05-18 | Polymer | Post |  |  |  |  | 0.0073257 | 762.9542
121453396 | E | LC | ETL.1400.POLE.WDPS | 44781291 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40643200 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0027337 | 31.7334 | 0.08675
121453745 | E | LC | ETL.6220.POLE.WOOD | 40752659 | EUREKA | HUMBOLDT | 2021-06-01 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40752659 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.52335 | 1028.302 | 538.1608
121454358 | A | LC | ETL.1710.INSL | 40623813 | MOSSLNDG | CENTRAL COAST | 2021-06-03 | 2021-06-11 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Emergency-Steel | Other | [Replace, Completed, Completed] | Tier3 |  |  | COMP
121467650 | B | LC | ETL.6020.TOWR | 40863454 | TABLEMTN | NORTH VALLEY | 2021-06-03 | 2021-06-11 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863454 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.7109e-09 | 1281.1857
121474658 | E | LC | ETL.6750.POLE.WDPS | 44562147 | TABLEMTN | NORTH VALLEY | 2021-06-05 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44561577 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00033586 | 411.4229 | 0.13818
121491807 | E | LC | ETL.5140.POLE.WDPS | 44552400 | SACTO | SACRAMENTO | 2021-05-28 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44551554 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.019937 | 4160.9766 | 82.9591
121500491 | F | LC | ETL.7390.POLE.WDPS | 44412010 | LAKEVLLE |  | 2021-06-04 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44412009 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.053448 | 2652.9001
121511225 | F | LC | ETL.1350.POLE.WDPS | 44513790 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44512309 |  | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.042743 | 205.7693
121516144 | F | LC | ETL.9330.TOWR | 40763364 | FRESNO | FRESNO | 2021-06-03 |  | ETL.9330 | WISHON-COPPERMINE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40763364 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Polymer | [5 empty] | 0.0020638 | 6932.5156
121516766 | F | LC | ETL.7180.POLE.STPS | 44376989 | LAKEVLLE | NORTH BAY | 2021-06-04 | 2021-07-26 | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44376987 | 2016-10-12 | 2-Pole Non Wood | Unknown | [7 empty] | 1.4979e-08 | 1820.5125
121518249 | E | LC | ETL.6760.INSL.NCER | 40615674 | SACTO | SACRAMENTO | 2021-05-29 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40590234 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0018994 | 618.184 | 1.1742
121523308 | B | LC | ETL.6500.POLE.NWOD | 45095022 | SACTO | SIERRA | 2021-06-10 | 2021-08-12 | ETL.6500 | COLGATE-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45095022 | 2021-04-27 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2021-04-27 | Glass | Dead End |  |  |  |  | 3.4819e-05 | 428.1771
121523418 | F | LC | ETL.1350.POLE.STPS | 44409304 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44409303 | 2017-10-27 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0001304 | 221.5655
121525430 | E | LC | ETL.4040.INSL.NCER | 44942645 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44942633 | 2020-07-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-07-09 | Glass | Suspension |  |  |  |  | 0.0011968
121525430 | E | LC | ETL.4040.INSL.NCER | 44942645 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44942633 | 2020-07-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-07-09 | Glass | Suspension |  |  |  |  | 0.0011968
121525704 | B | LC | ETL.6020.INSL | 40891271 | TABLEMTN | NORTH VALLEY | 2021-06-11 | 2021-07-20 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40868281 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 7.6212e-09 | 3100.9255
121527093 | E | LC | ETL.3745.INSL.CERA | 40887548 | LAKEVLLE | SONOMA | 2021-06-08 |  | ETL.3745 | LAKEVILLE-IGNACIO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40863612 | 1956-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 1.1146e-06 | 94.985 | 0.00010587
121544874 | F | LC | ETL.5420.POLE.WDPS | 44559036 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44558516 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0065752 | 177.2654
121550163 | F | LC | ETL.1820.POLE.STPS | 44395537 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395535 | 2020-03-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.026789 | 712.0305
121557794 | F | LC | ETL.5390.TOWR | 40817594 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40817594 | 1956-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.7106e-07 | 206.0313 | 5.5847e-05
121577828 | E | LC | ETL.6070.TOWR | 40601350 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6070 | ROUND MTN-TABLE MTN #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40601350 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-05-27 | Ceramic | Suspension |  |  |  |  | 7.3527e-06 | 300.9864 | 0.0022131
121592192 | F | LC | ETL.1350.POLE.STPS | 44990451 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44990397 | 2020-10-07 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0082213 | 490.5302
121593905 | E | LC | ETL.6650.POLE.WDPS | 44386812 | TABLEMTN | NORTH VALLEY | 2021-06-24 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44386810 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0036702 | 2155.7687 | 7.912
121608433 | F | LC | ETL.1420.TOWR | 40753597 | SACTO | SIERRA | 2021-06-14 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40753597 | 1913-01-01 | LATTICE STEEL TOWER | FDDE - Flat Dead End Construction | 2016-08-08 | Porcelain | Dead End |  |  |  |  | 8.5272e-06 | 1993.4753 | 0.016999
121631671 | E | LC | ETL.6890.POLE.WOOD | 40587795 | LAKEVLLE | SONOMA | 2021-06-28 |  | ETL.6890 | FULTON-HOPLAND | Crossarm-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587795 | 1976-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Other |  |  |  |  | 0.013696 | 1761.2977 | 24.1231
121649545 | E | LC | ETL.6470.POLE.WOOD | 40874813 | SACTO | SIERRA | 2021-06-18 |  | ETL.6470 | COLGATE-ALLEGHANY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40874813 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 0.21774 | 110.8481 | 24.1357
121655532 | E | LC | ETL.1650.POLE.WOOD | 40576031 | LAKEVLLE | SONOMA | 2021-06-26 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40576031 | 1983-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1966-01-01 | Polymer | Dead End |  |  |  |  | 0.00031417 | 4022.6609 | 1.2638
121658943 | E | LC | ETL.3530.POLE.WDPS | 44269064 | PISMOBCH | LOS PADRES | 2021-07-01 |  | ETL.3530 | SAN LUIS OBISPO-OCEANO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44269063 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00035636 | 2690.7754 | 0.95888
121659175 | E | LC | ETL.7590.POLE.NWOD | 45040640 | MOSSLNDG | CENTRAL COAST | 2021-07-01 |  | ETL.7590 | MONTA VISTA-BURNS | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45040640 | 2020-09-17 | Light Duty Steel Pole | T2N | 2020-09-17 | Polymer | Post |  |  |  |  | 0.15223 | 15.8866 | 2.4183
121668347 | B | LC | ETL.7490.INSL.CERA | 40611551 | EUREKA | HUMBOLDT | 2021-07-06 | 2021-08-02 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
121705121 | F | LC | ETL.4430.TOWR | 40660287 | TABLEMTN | NORTH VALLEY | 2021-07-09 | 2021-10-11 | ETL.4430 | BUCKS CREEK-ROCK CREEK-CRESTA | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40660287 |  | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2019-08-26 | Glass | Suspension |  |  |  |  | 0.0017996 | 6806.3008
121725010 | E | LC | ETL.7055.POLE.WOOD | 40599556 | CONCORD | DIABLO | 2021-07-07 |  | ETL.7055 | BRIONES TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40599556 | 1982-01-01 | Single Wood Pole | T-1 - Tri Post | 1991-01-01 | Non Ceramic | Post |  |  |  |  | 0.0018152 | 6634.8398 | 12.0438
121725964 | B | LC | ETL.1820.POLE.WDPS | 44562693 | EUREKA | HUMBOLDT | 2021-07-14 | 2021-08-04 | ETL.1820 | HUMBOLDT-TRINITY | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562443 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.05269 | 221.983
121725996 | F | LC | ETL.1730.POLE.NWOD | 44601330 | MOSSLNDG | CENTRAL COAST | 2021-07-10 | 2021-07-26 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44601330 | 2017-09-25 | Light Duty Steel Pole | SVDE - Single Vertical Dead End | 2017-09-25 | Polymer | Dead End - Suspension | [5 empty] | 15.88
121730038 | E | LC | ETL.1820.POLE.WDPS | 44562793 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562388 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.097027 | 237.3869 | 23.033
121741357 | E | LC | ETL.6650.POLE.WDPS | 44386814 | TABLEMTN | NORTH VALLEY | 2021-07-13 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44386813 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.25279 | 311.9365 | 78.8544
121745699 | F | LC | ETL.1820.POLE.WDPS | 44562951 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-09-14 | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [12 empty] | 79.1724
121750813 | F | LC | ETL.2390.POLE.WDPS | 44391280 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44391279 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.1585e-05 | 5541.6973
121785940 | E | LC | ETL.4316.POLE.NWOD | 40816598 | TABLEMTN | NORTH VALLEY | 2021-07-21 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40816598 |  | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 1949-01-01 | Polymer | Unknown |  |  |  |  | 0.019312 | 230.1254 | 4.4442
121793362 | F | LC | ETL.2141.POLE.WDPS | 44264833 | MIDWAY | KERN | 2021-07-20 | 2021-09-29 | ETL.2141 | VEDDER TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44264832 |  | 3-Pole Wood | DDE - Double Dead End | [7 empty] | 6.4787e-05 | 5461.5088
121807462 | E | LC | ETL.8365.POLE.NWOD | 40769308 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40769308 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0052925 | 933.3572 | 4.9397
121808209 | E | LC | ETL.8365.POLE.WOOD | 40768635 | EUREKA | HUMBOLDT | 2021-07-27 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40768635 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.015223 | 1966.5326 | 29.9358
121825127 | F | LC | ETL.9250.POLE.WOOD | 40749631 | MIDWAY | KERN | 2021-07-28 |  | ETL.9250 | TEJON-LEBEC | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40749631 |  | Single Wood Pole | SV-PJ - Single Vertical Post Jumper |  | Ceramic | [5 empty] | 0.009846 | 6593.6138 | 64.9208
121855717 | E | LC | ETL.5420.POLE.WDPS | 44558980 | TABLEMTN | NORTH VALLEY | 2021-07-20 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44558527 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0051346 | 649.1145 | 3.3329
121860077 | B | LC | ETL.6300.POLE.WOOD | 40824727 | TABLEMTN | NORTH VALLEY | 2021-08-07 | 2021-09-28 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.8859e-06 | 15.8815
121890529 | F | LC | ETL.5140.POLE.STPS | 44411073 | SACTO | SIERRA | 2021-07-05 | 2021-10-11 | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44411071 | 2018-12-01 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.4968e-08 | 6079.75
122054003 | E | LC | ETL.4780.INSL.NCER | 45129002 | LAKEVLLE | SONOMA | 2021-09-15 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129314 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.016882 | 2537.3948 | 42.836
122054003 | E | LC | ETL.4780.INSL.NCER | 45129002 | LAKEVLLE | SONOMA | 2021-09-15 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129314 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.016882 | 2537.3948 | 42.836
122271484 | F | LC | ETL.2390.POLE.NWOD | 45169963 | VICTOR | YOSEMITE | 2021-10-28 |  | ETL.2390 | MELONES-CURTIS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45169963 | 2021-10-14 | Light Duty Steel Pole | DDE - Double Dead End | 2021-10-14 | Glass | Dead End
122429637 | F | LC | ETL.2395.POLE.WOOD | 45114378 | TABLEMTN | NORTH VALLEY | 2021-11-29 |  | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45114378 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension | [5 empty] | 300.6002
118522125 | E | LC | ETL.7660.INSL.NCER | 40830360 | CONCORD | EAST BAY | 2020-02-05 | 2021-04-07 | ETL.7660 | NEWARK-LIVERMORE | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40804518 | 1917-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1919-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.4878e-06 | 3295.094
118522125 | E | LC | ETL.7660.INSL.NCER | 40830360 | CONCORD | EAST BAY | 2020-02-05 | 2021-04-07 | ETL.7660 | NEWARK-LIVERMORE | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40804518 | 1917-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1919-01-01 | Ceramic | Suspension |  |  |  |  | 1.4878e-06 | 3295.094
118575868 | E | LC | ETL.5930.INSL.NCER | 44768968 | CONCORD |  | 2020-02-25 | 2021-06-21 | ETL.5930 | PARKWAY-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862755 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-26 | Glass Silicone Coated | Suspension |  |  |  |  | 1.3065e-08 | 556.4825
118575868 | E | LC | ETL.5930.INSL.NCER | 44768968 | CONCORD |  | 2020-02-25 | 2021-06-21 | ETL.5930 | PARKWAY-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862755 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.3065e-08 | 556.4825
118603857 | F | LC | ETL.2063.POLE.NWOD | 44191894 | LAKEVLLE | SONOMA | 2020-03-04 | 2020-04-09 | ETL.2063 | LAKEVILLE-SONOMA #1 | Marker (i.e. signs)-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191894 |  | Tubular Steel Pole | DCPOST - Double Circuit Post |  | Non Ceramic | Other | [5 empty] | 2314.5901
118603857 | F | LC | ETL.2063.POLE.NWOD | 44191894 | LAKEVLLE | SONOMA | 2020-03-04 | 2020-04-09 | ETL.2063 | LAKEVILLE-SONOMA #1 | Marker (i.e. signs)-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191894 |  | Tubular Steel Pole | DCPOST - Double Circuit Post |  | Polymer | Other | [5 empty] | 2314.5901
118729892 | E | LC | ETL.7930.POLE.WOOD | 40809891 | MOSSLNDG | CENTRAL COAST | 2020-03-20 | 2021-02-03 | ETL.7930 | SALINAS-LAURELES | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40809891 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Other |  |  |  |  | 0.024366 | 15.8926
118756958 | E | LC | ETL.1481.POLE.WOOD | 40648937 | LAKEVLLE | SONOMA | 2020-03-30 | 2020-03-31 | ETL.1481 | LOWER LAKE-HOMESTAKE | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648937 | 1985-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1985-01-01 | Porcelain | Post |  |  |  |  | 3.9159e-05 | 4212.6665
118915971 | E | LC | ETL.1330.TOWR | 40750599 | LAKEVLLE | HUMBOLDT | 2020-04-13 | 2021-09-07 | ETL.1330 | CORTINA-MENDOCINO #1 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40750599 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 8.1358e-05 | 1443.0288
118943087 | E | LC | ETL.5440.POLE.WDPS | 44558427 | TABLEMTN | NORTH VALLEY | 2020-04-22 | 2020-06-09 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118945133 | E | LC | ETL.8220.POLE.WOOD | 40600013 | VICTOR | STOCKTON | 2020-04-22 | 2020-06-04 | ETL.8220 | VALLEY SPRINGS-CALAVERAS CEMENT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600013 | 1992-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Other |  |  |  |  | 5.8463e-05 | 1079.3326
118947262 | E | LC | ETL.5660.TOWR | 40644606 | CONCORD | MISSION | 2020-04-23 | 2021-02-01 | ETL.5660 | SAN RAMON-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40644606 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 6.5086e-06 | 3154.5959
118947262 | E | LC | ETL.5660.TOWR | 40644606 | CONCORD | MISSION | 2020-04-23 | 2021-02-01 | ETL.5660 | SAN RAMON-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40644606 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.5086e-06 | 3154.5959
118962990 | B | LC | ETL.1660.POLE.NWOD | 44330940 | LAKEVLLE | SONOMA | 2020-04-24 | 2020-05-18 | ETL.1660 | GEYSERS #3-EAGLE ROCK | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44330940 | 2014-12-01 | Light Duty Steel Pole | Other | [7 empty] | 1.879e-07 | 5274.8779
118993446 | E | LC | ETL.8410.POLE.WOOD | 40770654 | LAKEVLLE | SONOMA | 2020-05-07 | 2020-05-07 | ETL.8410 | ELK-GUALALA | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770654 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 0.2258 | 950.644
119003186 | E | LC | ETL.1710.POLE.WDPS | 44513752 | MOSSLNDG | CENTRAL COAST | 2020-05-05 | 2020-08-27 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Vegetation | Overgrown | [Remove, Completed] | Tier3 |  |  | COMP
119004981 | E | LC | ETL.1430.INSL | 40896820 | SACTO | SACRAMENTO | 2020-05-06 | 2021-03-25 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119019961 | E | LC | ETL.3160.INSL | 40774777 | CONCORD | EAST BAY | 2020-05-11 | 2021-06-01 | ETL.3160 | OLEUM-G #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119036773 | E | LC | ETL.8410.POLE.WOOD | 40877405 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-05-25 | ETL.8410 | ELK-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877405 | 1986-01-01 | Single Wood Pole | 3P DV - 3 Pole Double Vertical | 1960-01-01 | Ceramic | Double Dead End - Suspension |  |  |  |  | 0.099182 | 687.7852
119041532 | E | LC | ETL.8650.TOWR | 40651183 | FRESNO | YOSEMITE | 2020-05-05 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40651183 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0034678 | 671.0923
119085060 | E | LC | ETL.6690.INSL.NCER | 40615660 | SACTO | SACRAMENTO | 2020-05-28 | 2021-03-29 | ETL.6690 | DEER CREEK-DRUM | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40590220 |  | Single Wood Pole | DV - Double Vertical |  | Non Ceramic | [5 empty] | 0.73195 | 158.2976
119103572 | F | LC | ETL.9090.POLE.WOOD | 40678953 | PISMOBCH | LOS PADRES | 2020-05-18 |  | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40678953 |  | Single Wood Pole | FIG4W - Wood X Arm | [7 empty] | 0.0089543 | 2313.9648
119103730 | F | LC | ETL.7780.POLE.WOOD | 40768476 | LAKEVLLE | HUMBOLDT | 2020-05-15 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40768476 |  | Single Wood Pole | 3P DV - 3 Pole Double Vertical |  | Ceramic | [5 empty] | 0.00016437 | 237.3428
119104069 | B | LC | ETL.8170.INSL.CERA | 40780015 | EUREKA | HUMBOLDT | 2020-06-03 | 2020-06-24 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119111346 | F | LC | ETL.1400.POLE.WDPS | 44776452 | VICTOR | YOSEMITE | 2020-05-26 | 2021-01-19 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44776423 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0010801 | 95.004
119112040 | F | LC | ETL.8240.POLE.WOOD | 40768897 | VICTOR | STOCKTON | 2020-06-01 | 2021-09-01 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768897 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0039182 | 3815.678
119115195 | F | LC | ETL.7290.POLE.WOOD | 40817418 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40817418 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Unknown |  |  |  |  | 0.063318 | 1158.6814
119117763 | F | LC | ETL.6950.POLE.WOOD | 40666253 | SACTO | SIERRA | 2020-05-28 | 2021-10-21 | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40666253 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0019906 | 3989.6598
119117930 | F | LC | ETL.7290.POLE.WOOD | 40701720 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40701720 |  | Single Wood Pole | 3HPD-S - 3 Horizontal Post Delta Short |  | Ceramic | Unknown |  |  |  |  | 0.11669 | 364.8483
119118770 | E | LC | ETL.8170.POLE.WOOD | 43950784 | EUREKA | HUMBOLDT | 2020-06-02 | 2021-09-28 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 43950784 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.012498 | 5239.7363
119119223 | F | LC | ETL.6490.POLE.WOOD | 40665609 | SACTO | SIERRA | 2020-06-02 | 2020-08-19 | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL
119122247 | F | LC | ETL.1400.POLE.WDPS | 45087037 | VICTOR | YOSEMITE | 2020-06-02 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40816005 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0078569 | 2436.5813
119125697 | F | LC | ETL.7300.POLE.WOOD | 40617685 | TABLEMTN |  | 2020-06-04 | 2021-03-22 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119144826 | E | LC | ETL.7390.POLE.WOOD | 44412207 | LAKEVLLE | HUMBOLDT | 2020-06-09 | 2020-09-10 | ETL.7390 | LAYTONVILLE-COVELO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44412207 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.080209
119158881 | E | LC | ETL.8170.POLE.WDPS | 44761230 | EUREKA | HUMBOLDT | 2020-06-12 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | PEND | 40810482 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.019833 | 237.3869 | 4.7082
119162984 | F | LC | ETL.6950.POLE.WOOD | 40768917 | SACTO | SACRAMENTO | 2020-06-13 |  | ETL.6950 | GOLD HILL #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 |  |  | PEND
119163355 | F | LC | ETL.1810.POLE.WDPS | 44322236 | EUREKA | HUMBOLDT | 2020-06-12 | 2021-05-18 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | DLFL | 44322234 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 3.3806e-06
119165683 | E | LC | ETL.1600.SWIT | 40743260 | LAKEVLLE | SONOMA | 2020-06-09 |  | ETL.1600 | FULTON-PUEBLO | Switch-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | PEND | [8 empty] | Other | NO ATTACHMENTS | Manual
119169331 | F | LC | ETL.6480.POLE.NWOD | 44695477 | SACTO | SIERRA | 2020-06-15 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44695477 | 2018-12-10 | Light Duty Steel Pole | T-1 - Tri Post | 2018-12-10 | Polymer | Post |  |  |  |  | 0.08998 | 3859.7815
119183689 | E | LC | ETL.1650.POLE.WOOD | 40750635 | LAKEVLLE | SONOMA | 2020-06-17 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40750635 | 1987-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1978-01-01 | Porcelain | Suspension |  |  |  |  | 0.0013549 | 2802.2717 | 3.7969
119187676 | F | LC | ETL.4680.TOWR | 40863592 | LAKEVLLE | SONOMA | 2020-04-14 | 2021-03-08 | ETL.4680 | FULTON-IGNACIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40863592 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.6458e-07 | 31.7331
119190231 | E | LC | ETL.1820.POLE.NWOD | 44926549 | EUREKA | HUMBOLDT | 2020-06-19 | 2020-10-27 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44926549 | 2020-06-11 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-11 | Glass | Dead End |  |  |  |  | 0.019298 | 79.1467
119199200 | F | LC | ETL.6470.POLE.WOOD | 40658307 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40658307 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.16852 | 269.0426
119202542 | B | LC | ETL.4220.POLE.WDPS | 44512143 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-07-15 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue] |  | Tier 2 | Within Both | DLFL | 40598518 | 2013-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.5674e-05 | 822.7042
119210655 | E | LC | ETL.5440.POLE.WDPS | 44558339 | TABLEMTN |  | 2020-06-24 | 2020-08-20 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119235943 | E | LC | ETL.6890.POLE.WOOD | 40874585 | LAKEVLLE | SONOMA | 2020-06-29 | 2021-03-08 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Tier 2 | Within Both | COMP | 40874585 | 1965-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Other |  |  |  |  | 0.00025078 | 2236.0244
119295023 | F | LC | ETL.7270.POLE.WOOD | 40906494 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.7270 | KESWICK-TRINITY | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40906494 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0031996 | 996.8419
119300714 | F | LC | ETL.4220.POLE.WOOD | 40673848 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2020-09-03 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40673848 | 1962-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2020-08-12 | Glass | Dead End |  |  |  |  | 0.01769 | 0.065151
119301212 | F | LC | ETL.6760.POLE.WOOD | 40611209 | SACTO | SACRAMENTO | 2020-07-02 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40611209 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.21556 | 63.348
119302036 | E | LC | ETL.1110.POLE.WDPS | 44423954 | TABLEMTN | HUMBOLDT | 2020-07-02 | 2021-07-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423953 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0023521 | 3217.7615
119303609 | F | LC | ETL.6070.TOWR | 40765614 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-01-15 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40765614 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-10-03 | Glass | Suspension |  |  |  |  | 0.0021674 | 2358.1025
119309447 | F | LC | ETL.1470.POLE.WOOD | 41176352 | LAKEVLLE | SONOMA | 2020-07-03 | 2021-03-17 | ETL.1470 | EAGLE ROCK-CORTINA | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41176352 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Porcelain | Post |  |  |  |  | 0.026245 | 5177.4746
119312516 | E | LC | ETL.8560.POLE.WOOD | 40763015 | PISMOBCH | LOS PADRES | 2020-07-02 | 2021-08-05 | ETL.8560 | CAYUCOS-CAMBRIA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40763015 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0082086 | 382.8347
119314174 | F | LC | ETL.6760.POLE.WOOD | 40814284 | SACTO | SACRAMENTO | 2020-07-06 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40814284 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.083972 | 933.5001
119324382 | F | LC | ETL.6280.POLE.NWOD | 40666792 | TABLEMTN | NORTH VALLEY | 2020-07-07 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40666792 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.00018504 | 5142.6284
119325057 | B | LC | ETL.7180.POLE.NWOD | 40877637 | LAKEVLLE | SONOMA | 2020-07-07 | 2020-10-27 | ETL.7180 | IGNACIO-BOLINAS #2 | Other | Customer Issue | [Customer Refusal, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877637 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 6.4626e-09 | 2109.2532
119328675 | F | LC | ETL.7270.POLE.WOOD | 40909426 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40909426 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0024381 | 237.5134
119335102 | F | LC | ETL.7030.POLE.NWOD | 44686500 | TABLEMTN | NORTH VALLEY | 2020-07-08 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44686500 | 2018-11-24 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2018-11-24 | Polymer | Post |  |  |  |  | 0.0029509 | 15.8837
119335938 | E | LC | ETL.6900.POLE.WOOD | 40616449 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-04-19 | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | DLFL | 40616449 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 3.0106e-05 | 0.065158
119340790 | B | LC | ETL.1370.INSL.CERA | 40719771 | PISMOBCH | LOS PADRES | 2020-07-08 | 2020-10-05 | ETL.1370 | DIVIDE-CABRILLO #2 | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119341634 | F | LC | ETL.6280.POLE.WOOD | 40865182 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40865182 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Other |  |  |  |  | 5.0512e-05 | 5520.0938
119341635 | F | LC | ETL.6280.POLE.WOOD | 40824639 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40824639 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 7.1167e-05 | 5239.1455
119356171 | E | LC | ETL.5970.TOWR | 40764249 | PISMOBCH | LOS PADRES | 2020-07-10 | 2021-05-10 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40764249 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-04-24 | Glass | Suspension |  |  |  |  | 1.7677e-08 | 4566.5933
119356322 | E | LC | ETL.1810.POLE.WDPS | 44322356 | EUREKA | HUMBOLDT | 2020-07-10 | 2021-04-20 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 44322354 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00076124
119357052 | E | LC | ETL.7030.POLE.WOOD | 40770739 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-06-08 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770739 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0053133 | 664.4426
119357101 | E | LC | ETL.7030.POLE.WOOD | 40601689 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-07-08 | ETL.7030 | HAT CREEK #1-WESTWOOD | Ground Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40601689 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.01153 | 2788.5168
119358285 | E | LC | ETL.5440.TOWR | 40873519 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2020-09-03 | ETL.5440 | PIT #6 JCT-ROUND MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873519 | 1942-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1942-01-01 | Ceramic | Suspension |  |  |  |  | 0.00015398 | 974.9968
119362591 | E | LC | ETL.1880.TOWR | 40859516 | FRESNO | FRESNO | 2020-07-13 |  | ETL.1880 | KERCKHOFF #1-KERCKHOFF #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40859516 | 1940-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-03-03 | Polymer | Dead End |  |  |  |  | 3.2657e-07 | 3816.918 | 0.0012465
119363269 | E | LC | ETL.1450.POLE.WOOD | 40650155 | SACTO | SIERRA | 2020-07-13 | 2021-05-19 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650155 | 1948-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 1948-01-01 | Ceramic | Suspension |  |  |  |  | 0.00074718 | 31.7066
119369104 | F | LC | ETL.7490.POLE.WDPS | 44743798 | EUREKA | HUMBOLDT | 2020-07-13 | 2021-09-16 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL | [12 empty] | 0.065148
119369820 | F | LC | ETL.6280.POLE.WOOD | 40698652 | TABLEMTN | NORTH VALLEY | 2020-07-14 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40698652 |  | Single Wood Pole | LB - Line and Buck | 2014-08-20 | Polymer | Suspension |  |  |  |  | 0.00013194 | 1573.8139
119369820 | F | LC | ETL.6280.POLE.WOOD | 40698652 | TABLEMTN | NORTH VALLEY | 2020-07-14 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40698652 |  | Single Wood Pole | LB - Line and Buck |  | Polymer | Post |  |  |  |  | 0.00013194 | 1573.8139
119378123 | E | LC | ETL.8060.POLE.WOOD | 40603899 | SACTO | SACRAMENTO | 2020-07-15 | 2021-10-06 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.030011 | 0.065152
119470148 | E | LC | ETL.7030.POLE.WOOD | 40589883 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-06-17 | ETL.7030 | HAT CREEK #1-WESTWOOD | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40589883 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.010579 | 118.8961
119475266 | E | LC | ETL.6880.POLE.WOOD | 40588899 | LAKEVLLE | SONOMA | 2020-07-20 | 2020-08-14 | ETL.6880 | FULTON-CALISTOGA | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL | [11 empty] | 0.002526 | 1534.6033
119478160 | F | LC | ETL.6290.POLE.WOOD | 40600663 | TABLEMTN | NORTH VALLEY | 2020-07-20 | 2021-10-04 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40600663 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.33787 | 158.4559
119481201 | F | LC | ETL.8960.POLE.NWOD | 41196590 | FRESNO | FRESNO | 2020-07-21 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 41196590 |  | Tubular Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 3.8198e-07
119496275 | F | LC | ETL.3190.TOWR | 40771764 | TABLEMTN | NORTH VALLEY | 2020-07-23 |  | ETL.3190 | CARIBOU-PALERMO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40771764 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.015334 | 4496.7499
119496278 | F | LC | ETL.7270.POLE.NWOD | 44649292 | TABLEMTN | NORTH VALLEY | 2020-07-23 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44649292 | 2018-08-17 | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2018-08-17 | Polymer | Dead End |  |  |  |  | 2.0401e-07 | 0.065152
119497621 | E | LC | ETL.9210.POLE.WOOD | 40595780 | MIDWAY | KERN | 2020-07-23 |  | ETL.9210 | TAFT-CUYAMA #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40595780 | 1946-01-01 | Single Wood Pole | 2P DDE - 2 Pole Double Dead End | 1946-01-01 | Ceramic | Dead End |  |  |  |  | 0.012387
119510177 | B | LC | ETL.7380.POLE.WOOD | 40601871 | MOSSLNDG | CENTRAL COAST | 2020-07-27 | 2020-11-19 | ETL.7380 | LAURELES-OTTER | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40601871 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.061891 | 0.065148
119519143 | E | LC | ETL.6880.POLE.WOOD | 40649345 | LAKEVLLE | SONOMA | 2020-07-28 | 2020-12-04 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | DLFL | [12 empty] | 506.3281
119529579 | F | LC | ETL.7510.POLE.WOOD | 40826584 | LAKEVLLE | SONOMA | 2020-07-30 | 2020-08-24 | ETL.7510 | MENDOCINO-HARTLEY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826584 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00013286 | 5114.5327
119561467 | E | LC | ETL.7180.POLE.WOOD | 40668139 | LAKEVLLE | NORTH BAY | 2020-08-04 | 2021-04-13 | ETL.7180 | IGNACIO-BOLINAS #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40668139 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 0.0001739 | 253.1975
119569504 | F | LC | ETL.6880.POLE.WOOD | 40912474 | LAKEVLLE | NORTH BAY | 2020-08-05 | 2021-04-15 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.010768 | 411.9098
119595264 | E | LC | ETL.5463.TOWR | 40857950 | CONCORD | DIABLO | 2020-08-10 | 2021-04-27 | ETL.5463 | PITTSBURG-SAN MATEO | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40857950 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 5.7545e-08 | 3798.8403
119624160 | F | LC | ETL.8170.POLE.WOOD | 40906468 | EUREKA | HUMBOLDT | 2020-08-03 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906468 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.032119 | 31.7081
119628299 | F | LC | ETL.7380.POLE.WOOD | 40617432 | MOSSLNDG | CENTRAL COAST | 2020-08-17 |  | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40617432 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.11744 | 142.4119
119670262 | B | LC | ETL.7180.POLE.WOOD | 40649389 | LAKEVLLE | SONOMA | 2020-08-25 | 2020-10-19 | ETL.7180 | IGNACIO-BOLINAS #2 | Other | Customer Issue | [Customer Refusal] | Tier2 | Tier 2 | Within Both | COMP | 40649389 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 2.6753e-05 | 2156.8303
119670405 | F | LC | ETL.2060.POLE.WOOD | 40586954 | LAKEVLLE | SONOMA | 2020-08-25 |  | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40586954 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.32375 | 31.6963
119677971 | E | LC | ETL.3800.TOWR | 40646594 | CONCORD | EAST BAY | 2020-08-26 | 2021-04-19 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40646594 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 7.4865e-08 | 253.126
119698964 | F | LC | ETL.6280.POLE.WOOD | 44465287 | TABLEMTN | NORTH VALLEY | 2020-08-31 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44465287 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2020-11-16 | Polymer | Dead End |  |  |  |  | 0.010339 | 6742.9849
119699617 | B | LC | ETL.8060.INSL.CERA | 40610619 | SACTO | SIERRA | 2020-08-28 | 2020-11-17 | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119702363 | E | LC | ETL.6770.POLE.WOOD | 40650020 | SACTO | SIERRA | 2020-08-29 | 2021-04-21 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119707313 | B | LC | ETL.6310.POLE.WOOD | 40600710 | TABLEMTN | NORTH VALLEY | 2020-08-29 | 2020-09-24 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600710 |  | Single Wood Pole | T2N | 2021-10-18 | Polymer | Post |  |  |  |  | 1.3566e-05 | 3880.2761
119720509 | A | LC | ETL.6240.POLE.WOOD | 40874269 | MOSSLNDG | CENTRAL COAST | 2020-09-05 | 2020-09-24 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40874269 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.19166 | 110.8153
119722966 | E | LC | ETL.2790.TOWR | 40804670 | CONCORD | EAST BAY | 2020-08-04 | 2021-03-10 | ETL.2790 | MORAGA-SAN LEANDRO #3 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40804670 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 2.6626e-06 | 0.065147
119723690 | F | LC | ETL.8650.POLE.NWOD | 44420175 | FRESNO | YOSEMITE | 2020-07-30 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44420175 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0021672 | 3305.365
119723694 | E | LC | ETL.6950.POLE.WOOD | 40905852 | SACTO | SIERRA | 2020-08-03 | 2021-10-20 | ETL.6950 | GOLD HILL #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40905852 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.0005674 | 3591.1831 | 2.0376
119725055 | E | LC | ETL.1240.POLE.WDPS | 44386150 | TABLEMTN | NORTH VALLEY | 2020-08-06 |  | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44386149 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.387e-06 | 2791.1111 | 0.023409
119730701 | E | LC | ETL.6280.POLE.WOOD | 40826361 | TABLEMTN | NORTH VALLEY | 2020-09-09 | 2021-08-18 | ETL.6280 | CARIBOU #2 | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40826361 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 6.0205e-06 | 1298.3811
119753687 | E | LC | ETL.1240.POLE.WDPS | 44386111 | TABLEMTN | NORTH VALLEY | 2020-07-31 | 2021-04-19 | ETL.1240 | CASCADE-COTTONWOOD | Ground Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | DLFL | 44386110 |  | 2-Pole Wood | 2PS TRP - 2 Pole SUSP. Transposition | [7 empty] | 2.9815e-05 | 3619.7201
119774779 | F | LC | ETL.6480.POLE.NWOD | 45122765 | SACTO | NORTH VALLEY | 2020-09-16 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45122765 | 2021-06-14 | Light Duty Steel Pole | T-1 - Tri Post | 2021-06-14 | Polymer | Post | [5 empty] | 680.261
119785751 | F | LC | ETL.4750.TOWR | 40756496 | LAKEVLLE | SONOMA | 2020-07-28 | 2021-04-08 | ETL.4750 | GEYSERS #12-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756496 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Porcelain | Suspension |  |  |  |  | 3.3826e-09 | 2312.1152
119787654 | E | LC | ETL.6490.POLE.WOOD | 40874570 | SACTO | SIERRA | 2020-09-17 | 2021-03-02 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119803643 | E | LC | ETL.8580.TOWR | 40609678 | FRESNO | FRESNO | 2020-09-21 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40609678 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 4.063e-06
119811250 | F | LC | ETL.4040.POLE.STPS | 44647102 | TABLEMTN | NORTH VALLEY | 2020-08-26 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44646905 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0003614 | 538.0957
119815138 | F | LC | ETL.1130.INSL | 40828423 | CONCORD | EAST BAY | 2020-09-24 | 2021-09-23 | ETL.1130 | BRIGHTON-CLAYTON #2 | Jumper-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119815788 | F | LC | ETL.6690.POLE.WOOD | 40664853 | SACTO | SIERRA | 2020-09-08 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40664853 |  | Single Wood Pole | T-1 - Tri Post | 2015-08-10 | Polymer | Post |  |  |  |  | 0.079981 | 142.4769
119816137 | F | LC | ETL.1421.POLE.NWOD | 44814407 | SACTO | SIERRA | 2020-08-29 |  | ETL.1421 | DUTCH FLAT #2 TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44814407 | 2019-06-04 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-06-04 | Glass | Suspension |  |  |  |  | 5.3443e-07 | 664.5352
119853558 | F | LC | ETL.7030.POLE.WOOD | 40817103 | TABLEMTN | NORTH VALLEY | 2020-10-02 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40817103 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.02425 | 126.76
119898535 | E | LC | ETL.6240.POLE.WOOD | 40665107 | MOSSLNDG | CENTRAL COAST | 2020-10-07 | 2021-08-17 | ETL.6240 | BURNS-LONE STAR #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40665107 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.16061 | 1028.9148
119918262 | E | LC | ETL.2470.POLE.WOOD | 40589228 | MOSSLNDG | SAN JOSE | 2020-10-16 |  | ETL.2470 | METCALF-COYOTE PUMPING PLANT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40589228 | 1986-01-01 | Single Wood Pole | T-1 - Tri Post | 1986-01-01 | Ceramic | Post |  |  |  |  | 3.4301e-05
119950665 | F | LC | ETL.3020.TOWR | 40871964 | CONCORD | MISSION | 2020-10-23 | 2021-02-09 | ETL.3020 | NEWARK-JARVIS #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40871964 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.265e-07
119950665 | F | LC | ETL.3020.TOWR | 40871964 | CONCORD | MISSION | 2020-10-23 | 2021-02-09 | ETL.3020 | NEWARK-JARVIS #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40871964 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-11-03 | Ceramic | Suspension |  |  |  |  | 2.265e-07
119965193 | E | LC | ETL.1110.INSL.CERA | 40781285 | TABLEMTN | HUMBOLDT | 2020-08-25 | 2021-05-13 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119995717 | F | LC | ETL.6480.POLE.NWOD | 44695523 | SACTO | NORTH VALLEY | 2020-10-06 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44695523 | 2018-12-10 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-12-10 | Polymer | Dead End |  |  |  |  | 0.013873 | 269.0304
120088025 | B | LC | ETL.6230.SWIT | 40743493 | MOSSLNDG | CENTRAL COAST | 2020-11-23 | 2020-12-03 | ETL.6230 | BURNS-LONE STAR #1 | FAA Battery-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [7 empty] | 2010-05-10 | Inertia | VACUUM INTERRUPTER (3 GAP) | SCADA Only
120097182 | F | LC | ETL.3180.POLE.NWOD | 44231991 | CONCORD | EAST BAY | 2020-11-16 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44231991 | 2014-10-23 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees |  | Non Ceramic | Suspension |  |  |  |  | 7.9211e-07 | 16.3369
120112589 | F | LC | ETL.7260.POLE.WOOD | 40601951 | TABLEMTN | NORTH VALLEY | 2020-12-01 | 2021-03-10 | ETL.7260 | KESWICK-CASCADE | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601951 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 1.3549e-05 | 3722.593
120119327 | E | LC | ETL.6300.POLE.WOOD | 40656504 | TABLEMTN |  | 2020-11-23 | 2021-08-23 | ETL.6300 | CARIBOU-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656504 |  | Single Wood Pole | FDDE - Flat Dead End Construction | 2014-11-06 | Non Ceramic | Post |  |  |  |  | 0.0034739 | 47.5141
120130938 | E | LC | ETL.1110.INSL.CERA | 43693238 | EUREKA | HUMBOLDT | 2020-12-04 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40682650 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.001993 | 79.1724 | 0.15779
120133403 | F | LC | ETL.6880.POLE.WOOD | 40588917 | LAKEVLLE | NORTH BAY | 2020-10-20 | 2021-04-19 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40588917 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.0014233 | 4321.8276
120211337 | F | LC | ETL.5462.TOWR | 40746176 | CONCORD | DIABLO | 2020-11-10 |  | ETL.5462 | PITTSBURG-EASTSHORE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40746176 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2001-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 1.9906e-06 | 5619.5354 | 0.011186
120211337 | F | LC | ETL.5462.TOWR | 40746176 | CONCORD | DIABLO | 2020-11-10 |  | ETL.5462 | PITTSBURG-EASTSHORE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40746176 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2001-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.9906e-06 | 5619.5354 | 0.011186
120229746 | F | LC | ETL.6280.POLE.NWOD | 44259056 | TABLEMTN | NORTH VALLEY | 2020-11-20 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44259056 | 2020-07-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-07-16 | Polymer | Dead End |  |  |  |  | 2.5138e-10 | 31.6978
120330516 | F | LC | ETL.6880.POLE.NWOD | 40700638 | LAKEVLLE | SONOMA | 2020-12-21 | 2021-04-19 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 |  |  | DLFL
120661904 | F | LC | ETL.4392.TOWR | 41129390 | LAKEVLLE | SONOMA | 2021-03-17 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 41129390 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.0011045 | 996.9683
120664476 | F | LC | ETL.5932.TOWR | 40651144 | METCALF | SAN JOSE | 2021-03-19 |  | ETL.5932 | VASONA-METCALF | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40651144 | 1957-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1957-01-01 | Ceramic | Suspension |  |  |  |  | 3.6602e-07 | 969.1223 | 0.00035472
120671678 | B | LC | ETL.4040.INSL.CERA | 40920425 | TABLEMTN |  | 2021-03-22 | 2021-04-01 | ETL.4040 | TRINITY-COTTONWOOD | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564995 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.15747
120671678 | B | LC | ETL.4040.INSL.CERA | 40920425 | TABLEMTN |  | 2021-03-22 | 2021-04-01 | ETL.4040 | TRINITY-COTTONWOOD | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564995 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.15747
120679882 | E | LC | ETL.4960.INSL | 40894167 | LAKEVLLE | SONOMA | 2021-03-23 |  | ETL.4960 | LAKEVILLE-SOBRANTE #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40869529 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Dead End |  |  |  |  | 0.00099774 | 0.066432 | 6.6282e-05
120679882 | E | LC | ETL.4960.INSL | 40894167 | LAKEVLLE | SONOMA | 2021-03-23 |  | ETL.4960 | LAKEVILLE-SOBRANTE #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40869529 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00099774 | 0.066432 | 6.6282e-05
120687190 | E | LC | ETL.8290.POLE.WOOD | 40825136 | TABLEMTN | NORTH VALLEY | 2021-03-24 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40825136 |  | Single Wood Pole | T2N | 2021-04-20 | Polymer | Post |  |  |  |  | 0.00057161 | 620.4225 | 0.35464
120714410 | B | LC | ETL.5630.INSL.CERA | 40885501 | TABLEMTN | NORTH VALLEY | 2021-03-30 | 2021-07-01 | ETL.5630 | ROCK CREEK-POE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862111 | 1958-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1958-01-01 | Ceramic | Other |  |  |  |  | 1.0439e-05 | 5382.2134
120714576 | E | LC | ETL.4040.POLE.STPS | 44630192 | TABLEMTN |  | 2021-03-30 | 2021-04-22 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44630139 | 2018-07-02 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 3.7073e-05 | 1823.3884
120716094 | E | LC | ETL.1730.POLE.WDPS | 44413412 | MOSSLNDG | CENTRAL COAST | 2021-03-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44413411 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 2.4202e-05 | 0.065147 | 1.5767e-06
120725737 | E | LC | ETL.7380.POLE.WDPS | 44562832 | MOSSLNDG | CENTRAL COAST | 2021-04-01 |  | ETL.7380 | LAURELES-OTTER | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44562375 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.10504 | 47.5141 | 4.9908
120739641 | E | LC | ETL.8365.INSL.NCER | 40710619 | EUREKA | HUMBOLDT | 2021-04-03 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40656822 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Dead End |  |  |  |  | 0.00045066 | 1167.7505 | 0.52626
120745902 | F | LC | ETL.7040.POLE.WOOD | 40867675 | TABLEMTN | NORTH VALLEY | 2021-04-05 | 2021-04-26 | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40867675 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.12153 | 1870.6526
120746469 | F | LC | ETL.7380.POLE.WDPS | 44562940 | MOSSLNDG | CENTRAL COAST | 2021-04-05 |  | ETL.7380 | LAURELES-OTTER | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44562405 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.60797 | 0.065148
120749181 | F | LC | ETL.1350.POLE.WDPS | 44512170 | TABLEMTN |  | 2021-04-06 | 2021-10-11 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40759599 | 1993-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.013911 | 63.351
120763720 | E | LC | ETL.1350.POLE.WDPS | 44513798 | TABLEMTN | NORTH VALLEY | 2021-04-08 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44512314 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.11102 | 273.7763
120773026 | F | LC | ETL.3830.TOWR | 40819887 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40819887 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.0445e-09 | 5207.0464
120808023 | B | LC | ETL.6870.INSL | 40854245 | SACTO | SACRAMENTO | 2021-04-13 | 2021-04-22 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Tie Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
120850188 | E | LC | ETL.3740.INSL.NCER | 42582030 | CONCORD | EAST BAY | 2021-04-20 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44188839 | 2008-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | Dead End |  |  |  |  | 0.016508 | 445.731 | 7.3582
120854854 | E | LC | ETL.1400.POLE.WDPS | 44773696 | VICTOR | STOCKTON | 2021-04-20 | 2021-09-01 | ETL.1400 | DONNELLS-MI-WUK | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40648361 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0010904 | 31.7334
120859719 | E | LC | ETL.1530.TOWR | 40810217 | SACTO | SIERRA | 2021-04-13 | 2021-06-09 | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40810217 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 1.1374e-05 | 2309.6055
120861814 | E | LC | ETL.4040.POLE.STPS | 45006978 | TABLEMTN | NORTH VALLEY | 2021-04-21 |  | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45006453 | 2020-09-17 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.6921e-05 | 2294.1755 | 0.17647
120862456 | F | LC | ETL.1820.POLE.STPS | 44763082 | EUREKA | HUMBOLDT | 2021-04-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Right of Way | Encroachment | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44763052 | 2019-04-29 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0020624 | 0.065148
120874309 | E | LC | ETL.5510.TOWR | 40682744 | CONCORD | DIABLO | 2021-04-23 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40682744 | 1953-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1953-01-01 | Ceramic | Dead End |  |  |  |  | 3.9539e-07 | 5497.5933 | 0.0021737
120879423 | E | LC | ETL.4040.POLE.STPS | 44647062 | TABLEMTN | NORTH VALLEY | 2021-04-24 |  | ETL.4040 | TRINITY-COTTONWOOD | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44646838 | 2018-08-17 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00066038 | 206.9966 | 0.1367
120891368 | E | LC | ETL.4460.INSL | 40781685 | MOSSLNDG | CENTRAL COAST | 2021-04-22 |  | ETL.4460 | COBURN-LAS AGUILAS SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40753106 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 7.0715e-08 | 15.8926 | 1.1238e-06
120891368 | E | LC | ETL.4460.INSL | 40781685 | MOSSLNDG | CENTRAL COAST | 2021-04-22 |  | ETL.4460 | COBURN-LAS AGUILAS SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40753106 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 7.0715e-08 | 15.8926 | 1.1238e-06
120900166 | E | LC | ETL.8060.POLE.WOOD | 40771515 | SACTO | SACRAMENTO | 2021-04-29 | 2021-08-03 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771515 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | [5 empty] | 0.0099896 | 9.5576
120906729 | A | LC | ETL.3960.TOWR | 40586148 | PISMOBCH | LOS PADRES | 2021-04-30 | 2021-05-04 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Emergency | Storm Related | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586148 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 1.1352e-08 | 4958.5791
120906729 | A | LC | ETL.3960.TOWR | 40586148 | PISMOBCH | LOS PADRES | 2021-04-30 | 2021-05-04 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Emergency | Storm Related | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586148 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 1.1352e-08 | 4958.5791
120907479 | F | LC | ETL.8060.POLE.WOOD | 44156130 | SACTO | SACRAMENTO | 2021-04-30 |  | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44156130 | 2013-09-20 | Single Wood Pole | TH - TriAngle Post 70 | 2013-09-20 | Polymer | Post |  |  |  |  | 0.0032775 | 0.065152
120910707 | E | LC | ETL.7550.POLE.WOOD | 40768555 | LAKEVLLE | SONOMA | 2021-04-30 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40768555 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 4.8523e-05 | 110.7947 | 0.0053761
120911287 | E | LC | ETL.1820.POLE.WDPS | 44560515 | EUREKA | HUMBOLDT | 2021-04-30 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560109 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.11951 | 1313.3468 | 156.9639
120926865 | E | LC | ETL.4950.INSL | 40631547 | LAKEVLLE |  | 2021-05-03 |  | ETL.4950 | FULTON-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40592333 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.8812e-05 | 190.6293 | 0.0093051
120928158 | E | LC | ETL.3820.TOWR | 40592619 | VICTOR | STOCKTON | 2021-05-04 | 2021-05-14 | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40592619 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 1.8384e-05 | 5666.2915
120929662 | B | LC | ETL.4550.TOWR | 40601452 | TABLEMTN | NORTH VALLEY | 2021-05-04 | 2021-06-16 | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601452 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 8.5888e-08 | 4753.4985
120930906 | B | LC | ETL.5934.INSL.CERA | 44454587 | PISMOBCH | LOS PADRES | 2021-05-04 | 2021-06-28 | ETL.5934 | TEMPLETON-GATES | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40604882 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-08-27 | Ceramic | Suspension |  |  |  |  | 2.641e-08 | 5199.2328
120948443 | E | LC | ETL.6470.POLE.WOOD | 40766725 | SACTO | SACRAMENTO | 2021-05-07 | 2021-08-25 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40766725 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.03655 | 79.2067
121321474 | B | LC | ETL.1810.POLE.WDPS | 44322719 | EUREKA | HUMBOLDT | 2021-05-12 | 2021-07-20 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
121331335 | F | LC | ETL.9250.POLE.WOOD | 40749492 | MIDWAY | KERN | 2021-04-22 |  | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40749492 | 1967-01-01 | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Other |  |  |  |  | 0.0083125 | 5260.3872
121341086 | F | LC | ETL.1430.TOWR | 40655122 | SACTO | SIERRA | 2021-05-15 | 2021-09-30 | ETL.1430 | DRUM-RIO OSO #2 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40655122 | 1913-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-02-24 | Glass | Dead End |  |  |  |  | 0.047141 | 1993.4753
121346405 | F | LC | ETL.1420.TOWR | 40659461 | SACTO | SIERRA | 2021-04-28 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40659461 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1913-01-01 | Porcelain | Dead End |  |  |  |  | 0.0017025 | 223.1074 | 0.37984
121346980 | E | LC | ETL.1420.TOWR | 40588543 | SACTO | SIERRA | 2021-05-13 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40588543 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm | 1913-01-01 | Polymer | Suspension |  |  |  |  | 7.811e-08 | 316.4733 | 2.472e-05
121348535 | E | LC | ETL.2780.INSL | 40604491 | CONCORD | EAST BAY | 2021-04-24 |  | ETL.2780 | MORAGA-SAN LEANDRO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40580808 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 3.1885e-08 | 332.4702 | 1.0601e-05
121364071 | E | LC | ETL.5250.INSL | 40729459 | CONCORD | EAST BAY | 2021-04-29 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40689988 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 7.3615e-06 | 7.9726 | 5.869e-05
121364870 | F | LC | ETL.6870.POLE.WOOD | 40751836 | SACTO | SIERRA | 2021-05-01 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40751836 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.068254 | 0.065152
121370097 | F | LC | ETL.1600.TOWR | 40582777 | LAKEVLLE | SONOMA | 2021-05-03 | 2021-09-27 | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40582777 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 1.6844e-06 | 190.6293
121379455 | F | LC | ETL.6470.POLE.WOOD | 40598561 | SACTO | SIERRA | 2021-05-07 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40598561 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.16255 | 474.9903
121380241 | F | LC | ETL.8350.POLE.NWOD | 44920050 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44920050 |  | Light Duty Steel Pole | T-1 - Tri Post | 2020-01-15 | Polymer | Post |  |  |  |  | 2.9375e-07 | 889.963
121384125 | E | LC | ETL.6640.INSL | 40885832 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40862384 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.01347 | 933.8852 | 12.579
121385594 | E | LC | ETL.1650.POLE.WOOD | 40659189 | LAKEVLLE | SONOMA | 2021-05-14 | 2021-07-08 | ETL.1650 | GEYSERS #3-CLOVERDALE | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40659189 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 5.3451e-05 | 3938.675
121394750 | E | LC | ETL.4590.INSL | 40892308 | TABLEMTN | NORTH VALLEY | 2021-05-25 |  | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40867827 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.3818e-05 | 1847.4751 | 0.025528
121429880 | F | LC | ETL.8290.POLE.WOOD | 40769428 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40769428 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00013273 | 620.4352
121436164 | E | LC | ETL.5640.INSL | 40844167 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40816241 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 2.5871e-06 | 2710.3174 | 0.0070118
121445234 | E | LC | ETL.1400.POLE.STPS | 44806636 | VICTOR | YOSEMITE | 2021-06-01 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44779589 | 2019-06-25 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.3911e-05 | 1242.0833 | 0.054541
121448513 | E | LC | ETL.6500.INSL.NCER | 45095071 | SACTO | SIERRA | 2021-06-02 |  | ETL.6500 | COLGATE-PALERMO | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45095019 | 2021-04-22 | Light Duty Steel Pole | T-1 - Tri Post | 2021-04-22 | Polymer | Post |  |  |  |  | 3.4682e-05 | 3231.9753 | 0.11209
121450464 | E | LC | ETL.5640.TOWR | 40758172 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40758172 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 6.6115e-09 | 4167.8633 | 2.7556e-05
121469949 | B | LC | ETL.2760.INSL | 40792397 | CONCORD | EAST BAY | 2021-06-04 | 2021-07-26 | ETL.2760 | MORAGA-OAKLAND J | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40761845 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 4.2616e-06 | 0.065147
121474266 | B | LC | ETL.1820.INSL.CERA | 44260565 | EUREKA | HUMBOLDT | 2021-06-04 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562403 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 2016-10-03 | Ceramic | Suspension |  |  |  |  | 0.072013
121474266 | B | LC | ETL.1820.INSL.CERA | 44260565 | EUREKA | HUMBOLDT | 2021-06-04 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562403 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 2016-10-03 | Ceramic | Suspension |  |  |  |  | 0.072013
121484891 | E | LC | ETL.6980.INSL.NCER | 40800679 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.6980 | FORT ROSS-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40769863 | 1953-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.88806 | 15.88 | 14.1024
121485860 | F | LC | ETL.7550.POLE.NWOD | 44922050 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44922050 | 2020-06-02 | Light Duty Steel Pole | T2N | 2020-06-02 | Polymer | Post |  |  |  |  | 2.1449e-11 | 3416.6756
121496151 | F | LC | ETL.7000.POLE.NWOD | 44177809 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44177809 | 2014-09-27 | Light Duty Steel Pole | FDDE - Flat Dead End Construction |  | Porcelain | Dead End |  |  |  |  | 4.7736e-07 | 0.065148
121497148 | F | LC | ETL.1180.POLE.STPS | 44282786 | TABLEMTN | NORTH VALLEY | 2021-06-08 | 2021-06-24 | ETL.1180 | BUTTE VALLEY-CARIBOU | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44282784 | 2015-11-09 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 6.5803e-08 | 0.065148
121516372 | F | LC | ETL.6320.POLE.NWOD | 44820189 | TABLEMTN | NORTH VALLEY | 2021-06-04 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44820189 | 2019-06-30 | Fiberglass | TPD - Tri Post Dead End Construction | 2019-06-30 | Glass | Dead End |  |  |  |  | 0.00050151 | 176.3957
121518393 | B | LC | ETL.6880.POLE.NWOD | 44928865 | LAKEVLLE | NORTH BAY | 2021-06-04 | 2021-07-08 | ETL.6880 | FULTON-CALISTOGA | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44928865 | 2020-06-10 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-06-10 | Glass | Dead End |  |  |  |  | 0.00065069 | 750.6181
121520214 | F | LC | ETL.4040.POLE.WDPS | 44557527 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44553893 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.065751 | 620.621
121523063 | F | LC | ETL.7490.POLE.WDPS | 44761213 | EUREKA | HUMBOLDT | 2021-06-04 | 2021-07-12 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40811053 |  | 3-Pole Wood | Unknown | [7 empty] | 0.041571 | 142.4119
121524231 | E | LC | ETL.5390.TOWR | 40677453 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40677453 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 7.1031e-06 | 2156.92 | 0.015321
121525615 | E | LC | ETL.6020.INSL | 40891271 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40868281 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 7.6212e-09 | 3100.9255 | 2.3633e-05
121526014 | E | LC | ETL.1350.INSL | 40897086 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40871617 | 1943-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.089476
121526014 | E | LC | ETL.1350.INSL | 40897086 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40871617 | 1943-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.089476
121527099 | E | LC | ETL.8060.POLE.WOOD | 40826216 | SACTO | SIERRA | 2021-06-08 | 2021-06-24 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40826216 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.028681 | 15.8859
121527220 | E | LC | ETL.8350.POLE.WOOD | 40643822 | VICTOR | STOCKTON | 2021-06-08 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40643822 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0031737 | 553.7256 | 1.7574
121531182 | E | LC | ETL.6500.POLE.WOOD | 40757211 | SACTO | NORTH VALLEY | 2021-06-12 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40757211 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0093037 | 2376.323 | 22.1087
121531454 | E | LC | ETL.6470.POLE.WOOD | 40664607 | SACTO | SIERRA | 2021-06-09 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40664607 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.064247 | 427.3383 | 27.4551
121531586 | E | LC | ETL.2390.POLE.WDPS | 44390958 | VICTOR | STOCKTON | 2021-06-14 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44390956 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.6762e-06 | 1505.5992 | 0.013063
121535391 | E | LC | ETL.6360.POLE.WDPS | 44560646 | CONCORD | DIABLO | 2021-06-14 |  | ETL.6360 | CHRISTIE-FRANKLIN #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560144 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00019741 | 127.6204 | 0.025193
121536221 | F | LC | ETL.1600.TOWR | 40581562 | LAKEVLLE | NORTH BAY | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40581562 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 2.4635e-09 | 697.7503 | 1.7189e-06
121539570 | F | LC | ETL.1350.TOWR | 40856556 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40856556 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0028417 | 411.4229
121539570 | F | LC | ETL.1350.TOWR | 40856556 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40856556 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.0028417 | 411.4229
121548291 | F | LC | ETL.3150.TOWR | 40746008 | CONCORD | DIABLO | 2021-06-16 |  | ETL.3150 | OLEUM-G #1 | Road | Brush Fuel | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40746008 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2005-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 9.6401e-05 | 571.4411
121549961 | F | LC | ETL.1600.TOWR | 40762234 | LAKEVLLE | SONOMA | 2021-06-16 | 2021-10-14 | ETL.1600 | FULTON-PUEBLO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40762234 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Dead End |  |  |  |  | 3.3404e-07 | 2346.1775
121557097 | E | LC | ETL.6750.POLE.WDPS | 44561414 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560769 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00050883 | 94.9939 | 0.048336
121560054 | B | LC | ETL.1810.INSL.NCER | 40854178 | EUREKA | HUMBOLDT | 2021-06-17 | 2021-07-08 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322619 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.0019289
121560054 | B | LC | ETL.1810.INSL.NCER | 40854178 | EUREKA | HUMBOLDT | 2021-06-17 | 2021-07-08 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322619 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.0019289
121561583 | F | LC | ETL.6070.TOWR | 40816721 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6070 | ROUND MTN-TABLE MTN #2 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40816721 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.4281e-05 | 1729.0863
121578929 | E | LC | ETL.6430.POLE.WDPS | 44274853 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6430 | COLEMAN-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44274852 | 2014-11-04 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0069934 | 3946.1392 | 27.5969
121592906 | B | LC | ETL.7180.POLE.WDPS | 44360859 | LAKEVLLE | NORTH BAY | 2021-06-23 | 2021-07-13 | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44360859 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 3.9765e-05
121592906 | B | LC | ETL.7180.POLE.WDPS | 44360859 | LAKEVLLE | NORTH BAY | 2021-06-23 | 2021-07-13 | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44360859 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 3.9765e-05
121592906 | B | LC | ETL.7180.POLE.WDPS | 44360859 | LAKEVLLE | NORTH BAY | 2021-06-23 | 2021-07-13 | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44360859 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 3.9765e-05
121608659 | F | LC | ETL.7550.POLE.WOOD | 40698029 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40698029 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | [5 empty] | 9.6298e-05 | 31.7022
121617738 | B | LC | ETL.6070.INSL | 40792895 | TABLEMTN | NORTH VALLEY | 2021-06-27 | 2021-07-22 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762619 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 2.8124e-06 | 3658.251
121623779 | E | LC | ETL.6760.INSL.NCER | 40798751 | SACTO | SACRAMENTO | 2021-06-28 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40767253 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.052766 | 126.6132 | 6.6808
121630009 | F | LC | ETL.1070.POLE.NWOD | 45073099 | VICTOR | STOCKTON | 2021-06-22 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45073099 | 2021-03-05 | Light Duty Steel Pole | TPS1D - Tri Post & Susp DDE 115 KV | 2021-03-05 | Glass | Dead End - Suspension |  |  |  |  | 4.8291e-10 | 2633.8957
121657029 | F | LC | ETL.6760.POLE.WOOD | 40598946 | SACTO | SIERRA | 2021-06-28 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40598946 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Dead End |  |  |  |  | 0.094471 | 901.7202
121659234 | E | LC | ETL.6831.INSL.CERA | 40784841 | METCALF | SAN JOSE | 2021-07-02 |  | ETL.6831 | JEFFERSON #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40755213 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 7.3057e-06 | 1407.5852 | 0.010283
121659503 | F | LC | ETL.7060.POLE.WOOD | 40767293 | METCALF | PENINSULA | 2021-07-01 | 2021-11-02 | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767293 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 0.0022355 | 0.066432 | 0.00014851
121688545 | F | LC | ETL.7390.POLE.NWOD | 44647516 | LAKEVLLE | HUMBOLDT | 2021-06-27 |  | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44647516 | 2018-09-02 | Light Duty Steel Pole | 3P DDE - 3 Pole Double Dead End | 2018-09-02 | Ceramic | Suspension |  |  |  |  | 0.0013195 | 1265.6091
121689030 | E | LC | ETL.7390.POLE.NWOD | 44647525 | LAKEVLLE | HUMBOLDT | 2021-06-27 | 2021-10-26 | ETL.7390 | LAYTONVILLE-COVELO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44647525 | 2018-09-02 | Light Duty Steel Pole | 3P DDE - 3 Pole Double Dead End | 2018-09-02 | Ceramic | Suspension |  |  |  |  | 0.0013195 | 1265.6091 | 1.6699
121717953 | F | LC | ETL.1450.POLE.NWOD | 44558490 | SACTO | SIERRA | 2021-07-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44558490 |  | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Suspension |  |  |  |  | 1.4538e-06 | 47.5273
121723230 | E | LC | ETL.6020.TOWR | 40759867 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40759867 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00015948 | 427.2444 | 0.068138
121738827 | F | LC | ETL.1400.POLE.WDPS | 44776444 | VICTOR | STOCKTON | 2021-07-08 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40656095 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.0044401 | 221.5655
121748280 | F | LC | ETL.1720.POLE.NWOD | 44402456 | MOSSLNDG | SAN JOSE | 2021-07-14 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44402456 | 2015-07-02 | Light Duty Steel Pole | DDE - Double Dead End | 2015-07-02 | Polymer | Dead End |  |  |  |  | 1.5307e-10 | 2915.1851
121782925 | F | LC | ETL.2141.POLE.WDPS | 44264819 | MIDWAY | KERN | 2021-07-20 | 2021-09-08 | ETL.2141 | VEDDER TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44264816 |  | 3-Pole Wood | DDE - Double Dead End | [7 empty] | 6.4734e-05 | 5461.5088
121800378 | E | LC | ETL.3690.INSL.CERA | 42574130 | PISMOBCH | LOS PADRES | 2021-07-26 |  | ETL.3690 | SISQUOC-GAREY | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42574126 |  | Single Wood Pole | 3P DDE - 3 Pole Double Dead End |  | Ceramic | [5 empty] | 9.4902e-05 | 5160.9634 | 0.48979
121803402 | E | LC | ETL.6020.TOWR | 41111819 | TABLEMTN | NORTH VALLEY | 2021-07-26 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41111819 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | [7 empty] | 4.6921e-08 | 379.78 | 1.782e-05
121810401 | F | LC | ETL.6760.POLE.NWOD | 44964262 | SACTO | SIERRA | 2021-07-27 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44964262 | 2020-06-02 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-06-02 | Glass | Dead End |  |  |  |  | 0.00057391 | 63.3392
121816112 | F | LC | ETL.2540.POLE.WDPS | 44551444 | MOSSLNDG | CENTRAL COAST | 2021-07-29 |  | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44550896 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014918 | 823.3626
121900729 | B | LC | ETL.8170.POLE.WOOD | 40752180 | EUREKA | HUMBOLDT | 2021-08-13 | 2021-09-09 | ETL.8170 | TRINITY-MAPLE CREEK | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.027288 | 6300.0015
121900742 | E | LC | ETL.1820.POLE.WDPS | 44560670 | EUREKA | HUMBOLDT | 2021-08-13 | 2021-09-30 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 6300.0015
121959112 | B | LC | ETL.6880.POLE.NWOD | 45140649 | LAKEVLLE | SONOMA | 2021-08-26 | 2021-11-30 | ETL.6880 | FULTON-CALISTOGA | Right of Way | Encroachment | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 45140649 | 2021-08-01 | Light Duty Steel Pole | T-1 - Tri Post | 2021-08-01 | Polymer | Post
121961520 | E | LC | ETL.5660.INSL | 40844890 | CONCORD | EAST BAY | 2021-08-26 |  | ETL.5660 | SAN RAMON-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40816972 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-05-24 | Glass | Dead End |  |  |  |  | 5.5158e-08 | 158.2135 | 8.7267e-06
121961520 | E | LC | ETL.5660.INSL | 40844890 | CONCORD | EAST BAY | 2021-08-26 |  | ETL.5660 | SAN RAMON-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40816972 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.5158e-08 | 158.2135 | 8.7267e-06
121983026 | F | LC | ETL.2540.POLE.WOOD | 40751280 | MOSSLNDG | CENTRAL COAST | 2021-09-01 |  | ETL.2540 | METCALF-GREEN VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40751280 | 1952-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-08-21 | Glass | Double Dead End |  |  |  |  | 0.060927 | 158.2797
122063787 | E | LC | ETL.4780.INSL | 40620237 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40594213 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0037861 | 411.6203 | 1.5584
122063787 | E | LC | ETL.4780.INSL | 40620237 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40594213 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.0037861 | 411.6203 | 1.5584
118423706 | E | LC | ETL.1240.POLE.WDPS | 44386319 | TABLEMTN | NORTH VALLEY | 2020-01-11 | 2020-04-20 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118480188 | E | LC | ETL.1070.POLE.WOOD | 40662358 | VICTOR | STOCKTON | 2020-01-30 | 2020-02-06 | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662358 | 1957-01-01 | Single Wood Pole | WB - Wishbone | 1957-01-01 | Polymer | Suspension |  |  |  |  | 1.8664e-05 | 3617.2195
118601787 | B | LC | ETL.7780.POLE.WOOD | 40875196 | LAKEVLLE | SONOMA | 2020-03-03 | 2020-04-21 | ETL.7780 | PHILO JCT-ELK | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40875196 |  | Single Wood Pole | T-1 - Tri Post | 2016-05-16 | Polymer | Post |  |  |  |  | 2.2395e-06 | 1842.2696
118915975 | E | LC | ETL.1330.TOWR | 40808943 | LAKEVLLE | HUMBOLDT | 2020-04-13 | 2021-05-12 | ETL.1330 | CORTINA-MENDOCINO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40808943 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00012507 | 636.4999
118915975 | E | LC | ETL.1330.TOWR | 40808943 | LAKEVLLE | HUMBOLDT | 2020-04-13 | 2021-05-12 | ETL.1330 | CORTINA-MENDOCINO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40808943 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Dead End |  |  |  |  | 0.00012507 | 636.4999
118947800 | E | LC | ETL.9340.POLE.WOOD | 40748452 | FRESNO | YOSEMITE | 2020-04-23 | 2021-04-29 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118962806 | F | LC | ETL.4750.TOWR | 40870878 | LAKEVLLE | SONOMA | 2020-04-30 | 2020-05-27 | ETL.4750 | GEYSERS #12-FULTON | Structure-Tower | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40870878 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 5.7144e-09 | 362.5293
118971590 | F | LC | ETL.2060.POLE.WOOD | 40876310 | LAKEVLLE | HUMBOLDT | 2020-04-30 | 2020-11-10 | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40876310 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 2020-07-24 | Glass | Suspension |  |  |  |  | 0.24452 | 15.8807
119047357 | E | LC | ETL.1430.INSL | 40894424 | SACTO | SACRAMENTO | 2020-05-19 | 2021-03-24 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119063705 | E | LC | ETL.1240.POLE.WDPS | 44386203 | TABLEMTN | NORTH VALLEY | 2020-05-20 | 2020-06-09 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119072797 | B | LC | ETL.6690.POLE.WOOD | 40671640 | SACTO | SACRAMENTO | 2020-05-28 | 2020-08-12 | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119084676 | F | LC | ETL.6760.POLE.WOOD | 40654095 | SACTO | SIERRA | 2020-05-28 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40654095 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.1042 | 110.8102
119100627 | E | LC | ETL.4392.INSL.CERA | 40690781 | LAKEVLLE | SONOMA | 2020-06-03 | 2021-03-30 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119113458 | E | LC | ETL.1110.POLE.WDPS | 44424455 | TABLEMTN | NORTH VALLEY | 2020-05-27 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424455 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.00075912
119113458 | E | LC | ETL.1110.POLE.WDPS | 44424455 | TABLEMTN | NORTH VALLEY | 2020-05-27 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424455 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.00075912
119115190 | E | LC | ETL.7380.POLE.WOOD | 40617420 | MOSSLNDG | CENTRAL COAST | 2020-05-29 | 2021-08-17 | ETL.7380 | LAURELES-OTTER | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40617420 |  | Single Wood Pole | FIG4W - Wood X Arm |  | Ceramic | [5 empty] | 0.49604 | 0.065148
119117949 | E | LC | ETL.8170.POLE.WOOD | 40810498 | EUREKA | HUMBOLDT | 2020-06-04 |  | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810498 |  | Single Wood Pole | Unknown |  | Ceramic | Unknown |  |  |  |  | 0.014663 | 348.0238 | 5.1029
119127403 | F | LC | ETL.1430.TOWR | 40815440 | SACTO | SIERRA | 2020-06-04 | 2021-03-08 | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40815440 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.00043136 | 1328.8579
119132553 | F | LC | ETL.8290.POLE.WOOD | 40759051 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2020-11-09 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40759051 |  | Single Wood Pole | T2N | 2021-04-21 | Polymer | Post |  |  |  |  | 0.0014473 | 762.0938
119142592 | E | LC | ETL.9340.POLE.WOOD | 40595607 | FRESNO | FRESNO | 2020-06-10 | 2021-08-02 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40595607 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.011412 | 5176.5
119148973 | F | LC | ETL.4392.TOWR | 40605188 | LAKEVLLE | SONOMA | 2020-06-11 | 2021-01-28 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40605188 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | [5 empty] | 5.8043e-07 | 2581.509
119156221 | F | LC | ETL.3740.TOWR | 40746110 | CONCORD | DIABLO | 2020-06-08 | 2021-04-20 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746110 | 1958-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-03-16 | Glass | Dead End |  |  |  |  | 0.016333 | 0.065153
119156221 | F | LC | ETL.3740.TOWR | 40746110 | CONCORD | DIABLO | 2020-06-08 | 2021-04-20 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746110 | 1958-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.016333 | 0.065153
119159080 | B | LC | ETL.6760.POLE.NWOD | 40816309 | SACTO | SIERRA | 2020-06-09 | 2020-08-31 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40816309 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.012437 | 110.7947
119161721 | E | LC | ETL.5630.TOWR | 40804249 | TABLEMTN | NORTH VALLEY | 2020-06-11 | 2021-04-19 | ETL.5630 | ROCK CREEK-POE | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40804249 | 1968-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1968-01-01 | Ceramic | Other |  |  |  |  | 0.00022621 | 5962.8364
119166300 | F | LC | ETL.6280.POLE.WOOD | 40600571 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2021-09-14 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40600571 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 4.3117e-05 | 490.3705
119168933 | E | LC | ETL.1350.INSL | 40834727 | TABLEMTN |  | 2020-06-15 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Damper-Wood | Missing | [Install, Completed] | Tier2 |  |  | COMP
119173302 | E | LC | ETL.6440.POLE.WOOD | 41144196 | TABLEMTN | NORTH VALLEY | 2020-06-16 | 2020-09-03 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119173602 | E | LC | ETL.8650.TOWR | 40688818 | FRESNO | FRESNO | 2020-06-16 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 |  |  | DLFL
119174963 | F | LC | ETL.6280.POLE.WOOD | 40591763 | TABLEMTN | NORTH VALLEY | 2020-06-16 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40591763 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 4.8782e-06 | 39.6059
119175030 | F | LC | ETL.8170.POLE.WDPS | 44565475 | EUREKA | HUMBOLDT | 2020-06-12 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44564295 | 2010-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0020266 | 68.0753
119179786 | F | LC | ETL.2450.TOWR | 40742657 | PISMOBCH | LOS PADRES | 2020-06-15 |  | ETL.2450 | MESA-SANTA MARIA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40742657 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-02-19 | Glass | Dead End |  |  |  |  | 2.1826e-07 | 969.1475 | 0.00021153
119179786 | F | LC | ETL.2450.TOWR | 40742657 | PISMOBCH | LOS PADRES | 2020-06-15 |  | ETL.2450 | MESA-SANTA MARIA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40742657 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Porcelain | Dead End |  |  |  |  | 2.1826e-07 | 969.1475 | 0.00021153
119180890 | F | LC | ETL.6280.POLE.WOOD | 40815736 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-08-02 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | DLFL
119187546 | E | LC | ETL.8210.POLE.WOOD | 40903819 | VICTOR | STOCKTON | 2020-06-16 | 2021-08-30 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40903819 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.027516 | 2645.9873
119228110 | E | LC | ETL.9330.TOWR | 40606329 | FRESNO | FRESNO | 2020-06-25 |  | ETL.9330 | WISHON-COPPERMINE | Structure-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40606329 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 7.985e-05
119232974 | E | LC | ETL.1240.POLE.WOOD | 40650390 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2020-07-29 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650390 | 1993-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1993-01-01 | Polymer | Double Dead End |  |  |  |  | 2.0398e-08 | 8495.9658
119291712 | E | LC | ETL.1440.POLE.WDPS | 44768899 | SACTO | SACRAMENTO | 2020-07-01 | 2020-07-28 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP | [12 empty] | 79.1687
119302513 | E | LC | ETL.6880.POLE.WOOD | 40905729 | LAKEVLLE | SONOMA | 2020-07-02 | 2021-10-27 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40905729 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.023658 | 3880.3723 | 91.8005
119304604 | F | LC | ETL.7030.POLE.WOOD | 40617098 | TABLEMTN | NORTH VALLEY | 2020-07-02 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40617098 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0057941 | 31.7022
119305373 | E | LC | ETL.1400.POLE.WDPS | 44770780 | VICTOR | STOCKTON | 2020-07-01 | 2021-05-14 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40643720 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0016287 | 5031.312
119308521 | E | LC | ETL.4393.POLE.WDPS | 44172237 | SACTO | SACRAMENTO | 2020-06-30 | 2021-04-06 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119310908 | F | LC | ETL.6290.POLE.WOOD | 40588932 | TABLEMTN | NORTH VALLEY | 2020-07-03 | 2021-10-25 | ETL.6290 | CARIBOU-PLUMAS JCT | Vegetation | Overgrown | [Trim, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40588932 | 1958-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1973-01-01 | Polymer | Post |  |  |  |  | 0.031062 | 0.066432 | 0.0020635
119324564 | E | LC | ETL.1650.POLE.WOOD | 40861189 | LAKEVLLE | SONOMA | 2020-07-07 | 2021-02-09 | ETL.1650 | GEYSERS #3-CLOVERDALE | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40861189 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1976-01-01 | Polymer | Suspension |  |  |  |  | 4.8968e-05 | 2677.4683
119339744 | F | LC | ETL.6280.POLE.NWOD | 44259020 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44259020 | 2020-07-21 | Light Duty Steel Pole | T2N | 2020-07-21 | Polymer | Post |  |  |  |  | 3.0043e-08 | 158.2282
119341431 | E | LC | ETL.8170.POLE.WDPS | 44420677 | EUREKA | HUMBOLDT | 2020-07-09 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44420674 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.013863 | 126.6368 | 1.7556
119351275 | E | LC | ETL.6470.POLE.WOOD | 40760713 | SACTO | SIERRA | 2020-07-08 | 2021-07-29 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [12 empty] | 680.261
119354668 | E | LC | ETL.7590.POLE.WOOD | 40612267 | MOSSLNDG | CENTRAL COAST | 2020-07-10 | 2020-09-24 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119354744 | E | LC | ETL.1480.TOWR | 40857279 | LAKEVLLE | SACRAMENTO | 2020-07-10 | 2021-07-12 | ETL.1480 | EAGLE ROCK-REDBUD | Vegetation | Overgrown | [Trim, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857279 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Polymer | Suspension |  |  |  |  | 0.0059282 | 585.3354
119356173 | E | LC | ETL.5970.TOWR | 40863573 | PISMOBCH | LOS PADRES | 2020-07-10 | 2021-04-29 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863573 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-04-24 | Glass Silicone Coated | Suspension |  |  |  |  | 7.4829e-09 | 5049.7915
119359548 | F | LC | ETL.7030.POLE.WOOD | 40617095 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-02-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40617095 |  | Single Wood Pole | T2N | 2018-11-30 | Polymer | Post |  |  |  |  | 0.017961 | 94.9762
119359554 | E | LC | ETL.7030.POLE.WOOD | 40770737 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-07-08 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40770737 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.017387 | 94.9762
119364333 | E | LC | ETL.1430.TOWR | 40647572 | SACTO | SACRAMENTO | 2020-07-13 | 2021-01-28 | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40647572 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2015-08-13 | Ceramic | Suspension |  |  |  |  | 0.0029035 | 1993.4753
119366566 | E | LC | ETL.7490.POLE.WOOD | 40877972 | EUREKA | HUMBOLDT | 2020-07-14 | 2021-08-17 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877972 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Post |  |  |  |  | 0.031141 | 126.5956
119367187 | E | LC | ETL.7590.POLE.WOOD | 40665297 | MOSSLNDG | CENTRAL COAST | 2020-07-14 | 2021-01-12 | ETL.7590 | MONTA VISTA-BURNS | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119368083 | F | LC | ETL.7030.POLE.WOOD | 40600152 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-02-11 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40600152 |  | Single Wood Pole | T2N | 2021-07-07 | Polymer | Post |  |  |  |  | 0.048615 | 95.178
119369384 | F | LC | ETL.6380.POLE.WOOD | 40862758 | LAKEVLLE | SONOMA | 2020-07-14 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40862758 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Other |  |  |  |  | 2.7394e-09 | 2536.9316
119372491 | F | LC | ETL.7030.POLE.WOOD | 40592095 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40592095 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.014004 | 94.9762
119376763 | E | LC | ETL.1440.POLE.WDPS | 44837694 | SACTO | SACRAMENTO | 2020-07-14 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40654770 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00051276 | 1819.4475
119380753 | B | LC | ETL.6222.POLE.WOOD | 40769635 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6222 | FORT SEWARD TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40769635 | 1952-01-01 | Single Wood Pole | SVDE - Single Vertical Dead End | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 0.010013 | 3041.9922 | 30.4587
119481378 | F | LC | ETL.6290.POLE.NWOD | 44883383 | TABLEMTN | NORTH VALLEY | 2020-07-21 | 2021-11-18 | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44883383 | 2020-02-03 | Light Duty Steel Pole | T2N | 2020-02-03 | Polymer | Post |  |  |  |  | 0.1643 | 63.4948
119483778 | F | LC | ETL.6890.POLE.WOOD | 40759712 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-09-23 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40759712 | 1986-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0015447 | 981.3776
119487580 | F | LC | ETL.8170.POLE.NWOD | 44366780 | EUREKA | HUMBOLDT | 2020-07-21 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44366780 | 2013-11-26 | Light Duty Steel Pole | T-1 - Tri Post | 2013-11-26 | Polymer | Post |  |  |  |  | 0.00041215 | 632.9359
119492947 | F | LC | ETL.1400.POLE.WDPS | 44771110 | VICTOR | STOCKTON | 2020-07-22 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40684273 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.003691 | 2278.3794
119493448 | F | LC | ETL.1110.POLE.WDPS | 44423386 | TABLEMTN | HUMBOLDT | 2020-07-22 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
119494309 | E | LC | ETL.9200.POLE.WOOD | 40763589 | MIDWAY | KERN | 2020-07-22 | 2021-05-18 | ETL.9200 | TAFT-CUYAMA #1 | Damper-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | DLFL | 40763589 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Ceramic | Pin |  |  |  |  | 0.024326
119495291 | E | LC | ETL.9200.POLE.WDPS | 44976204 | MIDWAY | KERN | 2020-07-22 | 2021-08-23 | ETL.9200 | TAFT-CUYAMA #1 | Anchor-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 42696685 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.014778
119517497 | E | LC | ETL.6480.POLE.WOOD | 44695489 | SACTO | SACRAMENTO | 2020-07-28 | 2021-06-29 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44695489 | 2018-12-10 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-12-10 | Polymer | Dead End |  |  |  |  | 0.073313 | 664.4426
119553972 | F | LC | ETL.1400.POLE.WOOD | 40587142 | VICTOR | STOCKTON | 2020-08-03 | 2021-03-18 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587142 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0094261
119553972 | F | LC | ETL.1400.POLE.WOOD | 40587142 | VICTOR | STOCKTON | 2020-08-03 | 2021-03-18 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587142 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0094261
119553972 | F | LC | ETL.1400.POLE.WOOD | 40587142 | VICTOR | STOCKTON | 2020-08-03 | 2021-03-18 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587142 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0094261
119558576 | F | LC | ETL.7490.POLE.WOOD | 40662189 | EUREKA | HUMBOLDT | 2020-08-04 | 2021-08-05 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40662189 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.19839 | 142.4245
119576845 | F | LC | ETL.1073.POLE.STPS | 44385274 | VICTOR | STOCKTON | 2020-08-07 | 2021-04-19 | ETL.1073 | MI-WUK-CURTIS | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] |  | Tier 3 | Within Both | COMP | 44385273 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.995e-06 | 15.88
119599422 | F | LC | ETL.6520.POLE.WOOD | 42562723 | SACTO | SACRAMENTO | 2020-08-11 |  | ETL.6520 | COLGATE-SMARTVILLE #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 |  |  | PEND
119612480 | B | LC | ETL.8650.TOWR | 40584411 | FRESNO | FRESNO | 2020-08-13 | 2020-12-09 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40584411 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1929-01-01 | Porcelain | Suspension |  |  |  |  | 0.0033644 | 6915.5117
119615964 | A | LC | ETL.7510.INSL | 40915462 | LAKEVLLE | SONOMA | 2020-08-14 | 2020-10-16 | ETL.7510 | MENDOCINO-HARTLEY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119617626 | E | LC | ETL.3500.TOWR | 40643017 | VICTOR | STOCKTON | 2020-08-14 | 2021-06-28 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40643017 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 0.0013941 | 6523.0078
119631737 | F | LC | ETL.6870.POLE.WOOD | 40751844 | SACTO | SIERRA | 2020-08-18 | 2021-09-27 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40751844 | 1966-01-01 | Single Wood Pole | T2N | 2021-04-10 | Polymer | Post |  |  |  |  | 0.080528 | 110.8481
119632394 | E | LC | ETL.6870.POLE.WOOD | 40824463 | SACTO | SIERRA | 2020-08-18 | 2021-05-20 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40824463 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.25484 | 63.386
119636107 | E | LC | ETL.3500.TOWR | 40744676 | VICTOR | STOCKTON | 2020-08-19 | 2021-08-17 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40744676 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-08-05 | Glass | Dead End |  |  |  |  | 2.5653e-06 | 1186.6569
119644993 | B | LC | ETL.8650.TOWR | 40859245 | FRESNO | FRESNO | 2020-08-20 | 2020-12-09 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40859245 | 1929-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0044388 | 5662.9517
119655745 | E | LC | ETL.6520.POLE.WOOD | 40771345 | SACTO | SIERRA | 2020-06-18 | 2021-06-24 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
119667284 | B | LC | ETL.7180.POLE.WOOD | 40877622 | LAKEVLLE | NORTH BAY | 2020-08-24 | 2020-11-04 | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119676497 | E | LC | ETL.7560.POLE.WOOD | 40913140 | SACTO | SACRAMENTO | 2020-08-26 | 2021-04-05 | ETL.7560 | WEIMAR #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40913140 |  | Single Wood Pole | T2N | 2021-03-29 | Polymer | Post |  |  |  |  | 0.14681 | 2768.4309
119699973 | B | LC | ETL.1130.INSL.CERA | 40773104 | CONCORD | EAST BAY | 2020-08-29 | 2020-10-28 | ETL.1130 | BRIGHTON-CLAYTON #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119708996 | B | LC | ETL.8350.POLE.NWOD | 44331432 | VICTOR | STOCKTON | 2020-09-03 | 2020-11-19 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44331432 | 2016-12-23 | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 4.0858e-05 | 300.6168
119710787 | A | LC | ETL.6240.POLE.WOOD | 40599247 | MOSSLNDG | CENTRAL COAST | 2020-09-03 | 2020-10-13 | ETL.6240 | BURNS-LONE STAR #2 | Conductor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.5743 | 11.1402
119714416 | E | LC | ETL.6290.POLE.WOOD | 40599506 | TABLEMTN | NORTH VALLEY | 2020-08-31 | 2021-11-15 | ETL.6290 | CARIBOU-PLUMAS JCT | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40599506 | 2010-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.060069 | 3179.5974
119718596 | E | LC | ETL.1330.TOWR | 40861866 | LAKEVLLE | HUMBOLDT | 2020-07-28 | 2021-04-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | Missing | [Install, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861866 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-10 | Glass | Suspension |  |  |  |  | 1.1521e-05 | 2815.7427
119718596 | E | LC | ETL.1330.TOWR | 40861866 | LAKEVLLE | HUMBOLDT | 2020-07-28 | 2021-04-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | Missing | [Install, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861866 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-03-31 | Glass | Suspension |  |  |  |  | 1.1521e-05 | 2815.7427
119720836 | E | LC | ETL.1730.INSL.CERA | 40641667 | MOSSLNDG | CENTRAL COAST | 2020-07-28 | 2021-02-09 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator | Contaminated | [Helicopter Wash] | Tier3 | Tier 3 | Within Both | DLFL | 40618416 | 1972-01-01 | Single Wood Pole | WB - Wishbone | 1972-01-01 | Porcelain | Dead End |  |  |  |  | 0.00023803 | 0.065147
119723032 | B | LC | ETL.6760.INSL.NCER | 40798729 | SACTO | SACRAMENTO | 2020-08-04 | 2020-11-12 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767231 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.14981 | 47.5526
119723220 | A | LC | ETL.6240.POLE.WOOD | 40593143 | MOSSLNDG | CENTRAL COAST | 2020-09-07 | 2020-10-13 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593143 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.32393 | 110.8153
119740886 | F | LC | ETL.6480.POLE.WOOD | 40824364 | SACTO | NORTH VALLEY | 2020-09-08 | 2021-02-12 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
119770063 | B | LC | ETL.6870.INSL | 40780092 | SACTO | SACRAMENTO | 2020-09-15 | 2020-10-06 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751848 | 2000-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 2000-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.022125 | 63.386
119772373 | E | LC | ETL.2060.POLE.WDPS | 44558398 | LAKEVLLE | HUMBOLDT | 2020-06-23 | 2021-09-07 | ETL.2060 | FORT BRAGG-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44557846 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.13578 | 427.7922
119778285 | F | LC | ETL.6760.POLE.WOOD | 40693452 | SACTO | SIERRA | 2020-08-04 | 2021-02-12 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40693452 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.056029 | 949.3081
119780715 | F | LC | ETL.8240.POLE.WOOD | 40876091 | VICTOR | STOCKTON | 2020-09-12 |  | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40876091 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0055541 | 1550.8043
119786031 | E | LC | ETL.7490.POLE.WOOD | 40811059 | EUREKA | HUMBOLDT | 2020-09-11 | 2021-08-30 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 189.8608
119787719 | F | LC | ETL.4221.POLE.STPS | 44374336 | TABLEMTN |  | 2020-09-17 |  | ETL.4221 | SLY CREEK TAP | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | PEND | 44374335 | 2016-11-27 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.3641e-07 | 490.5099
119806910 | F | LC | ETL.7390.POLE.WOOD | 40577254 | LAKEVLLE | HUMBOLDT | 2020-08-11 | 2021-09-28 | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40577254 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.0092385
119810039 | F | LC | ETL.6280.POLE.NWOD | 44688365 | TABLEMTN | NORTH VALLEY | 2020-08-25 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44688365 | 2018-11-24 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-24 | Polymer | Post |  |  |  |  | 1.2266e-06 | 5239.1455
119819149 | F | LC | ETL.8490.TOWR | 40606014 | PISMOBCH | LOS PADRES | 2020-09-14 | 2020-12-17 | ETL.8490 | ATASCADERO-SAN LUIS OBISPO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40606014 | 1932-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0012442 | 189.8608
119829966 | B | LC | ETL.6880.POLE.WOOD | 40649341 | LAKEVLLE | NORTH BAY | 2020-09-29 | 2020-10-16 | ETL.6880 | FULTON-CALISTOGA | Emergency | Fire | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40649341 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.00074138 | 1321.0878
119839365 | B | LC | ETL.6880.POLE.WOOD | 40658466 | LAKEVLLE | NORTH BAY | 2020-09-30 | 2020-10-15 | ETL.6880 | FULTON-CALISTOGA | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119910984 | E | LC | ETL.5960.TOWR | 40659976 | PISMOBCH | LOS PADRES | 2020-10-15 | 2021-08-31 | ETL.5960 | DIABLO-GATES #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40659976 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-05-05 | Glass Silicone Coated | Suspension |  |  |  |  | 2.3954e-07 | 619.8801
119911325 | F | LC | ETL.8365.POLE.NWOD | 40906632 | EUREKA | HUMBOLDT | 2020-10-13 | 2021-02-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40906632 | 2010-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0017588
119916971 | F | LC | ETL.7030.POLE.WOOD | 40816888 | TABLEMTN | NORTH VALLEY | 2020-09-19 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40816888 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.019705 | 0.06515
119929385 | B | LC | ETL.5980.TOWR | 40820145 | PISMOBCH | LOS PADRES | 2020-10-20 | 2020-12-21 | ETL.5980 | DIABLO-MIDWAY #3 | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40820145 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2005-01-01 | Ceramic | Suspension |  |  |  |  | 8.7172e-11 | 2358.626
119946805 | E | LC | ETL.7160.TOWR | 40770152 | LAKEVLLE | SONOMA | 2020-10-26 |  | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Vegetation | Overgrown | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40770152 |  | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Polymer | [5 empty] | 0.016508 | 71.3735 | 1.1782
119985645 | E | LC | ETL.8170.POLE.WOOD | 44948568 | EUREKA | HUMBOLDT | 2020-11-05 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44948568 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | Dead End |  |  |  |  | 0.038532 | 6300.0015 | 242.7489
120091491 | E | LC | ETL.1450.POLE.WDPS | 44553571 | SACTO | SACRAMENTO | 2020-09-10 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Rotten | [Replace] |  | Tier 2 | Within Both | PEND | 44553219 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0002956 | 31.7066 | 0.0093726
120107805 | E | LC | ETL.3180.INSL | 40773416 | CONCORD | EAST BAY | 2020-11-19 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40746029 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 2.6332e-05 | 47.7671 | 0.0012578
120107805 | E | LC | ETL.3180.INSL | 40773416 | CONCORD | EAST BAY | 2020-11-19 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40746029 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 2.6332e-05 | 47.7671 | 0.0012578
120119202 | E | LC | ETL.1401.INSL.NCER | 42834650 | VICTOR | STOCKTON | 2020-11-25 | 2021-06-01 | ETL.1401 | BEARDSLEY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120119202 | E | LC | ETL.1401.INSL.NCER | 42834650 | VICTOR | STOCKTON | 2020-11-25 | 2021-06-01 | ETL.1401 | BEARDSLEY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120124648 | F | LC | ETL.6720.POLE.WDPS | 44926545 | TABLEMTN | NORTH VALLEY | 2020-12-03 | 2021-04-19 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | DLFL | 42578821 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 6.5736e-05 | 949.264
120240992 | F | LC | ETL.4440.POLE.NWOD | 40870137 | TABLEMTN | NORTH VALLEY | 2020-12-04 |  | ETL.4440 | CARIBOU-TABLE MTN | Structure-Steel | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40870137 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle | 2019-05-13 | Glass | Dead End |  |  |  |  | 3.7729e-12 | 713.1375
120241323 | F | LC | ETL.4440.POLE.NWOD | 41162691 | TABLEMTN | NORTH VALLEY | 2020-12-04 |  | ETL.4440 | CARIBOU-TABLE MTN | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 41162691 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | Dead End |  |  |  |  | 4.1027e-12 | 713.1375
120485827 | E | LC | ETL.1420.TOWR | 40865474 | SACTO | SIERRA | 2021-02-01 | 2021-11-30 | ETL.1420 | DRUM-RIO OSO #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40865474 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-08-08 | Porcelain | Dead End |  |  |  |  | 2.2971e-07 | 1360.4569 | 0.00031251
120572024 | E | LC | ETL.6710.POLE.WOOD | 40659335 | MOSSLNDG | CENTRAL COAST | 2021-02-24 |  | ETL.6710 | DEL MONTE-VIEJO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40659335 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.047119 | 0.066432 | 0.0031302
120673278 | F | LC | ETL.4920.TOWR | 40870810 | LAKEVLLE | SONOMA | 2021-03-22 |  | ETL.4920 | IGNACIO-SOBRANTE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40870810 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.00049843 | 174.8163 | 0.087134
120675004 | E | LC | ETL.8340.POLE.WOOD | 40577122 | SACTO | SACRAMENTO | 2021-03-22 |  | ETL.8340 | WEIMAR-HALSEY | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40577122 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 6.4283e-05 | 0.06515 | 4.188e-06
120690530 | F | LC | ETL.6760.POLE.WOOD | 40913014 | SACTO | SACRAMENTO | 2021-03-25 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40913014 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.0059002 | 4000.8238
120701212 | E | LC | ETL.6979.POLE.WDPS | 44312208 | LAKEVLLE | SONOMA | 2021-03-27 |  | ETL.6979 | MONTE RIO-FORT ROSS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44312206 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0013572 | 126.7015 | 0.17196
120706532 | E | LC | ETL.7140.POLE.STPS | 44874798 | LAKEVLLE | SONOMA | 2021-03-29 | 2021-06-08 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44870392 | 2019-05-10 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0031723 | 553.9316
120706579 | E | LC | ETL.1710.POLE.WDPS | 44510612 | MOSSLNDG | CENTRAL COAST | 2021-03-29 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44509644 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0021389 | 63.3245 | 0.13544
120735490 | E | LC | ETL.4393.TOWR | 41162645 | SACTO | SACRAMENTO | 2021-04-02 |  | ETL.4393 | DRUM-HIGGINS | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41162645 |  | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2016-06-14 | Ceramic | Dead End |  |  |  |  | 3.2338e-06 | 838.4462 | 0.0027114
120750243 | E | LC | ETL.3830.TOWR | 40756401 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40756401 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.9665e-07 | 5398.1479 | 0.0010616
120752714 | E | LC | ETL.1070.INSL.NCER | 40621180 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40580899 | 1957-01-01 | Single Wood Pole | WB - Wishbone | 1957-01-01 | Polymer | Dead End |  |  |  |  | 2.9871e-05 | 2393.3862 | 0.071492
120756837 | E | LC | ETL.1720.INSL.NCER | 40635160 | MOSSLNDG | SAN JOSE | 2021-03-23 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Hardware-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40601496 | 1948-01-01 | Single Wood Pole | T-1 - Tri Post | 1948-01-01 | Polymer | Suspension |  |  |  |  | 0.00021136 | 2341.6399 | 0.49492
120761525 | E | LC | ETL.1440.POLE.STPS | 45014869 | SACTO | SACRAMENTO | 2021-04-06 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45014846 | 2020-06-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.9369e-06 | 205.7724 | 0.00039856
120765688 | B | LC | ETL.5980.TOWR | 40576868 | PISMOBCH | LOS PADRES | 2021-04-08 | 2021-06-01 | ETL.5980 | DIABLO-MIDWAY #3 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40576868 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.3901e-07 | 1725.3241
120803407 | E | LC | ETL.3820.INSL.CERA | 40630089 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40589038 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 5.4919e-05 | 4843.4395 | 0.266
120811557 | F | LC | ETL.9100.POLE.WOOD | 44191218 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191218 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 2.9458e-05 | 1523.1348
120812131 | F | LC | ETL.9100.POLE.WOOD | 44191233 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191233 |  | Single Wood Pole | 3HP - 3 Horizontal Post |  | Porcelain | [5 empty] | 6.1039e-06 | 2059.4562
120833768 | E | LC | ETL.6760.POLE.WOOD | 40874729 | SACTO | SACRAMENTO | 2021-04-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Rotten | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40874729 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.028839 | 94.9894 | 2.7394
120834073 | F | LC | ETL.6760.POLE.NWOD | 45072092 | SACTO | SACRAMENTO | 2021-04-17 | 2021-06-15 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 45072092 | 2019-08-05 | Light Duty Steel Pole | T2N | 2019-08-05 | Polymer | Post |  |  |  |  | 0.0032542 | 94.9894
120842745 | E | LC | ETL.4040.POLE.STPS | 44647131 | TABLEMTN | NORTH VALLEY | 2021-04-19 | 2021-09-20 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44646867 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 9.0045e-05 | 538.1084
120848787 | E | LC | ETL.2780.INSL | 40850662 | CONCORD | EAST BAY | 2021-04-19 | 2021-05-04 | ETL.2780 | MORAGA-SAN LEANDRO #2 | Splice-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
120865328 | E | LC | ETL.3500.TOWR | 40579792 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40579792 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.053654 | 5982.1558 | 320.9636
120867067 | B | LC | ETL.6870.POLE.WOOD | 40586044 | SACTO | SACRAMENTO | 2021-04-22 | 2021-05-05 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40586044 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post | 1966-01-01 | Ceramic | Post |  |  |  |  | 0.14453 | 126.6562
120873136 | E | LC | ETL.1820.POLE.WDPS | 44557507 | EUREKA | HUMBOLDT | 2021-04-23 |  | ETL.1820 | HUMBOLDT-TRINITY | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44554046 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.46162 | 47.5118 | 21.9324
120874054 | B | LC | ETL.1250.INSL.NCER | 40684549 | FRESNO | FRESNO | 2021-04-22 | 2021-05-26 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40655091 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0034423 | 5793.8223
120874305 | F | LC | ETL.6470.POLE.WOOD | 40602487 | SACTO | SACRAMENTO | 2021-04-23 | 2021-08-17 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602487 |  | Single Wood Pole | T2N | 2021-08-07 | Polymer | Post |  |  |  |  | 0.0090941 | 5857.8857
120874667 | E | LC | ETL.6470.POLE.WOOD | 40818474 | SACTO | SACRAMENTO | 2021-04-23 | 2021-08-17 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818474 |  | Single Wood Pole | T2N | 2021-08-09 | Polymer | Post |  |  |  |  | 0.01079 | 5778.0215
120878641 | E | LC | ETL.3830.TOWR | 40818418 | VICTOR | STOCKTON | 2021-04-24 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40818418 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 0.00018831 | 428.7104 | 0.08073
120886769 | F | LC | ETL.5490.TOWR | 40746311 | CONCORD | DIABLO | 2021-04-26 |  | ETL.5490 | PITTSBURG-SAN RAMON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40746311 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.00040638 | 3561.409 | 1.4473
120889536 | E | LC | ETL.1820.POLE.WDPS | 44560464 | EUREKA | HUMBOLDT | 2021-04-27 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560132 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.91082 | 284.7712 | 259.3747
120904186 | E | LC | ETL.6890.POLE.WOOD | 40587004 | LAKEVLLE | SONOMA | 2021-04-29 |  | ETL.6890 | FULTON-HOPLAND | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | PEND | 40587004 | 1994-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 7.1027e-05 | 3311.1438 | 0.23518
120912644 | E | LC | ETL.6470.POLE.WOOD | 40868952 | SACTO | SACRAMENTO | 2021-05-01 | 2021-08-05 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40868952 |  | Single Wood Pole | T2N | 2021-07-19 | Polymer | Post |  |  |  |  | 0.07305 | 221.5243
120914653 | E | LC | ETL.5930.TOWR | 40817041 | LAKEVLLE | DIABLO | 2021-05-01 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40817041 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 2.9568e-09 | 1692.6119 | 5.0046e-06
120919777 | E | LC | ETL.9100.INSL.CERA | 44189036 | PISMOBCH | LOS PADRES | 2021-05-01 | 2021-06-29 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
120951461 | E | LC | ETL.6890.INSL.NCER | 40722348 | LAKEVLLE | SONOMA | 2021-05-07 |  | ETL.6890 | FULTON-HOPLAND | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | PEND | 40677876 | 1997-01-01 | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 0.00068671 | 395.8061 | 0.2718
120995770 | E | LC | ETL.7550.POLE.WOOD | 40769190 | LAKEVLLE | SONOMA | 2021-05-08 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40769190 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0041877 | 0.065148 | 0.00027282
121191583 | E | LC | ETL.1820.POLE.WDPS | 44562819 | EUREKA | HUMBOLDT | 2021-05-11 |  | ETL.1820 | HUMBOLDT-TRINITY | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562419 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.99958 | 395.8017 | 395.6336
121325395 | F | LC | ETL.4393.TOWR | 40809704 | SACTO | SIERRA | 2021-05-12 |  | ETL.4393 | DRUM-HIGGINS | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40809704 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [6 empty] | 1914.2439
121328171 | B | LC | ETL.7490.INSL | 40699907 | EUREKA | HUMBOLDT | 2021-05-13 | 2021-07-29 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
121329015 | E | LC | ETL.5540.TOWR | 40866655 | TABLEMTN | NORTH VALLEY | 2021-04-21 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40866655 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | Suspension |  |  |  |  | 1.0068e-06 | 6375.1865 | 0.0064186
121330763 | F | LC | ETL.2790.TOWR | 40808549 | CONCORD | DIABLO | 2021-04-19 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40808549 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.379e-06 | 31.6978 | 0.00010711
121336148 | B | LC | ETL.1820.POLE.WDPS | 44560508 | EUREKA | HUMBOLDT | 2021-05-14 | 2021-06-01 | ETL.1820 | HUMBOLDT-TRINITY | Other | Land/Enviro Issue | [Access Issue, Completed] |  | Tier 2 | Within Both | COMP | 44560123 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.068104 | 1028.5986
121338878 | E | LC | ETL.1420.TOWR | 40596168 | SACTO | SIERRA | 2021-04-28 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40596168 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.00096281 | 4276.3892 | 4.1173
121354532 | B | LC | ETL.8060.INSL.NCER | 40628953 | SACTO | SACRAMENTO | 2021-05-18 | 2021-07-26 | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602252 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.072051 | 427.2245
121355832 | F | LC | ETL.5300.TOWR | 40753279 | PISMOBCH | LOS PADRES | 2021-04-23 | 2021-05-20 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40753279 | 1960-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 1.0639e-07 | 6657.8584
121361049 | F | LC | ETL.4870.TOWR | 40576892 | FRESNO | FRESNO | 2021-05-19 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576892 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.1932e-07 | 6105.1958 | 0.0031705
121372146 | E | LC | ETL.1610.SWIT | 43242937 | LAKEVLLE | SONOMA | 2021-05-17 |  | ETL.1610 | SILVERADO-FULTON JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | PEND | [8 empty] | Unknown | NO ATTACHMENTS | Manual
121376525 | E | LC | ETL.6760.POLE.WOOD | 40766668 | SACTO | SIERRA | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40766668 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.033304 | 15.8837 | 0.52899
121379648 | E | LC | ETL.1420.TOWR | 40746548 | SACTO | SIERRA | 2021-05-06 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40746548 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.00058562 | 4100.3613 | 2.4012
121380217 | F | LC | ETL.4850.TOWR | 40660155 | FRESNO | FRESNO | 2021-05-07 |  | ETL.4850 | HAAS-MCCALL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40660155 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1957-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.5955e-07 | 7336.5786 | 0.0019042
121381900 | E | LC | ETL.6500.POLE.WOOD | 40767109 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40767109 |  | Single Wood Pole | T2N | 2018-06-29 | Polymer | Post |  |  |  |  | 0.0018074 | 476.5182 | 0.86128
121384723 | E | LC | ETL.4393.TOWR | 40809702 | SACTO | SIERRA | 2021-05-12 |  | ETL.4393 | DRUM-HIGGINS | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40809702 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 0.00011288 | 364.0427 | 0.041092
121403324 | F | LC | ETL.7212.POLE.WOOD | 40823352 | METCALF | PENINSULA | 2021-05-19 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40823352 |  | Single Wood Pole | WB - Wishbone | 2019-10-30 | Glass | Suspension |  |  |  |  | 0.41916 | 1092.5157
121404517 | E | LC | ETL.7560.POLE.WOOD | 40913134 | SACTO | SIERRA | 2021-05-20 |  | ETL.7560 | WEIMAR #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40913134 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.181 | 3606.8623 | 652.8396
121406169 | E | LC | ETL.7060.POLE.NWOD | 43250001 | METCALF | PENINSULA | 2021-05-17 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 43250001 | 2008-01-01 | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0018356 | 981.1414 | 1.801
121417433 | E | LC | ETL.6220.INSL.CERA | 40886394 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40862826 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.013422 | 633.9066 | 8.5084
121419812 | E | LC | ETL.7212.POLE.WOOD | 44799075 | METCALF | PENINSULA | 2021-05-27 | 2021-08-18 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44799075 | 2019-07-01 | Single Wood Pole | T-1 - Tri Post | 2019-07-01 | Polymer | Post |  |  |  |  | 0.17472 | 1060.9368
121428520 | E | LC | ETL.1400.POLE.WDPS | 44774112 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40803727 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00050457 | 79.1724 | 0.039948
121451518 | F | LC | ETL.4610.POLE.NWOD | 45108808 | PISMOBCH | LOS PADRES | 2021-06-03 | 2021-08-02 | ETL.4610 | DIABLO PP STANDBY SUPPLY | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45108808 |  | Tubular Steel Pole | DDE - Double Dead End | 2020-10-26 | Glass Silicone Coated | Double Dead End | [5 empty] | 1061
121474247 | E | LC | ETL.6750.POLE.WDPS | 44209117 | TABLEMTN | NORTH VALLEY | 2021-06-05 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44209114 | 2014-05-08 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.3657e-05 | 142.4582 | 0.0062192
121492097 | E | LC | ETL.3750.TOWR | 40804878 | CONCORD | DIABLO | 2021-06-08 | 2021-09-01 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | HFRA Removal | COMP | 40804878 | 1932-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 1.2388e-06 | 15.88
121493230 | E | LC | ETL.4550.TOWR | 40678293 | TABLEMTN | NORTH VALLEY | 2021-06-01 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40678293 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.545e-07 | 3787.772 | 0.0021003
121516444 | E | LC | ETL.4040.POLE.STPS | 44202855 | TABLEMTN | NORTH VALLEY | 2021-06-04 |  | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44202852 | 2015-06-09 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.1943e-05 | 4067.0386 | 0.12991
121516500 | F | LC | ETL.6870.POLE.NWOD | 44340603 | SACTO | SIERRA | 2021-06-05 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44340603 | 2014-10-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2014-10-01 | Non Ceramic | Dead End |  |  |  |  | 0.0052763 | 125.0754
121521040 | F | LC | ETL.7820.POLE.WOOD | 40808408 | LAKEVLLE | HUMBOLDT | 2021-06-03 | 2021-07-27 | ETL.7820 | POTTER VALLEY-WILLITS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808408 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-07-15 | Glass | Double Dead End |  |  |  |  | 8.0913e-05 | 885.9953
121523492 | F | LC | ETL.8170.POLE.WOOD | 40862464 | EUREKA | HUMBOLDT | 2021-06-11 | 2021-09-23 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40862464 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.011192 | 6461.5288
121540058 | B | LC | ETL.4393.POLE.WOOD | 44202753 | SACTO | SIERRA | 2021-06-15 | 2021-06-23 | ETL.4393 | DRUM-HIGGINS | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44202753 | 2015-03-27 | Single Wood Pole | DV - Double Vertical | 2015-03-27 | Ceramic | Dead End |  |  |  |  | 1.3763e-05 | 269.0937
121544769 | E | LC | ETL.7260.INSL.CERA | 44651548 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.7260 | KESWICK-CASCADE | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44651530 | 2018-08-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-08-01 | Ceramic | Dead End |  |  |  |  | 0.017354
121544769 | E | LC | ETL.7260.INSL.CERA | 44651548 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.7260 | KESWICK-CASCADE | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44651530 | 2018-08-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-08-01 | Ceramic | Dead End |  |  |  |  | 0.017354
121544769 | E | LC | ETL.7260.INSL.CERA | 44651548 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.7260 | KESWICK-CASCADE | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44651530 | 2018-08-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-08-01 | Ceramic | Dead End |  |  |  |  | 0.017354
121547491 | E | LC | ETL.6222.POLE.WDPS | 44741480 | EUREKA | HUMBOLDT | 2021-06-14 |  | ETL.6222 | FORT SEWARD TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40770377 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00019902 | 714.1774 | 0.14214
121548380 | E | LC | ETL.5390.TOWR | 40872613 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40872613 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 3.464e-07 | 1569.4597 | 0.00054366
121550285 | E | LC | ETL.7390.POLE.WOOD | 40666668 | LAKEVLLE | HUMBOLDT | 2021-06-14 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40666668 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0015499
121550786 | F | LC | ETL.7990.POLE.NWOD | 44934058 | SACTO | SIERRA | 2021-06-12 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44934058 | 2020-06-30 | Light Duty Steel Pole | T-1 - Tri Post | 2020-06-30 | Polymer | Post |  |  |  |  | 2.8221e-06 | 4340.0908
121560589 | F | LC | ETL.1820.POLE.WDPS | 44562818 | EUREKA | HUMBOLDT | 2021-06-08 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44562460 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.94292 | 395.7131
121573451 | F | LC | ETL.7300.POLE.WOOD | 40701768 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.7300 | KILARC-DESCHUTES | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40701768 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2018-06-02 | Polymer | Post |  |  |  |  | 0.022614 | 301.3406 | 6.8144
121590795 | E | LC | ETL.6760.POLE.WOOD | 40611297 | SACTO | SIERRA | 2021-06-22 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40611297 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.071558 | 4399.0391 | 314.7846
121592532 | E | LC | ETL.8210.POLE.WOOD | 45106333 | VICTOR | STOCKTON | 2021-06-24 | 2021-08-19 | ETL.8210 | VALLEY SPRINGS #1 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45106333 | 2021-05-23 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-05-23 | Polymer | Dead End | [5 empty] | 1475.0956
121605680 | B | LC | ETL.4440.INSL.CERA | 40633886 | TABLEMTN | NORTH VALLEY | 2021-06-25 | 2021-08-05 | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40598125 | 1958-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 1.1216e-07 | 15.8815
121606209 | E | LC | ETL.1183.TOWR | 45098585 | LAKEVLLE | SONOMA | 2021-06-26 | 2021-09-10 | ETL.1183 | CALPINE-WEST FORD FLAT | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45098585 |  | LATTICE STEEL TOWER | Unknown |  | Unknown | Unknown | [5 empty] | 190.4918
121621161 | E | LC | ETL.7130.POLE.WDPS | 44315163 | EUREKA | HUMBOLDT | 2021-06-27 |  | ETL.7130 | HUMBOLDT-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44315160 | 2013-10-26 | 3-Pole Wood | SVDE - Single Vertical Dead End | [7 empty] | 0.0095661 | 0.065148 | 0.00062321
121641982 | F | LC | ETL.4220.POLE.WOOD | 44387623 | TABLEMTN |  | 2021-06-23 |  | ETL.4220 | WOODLEAF-PALERMO | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44387622 | 2017-09-24 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 8.2104e-05 | 537.9951
121648821 | F | LC | ETL.6760.POLE.WOOD | 40813445 | SACTO | SIERRA | 2021-06-28 | 2021-09-29 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40813445 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.049446 | 142.5076
121654474 | B | LC | ETL.4620.INSL | 40782264 | PISMOBCH | LOS PADRES | 2021-07-01 | 2021-07-06 | ETL.4620 | DIABLO-MESA | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
121655225 | E | LC | ETL.1730.POLE.WDPS | 44413228 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44413227 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00012275 | 0.065147 | 7.9965e-06
121661961 | E | LC | ETL.5250.TOWR | 40821360 | CONCORD | MISSION | 2021-06-30 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40821360 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.0556e-07 | 506.1398 | 0.00010404
121661961 | E | LC | ETL.5250.TOWR | 40821360 | CONCORD | MISSION | 2021-06-30 |  | ETL.5250 | MORAGA-CASTRO VALLEY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40821360 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 2.0556e-07 | 506.1398 | 0.00010404
121684708 | F | LC | ETL.1440.POLE.NWOD | 44930396 | SACTO | SIERRA | 2021-06-14 |  | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44930396 | 2020-05-27 | Light Duty Steel Pole | DDE - Double Dead End | 2020-05-27 | Glass | Dead End |  |  |  |  | 0.0058304 | 696.1766
121684826 | F | LC | ETL.9240.POLE.NWOD | 45127999 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45127999 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Unknown | Dead End | [5 empty] | 746.7623
121685687 | F | LC | ETL.4440.POLE.NWOD | 41162738 | TABLEMTN | NORTH VALLEY | 2021-06-27 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41162738 |  | Lattice Steel Pole | DV-DE - Double Vertical Dead End |  | Porcelain | [5 empty] | 3.2885e-13 | 1069.7238
121711923 | F | LC | ETL.1440.POLE.NWOD | 44961235 | SACTO | SIERRA | 2021-06-14 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44961235 | 2020-06-03 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-06-03 | Glass | Suspension |  |  |  |  | 1.741e-06 | 1344.8513
121724742 | F | LC | ETL.4040.POLE.STPS | 44783235 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908628 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00015408 | 2441.9417
121742267 | E | LC | ETL.6650.POLE.WDPS | 44386778 | TABLEMTN | NORTH VALLEY | 2021-07-13 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44386776 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00020417 | 237.4642 | 0.048484
121746309 | E | LC | ETL.2390.POLE.WDPS | 44390976 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44390975 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.3004e-05 | 1440.1511 | 0.061932
121747372 | E | LC | ETL.8405.POLE.WOOD | 44236040 | SACTO | SIERRA | 2021-07-16 |  | ETL.8405 | MIDDLE FORK #1 | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44236040 | 2016-02-29 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2016-02-29 | Polymer | Dead End |  |  |  |  | 0.00082897 | 6874.0736 | 5.6984
121747645 | F | LC | ETL.1820.POLE.NWOD | 44395288 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395288 | 2020-03-10 | Light Duty Steel Pole | 3P DDE - 3 Pole Double Dead End | 2020-03-10 | Glass | Dead End |  |  |  |  | 0.00048176 | 3041.8704
121749384 | E | LC | ETL.6470.POLE.WOOD | 40693549 | SACTO | SIERRA | 2021-07-17 |  | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40693549 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.16369 | 269.0426 | 44.0393
121754228 | E | LC | ETL.1710.POLE.NWOD | 45111379 | MOSSLNDG | CENTRAL COAST | 2021-07-19 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45111379 | 2017-08-23 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2017-08-23 | Polymer | Dead End | [5 empty] | 3.2281
121758750 | B | LC | ETL.6280.POLE.WOOD | 40675402 | TABLEMTN | NORTH VALLEY | 2021-07-19 | 2021-10-11 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40675402 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00030069 | 490.3705
121759999 | F | LC | ETL.1820.POLE.WDPS | 44562763 | EUREKA | HUMBOLDT | 2021-07-13 | 2021-08-25 | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44562468 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.028572 | 47.5295
121761227 | F | LC | ETL.1440.POLE.STPS | 45110007 | SACTO | SIERRA | 2021-07-19 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45109882 | 2020-07-18 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [8 empty] | 0.065152
121770610 | F | LC | ETL.8360.POLE.WDPS | 44412049 | LAKEVLLE |  | 2021-07-20 |  | ETL.8360 | LAYTONVILLE-WILLITS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44412048 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0035111 | 2913.8086
121777954 | F | LC | ETL.2390.POLE.WDPS | 44195259 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44195258 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.6093e-06 | 713.7063
121780999 | F | LC | ETL.2540.POLE.WDPS | 44551366 | MOSSLNDG | CENTRAL COAST | 2021-07-21 |  | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44550897 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0090247 | 823.3626
121810582 | E | LC | ETL.6430.POLE.WOOD | 40674122 | TABLEMTN | NORTH VALLEY | 2021-07-28 |  | ETL.6430 | COLEMAN-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40674122 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 0.013415 | 2980.1345 | 39.9775
121816250 | F | LC | ETL.6690.POLE.WOOD | 40815088 | SACTO | SIERRA | 2021-07-29 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40815088 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | [5 empty] | 0.22892 | 158.2976
121816446 | F | LC | ETL.7140.POLE.WOOD | 40825698 | LAKEVLLE | NORTH BAY | 2021-07-28 | 2021-08-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825698 |  | Single Wood Pole | SUSP - Suspension (TWR) | 2018-01-29 | Ceramic | Suspension |  |  |  |  | 0.010829 | 2487.8337
121860176 | B | LC | ETL.6300.POLE.WOOD | 40589829 | TABLEMTN | NORTH VALLEY | 2021-08-07 | 2021-09-22 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.7825e-05 | 221.7338
121940382 | B | LC | ETL.6300.POLE.WOOD | 42624257 | TABLEMTN | NORTH VALLEY | 2021-08-23 | 2021-09-23 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.8859e-06 | 0.065148
121985938 | F | LC | ETL.9460.POLE.WOOD | 44207030 | VICTOR | YOSEMITE | 2021-09-01 | 2021-09-16 | ETL.9460 | VALLEY SPRINGS #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44207030 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Dead End |  |  |  |  | 0.0025769 | 2773.5339
121985943 | F | LC | ETL.4310.POLE.WOOD | 40643283 | VICTOR | YOSEMITE | 2021-09-01 | 2021-09-16 | ETL.4310 | VIERRA-TRACY-KASSON | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Non-HFTD | Non-HFRA | DLFL | 40643283 | 1964-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1974-01-01 | Polymer | Post
122054044 | E | LC | ETL.4780.INSL.NCER | 45129003 | LAKEVLLE | SONOMA | 2021-09-15 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129315 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-03-04 | Glass | Dead End |  |  |  |  | 0.0017387 | 2235.5632 | 3.887
122054044 | E | LC | ETL.4780.INSL.NCER | 45129003 | LAKEVLLE | SONOMA | 2021-09-15 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129315 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.0017387 | 2235.5632 | 3.887
118525816 | E | LC | ETL.4870.TOWR | 40761930 | FRESNO | FRESNO | 2020-02-11 | 2021-06-29 | ETL.4870 | HELMS-GREGG #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40761930 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 5.6918e-09 | 5176.6899
118702693 | E | LC | ETL.6500.POLE.NWOD | 44882627 | SACTO | SACRAMENTO | 2020-03-13 | 2021-02-18 | ETL.6500 | COLGATE-PALERMO | Conductor-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44882627 | 2020-02-14 | Light Duty Steel Pole | T1-1A | 2020-02-14 | Polymer | Post |  |  |  |  | 7.664e-07 | 2361.856
118753323 | E | LC | ETL.3500.TOWR | 40856678 | VICTOR | STOCKTON | 2020-03-27 | 2020-04-15 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40856678 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 6.9902e-06 | 1202.4396
118938268 | F | LC | ETL.8210.POLE.NWOD | 44845127 | VICTOR | STOCKTON | 2020-04-20 |  | ETL.8210 | VALLEY SPRINGS #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44845127 | 2019-06-06 | Light Duty Steel Pole | T-1 - Tri Post | 2019-06-06 | Polymer | Post |  |  |  |  | 0.00047054 | 3041.1814
118944791 | F | LC | ETL.5940.TOWR | 40575759 | PISMOBCH | LOS PADRES | 2020-04-23 | 2021-01-28 | ETL.5940 | DIABLO UNIT #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40575759 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00081845 | 982.7609
118947777 | E | LC | ETL.5660.INSL | 40633105 | CONCORD | EAST BAY | 2020-04-20 | 2021-08-05 | ETL.5660 | SAN RAMON-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118977370 | E | LC | ETL.6220.POLE.WOOD | 40824514 | EUREKA | HUMBOLDT | 2020-05-03 | 2021-06-04 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40824514 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.15349 | 1537.8777
119004886 | B | LC | ETL.5930.TOWR | 40816009 | CONCORD | DIABLO | 2020-05-01 | 2020-07-28 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40816009 | 1986-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-04 | Glass Silicone Coated | Suspension |  |  |  |  | 5.8649e-09 | 585.7291
119005128 | E | LC | ETL.7820.POLE.WOOD | 40587664 | LAKEVLLE | HUMBOLDT | 2020-04-30 | 2021-08-03 | ETL.7820 | POTTER VALLEY-WILLITS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587664 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Non Ceramic | [5 empty] | 0.00082059 | 253.2372
119061232 | E | LC | ETL.1430.INSL | 40690865 | SACTO | SACRAMENTO | 2020-05-19 | 2021-03-18 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119066642 | B | LC | ETL.8410.POLE.WOOD | 40825506 | LAKEVLLE | HUMBOLDT | 2020-05-21 | 2020-07-07 | ETL.8410 | ELK-GUALALA | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825506 | 1960-01-01 | Single Wood Pole | T-1 - Tri Post | 2020-06-26 | Polymer | Post |  |  |  |  | 0.23096 | 31.6963
119077871 | E | LC | ETL.4392.INSL.CERA | 40842372 | LAKEVLLE |  | 2020-05-27 | 2021-06-15 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119087954 | E | LC | ETL.5430.POLE.WDPS | 44562765 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2020-07-01 | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119088059 | E | LC | ETL.6720.POLE.NWOD | 44324212 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-02-22 | ETL.6720 | DESABLA-CENTERVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44324212 | 2015-11-03 | Fiberglass | T-1 - Tri Post | 2015-11-03 | Polymer | Post |  |  |  |  | 0.0010535 | 79.2789
119096197 | E | LC | ETL.8290.POLE.WOOD | 40650371 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-21 | ETL.8290 | VOLTA-DESCHUTES | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40650371 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0014283 | 4767.2183
119097081 | A | LC | ETL.8170.POLE.WOOD | 40752252 | EUREKA | HUMBOLDT | 2020-06-02 | 2020-06-09 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752252 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Ceramic | [5 empty] | 0.12738 | 4621.6372
119097277 | F | LC | ETL.3720.TOWR | 40857649 | CONCORD | EAST BAY | 2020-05-18 | 2021-04-06 | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857649 | 1968-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1968-01-01 | Porcelain | Dead End |  |  |  |  | 4.6818e-06 | 253.126
119097277 | F | LC | ETL.3720.TOWR | 40857649 | CONCORD | EAST BAY | 2020-05-18 | 2021-04-06 | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857649 | 1968-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1968-01-01 | Polymer | Dead End |  |  |  |  | 4.6818e-06 | 253.126
119103260 | E | LC | ETL.8300.POLE.WOOD | 40700038 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-07-22 | ETL.8300 | VOLTA-SOUTH | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40700038 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.016457 | 1918.8628
119114996 | F | LC | ETL.1050.TOWR | 40862352 | FRESNO | FRESNO | 2020-05-27 | 2021-07-26 | ETL.1050 | BALCH-SANGER | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862352 | 1961-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1923-01-01 | Porcelain | Dead End |  |  |  |  | 0.0029231 | 5429.9297
119114996 | F | LC | ETL.1050.TOWR | 40862352 | FRESNO | FRESNO | 2020-05-27 | 2021-07-26 | ETL.1050 | BALCH-SANGER | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862352 | 1961-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2019-04-01 | Ceramic | Dead End |  |  |  |  | 0.0029231 | 5429.9297
119117021 | E | LC | ETL.6880.INSL.NCER | 44860477 | LAKEVLLE | NORTH BAY | 2020-05-18 | 2021-03-31 | ETL.6880 | FULTON-CALISTOGA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44647528 | 2018-08-26 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2019-10-31 | Glass | Dead End |  |  |  |  | 3.4212e-05
119117021 | E | LC | ETL.6880.INSL.NCER | 44860477 | LAKEVLLE | NORTH BAY | 2020-05-18 | 2021-03-31 | ETL.6880 | FULTON-CALISTOGA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44647528 | 2018-08-26 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2019-10-31 | Glass | Dead End |  |  |  |  | 3.4212e-05
119117021 | E | LC | ETL.6880.INSL.NCER | 44860477 | LAKEVLLE | NORTH BAY | 2020-05-18 | 2021-03-31 | ETL.6880 | FULTON-CALISTOGA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44647528 | 2018-08-26 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2019-10-31 | Glass | Dead End |  |  |  |  | 3.4212e-05
119117920 | F | LC | ETL.6770.POLE.WOOD | 40589980 | SACTO | SIERRA | 2020-06-01 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40589980 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0080614 | 443.0452
119118019 | F | LC | ETL.7290.POLE.WOOD | 40771271 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40771271 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.011334 | 779.47
119118144 | E | LC | ETL.6220.POLE.WOOD | 40600509 | EUREKA | HUMBOLDT | 2020-06-02 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600509 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.090226 | 2232.1048 | 201.3938
119119333 | E | LC | ETL.8290.POLE.WOOD | 40769428 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-02 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40769428 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00013273 | 620.4352
119120135 | F | LC | ETL.8170.POLE.WOOD | 44947141 | EUREKA | HUMBOLDT | 2020-06-03 | 2021-08-27 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119123513 | E | LC | ETL.6470.POLE.NWOD | 44398586 | SACTO | SIERRA | 2020-06-02 | 2021-08-10 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44398586 | 2017-05-18 | Light Duty Steel Pole | Other | 2017-05-18 | Polymer | Suspension |  |  |  |  | 0.00010988 | 221.5243
119125729 | F | LC | ETL.5290.TOWR | 40870427 | PISMOBCH | LOS PADRES | 2020-06-04 | 2021-01-19 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870427 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.4313e-08 | 3199.4436
119125729 | F | LC | ETL.5290.TOWR | 40870427 | PISMOBCH | LOS PADRES | 2020-06-04 | 2021-01-19 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870427 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-04 | Glass | Suspension |  |  |  |  | 1.4313e-08 | 3199.4436
119142858 | F | LC | ETL.1810.TOWR | 44321392 | EUREKA | HUMBOLDT | 2020-06-05 | 2021-05-12 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44321392 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-04-27 | Polymer | Suspension |  |  |  |  | 2.7789e-05
119150199 | F | LC | ETL.6490.POLE.WOOD | 40823687 | SACTO | SIERRA | 2020-06-03 |  | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40823687 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Pin |  |  |  |  | 0.01222 | 2926.5906
119151056 | E | LC | ETL.8290.POLE.WOOD | 40759053 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-27 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119161245 | F | LC | ETL.1810.TOWR | 44321415 | EUREKA | HUMBOLDT | 2020-06-05 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44321415 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 9.7407e-06
119161609 | F | LC | ETL.7260.POLE.WOOD | 41177742 | TABLEMTN | NORTH VALLEY | 2020-06-09 |  | ETL.7260 | KESWICK-CASCADE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41177742 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 1.3713e-05 | 3722.593
119162809 | F | LC | ETL.6760.POLE.WOOD | 40874754 | SACTO | SACRAMENTO | 2020-06-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Steel | Paint/Coating | [Other] | Tier2 |  |  | PEND
119163147 | F | LC | ETL.5441.POLE.STPS | 44965353 | TABLEMTN | NORTH VALLEY | 2020-06-13 |  | ETL.5441 | PIT #6 TAP | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 44965321 | 2020-05-28 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.0346e-06 | 300.6727 | 0.0018144
119166200 | E | LC | ETL.7300.POLE.WOOD | 40877958 | TABLEMTN | NORTH VALLEY | 2020-06-11 | 2021-03-15 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
119169892 | E | LC | ETL.6480.POLE.WOOD | 40874659 | SACTO | SIERRA | 2020-06-15 | 2020-11-12 | ETL.6480 | COLGATE-CHALLENGE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40874659 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.23221 | 268.9798
119177346 | E | LC | ETL.7590.POLE.WOOD | 42565671 | MOSSLNDG | DE ANZA | 2020-04-15 | 2020-09-16 | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42565671 |  | Single Wood Pole | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Pin |  |  |  |  | 0.26444 | 95.0065
119179489 | E | LC | ETL.7300.POLE.WOOD | 40668429 | TABLEMTN |  | 2020-06-16 | 2021-03-05 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40668429 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.00012121 | 4088.6799
119189097 | E | LC | ETL.1330.TOWR | 40860979 | LAKEVLLE | HUMBOLDT | 2020-06-19 | 2021-06-10 | ETL.1330 | CORTINA-MENDOCINO #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40860979 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-09 | Glass | Dead End |  |  |  |  | 5.6579e-06 | 5937.1836
119189097 | E | LC | ETL.1330.TOWR | 40860979 | LAKEVLLE | HUMBOLDT | 2020-06-19 | 2021-06-10 | ETL.1330 | CORTINA-MENDOCINO #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40860979 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Dead End |  |  |  |  | 5.6579e-06 | 5937.1836
119194579 | F | LC | ETL.6470.POLE.WOOD | 40818497 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40818497 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.044724 | 95.0148
119206203 | F | LC | ETL.8640.POLE.NWOD | 44172591 | FRESNO | YOSEMITE | 2020-06-23 |  | ETL.8640 | EXCHEQUER-MARIPOSA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44172591 | 2016-02-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2016-02-18 | Polymer | Dead End |  |  |  |  | 5.9144e-09 | 66.5128
119210451 | E | LC | ETL.7790.POLE.WOOD | 40674158 | TABLEMTN | NORTH VALLEY | 2020-06-24 | 2020-09-28 | ETL.7790 | PIT #1-MCARTHUR | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40674158 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | Dead End |  |  |  |  | 0.040074 | 4131.7891
119212366 | F | LC | ETL.7270.POLE.WOOD | 40816286 | TABLEMTN | NORTH VALLEY | 2020-06-25 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40816286 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.029085 | 744.5844
119221300 | E | LC | ETL.8290.POLE.WOOD | 40656917 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2021-05-14 | ETL.8290 | VOLTA-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40656917 |  | Single Wood Pole | T2N | 2021-04-20 | Polymer | Post |  |  |  |  | 0.00038157 | 779.1284
119232383 | E | LC | ETL.8170.INSL | 40855879 | EUREKA | HUMBOLDT | 2020-06-29 | 2021-06-11 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119232407 | F | LC | ETL.8170.POLE.WDPS | 44743795 | EUREKA | HUMBOLDT | 2020-06-29 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] |  | Tier 2 | Within Both | DLFL | 40828013 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0068975 | 395.5107
119237670 | E | LC | ETL.8170.POLE.WOOD | 40861363 | EUREKA | HUMBOLDT | 2020-06-30 | 2021-04-06 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40861363 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Non Ceramic | [5 empty] | 0.017061 | 79.1467
119237676 | F | LC | ETL.7270.POLE.WOOD | 40906115 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906115 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0033248 | 4367.7598
119295734 | E | LC | ETL.7180.POLE.WDPS | 44360898 | LAKEVLLE | SONOMA | 2020-07-01 | 2021-04-12 | ETL.7180 | IGNACIO-BOLINAS #2 | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44360896 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 1.3668e-05 | 1071.3569
119300228 | E | LC | ETL.7300.POLE.WOOD | 40877962 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-03-12 | ETL.7300 | KILARC-DESCHUTES | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877962 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00058658 | 537.9698
119308013 | B | LC | ETL.7140.POLE.WOOD | 40701396 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40701396 |  | Single Wood Pole | T-1 - Tri Post | 2020-06-21 | Polymer | Post |  |  |  |  | 0.0034809 | 2185.4529
119308094 | B | LC | ETL.7140.POLE.STPS | 44818545 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-26 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] |  | Tier 3 | Within Both | COMP | 44817633 | 2019-05-07 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0015726 | 4211.6216
119309731 | F | LC | ETL.1810.POLE.WDPS | 44322563 | EUREKA | HUMBOLDT | 2020-07-03 | 2021-02-09 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44322561 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0030461
119311452 | B | LC | ETL.8410.POLE.WOOD | 40601558 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-27 | ETL.8410 | ELK-GUALALA | Other | Customer Issue | [Appointment Required, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601558 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Porcelain | Suspension |  |  |  |  | 0.09597 | 1403.2123
119312745 | F | LC | ETL.8060.POLE.WOOD | 40826218 | SACTO | SIERRA | 2020-07-02 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826218 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.087146 | 784.8264
119313265 | F | LC | ETL.1350.POLE.WDPS | 44549924 | TABLEMTN |  | 2020-07-02 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44549440 |  | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.01247 | 522.173
119314923 | E | LC | ETL.1430.TOWR | 40647222 | SACTO | SACRAMENTO | 2020-07-06 | 2021-03-02 | ETL.1430 | DRUM-RIO OSO #2 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40647222 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Dead End |  |  |  |  | 0.00015686 | 838.4462
119323484 | F | LC | ETL.7270.POLE.WOOD | 40617641 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40617641 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.013176 | 205.7693
119324353 | E | LC | ETL.6300.POLE.WOOD | 40751773 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-08-24 | ETL.6300 | CARIBOU-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751773 |  | Single Wood Pole | TH - TriAngle Post 70 | 2014-11-07 | Non Ceramic | Post |  |  |  |  | 1.8859e-06 | 1.6468
119327251 | E | LC | ETL.7300.POLE.WOOD | 40617715 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-03-18 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119328505 | F | LC | ETL.1110.TOWR | 40660355 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-07-16 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660355 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 2.8604e-05 | 3326.4922
119334996 | E | LC | ETL.8170.POLE.WOOD | 40821164 | EUREKA | HUMBOLDT | 2020-07-08 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40821164 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.011553 | 79.1724 | 0.91464
119335693 | F | LC | ETL.6300.POLE.WOOD | 40600674 | TABLEMTN |  | 2020-07-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600674 |  | Single Wood Pole | T-1 - Tri Post | 2014-11-07 | Non Ceramic | Post |  |  |  |  | 1.8931e-06 | 0.065148
119336642 | E | LC | ETL.7590.POLE.WOOD | 40824957 | MOSSLNDG | CENTRAL COAST | 2020-07-09 | 2020-09-30 | ETL.7590 | MONTA VISTA-BURNS | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119340323 | F | LC | ETL.6280.POLE.WOOD | 40600563 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-02-10 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40600563 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-01-07 | Polymer | Dead End |  |  |  |  | 6.7215e-06 | 443.3138
119358182 | F | LC | ETL.1450.POLE.WDPS | 44557672 | SACTO | SACRAMENTO | 2020-07-09 | 2021-01-25 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44554054 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.05406 | 1123.6396
119363581 | E | LC | ETL.5970.TOWR | 40753891 | PISMOBCH | LOS PADRES | 2020-07-13 | 2021-05-20 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40753891 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-04-24 | Glass | Suspension |  |  |  |  | 4.4396e-07 | 1298.0298
119363937 | F | LC | ETL.6900.POLE.NWOD | 43250062 | LAKEVLLE | SONOMA | 2020-07-13 | 2021-09-15 | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | HFRA Removal | COMP | 43250062 | 2011-01-01 | Tubular Steel Pole | TPD - Tri Post Dead End Construction | [7 empty] | 1.0116e-11 | 15.8932
119365236 | E | LC | ETL.2060.POLE.WOOD | 40826080 | LAKEVLLE | SONOMA | 2020-07-13 | 2021-08-17 | ETL.2060 | FORT BRAGG-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826080 | 1961-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.28023 | 205.6928
119370567 | E | LC | ETL.1450.POLE.WDPS | 44557725 | SACTO | SACRAMENTO | 2020-07-13 | 2021-02-18 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL | [12 empty] | 174.093
119470025 | F | LC | ETL.7030.POLE.WOOD | 40592098 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40592098 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0023724 | 2423.1184
119473897 | F | LC | ETL.3190.TOWR | 40910255 | TABLEMTN | NORTH VALLEY | 2020-07-20 |  | ETL.3190 | CARIBOU-PALERMO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40910255 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.0097861 | 174.0445 | 1.7032
119477317 | E | LC | ETL.1370.POLE.WDPS | 44283607 | PISMOBCH | LOS PADRES | 2020-07-20 | 2021-03-02 | ETL.1370 | DIVIDE-CABRILLO #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44283604 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.021835 | 3846.8015
119484107 | F | LC | ETL.1430.TOWR | 40765785 | SACTO | SACRAMENTO | 2020-07-21 | 2021-02-11 | ETL.1430 | DRUM-RIO OSO #2 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40765785 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.0074693 | 1234.2582
119485158 | F | LC | ETL.8170.POLE.WOOD | 40906333 | EUREKA | HUMBOLDT | 2020-07-21 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40906333 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.049561 | 5273.0366
119489280 | E | LC | ETL.1650.POLE.WOOD | 40750647 | LAKEVLLE | SONOMA | 2020-07-22 | 2021-03-16 | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750647 | 1985-01-01 | Single Wood Pole | T-1 - Tri Post | 1966-01-01 | Polymer | Suspension |  |  |  |  | 2.4311e-05 | 4022.6609
119491065 | B | LC | ETL.8060.INSL.NCER | 40700156 | SACTO | SACRAMENTO | 2020-07-22 | 2020-10-06 | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40668696 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Polymer | [5 empty] | 0.14038 | 110.9493
119492889 | E | LC | ETL.1370.POLE.WDPS | 44283611 | PISMOBCH | LOS PADRES | 2020-07-23 | 2021-09-09 | ETL.1370 | DIVIDE-CABRILLO #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44283608 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.016336 | 2213.428
119515326 | F | LC | ETL.1110.POLE.WDPS | 44424003 | TABLEMTN | HUMBOLDT | 2020-07-23 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44424002 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0080084 | 1993.7578
119524806 | F | LC | ETL.6870.POLE.WOOD | 40664841 | SACTO | SACRAMENTO | 2020-07-29 | 2021-04-13 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40664841 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.30504 | 0.065152
119561312 | E | LC | ETL.8170.POLE.WDPS | 44420621 | EUREKA | HUMBOLDT | 2020-08-05 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44420618 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.055324 | 3976.3742 | 219.9909
119571584 | E | LC | ETL.6490.POLE.WOOD | 40613018 | SACTO | SACRAMENTO | 2020-08-06 | 2021-02-18 | ETL.6490 | COLGATE-GRASS VALLEY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40613018 |  | Single Wood Pole | T2N | 2021-02-15 | Polymer | Post |  |  |  |  | 0.012818 | 3639.9543
119577297 | F | LC | ETL.7180.POLE.WOOD | 40649377 | LAKEVLLE | NORTH BAY | 2020-08-06 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40649377 |  | Single Wood Pole | TH - TriAngle Post 70 | 2020-11-06 | Polymer | Post |  |  |  |  | 5.3178e-06 | 4166.9434
119601425 | E | LC | ETL.7930.POLE.WOOD | 40761089 | MOSSLNDG | CENTRAL COAST | 2020-08-11 | 2021-07-29 | ETL.7930 | SALINAS-LAURELES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761089 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0031808 | 0.52063
119616102 | F | LC | ETL.1600.TOWR | 40818390 | LAKEVLLE | SONOMA | 2020-08-14 | 2021-01-25 | ETL.1600 | FULTON-PUEBLO | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818390 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-03-18 | Glass | Double Dead End |  |  |  |  | 4.2342e-07 | 697.5563
119616102 | F | LC | ETL.1600.TOWR | 40818390 | LAKEVLLE | SONOMA | 2020-08-14 | 2021-01-25 | ETL.1600 | FULTON-PUEBLO | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818390 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2020-03-18 | Porcelain | Dead End |  |  |  |  | 4.2342e-07 | 697.5563
119618201 | B | LC | ETL.8650.POLE.NWOD | 44420176 | FRESNO | FRESNO | 2020-08-14 | 2020-12-11 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420176 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0025978 | 3305.365
119639888 | B | LC | ETL.8650.TOWR | 40660816 | FRESNO | FRESNO | 2020-08-19 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660816 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.018242 | 5840.8999
119652851 | F | LC | ETL.4770.TOWR | 40587523 | LAKEVLLE | SONOMA | 2020-08-21 | 2021-03-15 | ETL.4770 | GEYSERS #17-FULTON | GO95 / Anti Climb | Clearance | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587523 | 1982-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-05-30 | Glass | Dead End |  |  |  |  | 0.00079051 | 1472.3439
119652851 | F | LC | ETL.4770.TOWR | 40587523 | LAKEVLLE | SONOMA | 2020-08-21 | 2021-03-15 | ETL.4770 | GEYSERS #17-FULTON | GO95 / Anti Climb | Clearance | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587523 | 1982-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00079051 | 1472.3439
119659129 | E | LC | ETL.1600.TOWR | 40808845 | LAKEVLLE | SONOMA | 2020-08-22 | 2021-03-08 | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808845 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 9.0814e-05 | 142.5877
119659129 | E | LC | ETL.1600.TOWR | 40808845 | LAKEVLLE | SONOMA | 2020-08-22 | 2021-03-08 | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808845 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 9.0814e-05 | 142.5877
119710195 | A | LC | ETL.7590.POLE.WOOD | 43595403 | MOSSLNDG | CENTRAL COAST | 2020-09-03 | 2020-09-24 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119719933 | B | LC | ETL.6280.POLE.WOOD | 40593014 | TABLEMTN | NORTH VALLEY | 2020-08-26 | 2020-10-28 | ETL.6280 | CARIBOU #2 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40593014 |  | Single Wood Pole | LB - Line and Buck |  | Ceramic | Other |  |  |  |  | 4.4034e-05 | 632.7172
119720858 | F | LC | ETL.1400.POLE.STPS | 44840547 | VICTOR | YOSEMITE | 2020-07-28 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44840521 | 2019-09-24 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.8782e-05 | 158.2923
119725973 | F | LC | ETL.1730.POLE.WOOD | 40618425 | MOSSLNDG | CENTRAL COAST | 2020-08-12 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40618425 | 1972-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1972-01-01 | Ceramic | Post |  |  |  |  | 0.00015671 | 0.065147
119742946 | E | LC | ETL.7140.INSL | 40629566 | LAKEVLLE | NORTH BAY | 2020-07-11 | 2021-05-10 | ETL.7140 | IGNACIO-BOLINAS #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119754586 | B | LC | ETL.7300.POLE.WOOD | 40877968 | TABLEMTN |  | 2020-09-11 | 2020-10-22 | ETL.7300 | KILARC-DESCHUTES | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877968 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0062564 | 134.549
119764610 | E | LC | ETL.1110.POLE.WDPS | 44424046 | TABLEMTN | HUMBOLDT | 2020-09-08 | 2021-07-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424045 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.001253 | 5069.9922
119769236 | F | LC | ETL.6300.POLE.WDPS | 44976237 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-09-14 | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [12 empty] | 15.9194
119781031 | F | LC | ETL.8240.POLE.WOOD | 40697154 | VICTOR | STOCKTON | 2020-09-12 | 2021-04-05 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40697154 | 1995-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2021-01-26 | Polymer | Post |  |  |  |  | 0.0031417 | 2425.3579
119786493 | F | LC | ETL.5650.TOWR | 40812727 | TABLEMTN | NORTH VALLEY | 2020-09-15 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40812727 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 3.5447e-07 | 967.9307
119814421 | E | LC | ETL.1450.POLE.WDPS | 44553685 | SACTO | SACRAMENTO | 2020-08-19 | 2021-04-28 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553174 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.5245e-06 | 386.1083
119819048 | F | LC | ETL.4221.POLE.STPS | 44356172 | TABLEMTN |  | 2020-09-12 |  | ETL.4221 | SLY CREEK TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44356171 | 2016-11-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.9921e-07 | 1629.6117
119829918 | E | LC | ETL.1420.TOWR | 40670147 | SACTO | SIERRA | 2020-09-28 | 2021-03-05 | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40670147 | 1975-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | [7 empty] | 0.00010638 | 1471.1865
119831061 | E | LC | ETL.5091.INSL | 41122518 | MOSSLNDG | CENTRAL COAST | 2020-09-30 |  | ETL.5091 | METCALF-MONTA VISTA #3 | FAA Lighting-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40862872 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.0006169 | 1044.4961 | 0.64435
119834662 | F | LC | ETL.2395.POLE.WDPS | 44551358 | TABLEMTN | NORTH VALLEY | 2020-09-08 | 2021-09-02 | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44550864 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0050318 | 300.6002
119848380 | F | LC | ETL.8365.POLE.NWOD | 40906639 | EUREKA | HUMBOLDT | 2020-09-16 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40906639 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0010295
119848512 | F | LC | ETL.6880.POLE.NWOD | 44877332 | LAKEVLLE | SONOMA | 2020-09-09 | 2021-04-19 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44877332 | 2019-08-14 | Lattice Steel Pole | DV-DE - Double Vertical Dead End | 2019-08-14 | Glass | Dead End |  |  |  |  | 2.8307e-06 | 1790.5603
119912703 | F | LC | ETL.7631.POLE.WOOD | 40750337 | LAKEVLLE | SONOMA | 2020-10-13 | 2021-07-14 | ETL.7631 | WOHLER TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40750337 | 1958-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 5.3142e-05 | 1094.5327
119912703 | F | LC | ETL.7631.POLE.WOOD | 40750337 | LAKEVLLE | SONOMA | 2020-10-13 | 2021-07-14 | ETL.7631 | WOHLER TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40750337 | 1958-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Non Ceramic | Post |  |  |  |  | 5.3142e-05 | 1094.5327
119916583 | E | LC | ETL.3800.INSL | 40884379 | CONCORD | EAST BAY | 2020-10-12 | 2021-06-09 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119967004 | E | LC | ETL.6720.POLE.STPS | 44984423 | TABLEMTN | NORTH VALLEY | 2020-10-30 | 2021-11-15 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [12 empty] | 47.5251
119978803 | E | LC | ETL.8960.POLE.WOOD | 40667142 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40667142 |  | Single Wood Pole | DDE - Double Dead End | 1974-01-01 | Porcelain | Dead End |  |  |  |  | 0.00014005
120016894 | E | LC | ETL.2870.POLE.WOOD | 43203523 | MOSSLNDG | SAN JOSE | 2020-11-10 |  | ETL.2870 | SARGENT SW STA-HOLLISTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 43203523 |  | Single Wood Pole | 3HP - 3 Horizontal Post |  | Porcelain | [5 empty] | 2.901e-05
120018556 | E | LC | ETL.3740.INSL.NCER | 42582023 | CONCORD | EAST BAY | 2020-11-10 | 2021-07-29 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120110526 | E | LC | ETL.8365.POLE.NWOD | 40912697 | EUREKA | HUMBOLDT | 2020-11-20 | 2021-04-30 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912697 | 2010-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0040996 | 5040.4707
120129640 | F | LC | ETL.8170.POLE.WOOD | 40826069 | EUREKA | HUMBOLDT | 2020-08-04 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40826069 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.010842 | 142.4119
120162349 | B | LC | ETL.7820.POLE.NWOD | 44904219 | LAKEVLLE | SONOMA | 2020-12-10 | 2021-02-02 | ETL.7820 | POTTER VALLEY-WILLITS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120231690 | F | LC | ETL.8961.POLE.WOOD | 44275782 | FRESNO | YOSEMITE | 2020-11-23 |  | ETL.8961 | DINOSAUR POINT TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44275782 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.0002417 | 1870.4016
120465737 | E | LC | ETL.4780.INSL.CERA | 40835630 | LAKEVLLE | SONOMA | 2021-01-26 | 2021-06-15 | ETL.4780 | GEYSERS #9-LAKEVILLE | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
120589910 | B | LC | ETL.2570.INSL.CERA | 40791807 | MOSSLNDG | CENTRAL COAST | 2021-03-01 | 2021-05-11 | ETL.2570 | METCALF-MORGAN HILL | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761851 | 1928-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1986-01-01 | Porcelain | Dead End |  |  |  |  | 4.1642e-05 | 2906.3125
120685673 | B | LC | ETL.5463.INSL | 40844072 | CONCORD | EAST BAY | 2021-03-23 | 2021-04-06 | ETL.5463 | PITTSBURG-SAN MATEO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817953 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 8.0255e-09 | 1572.3286
120685673 | B | LC | ETL.5463.INSL | 40844072 | CONCORD | EAST BAY | 2021-03-23 | 2021-04-06 | ETL.5463 | PITTSBURG-SAN MATEO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817953 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 8.0255e-09 | 1572.3286
120689973 | E | LC | ETL.1710.POLE.WDPS | 44512084 | MOSSLNDG | CENTRAL COAST | 2021-03-25 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44510832 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0022299 | 31.6948 | 0.070676
120696571 | E | LC | ETL.3840.INSL.NCER | 40836426 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40809680 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Polymer | Post |  |  |  |  | 1.9115e-07 | 5336.0039 | 0.00102
120696571 | E | LC | ETL.3840.INSL.NCER | 40836426 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40809680 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Polymer | Suspension |  |  |  |  | 1.9115e-07 | 5336.0039 | 0.00102
120698036 | E | LC | ETL.5960.TOWR | 40753856 | PISMOBCH | LOS PADRES | 2021-03-26 |  | ETL.5960 | DIABLO-GATES #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40753856 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-11-04 | Glass | Double Dead End |  |  |  |  | 1.4623e-08 | 619.4626 | 9.0583e-06
120698520 | F | LC | ETL.4393.TOWR | 40586119 | SACTO | SACRAMENTO | 2021-03-26 | 2021-07-22 | ETL.4393 | DRUM-HIGGINS | Road | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40586119 |  | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | [7 empty] | 0.00030317 | 822.7424
120712164 | B | LC | ETL.8360.POLE.WOOD | 40808812 | LAKEVLLE | SONOMA | 2021-03-30 | 2021-07-06 | ETL.8360 | LAYTONVILLE-WILLITS | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 |  |  | COMP
120714952 | E | LC | ETL.5980.INSL | 40783528 | PISMOBCH | LOS PADRES | 2021-03-27 |  | ETL.5980 | DIABLO-MIDWAY #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40753905 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 2.6104e-10 | 1647.1849 | 4.2999e-07
120717823 | E | LC | ETL.1070.INSL.NCER | 40878278 | VICTOR | STOCKTON | 2021-03-31 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44387574 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 9.7405e-06
120717823 | E | LC | ETL.1070.INSL.NCER | 40878278 | VICTOR | STOCKTON | 2021-03-31 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44387574 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 9.7405e-06
120717823 | E | LC | ETL.1070.INSL.NCER | 40878278 | VICTOR | STOCKTON | 2021-03-31 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44387574 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 9.7405e-06
120726859 | E | LC | ETL.6030.TOWR | 40586539 | MIDWAY | KERN | 2021-04-01 |  | ETL.6030 | MIDWAY-WHIRLWIND | Raptor Guard-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40586539 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 2.2848e-06 | 10007.9121 | 0.022866
120743487 | F | LC | ETL.2500.TOWR | 40762456 | METCALF | SAN JOSE | 2021-03-29 | 2021-04-19 | ETL.2500 | METCALF-EL PATIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40762456 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-08-08 | Glass | Double Dead End |  |  |  |  | 0.0065083 | 2374.251
120743487 | F | LC | ETL.2500.TOWR | 40762456 | METCALF | SAN JOSE | 2021-03-29 | 2021-04-19 | ETL.2500 | METCALF-EL PATIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40762456 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2003-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 0.0065083 | 2374.251
120752821 | E | LC | ETL.3820.INSL.CERA | 40829076 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40803372 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 5.416e-07 | 3950.2275 | 0.0021394
120757842 | F | LC | ETL.8365.POLE.NWOD | 45009256 | EUREKA | HUMBOLDT | 2021-04-07 | 2021-08-03 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 45009256 | 2020-09-02 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-09-02 | Glass | Dead End |  |  |  |  | 0.0093388
120761795 | E | LC | ETL.7140.POLE.WOOD | 41111791 | LAKEVLLE | SONOMA | 2021-04-07 | 2021-09-07 | ETL.7140 | IGNACIO-BOLINAS #1 | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111791 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.090128 | 4560.6943
120763402 | E | LC | ETL.7590.POLE.NWOD | 45033425 | MOSSLNDG | CENTRAL COAST | 2021-04-08 |  | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45033425 | 2020-09-18 | Light Duty Steel Pole | T-1 - Tri Post | 2020-09-18 | Polymer | Post |  |  |  |  | 0.011605 | 31.7081 | 0.36798
120795967 | F | LC | ETL.8250.POLE.NWOD | 44878701 | VICTOR | STOCKTON | 2021-04-12 |  | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44878701 | 2019-09-10 | Light Duty Steel Pole | T-1 - Tri Post | 2019-09-10 | Polymer | Post |  |  |  |  | 2.2323e-06 | 1822.205
120799051 | B | LC | ETL.3830.TOWR | 40659365 | VICTOR | STOCKTON | 2021-04-09 | 2021-05-27 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40659365 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.2802e-05 | 5966.103
120803865 | F | LC | ETL.7560.POLE.WOOD | 40913156 | SACTO | SACRAMENTO | 2021-04-13 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40913156 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.40482 | 3606.8623
120810840 | E | LC | ETL.8365.POLE.NWOD | 40600448 | EUREKA | HUMBOLDT | 2021-04-13 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40600448 |  | Lattice Steel Pole | FSS - Field Switch Structure | [7 empty] | 0.0001305
120813342 | E | LC | ETL.3750.TOWR | 40804899 | CONCORD | DIABLO | 2021-04-14 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40804899 | 1932-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 4.8749e-05 | 15.88 | 0.00077414
120815428 | E | LC | ETL.5463.TOWR | 40857954 | CONCORD | DIABLO | 2021-04-14 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40857954 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Ceramic | Double Dead End |  |  |  |  | 7.2542e-09 | 3043.1921 | 2.2076e-05
120815428 | E | LC | ETL.5463.TOWR | 40857954 | CONCORD | DIABLO | 2021-04-14 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40857954 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 7.2542e-09 | 3043.1921 | 2.2076e-05
120828371 | E | LC | ETL.9250.POLE.NWOD | 44515899 | MIDWAY | KERN | 2021-04-16 | 2021-11-17 | ETL.9250 | TEJON-LEBEC | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44515899 | 2016-06-02 | Single Wood Pole | T-1 - Tri Post | 2016-06-02 | Polymer | Post |  |  |  |  | 0.020432 | 5260.3872 | 107.4793
120850905 | E | LC | ETL.6470.POLE.WOOD | 40824238 | SACTO | SACRAMENTO | 2021-04-20 | 2021-08-17 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824238 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0054123 | 419.3189
120859391 | E | LC | ETL.6470.POLE.WOOD | 40593279 | SACTO | SACRAMENTO | 2021-04-21 | 2021-08-26 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40593279 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0052851 | 569.5441
120859489 | F | LC | ETL.5540.TOWR | 40866635 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40866635 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-12 | Glass | Suspension |  |  |  |  | 1.2179e-05 | 4386.7925 | 0.053428
120859631 | E | LC | ETL.6470.POLE.WOOD | 40611122 | SACTO | SACRAMENTO | 2021-04-21 | 2021-08-18 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40611122 |  | Single Wood Pole | T2N | 2021-08-04 | Polymer | Post |  |  |  |  | 0.12859 | 814.7879
120861471 | E | LC | ETL.2710.INSL | 40671296 | CONCORD | DIABLO | 2021-04-21 |  | ETL.2710 | MORAGA-CLAREMONT #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40644184 | 1944-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1944-01-01 | Ceramic | Suspension |  |  |  |  | 2.1942e-05 | 316.867 | 0.0069527
120866032 | E | LC | ETL.6470.POLE.WOOD | 40766584 | SACTO | SACRAMENTO | 2021-04-22 | 2021-08-12 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40766584 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 0.0089793 | 696.2946
120877227 | E | LC | ETL.8060.POLE.WOOD | 40771517 | SACTO | SACRAMENTO | 2021-04-23 | 2021-08-12 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771517 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.071297 | 174.093
120878887 | F | LC | ETL.3820.TOWR | 40579640 | VICTOR | STOCKTON | 2021-04-24 | 2021-05-20 | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40579640 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.6366e-06 | 253.1151
120886078 | E | LC | ETL.1250.INSL.NCER | 40840071 | FRESNO | FRESNO | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40814387 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Double Dead End |  |  |  |  | 7.7769e-06 | 6676.2596 | 0.05192
120889082 | E | LC | ETL.3830.TOWR | 40871563 | VICTOR | STOCKTON | 2021-04-27 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40871563 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 2.9052e-06 | 382.9233 | 0.0011125
120900961 | E | LC | ETL.2720.TOWR | 40580799 | CONCORD | DIABLO | 2021-04-14 |  | ETL.2720 | MORAGA-OAKLAND #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40580799 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 0.00043634 | 0.065152 | 2.8428e-05
120900961 | E | LC | ETL.2720.TOWR | 40580799 | CONCORD | DIABLO | 2021-04-14 |  | ETL.2720 | MORAGA-OAKLAND #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40580799 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-04 | Glass | Suspension |  |  |  |  | 0.00043634 | 0.065152 | 2.8428e-05
120913948 | E | LC | ETL.5400.POLE.NWOD | 41184137 | TABLEMTN | NORTH VALLEY | 2021-05-01 |  | ETL.5400 | PIT #3-PIT #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 41184137 |  | Lattice Steel Pole | DE - Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.0046889 | 4131.7891 | 19.3735
120922997 | E | LC | ETL.7000.POLE.WOOD | 40770679 | TABLEMTN | NORTH VALLEY | 2021-05-03 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40770679 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00015112 | 0.065148 | 9.8451e-06
120943710 | F | LC | ETL.1810.TOWR | 44321421 | EUREKA | HUMBOLDT | 2021-05-05 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44321421 |  | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2019-08-31 | Glass | Dead End |  |  |  |  | 1.9364e-08 | 15.8807 | 3.0751e-07
120948046 | E | LC | ETL.3830.INSL.NCER | 40829011 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40808610 | 1927-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1999-01-01 | Polymer | Dead End |  |  |  |  | 1.4139e-08 | 4179.6724 | 5.9096e-05
121190289 | E | LC | ETL.2900.TOWR | 40810458 | MOSSLNDG | CENTRAL COAST | 2021-04-20 | 2021-10-18 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Raptor Guard-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810458 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.014032 | 777.9778 | 10.9163
121329438 | F | LC | ETL.2395.POLE.WDPS | 44551414 | TABLEMTN | NORTH VALLEY | 2021-05-13 | 2021-06-28 | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44550851 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.032409 | 189.8861
121331767 | B | LC | ETL.4221.INSL.CERA | 40617708 | TABLEMTN | NORTH VALLEY | 2021-05-14 | 2021-05-20 | ETL.4221 | SLY CREEK TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44559179 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0010743
121331767 | B | LC | ETL.4221.INSL.CERA | 40617708 | TABLEMTN | NORTH VALLEY | 2021-05-14 | 2021-05-20 | ETL.4221 | SLY CREEK TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44559179 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0010743
121337793 | E | LC | ETL.5510.TOWR | 40586626 | CONCORD | DIABLO | 2021-04-26 | 2021-10-04 | ETL.5510 | PITTSBURG-TESLA #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586626 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 1.8477e-07 | 4497.2217 | 0.00083094
121339080 | E | LC | ETL.8250.INSL.NCER | 40913761 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40904155 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.4291e-06 | 1933.4785 | 0.0027632
121352997 | E | LC | ETL.3500.TOWR | 40857313 | VICTOR | STOCKTON | 2021-04-26 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40857313 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 3.4465e-05 | 94.9894 | 0.0032738
121358121 | E | LC | ETL.5463.TOWR | 40857956 | CONCORD | MISSION | 2021-04-29 | 2021-11-29 | ETL.5463 | PITTSBURG-SAN MATEO | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857956 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 1.201e-06 | 2754.8582 | 0.0033086
121358121 | E | LC | ETL.5463.TOWR | 40857956 | CONCORD | MISSION | 2021-04-29 | 2021-11-29 | ETL.5463 | PITTSBURG-SAN MATEO | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857956 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-10 | Glass | Suspension |  |  |  |  | 1.201e-06 | 2754.8582 | 0.0033086
121369103 | E | LC | ETL.4870.TOWR | 40576610 | FRESNO | FRESNO | 2021-05-20 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576610 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.0132e-07 | 616.9009 | 0.00018588
121378055 | F | LC | ETL.1820.POLE.NWOD | 44947378 | EUREKA | HUMBOLDT | 2021-05-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44947378 | 2018-11-05 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2018-11-05 | Glass | Suspension |  |  |  |  | 6.8793e-05 | 94.963
121379533 | F | LC | ETL.1420.TOWR | 40805285 | SACTO | SIERRA | 2021-05-06 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40805285 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.0024691 | 15.8837 | 0.039218
121379533 | F | LC | ETL.1420.TOWR | 40805285 | SACTO | SIERRA | 2021-05-06 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40805285 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-03-09 | Glass | Suspension |  |  |  |  | 0.0024691 | 15.8837 | 0.039218
121380398 | B | LC | ETL.4440.TOWR | 40674583 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-29 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40674583 | 1968-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1968-01-01 | Porcelain | Dead End |  |  |  |  | 0.00018762 | 5962.8364
121381416 | F | LC | ETL.6320.POLE.NWOD | 44417891 | TABLEMTN | NORTH VALLEY | 2021-05-08 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44417891 | 2019-03-12 | Light Duty Steel Pole | T-1 - Tri Post | 2019-03-12 | Polymer | Post |  |  |  |  | 0.00011491 | 4083.1003
121382161 | E | LC | ETL.8250.POLE.WOOD | 44513825 | VICTOR | STOCKTON | 2021-05-10 | 2021-09-01 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44513825 | 2017-01-08 | Single Wood Pole | T-1 - Tri Post | 2017-01-08 | Non Ceramic | Post |  |  |  |  | 1.9317e-05 | 1190.8021
121383271 | F | LC | ETL.8250.POLE.WOOD | 40908807 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40908807 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 2.5263e-05 | 5094.106
121384249 | F | LC | ETL.6760.POLE.WOOD | 40866685 | SACTO | SIERRA | 2021-05-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40866685 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.019501 | 31.7148
121388969 | E | LC | ETL.1420.TOWR | 40870507 | SACTO | SIERRA | 2021-05-15 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40870507 | 1913-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 1.2243e-05 | 126.6435 | 0.0015505
121391702 | F | LC | ETL.6760.POLE.WOOD | 40873747 | SACTO | SIERRA | 2021-05-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40873747 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0049888 | 4399.0391
121392243 | E | LC | ETL.8060.POLE.WOOD | 40876725 | SACTO | SIERRA | 2021-05-17 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40876725 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.078552 | 63.3733 | 4.9781
121405389 | F | LC | ETL.6640.POLE.NWOD | 44820232 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44820232 | 2019-08-21 | Light Duty Steel Pole | T2N | 2019-08-21 | Polymer | Post |  |  |  |  | 0.00016271 | 1079.6697
121406675 | B | LC | ETL.7490.POLE.WOOD | 40771313 | EUREKA | HUMBOLDT | 2021-05-27 | 2021-08-02 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40771313 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.0096405 | 215.1669
121421268 | E | LC | ETL.7040.POLE.WOOD | 42617963 | TABLEMTN | NORTH VALLEY | 2021-05-24 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 42617963 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.055299 | 1744.6283 | 96.4754
121468805 | B | LC | ETL.4780.INSL | 40846236 | LAKEVLLE | SONOMA | 2021-06-03 | 2021-06-21 | ETL.4780 | GEYSERS #9-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818221 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 7.7858e-05 | 31.7169
121480996 | B | LC | ETL.6020.TOWR | 40608604 | TABLEMTN | NORTH VALLEY | 2021-06-03 | 2021-06-14 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40608604 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.1329e-08 | 3100.9255
121482023 | B | LC | ETL.1350.POLE.WDPS | 44550000 | TABLEMTN |  | 2021-06-04 | 2021-06-10 | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44549446 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.23654 | 94.9939
121485517 | E | LC | ETL.6910.POLE.WOOD | 40825383 | LAKEVLLE | SONOMA | 2021-05-29 |  | ETL.6910 | FULTON-MOLINO-COTATI | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40825383 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.0653e-05 | 79.332 | 0.0008451
121489248 | E | LC | ETL.7550.POLE.WDPS | 44211123 | LAKEVLLE |  | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44211120 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00050251 | 1170.7487 | 0.58831
121496155 | F | LC | ETL.1440.POLE.WDPS | 44768889 | SACTO | SIERRA | 2021-06-08 | 2021-10-11 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40654771 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.011393 | 31.7066
121498559 | E | LC | ETL.5390.TOWR | 40759493 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5390 | PIT #1-COTTONWOOD | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40759493 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 5.4986e-07 | 5235.4814 | 0.0028788
121510358 | E | LC | ETL.1820.INSL.CERA | 40853410 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560151 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.44662
121510358 | E | LC | ETL.1820.INSL.CERA | 40853410 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560151 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.44662
121512073 | B | LC | ETL.1810.INSL.NCER | 40616450 | EUREKA | HUMBOLDT | 2021-06-09 | 2021-07-08 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322628 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.054927
121512073 | B | LC | ETL.1810.INSL.NCER | 40616450 | EUREKA | HUMBOLDT | 2021-06-09 | 2021-07-08 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322628 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.054927
121514020 | F | LC | ETL.1820.POLE.WDPS | 44560636 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44560108 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.057524 | 63.3274
121514476 | B | LC | ETL.1820.INSL.NCER | 44676380 | EUREKA | HUMBOLDT | 2021-06-10 | 2021-06-30 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44676372 | 2018-11-10 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2018-11-10 | Glass | Dead End |  |  |  |  | 0.0001682
121514476 | B | LC | ETL.1820.INSL.NCER | 44676380 | EUREKA | HUMBOLDT | 2021-06-10 | 2021-06-30 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44676372 | 2018-11-10 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2018-11-10 | Glass | Dead End |  |  |  |  | 0.0001682
121514476 | B | LC | ETL.1820.INSL.NCER | 44676380 | EUREKA | HUMBOLDT | 2021-06-10 | 2021-06-30 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44676372 | 2018-11-10 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2018-11-10 | Glass | Dead End |  |  |  |  | 0.0001682
121516827 | E | LC | ETL.6240.POLE.WOOD | 40863753 | MOSSLNDG | CENTRAL COAST | 2021-06-05 |  | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40863753 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2020-09-18 | Glass Silicone Coated | Dead End |  |  |  |  | 0.22176 | 31.7081 | 7.0317
121518467 | F | LC | ETL.1350.POLE.WDPS | 44512190 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40590563 | 1943-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.020782 | 743.6734 | 15.4548
121533835 | E | LC | ETL.5390.TOWR | 40657367 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40657367 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.0692e-08 | 3930.0723 | 4.202e-05
121534971 | E | LC | ETL.1610.INSL | 40611467 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1610 | SILVERADO-FULTON JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40586777 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 9.7983e-09 | 2610.3999 | 2.5578e-05
121536591 | E | LC | ETL.1350.INSL | 40618060 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40592427 | 1943-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.044097
121536591 | E | LC | ETL.1350.INSL | 40618060 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40592427 | 1943-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.044097
121541952 | E | LC | ETL.5630.TOWR | 40867799 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40867799 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 0.00022271 | 5761.729 | 1.2832
121545249 | F | LC | ETL.1820.POLE.NWOD | 44976953 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44976953 | 2020-03-09 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-03-09 | Glass | Suspension |  |  |  |  | 0.001087 | 5288.2002
121552636 | E | LC | ETL.7640.POLE.WDPS | 44565387 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564209 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 0.0002165 | 253.4679 | 0.054877
121562174 | E | LC | ETL.5650.TOWR | 40810238 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810238 | 1942-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-12-03 | Ceramic | Dead End |  |  |  |  | 1.5286e-06 | 2947.0984 | 0.0045049
121562752 | E | LC | ETL.6750.POLE.WDPS | 44374920 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44374918 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0003691 | 205.744 | 0.07594
121563228 | E | LC | ETL.6750.INSL.CERA | 40641540 | TABLEMTN |  | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44374914 | 2012-08-04 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 2.5737e-05
121563228 | E | LC | ETL.6750.INSL.CERA | 40641540 | TABLEMTN |  | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44374914 | 2012-08-04 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 2.5737e-05
121563228 | E | LC | ETL.6750.INSL.CERA | 40641540 | TABLEMTN |  | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44374914 | 2012-08-04 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 2.5737e-05
121568129 | F | LC | ETL.8290.POLE.NWOD | 45073096 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.8290 | VOLTA-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45073096 | 2021-06-12 | Light Duty Steel Pole | T-1 - Tri Post | 2019-06-12 | Polymer | Post |  |  |  |  | 8.8332e-05 | 3435.846
121568325 | F | LC | ETL.1400.POLE.WOOD | 44948149 | VICTOR | YOSEMITE | 2021-06-15 |  | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44948149 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.0013566 | 39.6314 | 0.053764
121568639 | E | LC | ETL.5390.TOWR | 40674077 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40674077 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.2349e-05 | 4131.7891 | 0.051025
121575605 | F | LC | ETL.6770.POLE.NWOD | 44396925 | SACTO | SIERRA | 2021-05-13 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44396925 | 2018-09-06 | Light Duty Steel Pole | T2N | [7 empty] | 0.0069987 | 1313.2985
121577815 | F | LC | ETL.4821.TOWR | 42594510 | FRESNO | FRESNO | 2021-06-22 | 2021-08-04 | ETL.4821 | PINE FLAT PH TAP (CDWR) | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42594510 | 1982-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 8.311e-06 | 6679.3267
121580016 | E | LC | ETL.6060.INSL | 40726265 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6060 | ROUND MTN-TABLE MTN #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40684102 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 5.9631e-07 | 728.5434 | 0.00043444
121583253 | E | LC | ETL.6020.TOWR | 40601283 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6020 | MALIN-ROUND MTN #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40601283 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 3.1842e-06 | 2548.3853 | 0.0081145
121585313 | E | LC | ETL.3770.TOWR | 40857876 | CONCORD | DIABLO | 2021-06-22 |  | ETL.3770 | SOBRANTE-R #1 | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier3 | Tier 3 | Within Both | PEND | 40857876 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0027031 | 253.126 | 0.68423
121597166 | F | LC | ETL.1070.POLE.WOOD | 40580902 | VICTOR | STOCKTON | 2021-06-22 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40580902 | 1998-01-01 | Single Wood Pole | T-1 - Tri Post | 1998-01-01 | Polymer | Post |  |  |  |  | 9.2202e-06 | 3073.886 | 0.028342
121630508 | E | LC | ETL.7490.INSL.NCER | 45129459 | EUREKA | HUMBOLDT | 2021-06-15 |  | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40586855 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-07-30 | Polymer | Dead End |  |  |  |  | 0.46676 | 126.5956 | 59.0899
121632825 | E | LC | ETL.5442.POLE.WDPS | 44553769 | TABLEMTN |  | 2021-06-28 |  | ETL.5442 | PIT #7 TAP | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44553122 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.034463 | 584.3575 | 20.1384
121634545 | F | LC | ETL.4040.POLE.STPS | 44647519 | TABLEMTN |  | 2021-06-23 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44646840 | 2018-08-17 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00063078 | 17.9615
121643608 | E | LC | ETL.1450.POLE.WDPS | 44947118 | SACTO | SIERRA | 2021-07-01 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42572863 | 1948-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0058674 | 212.0628 | 1.2443
121659067 | F | LC | ETL.3720.TOWR | 40804933 | CONCORD | EAST BAY | 2021-07-01 |  | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40804933 | 1968-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1968-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.4665e-06 | 356.4935 | 0.0012358
121676401 | E | LC | ETL.9240.TOWR | 43249701 | PISMOBCH | LOS PADRES | 2021-07-07 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier3 | Tier 3 | Within Both | PEND | 43249701 |  | LATTICE STEEL TOWER | [9 empty] | 158.4262
121712980 | E | LC | ETL.6110.INSL.CERA | 40851076 | METCALF | MISSION | 2021-07-12 |  | ETL.6110 | TESLA-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40822145 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 7.8359e-05 | 4246.6318 | 0.33276
121725200 | F | LC | ETL.7390.POLE.NWOD | 40808394 | LAKEVLLE | HUMBOLDT | 2021-07-08 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40808394 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0011554 | 2214.7324
121725240 | F | LC | ETL.6880.POLE.WOOD | 40588917 | LAKEVLLE | NORTH BAY | 2021-07-05 | 2021-10-25 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40588917 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.0014233 | 4321.8276
121728401 | B | LC | ETL.9250.INSL.CERA | 42574840 | MIDWAY | KERN | 2021-07-14 | 2021-09-02 | ETL.9250 | TEJON-LEBEC | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42574834 |  | Light Duty Steel Pole | Unknown |  | Ceramic | [5 empty] | 0.0027625 | 6083.5864
121737363 | E | LC | ETL.6852.INSL.NCER | 44891785 | LAKEVLLE | HUMBOLDT | 2021-07-12 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44891777 | 2020-02-26 | Light Duty Steel Pole | T-1 - Tri Post | 2020-02-26 | Polymer | Post |  |  |  |  | 0.00054618 | 5588.1421 | 3.0521
121738954 | E | LC | ETL.1820.POLE.STPS | 44395180 | EUREKA | HUMBOLDT | 2021-07-13 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395179 | 2017-10-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.057528 | 63.3527 | 3.6446
121746102 | F | LC | ETL.6650.POLE.WDPS | 44560580 | TABLEMTN | NORTH VALLEY | 2021-07-13 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44560156 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.024056 | 174.1578 | 4.1895
121746935 | E | LC | ETL.2395.INSL.CERA | 45105256 | TABLEMTN | NORTH VALLEY | 2021-07-15 | 2021-09-14 | ETL.2395 | GRIZZLY TAP | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45105242 |  | Single Wood Pole | SVDE - Single Vertical Dead End |  | Ceramic | Dead End | [5 empty] | 506.2121
121748325 | E | LC | ETL.1450.POLE.WOOD | 40761541 | SACTO | SIERRA | 2021-06-11 |  | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40761541 | 1948-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 1948-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.00078411 | 47.5526 | 0.037286
121748336 | E | LC | ETL.2390.POLE.WDPS | 44195285 | VICTOR | STOCKTON | 2021-07-14 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44195284 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00015075 | 0.066432 | 1.0015e-05
121752971 | E | LC | ETL.1400.POLE.STPS | 45095104 | VICTOR | YOSEMITE | 2021-07-16 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45095027 | 2021-04-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0031237 | 2246.7366 | 7.0182
121754583 | F | LC | ETL.1440.POLE.STPS | 45110010 | SACTO | SIERRA | 2021-07-19 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45109914 | 2019-08-07 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [8 empty] | 1321.4682
121760022 | B | LC | ETL.1440.INSL | 40615561 | SACTO | SIERRA | 2021-07-19 | 2021-09-14 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40590122 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0042156
121760022 | B | LC | ETL.1440.INSL | 40615561 | SACTO | SIERRA | 2021-07-19 | 2021-09-14 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40590122 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0042156
121791249 | E | LC | ETL.8365.POLE.NWOD | 40906671 | EUREKA | HUMBOLDT | 2021-07-24 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40906671 | 2011-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0020282
121791365 | B | LC | ETL.8365.INSL.NCER | 44356225 | EUREKA | HUMBOLDT | 2021-07-24 | 2021-08-21 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44356205 | 2016-06-21 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End | 2016-06-21 | Polymer | Dead End |  |  |  |  | 0.050365
121796771 | E | LC | ETL.9240.TOWR | 43249526 | PISMOBCH | LOS PADRES | 2021-07-26 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 43249526 |  | LATTICE STEEL TOWER | [9 empty] | 2931.7146
121797731 | E | LC | ETL.5281.INSL.CERA | 40879462 | PISMOBCH | FRESNO | 2021-07-26 |  | ETL.5281 | CALIFORNIA FLATS SW STA-GATES | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40858101 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00015184
121804588 | E | LC | ETL.5960.TOWR | 40658662 | PISMOBCH | LOS PADRES | 2021-07-26 | 2021-08-23 | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40658662 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-04-12 | Ceramic | Suspension |  |  |  |  | 1.3176e-05 | 807.0518
121807086 | F | LC | ETL.4393.POLE.STPS | 45074199 | SACTO | SIERRA | 2021-07-26 |  | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44172122 | 2021-03-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.5916e-05 | 949.3081
121809927 | F | LC | ETL.7390.POLE.NWOD | 44202129 | LAKEVLLE | HUMBOLDT | 2021-07-28 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44202129 | 2015-09-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End | 2015-09-01 | Porcelain | Dead End |  |  |  |  | 0.032623
121917565 | F | LC | ETL.9250.POLE.WOOD | 40749552 | MIDWAY | KERN | 2021-08-18 |  | ETL.9250 | TEJON-LEBEC | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40749552 |  | Single Wood Pole | DV - Double Vertical |  | Ceramic | [5 empty] | 0.04857 | 4334.67 | 210.5337
122163234 | E | LC | ETL.4392.INSL.NCER | 40706284 | LAKEVLLE | SONOMA | 2021-10-07 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Emergency | Storm Related | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40648150 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 6.6773e-06 | 1790.5603 | 0.011956
118545223 | E | LC | ETL.5970.TOWR | 40587683 | PISMOBCH | LOS PADRES | 2020-02-18 | 2020-10-19 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587683 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-02-23 | Glass Silicone Coated | Suspension |  |  |  |  | 2.0268e-07 | 2614.7756
118558695 | E | LC | ETL.2410.INSL | 40690028 | LAKEVLLE |  | 2020-02-21 | 2021-06-23 | ETL.2410 | MENDOCINO-REDBUD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118595955 | B | LC | ETL.2270.INSL.CERA | 44737529 | CONCORD | EAST BAY | 2020-03-02 | 2020-06-29 | ETL.2270 | MARTINEZ-SOBRANTE | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40745842 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.695e-06 | 16.3369
118595955 | B | LC | ETL.2270.INSL.CERA | 44737529 | CONCORD | EAST BAY | 2020-03-02 | 2020-06-29 | ETL.2270 | MARTINEZ-SOBRANTE | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40745842 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1941-01-01 | Ceramic | Suspension |  |  |  |  | 2.695e-06 | 16.3369
118679805 | E | LC | ETL.1470.INSL.CERA | 40629623 | LAKEVLLE | SONOMA | 2020-03-11 | 2021-07-09 | ETL.1470 | EAGLE ROCK-CORTINA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40588084 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 0.0016036 | 574.263
118747950 | E | LC | ETL.7030.POLE.NWOD | 44741489 | TABLEMTN | NORTH VALLEY | 2020-03-26 | 2021-06-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44741489 | 2019-04-11 | Light Duty Steel Pole | T-1 - Tri Post | 2019-04-11 | Polymer | Post |  |  |  |  | 0.0011991 | 2802.5758
118756013 | E | LC | ETL.5630.TOWR | 40821648 | TABLEMTN | NORTH VALLEY | 2020-03-30 | 2021-08-19 | ETL.5630 | ROCK CREEK-POE | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40821648 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-31 | Glass | Suspension |  |  |  |  | 3.7409e-09 | 0.065151
118913027 | F | LC | ETL.4850.TOWR | 40760132 | FRESNO | FRESNO | 2020-04-09 |  | ETL.4850 | HAAS-MCCALL | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40760132 | 1957-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1957-01-01 | Ceramic | Suspension |  |  |  |  | 5.1415e-08 | 3911.8955 | 0.00020113
118924898 | F | LC | ETL.6880.POLE.NWOD | 40770406 | LAKEVLLE | SONOMA | 2020-04-13 | 2020-11-10 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 |  |  | DLFL
118942465 | B | LC | ETL.7140.POLE.NWOD | 44618205 | LAKEVLLE | NORTH BAY | 2020-04-22 | 2020-05-19 | ETL.7140 | IGNACIO-BOLINAS #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44618205 | 2018-06-12 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2018-06-12 | Polymer | Suspension |  |  |  |  | 0.00020138 | 332.2847
118950503 | E | LC | ETL.6880.POLE.NWOD | 40593315 | LAKEVLLE | SONOMA | 2020-04-23 | 2021-04-08 | ETL.6880 | FULTON-CALISTOGA | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
118971995 | F | LC | ETL.4392.TOWR | 41129310 | LAKEVLLE | HUMBOLDT | 2020-04-30 | 2021-02-18 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Paint/Coating | [Other, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129310 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.0068729 | 4974.6279
118971995 | F | LC | ETL.4392.TOWR | 41129310 | LAKEVLLE | HUMBOLDT | 2020-04-30 | 2021-02-18 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Paint/Coating | [Other, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129310 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.0068729 | 4974.6279
119036466 | F | LC | ETL.4220.POLE.WDPS | 44557462 | TABLEMTN |  | 2020-05-11 | 2020-06-10 | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] |  | Tier 3 | Within Both | COMP | 44553930 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.085564 | 205.7755
119050017 | F | LC | ETL.6440.POLE.WOOD | 41144158 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-07-14 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41144158 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.006093 | 4531.9639
119061231 | E | LC | ETL.7260.POLE.WOOD | 44651522 | TABLEMTN | NORTH VALLEY | 2020-05-19 |  | ETL.7260 | KESWICK-CASCADE | Guy Pole-Wood | Rotten | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44651522 | 2018-08-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2018-08-01 | Ceramic | Dead End |  |  |  |  | 0.00033324 | 2074.0583 | 0.69116
119061871 | E | LC | ETL.7560.POLE.WOOD | 40586055 | SACTO | SACRAMENTO | 2020-05-25 | 2021-04-05 | ETL.7560 | WEIMAR #1 | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586055 |  | Single Wood Pole | T2N | 2021-04-01 | Polymer | Post |  |  |  |  | 0.042882 | 47.5207
119081580 | F | LC | ETL.1730.POLE.WDPS | 44413301 | MOSSLNDG | CENTRAL COAST | 2020-05-28 | 2020-07-01 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44413299 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.3458e-05 | 31.6948
119082158 | F | LC | ETL.6760.POLE.WOOD | 40767243 | SACTO | SIERRA | 2020-05-28 | 2021-02-10 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40767243 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.013239 | 79.1687
119084466 | F | LC | ETL.6760.POLE.WOOD | 40669960 | SACTO | SIERRA | 2020-05-28 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40669960 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.089311 | 142.4769
119085120 | F | LC | ETL.8405.POLE.WOOD | 40660027 | SACTO | SIERRA | 2020-05-28 | 2021-09-28 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660027 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.061251 | 142.4895
119094158 | F | LC | ETL.7300.POLE.WOOD | 40770403 | TABLEMTN | NORTH VALLEY | 2020-06-02 | 2020-09-03 | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770403 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00075338 | 7461.2464
119112252 | E | LC | ETL.5140.POLE.WDPS | 44557466 | SACTO | SACRAMENTO | 2020-05-22 | 2021-04-27 | ETL.5140 | MIDDLE FORK-GOLD HILL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44554050 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00035079 | 5937.4214
119115240 | F | LC | ETL.6220.POLE.WOOD | 40769355 | EUREKA | HUMBOLDT | 2020-06-02 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40769355 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.054248 | 300.5862
119118160 | F | LC | ETL.7290.POLE.NWOD | 44175301 | TABLEMTN | NORTH VALLEY | 2020-05-28 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
119118585 | F | LC | ETL.8290.POLE.WOOD | 40601143 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-03-29 | ETL.8290 | VOLTA-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40601143 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.007942 | 762.0938
119119338 | F | LC | ETL.8290.POLE.WOOD | 40752204 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40752204 |  | Single Wood Pole | TP - Tri Pin | 2013-03-29 | Ceramic | Pin |  |  |  |  | 0.00010915 | 3829.1331
119126108 | F | LC | ETL.6520.POLE.WOOD | 40772191 | SACTO | SIERRA | 2020-06-02 |  | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40772191 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0094663 | 1919.2795
119127470 | E | LC | ETL.6280.POLE.WOOD | 40816762 | TABLEMTN | NORTH VALLEY | 2020-06-03 | 2020-11-06 | ETL.6280 | CARIBOU #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40816762 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0020066 | 5538.7192
119127495 | E | LC | ETL.7300.POLE.WOOD | 41118629 | TABLEMTN |  | 2020-06-03 | 2021-01-13 | ETL.7300 | KILARC-DESCHUTES | Vegetation | Overgrown | [Trim, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 41118629 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00024582 | 4468.0879
119129576 | E | LC | ETL.7300.POLE.WOOD | 40701866 | TABLEMTN |  | 2020-06-03 | 2021-03-10 | ETL.7300 | KILARC-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40701866 |  | Single Wood Pole | T2N | 2021-03-05 | Polymer | Post |  |  |  |  | 0.00096151 | 367.2775
119161601 | F | LC | ETL.8365.POLE.NWOD | 40912541 | EUREKA | HUMBOLDT | 2020-06-09 | 2021-04-19 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40912541 |  | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | Suspension |  |  |  |  | 0.011654
119166668 | F | LC | ETL.1050.TOWR | 40663232 | FRESNO | FRESNO | 2020-06-15 |  | ETL.1050 | BALCH-SANGER | Fence / Gate | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40663232 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1923-01-01 | Porcelain | Suspension |  |  |  |  | 0.0012537 | 5430.0181
119174891 | E | LC | ETL.3540.INSL.CERA | 40636618 | PISMOBCH | LOS PADRES | 2020-06-16 | 2021-08-03 | ETL.3540 | SAN LUIS OBISPO-SANTA MARIA | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40604818 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1958-01-01 | Polymer | Suspension |  |  |  |  | 0.0010544 | 3152.6191
119174891 | E | LC | ETL.3540.INSL.CERA | 40636618 | PISMOBCH | LOS PADRES | 2020-06-16 | 2021-08-03 | ETL.3540 | SAN LUIS OBISPO-SANTA MARIA | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40604818 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 0.0010544 | 3152.6191
119198326 | E | LC | ETL.6470.POLE.WOOD | 40760743 | SACTO | SIERRA | 2020-06-22 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760743 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.26414 | 110.8608
119229098 | E | LC | ETL.7270.POLE.WOOD | 40908550 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2021-08-17 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908550 |  | Single Wood Pole | TRP DE - Tramp Dead End |  | Porcelain | [5 empty] | 0.0049078 | 1851.2888
119232372 | E | LC | ETL.6470.INSL.CERA | 40894345 | SACTO | SACRAMENTO | 2020-06-29 | 2021-07-29 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40869661 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.097185 | 129.8254
119235407 | F | LC | ETL.1331.POLE.WOOD | 40657163 | LAKEVLLE | SONOMA | 2020-06-30 | 2020-11-10 | ETL.1331 | LUCERNE #1 TAP | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40657163 | 1973-01-01 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 1973-01-01 | Non Ceramic | Dead End |  |  |  |  | 7.7958e-06 | 1518.6221
119291172 | E | LC | ETL.7030.POLE.WOOD | 40673602 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-05-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40673602 |  | Single Wood Pole | DDE - Double Dead End | 2018-12-03 | Polymer | Dead End - Suspension |  |  |  |  | 0.076251 | 3642.7617
119293329 | F | LC | ETL.8060.POLE.WOOD | 40702036 | SACTO | SIERRA | 2020-06-29 | 2021-08-19 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40702036 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.033608 | 3274.9534
119293978 | F | LC | ETL.6890.POLE.NWOD | 44235920 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44235920 | 2014-12-29 | Light Duty Steel Pole | T-1 - Tri Post | 2014-12-29 | Polymer | Post |  |  |  |  | 1.0043e-06 | 2236.0244
119337174 | E | LC | ETL.7180.POLE.WOOD | 40827654 | LAKEVLLE | SONOMA | 2020-07-09 | 2021-04-08 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827654 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 5.3178e-06 | 3027.2869
119341725 | E | LC | ETL.5140.POLE.WDPS | 44553638 | SACTO | SACRAMENTO | 2020-07-08 | 2021-11-08 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44553170 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.0219e-05 | 6774.7476 | 0.069228
119353991 | F | LC | ETL.9090.POLE.NWOD | 44888277 | PISMOBCH | LOS PADRES | 2020-07-09 |  | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44888277 |  | Light Duty Steel Pole | FSS - Field Switch Structure | [7 empty] | 0.0060039 | 1420.2612
119356018 | E | LC | ETL.6280.POLE.WOOD | 40758675 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758675 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00013392 | 6569.0815 | 0.87971
119357781 | E | LC | ETL.5440.POLE.WDPS | 44558416 | TABLEMTN |  | 2020-07-10 | 2020-08-19 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44557950 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.091112 | 253.2084
119358825 | E | LC | ETL.4750.TOWR | 41129175 | LAKEVLLE | SONOMA | 2020-07-11 | 2021-04-12 | ETL.4750 | GEYSERS #12-FULTON | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 41129175 | 1973-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.0005476 | 1172.524
119361341 | E | LC | ETL.8060.POLE.WOOD | 40828179 | SACTO | SACRAMENTO | 2020-07-13 | 2021-05-10 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40828179 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.085124 | 221.6944
119462216 | E | LC | ETL.6290.POLE.NWOD | 40875441 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-03-25 | ETL.6290 | CARIBOU-PLUMAS JCT | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40875441 | 2006-01-01 | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 0.0017039 | 3053.0505
119467509 | F | LC | ETL.7780.POLE.WOOD | 40763013 | LAKEVLLE | SONOMA | 2020-07-17 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40763013 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Other |  |  |  |  | 5.7212e-05 | 2422.8909
119471498 | E | LC | ETL.6220.POLE.NWOD | 44414891 | EUREKA | HUMBOLDT | 2020-07-18 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44414891 | 2018-07-22 | Light Duty Steel Pole | T-1 - Tri Post | 2018-07-22 | Polymer | Post |  |  |  |  | 0.020794 | 1737.1102 | 36.1211
119479886 | F | LC | ETL.5440.POLE.STPS | 44313720 | TABLEMTN | NORTH VALLEY | 2020-07-20 | 2020-08-19 | ETL.5440 | PIT #6 JCT-ROUND MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44313719 | 2016-10-10 | 2-Pole Non Wood | Unknown | [7 empty] | 9.9425e-05 | 2217.3672
119481134 | B | LC | ETL.6280.INSL.CERA | 44667892 | TABLEMTN | NORTH VALLEY | 2020-07-20 | 2020-10-08 | ETL.6280 | CARIBOU #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40875435 |  | Single Wood Pole | BDE - Buck Dead End | 2018-10-30 | Ceramic | Suspension |  |  |  |  | 1.1597e-05 | 1202.1041
119484937 | E | LC | ETL.1650.POLE.WOOD | 40587964 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-02-03 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587964 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post | 1966-01-01 | Polymer | Suspension |  |  |  |  | 0.00016708 | 3263.3687
119487599 | E | LC | ETL.7780.POLE.WOOD | 40819513 | LAKEVLLE | SONOMA | 2020-07-22 | 2021-09-23 | ETL.7780 | PHILO JCT-ELK | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40819513 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 1.0604e-05 | 1150.8735
119487626 | F | LC | ETL.7550.POLE.WOOD | 44676882 | LAKEVLLE | HUMBOLDT | 2020-07-21 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44676882 | 2017-10-16 | Single Wood Pole | T2N | 2018-10-17 | Polymer | Post |  |  |  |  | 0.00024989 | 1063.8021
119560725 | F | LC | ETL.7180.POLE.WOOD | 40743141 | LAKEVLLE | NORTH BAY | 2020-08-04 | 2021-09-28 | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40743141 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 0.00018926 | 31.7201
119566488 | E | LC | ETL.8365.POLE.WOOD | 40587732 | EUREKA | HUMBOLDT | 2020-08-05 | 2021-05-04 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40587732 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0018091 | 4895.8984
119567667 | E | LC | ETL.7780.POLE.NWOD | 44837852 | LAKEVLLE | HUMBOLDT | 2020-08-05 | 2021-03-15 | ETL.7780 | PHILO JCT-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44837852 | 2019-06-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-06-18 | Polymer | Dead End |  |  |  |  | 5.0201e-08 | 1870.5461
119591846 | F | LC | ETL.7590.POLE.WOOD | 40612288 | MOSSLNDG | CENTRAL COAST | 2020-08-10 | 2020-09-24 | ETL.7590 | MONTA VISTA-BURNS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
119591957 | F | LC | ETL.9210.POLE.WOOD | 40661133 | MIDWAY | KERN | 2020-08-10 | 2021-01-25 | ETL.9210 | TAFT-CUYAMA #2 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40661133 | 1946-01-01 | Single Wood Pole | 2P DDE - 2 Pole Double Dead End | 1946-01-01 | Ceramic | Pin |  |  |  |  | 0.010894
119609486 | B | LC | ETL.4050.POLE.WDPS | 44558421 | LAKEVLLE |  | 2020-04-01 | 2020-11-10 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119644984 | B | LC | ETL.8650.TOWR | 40606162 | FRESNO | FRESNO | 2020-08-20 | 2020-12-09 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40606162 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0044388 | 6995.4082
119652808 | F | LC | ETL.4770.POLE.NWOD | 44191443 | LAKEVLLE | SONOMA | 2020-08-21 |  | ETL.4770 | GEYSERS #17-FULTON | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44191443 |  | Tubular Steel Pole | DV-PJ - Double Vertical Post Jumper | [7 empty] | 1.395e-05 | 3726.486
119658792 | A | LC | ETL.6240.POLE.WOOD | 40864094 | MOSSLNDG | CENTRAL COAST | 2020-08-22 | 2020-10-19 | ETL.6240 | BURNS-LONE STAR #2 | Emergency-Wood | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40864094 |  | Single Wood Pole | T-1 - Tri Post | 2019-05-24 | Polymer | Post |  |  |  |  | 0.35203 | 19.0509
119685464 | F | LC | ETL.1110.POLE.WDPS | 44423240 | TABLEMTN | HUMBOLDT | 2020-08-25 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44423238 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014502 | 4765.7319
119687243 | B | LC | ETL.6490.POLE.WOOD | 44190861 | SACTO | SIERRA | 2020-08-26 | 2020-09-23 | ETL.6490 | COLGATE-GRASS VALLEY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44190861 |  | Single Wood Pole | Unknown | [7 empty] | 0.0088881 | 428.1771
119692393 | A | LC | ETL.7590.POLE.WOOD | 40599199 | MOSSLNDG | CENTRAL COAST | 2020-08-30 | 2020-09-24 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119696501 | B | LC | ETL.5462.TOWR | 40871900 | CONCORD | DIABLO | 2020-08-26 | 2020-10-07 | ETL.5462 | PITTSBURG-EASTSHORE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871900 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2001-01-01 | Non Ceramic | Suspension |  |  |  |  | 3.2039e-09 | 4987.3877
119696501 | B | LC | ETL.5462.TOWR | 40871900 | CONCORD | DIABLO | 2020-08-26 | 2020-10-07 | ETL.5462 | PITTSBURG-EASTSHORE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871900 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2001-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 3.2039e-09 | 4987.3877
119698845 | B | LC | ETL.6380.INSL.CERA | 44433442 | LAKEVLLE |  | 2020-08-31 | 2020-10-21 | ETL.6380 | KONOCTI-MIDDLETOWN | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750188 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-09-29 | Ceramic | Suspension |  |  |  |  | 6.8003e-05 | 4829.3574
119722513 | E | LC | ETL.8351.POLE.WOOD | 40600010 | VICTOR | STOCKTON | 2020-07-31 | 2021-06-10 | ETL.8351 | PINE GROVE TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.00036443 | 300.6168
119750430 | E | LC | ETL.7290.POLE.WOOD | 40816390 | TABLEMTN | NORTH VALLEY | 2020-08-27 |  | ETL.7290 | KILARC-CEDAR CREEK | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40816390 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.024133 | 1634.3816 | 39.4427
119762251 | B | LC | ETL.7490.INSL | 40835330 | EUREKA | HUMBOLDT | 2020-09-14 | 2020-11-17 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40810442 | 2011-01-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Ceramic | [5 empty] | 0.00018867 | 118.7001
119763863 | F | LC | ETL.2395.POLE.WDPS | 44551415 | TABLEMTN | NORTH VALLEY | 2020-09-08 | 2021-01-20 | ETL.2395 | GRIZZLY TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44550853 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0065526 | 189.8861
119781290 | E | LC | ETL.7380.POLE.NWOD | 40647417 | MOSSLNDG | CENTRAL COAST | 2020-09-09 | 2021-04-05 | ETL.7380 | LAURELES-OTTER | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40647417 | 2009-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.28157 | 15.8815
119787777 | E | LC | ETL.1440.POLE.WOOD | 42572718 | SACTO | SIERRA | 2020-09-17 | 2021-06-28 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0014502 | 458.8659
119790498 | F | LC | ETL.3740.TOWR | 40746124 | CONCORD | EAST BAY | 2020-07-31 | 2021-04-19 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746124 | 1961-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 0.044457 | 47.5494
119790808 | F | LC | ETL.4220.POLE.STPS | 44388373 | TABLEMTN |  | 2020-08-04 |  | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44388371 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.4925e-05 | 1012.6957
119800009 | F | LC | ETL.6490.POLE.WOOD | 40665880 | SACTO | SIERRA | 2020-09-19 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40665880 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.010027 | 5778.439
119818287 | F | LC | ETL.7290.POLE.WOOD | 40602033 | TABLEMTN | NORTH VALLEY | 2020-09-11 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40602033 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.076137 | 110.843
119819598 | F | LC | ETL.7300.POLE.NWOD | 44837870 | TABLEMTN | NORTH VALLEY | 2020-08-31 |  | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44837870 | 2019-03-25 | Light Duty Steel Pole | T2N |  | Porcelain | Post |  |  |  |  | 5.7576e-07 | 394.0576
119840494 | E | LC | ETL.7180.POLE.STPS | 44376987 | LAKEVLLE | NORTH BAY | 2020-07-28 |  | ETL.7180 | IGNACIO-BOLINAS #2 | FAA Lighting-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44376987 | 2016-10-12 | 2-Pole Non Wood | Unknown | 2016-10-12 | Polymer | Suspension |  |  |  |  | 1.4979e-08
119840494 | E | LC | ETL.7180.POLE.STPS | 44376987 | LAKEVLLE | NORTH BAY | 2020-07-28 |  | ETL.7180 | IGNACIO-BOLINAS #2 | FAA Lighting-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44376987 | 2016-10-12 | 2-Pole Non Wood | Unknown | 2016-10-12 | Polymer | Suspension |  |  |  |  | 1.4979e-08
119864607 | B | LC | ETL.6240.INSL.NCER | 40732019 | MOSSLNDG | CENTRAL COAST | 2020-10-06 | 2020-12-07 | ETL.6240 | BURNS-LONE STAR #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119898534 | F | LC | ETL.6980.POLE.WOOD | 40860964 | LAKEVLLE | HUMBOLDT | 2020-10-07 | 2021-02-10 | ETL.6980 | FORT ROSS-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40860964 | 1953-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.26392 | 174.2028
119899424 | E | LC | ETL.8170.POLE.NWOD | 44846598 | EUREKA | HUMBOLDT | 2020-10-07 | 2021-06-21 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44846598 | 2019-05-10 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-05-10 | Glass | Dead End |  |  |  |  | 0.00024379 | 0.065152
119917069 | E | LC | ETL.1650.POLE.NWOD | 40740186 | LAKEVLLE | SONOMA | 2020-10-13 | 2021-02-17 | ETL.1650 | GEYSERS #3-CLOVERDALE | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40740186 | 2011-01-01 | Light Duty Steel Pole | 3HP - 3 Horizontal Post | 1989-01-01 | Polymer | Dead End |  |  |  |  | 6.5575e-07 | 3278.8411
119972720 | F | LC | ETL.6240.POLE.WOOD | 40864096 | MOSSLNDG | CENTRAL COAST | 2020-10-28 |  | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40864096 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.1279 | 110.8153
119985910 | E | LC | ETL.6390.POLE.NWOD | 45004738 | LAKEVLLE | HUMBOLDT | 2020-11-05 | 2021-03-31 | ETL.6390 | CLEAR LAKE-HOPLAND | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45004738 | 2020-10-28 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-10-28 | Glass | Dead End |  |  |  |  | 7.0005e-09 | 601.7605
119995715 | F | LC | ETL.6880.POLE.NWOD | 44324057 | LAKEVLLE | NORTH BAY | 2020-10-06 | 2021-04-19 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44324057 | 2014-12-10 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | [7 empty] | 1.1883e-06 | 4876.5742
120015922 | E | LC | ETL.1650.POLE.WOOD | 40594051 | LAKEVLLE | SONOMA | 2020-11-12 | 2021-02-08 | ETL.1650 | GEYSERS #3-CLOVERDALE | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594051 | 1993-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1966-01-01 | Porcelain | Dead End |  |  |  |  | 0.00012446 | 3263.3687
120088800 | E | LC | ETL.3170.INSL | 40705066 | CONCORD | EAST BAY | 2020-11-18 |  | ETL.3170 | OLEUM-MARTINEZ | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40646332 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.0723e-06 | 16.3369 | 3.3855e-05
120144194 | F | LC | ETL.8650.TOWR | 44859214 | FRESNO | YOSEMITE | 2020-12-07 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44859214 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-11-18 | Glass | Suspension |  |  |  |  | 0.022296 | 0.077799
120163512 | F | LC | ETL.5100.TOWR | 40872309 | MOSSLNDG | SAN JOSE | 2020-11-04 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Structure-Steel | Paint/Coating | [Other] |  | Non-HFTD | HFRA Addition | PEND | 40872309 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2005-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.6249e-07 | 5160.8779 | 0.00083858
120190448 | E | LC | ETL.8405.SWIT | 40744199 | SACTO | SACRAMENTO | 2020-12-12 | 2020-12-14 | ETL.8405 | MIDDLE FORK #1 | Switch | Out of Adjustment | [Repair, Completed] | Tier3 |  |  | COMP | [8 empty] | Inertia | VACUUM INTERRUPTER (3 GAP) | SCADA Only
120237596 | F | LC | ETL.1450.POLE.NWOD | 44766954 | SACTO | SIERRA | 2020-12-02 | 2021-02-09 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44766954 | 2019-05-07 | Light Duty Steel Pole | DDE - Double Dead End | 2019-05-07 | Glass | Suspension |  |  |  |  | 2.3254e-07 | 443.0452
120664940 | F | LC | ETL.4430.POLE.NWOD | 40741832 | TABLEMTN | NORTH VALLEY | 2021-03-19 |  | ETL.4430 | BUCKS CREEK-ROCK CREEK-CRESTA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40741832 |  | Lattice Steel Pole | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 0.00013836 | 6806.3008
120695547 | F | LC | ETL.3830.TOWR | 40581586 | VICTOR | STOCKTON | 2021-03-25 | 2021-04-19 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | DLFL | 40581586 | 1963-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.971e-08 | 1962.8882
120715091 | B | LC | ETL.3830.INSL | 40669647 | VICTOR | STOCKTON | 2021-03-25 | 2021-05-26 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40642775 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.2069e-06 | 158.4159
120715193 | B | LC | ETL.8480.INSL.CERA | 44308909 | PISMOBCH | LOS PADRES | 2021-03-30 | 2021-04-29 | ETL.8480 | ATASCADERO-CAYUCOS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40596619 | 1954-01-01 | Single Wood Pole | WB - Wishbone | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 0.00024041 | 3400.6272
120724816 | B | LC | ETL.6760.POLE.WOOD | 44224123 | SACTO | SACRAMENTO | 2021-03-30 | 2021-06-23 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Switch | Out of Adjustment | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44224123 | 2016-05-16 | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0022105 | 1138.9978
120735028 | F | LC | ETL.5650.TOWR | 40608483 | TABLEMTN | NORTH VALLEY | 2021-04-02 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40608483 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 2.8968e-08 | 4294.4004 | 0.0001244
120737349 | E | LC | ETL.7390.POLE.WOOD | 44412208 | LAKEVLLE | HUMBOLDT | 2021-04-02 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44412208 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.087892
120757247 | F | LC | ETL.8350.POLE.NWOD | 44920046 | VICTOR | STOCKTON | 2021-04-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44920046 | 2020-01-15 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-01-15 | Polymer | Dead End |  |  |  |  | 8.267e-06 | 3626.2236
120757975 | E | LC | ETL.8405.POLE.WOOD | 40862123 | SACTO | SACRAMENTO | 2021-04-07 | 2021-10-04 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40862123 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.17006 | 2531.4304 | 430.493
120759114 | F | LC | ETL.4440.TOWR | 40588540 | TABLEMTN | NORTH VALLEY | 2021-03-26 | 2021-07-14 | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40588540 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 1.971e-08 | 0.39411
120770376 | E | LC | ETL.2540.POLE.WDPS | 44401579 | MOSSLNDG | CENTRAL COAST | 2021-04-08 | 2021-08-18 | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [12 empty] | 2455.0217
120771612 | B | LC | ETL.3190.TOWR | 40910329 | TABLEMTN | NORTH VALLEY | 2021-04-08 | 2021-06-23 | ETL.3190 | CARIBOU-PALERMO | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910329 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.18348 | 5994.5195
120786263 | E | LC | ETL.6030.TOWR | 40860578 | MIDWAY | KERN | 2021-04-10 |  | ETL.6030 | MIDWAY-WHIRLWIND | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40860578 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-12-09 | Glass Silicone Coated | Suspension |  |  |  |  | 5.8828e-05 | 6985.7988 | 0.41096
120793618 | E | LC | ETL.7140.INSL.NCER | 44663938 | LAKEVLLE | NORTH BAY | 2021-04-12 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44663908 | 2018-10-18 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2018-10-18 | Polymer | Dead End |  |  |  |  | 0.014946
120793618 | E | LC | ETL.7140.INSL.NCER | 44663938 | LAKEVLLE | NORTH BAY | 2021-04-12 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44663908 | 2018-10-18 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2018-10-18 | Polymer | Dead End |  |  |  |  | 0.014946
120793618 | E | LC | ETL.7140.INSL.NCER | 44663938 | LAKEVLLE | NORTH BAY | 2021-04-12 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44663908 | 2018-10-18 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2018-10-18 | Polymer | Dead End |  |  |  |  | 0.014946
120794897 | E | LC | ETL.7270.INSL.CERA | 40834665 | TABLEMTN | NORTH VALLEY | 2021-04-12 |  | ETL.7270 | KESWICK-TRINITY | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40809913 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.12457 | 840.0571 | 104.6453
120798248 | E | LC | ETL.4040.POLE.NWOD | 44964279 | TABLEMTN | NORTH VALLEY | 2021-04-12 | 2021-10-06 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44964279 | 2020-08-17 | Light Duty Steel Pole | DV - Double Vertical | 2020-08-17 | Glass | Dead End |  |  |  |  | 5.812e-07 | 0.065152 | 3.7866e-08
120799372 | B | LC | ETL.8250.POLE.WOOD | 40912851 | VICTOR | STOCKTON | 2021-04-12 | 2021-05-17 | ETL.8250 | CLAY-MARTEL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40912851 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0044938 | 2931.7273
120804616 | B | LC | ETL.3830.TOWR | 40803328 | VICTOR | STOCKTON | 2021-04-12 | 2021-06-08 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803328 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.1958e-05 | 2156.2512
120808147 | F | LC | ETL.5660.TOWR | 40857926 | CONCORD | DIABLO | 2021-04-13 |  | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40857926 | 1960-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2014-11-17 | Ceramic | Dead End |  |  |  |  | 2.3361e-07 | 3043.1921 | 0.00071091
120808954 | E | LC | ETL.8365.POLE.WOOD | 40912604 | EUREKA | HUMBOLDT | 2021-04-13 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Vegetation | Overgrown | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40912604 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-04-22 | Glass | Double Dead End |  |  |  |  | 0.19011
120872101 | E | LC | ETL.4460.INSL | 40724542 | MOSSLNDG | CENTRAL COAST | 2021-04-21 |  | ETL.4460 | COBURN-LAS AGUILAS SW STA | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40681545 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 3.0119e-08 | 1599.4381 | 4.8174e-05
120872101 | E | LC | ETL.4460.INSL | 40724542 | MOSSLNDG | CENTRAL COAST | 2021-04-21 |  | ETL.4460 | COBURN-LAS AGUILAS SW STA | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40681545 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 3.0119e-08 | 1599.4381 | 4.8174e-05
120874906 | E | LC | ETL.1820.POLE.WDPS | 44560038 | EUREKA | HUMBOLDT | 2021-04-23 |  | ETL.1820 | HUMBOLDT-TRINITY | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40662077 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.80044 | 71.3456 | 57.108
120879331 | E | LC | ETL.1810.POLE.STPS | 44994665 | EUREKA | HUMBOLDT | 2021-04-22 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44994623 | 2020-04-20 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.8524e-06
120880467 | E | LC | ETL.2770.TOWR | 40821788 | CONCORD | DIABLO | 2021-04-23 | 2021-09-01 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40821788 | 1925-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2021-08-22 | Glass | Double Dead End |  |  |  |  | 1.339e-06 | 443.3777
120880467 | E | LC | ETL.2770.TOWR | 40821788 | CONCORD | DIABLO | 2021-04-23 | 2021-09-01 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40821788 | 1925-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 1.339e-06 | 443.3777
120886007 | E | LC | ETL.1250.POLE.WOOD | 40748526 | FRESNO | YOSEMITE | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40748526 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 4.5878e-06 | 4946.1465 | 0.022692
120890294 | E | LC | ETL.3740.INSL.NCER | 42582021 | CONCORD | EAST BAY | 2021-04-27 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44188837 | 2008-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Polymer | Dead End |  |  |  |  | 0.068226 | 2042.6962 | 139.3646
120903716 | E | LC | ETL.5980.TOWR | 40651877 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40651877 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 3.3317e-08 | 3582.1601 | 0.00011935
120911560 | E | LC | ETL.5930.TOWR | 40758934 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758934 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-03-09 | Glass | Suspension |  |  |  |  | 1.8358e-05 | 461.5973 | 0.0084739
120911560 | E | LC | ETL.5930.TOWR | 40758934 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758934 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-29 | Glass | Suspension |  |  |  |  | 1.8358e-05 | 461.5973 | 0.0084739
120937516 | F | LC | ETL.4870.TOWR | 40576596 | FRESNO | FRESNO | 2021-05-05 |  | ETL.4870 | HELMS-GREGG #1 | Right of Way | Encroachment | [Remove] |  | Zone 1 | HFRA Removal | PEND | 40576596 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 9.1968e-06 | 15.8815
121099250 | F | LC | ETL.1530.TOWR | 40660238 | SACTO | SIERRA | 2021-04-19 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40660238 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Ceramic | Suspension |  |  |  |  | 8.3573e-06 | 63.3607 | 0.00052952
121188025 | E | LC | ETL.4000.INSL.NCER | 40913552 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.4000 | TESLA-SALADO-MANTECA | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40903946 | 1964-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 1964-01-01 | Polymer | [5 empty] | 0.020955 | 765.6094 | 16.0432
121328948 | F | LC | ETL.1480.TOWR | 40585024 | LAKEVLLE | HUMBOLDT | 2021-04-24 |  | ETL.1480 | EAGLE ROCK-REDBUD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40585024 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1978-01-01 | Glass | Dead End |  |  |  |  | 0.00010471 | 5161.9355 | 0.54048
121332585 | E | LC | ETL.1480.INSL.CERA | 40815880 | LAKEVLLE |  | 2021-05-14 |  | ETL.1480 | EAGLE ROCK-REDBUD | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40809066 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 0.041358 | 2620.2085 | 108.3675
121337020 | F | LC | ETL.2395.POLE.WOOD | 45001467 | TABLEMTN | NORTH VALLEY | 2021-05-14 | 2021-06-08 | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45001467 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | Dead End |  |  |  |  | 0.00026142 | 3021.0042
121339027 | F | LC | ETL.6480.POLE.NWOD | 45122792 | SACTO | NORTH VALLEY | 2021-05-14 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45122792 | 2021-06-20 | Light Duty Steel Pole | T-1 - Tri Post | 2021-06-20 | Polymer | Post | [5 empty] | 253.3131
121343408 | B | LC | ETL.8365.POLE.WOOD | 44820235 | EUREKA | HUMBOLDT | 2021-05-17 | 2021-07-06 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44820235 | 2019-06-23 | Single Wood Pole | TCDE - Tap Construction Dead End | 2019-06-23 | Polymer | Post |  |  |  |  | 0.010031
121355053 | E | LC | ETL.5540.TOWR | 40757663 | TABLEMTN | NORTH VALLEY | 2021-04-28 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40757663 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 1.2651e-07 | 8372.3613 | 0.0010592
121356930 | F | LC | ETL.4870.TOWR | 40576618 | FRESNO | FRESNO | 2021-04-21 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576618 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 2.3212e-07 | 3701.0801 | 0.0008591
121357172 | F | LC | ETL.7270.POLE.NWOD | 40577347 | TABLEMTN | NORTH VALLEY | 2021-04-29 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40577347 | 2011-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.0010835 | 1567.3287
121373391 | E | LC | ETL.5070.TOWR | 40591725 | FRESNO | YOSEMITE | 2021-05-04 |  | ETL.5070 | QUINTO SW STA-WESTLEY | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40591725 | 1947-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1947-01-01 | Ceramic | Suspension |  |  |  |  | 1.6523e-06 | 765.584 | 0.001265
121377891 | F | LC | ETL.1070.POLE.WOOD | 40822207 | VICTOR | YOSEMITE | 2021-05-05 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40822207 | 1957-01-01 | Single Wood Pole | T-1 - Tri Post | 1957-01-01 | Polymer | Suspension |  |  |  |  | 3.0419e-05 | 2009.5964
121379814 | B | LC | ETL.4440.POLE.NWOD | 44191409 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-30 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191409 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 3.3481e-06 | 1388.9466
121381239 | F | LC | ETL.8250.POLE.WOOD | 40908831 | VICTOR | STOCKTON | 2021-05-10 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908831 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0057346 | 1759.9811
121382802 | F | LC | ETL.6470.POLE.WOOD | 40874614 | SACTO | SIERRA | 2021-05-11 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40874614 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.014583 | 4700.8066
121383588 | F | LC | ETL.6470.POLE.WOOD | 40598533 | SACTO | SIERRA | 2021-05-11 | 2021-08-16 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40598533 |  | Single Wood Pole | T2N | 2021-08-08 | Polymer | Post |  |  |  |  | 0.010912 | 5650.8154
121385157 | E | LC | ETL.6760.POLE.WOOD | 40822742 | SACTO | SIERRA | 2021-05-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40822742 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | Post |  |  |  |  | 0.0070823 | 632.8055 | 4.4817
121388957 | E | LC | ETL.6220.POLE.NWOD | 45019161 | EUREKA | HUMBOLDT | 2021-05-24 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45019161 | 2020-10-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-10-03 | Glass | Dead End |  |  |  |  | 0.041282 | 475.8321 | 19.6431
121405496 | E | LC | ETL.8405.POLE.WOOD | 40824460 | SACTO | SIERRA | 2021-05-21 |  | ETL.8405 | MIDDLE FORK #1 | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40824460 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.17337 | 189.9644 | 32.9342
121416935 | E | LC | ETL.6640.POLE.WOOD | 40601179 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40601179 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0063214 | 933.8852 | 5.9035
121428438 | E | LC | ETL.7290.POLE.WOOD | 40873632 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40873632 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.015335 | 2329.9167 | 35.7288
121436109 | B | LC | ETL.5640.TOWR | 40816241 | TABLEMTN | NORTH VALLEY | 2021-05-29 | 2021-06-30 | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816241 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 2.5871e-06 | 2710.3174
121466051 | F | LC | ETL.9330.TOWR | 40758591 | FRESNO | FRESNO | 2021-06-02 |  | ETL.9330 | WISHON-COPPERMINE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758591 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.024784 | 6742.6743
121485676 | E | LC | ETL.1820.POLE.WDPS | 44560109 | EUREKA | HUMBOLDT | 2021-05-28 | 2021-07-12 | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44560109 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.11951
121485676 | E | LC | ETL.1820.POLE.WDPS | 44560109 | EUREKA | HUMBOLDT | 2021-05-28 | 2021-07-12 | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44560109 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.11951
121485676 | E | LC | ETL.1820.POLE.WDPS | 44560109 | EUREKA | HUMBOLDT | 2021-05-28 | 2021-07-12 | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44560109 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.11951
121491993 | B | LC | ETL.8350.POLE.WOOD | 40643843 | VICTOR | STOCKTON | 2021-06-08 | 2021-09-09 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40643843 | 1993-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Glass | [5 empty] | 1.1268e-05 | 4759.0768
121499047 | F | LC | ETL.1073.POLE.WDPS | 44974305 | VICTOR | YOSEMITE | 2021-06-04 | 2021-07-19 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40643749 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00060567 | 31.7081
121514104 | F | LC | ETL.1070.POLE.WDPS | 44387577 | VICTOR | STOCKTON | 2021-06-01 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44387574 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 9.7405e-06 | 1079.6021 | 0.010516
121514213 | E | LC | ETL.1450.POLE.WDPS | 44552575 | SACTO | SACRAMENTO | 2021-06-10 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44551679 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0047392 | 784.8264 | 3.7195
121516207 | B | LC | ETL.6500.INSL.CERA | 43690670 | TABLEMTN | NORTH VALLEY | 2021-06-09 | 2021-07-08 | ETL.6500 | COLGATE-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 43690666 | 2015-08-20 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2015-08-20 | Porcelain | Dead End |  |  |  |  | 0.01652 | 4948.6592
121517056 | E | LC | ETL.1440.POLE.WDPS | 44162092 | SACTO | SACRAMENTO | 2021-06-04 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44162091 | 2013-09-22 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0003565 | 177.2951 | 0.063206
121520540 | E | LC | ETL.4040.POLE.STPS | 44647153 | TABLEMTN | NORTH VALLEY | 2021-06-04 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44646903 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0017929 | 427.7504 | 0.76692
121523068 | E | LC | ETL.8060.POLE.NWOD | 44349479 | SACTO | SIERRA | 2021-06-07 |  | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44349479 | 2018-09-06 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-09-06 | Ceramic | Dead End |  |  |  |  | 0.00043456 | 31.7066 | 0.013778
121534538 | F | LC | ETL.1450.POLE.WDPS | 44150217 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44150216 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00026051 | 31.7066
121538326 | B | LC | ETL.4750.INSL.CERA | 40636809 | LAKEVLLE | SONOMA | 2021-06-14 | 2021-08-30 | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40605180 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Porcelain | Suspension |  |  |  |  | 2.9859e-06 | 2663.8809
121543217 | F | LC | ETL.1350.POLE.NWOD | 44993120 | TABLEMTN | NORTH VALLEY | 2021-06-12 |  | ETL.1350 | CRAG VIEW-CASCADE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44993120 | 2020-06-04 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-04 | Glass | Dead End |  |  |  |  | 5.9411e-05 | 0.065152
121545747 | E | LC | ETL.5650.INSL | 40899250 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40873486 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.0213e-06 | 4753.4604 | 0.0048546
121546800 | E | LC | ETL.6760.INSL.NCER | 40615677 | SACTO | SACRAMENTO | 2021-06-16 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40590237 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.022482 | 0.06515 | 0.0014647
121548244 | F | LC | ETL.6720.POLE.WDPS | 44950335 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42578837 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0025222 | 2104.1226 | 5.307
121562271 | F | LC | ETL.7550.POLE.WDPS | 44211137 | LAKEVLLE |  | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44211134 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00062638 | 110.7947 | 0.069399
121567929 | F | LC | ETL.7560.POLE.NWOD | 45083836 | SACTO | SIERRA | 2021-06-15 |  | ETL.7560 | WEIMAR #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45083836 | 2021-04-03 | Light Duty Steel Pole | T2N | 2021-04-03 | Polymer | Post |  |  |  |  | 0.014367 | 617.1262
121568292 | F | LC | ETL.6880.POLE.NWOD | 45063788 | LAKEVLLE | SONOMA | 2021-06-15 |  | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45063788 | 2019-08-21 | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-08-21 | Glass | Suspension |  |  |  |  | 3.2025e-06 | 15.8991
121579685 | E | LC | ETL.7180.POLE.WOOD | 40588075 | LAKEVLLE | NORTH BAY | 2021-06-18 | 2021-07-12 | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40588075 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-06-22 | Glass | Dead End |  |  |  |  | 1.4679e-05 | 269.9041
121605229 | F | LC | ETL.3180.POLE.STPS | 44229106 | CONCORD | EAST BAY | 2021-06-23 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44229105 | 2015-07-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.0043e-06 | 16.3369
121625483 | B | LC | ETL.1110.POLE.WOOD | 44191985 | TABLEMTN | NORTH VALLEY | 2021-06-28 | 2021-09-20 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191985 |  | Single Wood Pole | DE - Dead End |  | Polymer | Dead End |  |  |  |  | 0.0051183 | 332.3156
121627683 | E | LC | ETL.6500.POLE.NWOD | 44153662 | SACTO | SACRAMENTO | 2021-06-28 |  | ETL.6500 | COLGATE-PALERMO | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44153662 |  | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | Suspension |  |  |  |  | 4.932e-05 | 428.1771 | 0.021118
121630531 | E | LC | ETL.1450.POLE.WDPS | 44159081 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44159080 | 2013-09-30 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00024162 | 387.6727 | 0.093668
121651683 | F | LC | ETL.1440.POLE.WDPS | 40913111 | SACTO | SIERRA | 2021-06-23 | 2021-07-09 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 0.0044598
121692323 | F | LC | ETL.5960.TOWR | 40576869 | PISMOBCH | LOS PADRES | 2021-07-09 | 2021-07-13 | ETL.5960 | DIABLO-GATES #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40576869 |  | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 1.3509e-06 | 5082.1426
121705851 | E | LC | ETL.4316.POLE.STPS | 45074894 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.4316 | PARADISE-TABLE MTN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40758646 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0020407 | 2995.1147 | 6.112
121708531 | E | LC | ETL.2840.INSL | 40609283 | MOSSLNDG | CENTRAL COAST | 2021-07-10 | 2021-09-14 | ETL.2840 | MOSS LANDING-DEL MONTE #2 | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40584946 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2006-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 5.2304e-09 | 47.5118
121717395 | F | LC | ETL.1450.POLE.WOOD | 42572762 | SACTO | SIERRA | 2021-07-11 |  | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42572762 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Unknown |  |  |  |  | 0.00061711 | 1329.6379 | 0.82053
121717582 | F | LC | ETL.6979.POLE.NWOD | 45094980 | LAKEVLLE | SONOMA | 2021-07-08 |  | ETL.6979 | MONTE RIO-FORT ROSS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45094980 | 2020-04-25 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2020-04-25 | Glass | Double Dead End |  |  |  |  | 5.9003e-05 | 31.7139 | 0.0018712
121724441 | E | LC | ETL.5970.TOWR | 40760794 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.5970 | DIABLO-MIDWAY #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40760794 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 9.3288e-07 | 1298.0298 | 0.0012109
121736319 | E | LC | ETL.1820.POLE.NWOD | 44324169 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44324169 | 2015-12-01 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2015-12-01 | Ceramic | Suspension |  |  |  |  | 0.00051083 | 1174.8506 | 0.60015
121738455 | F | LC | ETL.1450.POLE.STPS | 44964402 | SACTO | SIERRA | 2021-07-12 |  | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44964285 | 2020-08-27 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.9132e-06 | 648.7145
121738833 | F | LC | ETL.6650.POLE.STPS | 44386872 | TABLEMTN | NORTH VALLEY | 2021-07-13 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44386871 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00087994 | 696.4862
121742330 | E | LC | ETL.5510.TOWR | 40590917 | CONCORD | DIABLO | 2021-07-12 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40590917 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 1.655e-06 | 4876.8511 | 0.0080712
121745572 | E | LC | ETL.4870.TOWR | 40858339 | FRESNO | FRESNO | 2021-07-13 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40858339 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 9.7396e-07
121746265 | E | LC | ETL.2395.POLE.WOOD | 44550085 | TABLEMTN | NORTH VALLEY | 2021-07-15 |  | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44550085 |  | Single Wood Pole | SVDE - Single Vertical Dead End |  | Ceramic | Suspension |  |  |  |  | 0.010078 | 1763.6081 | 17.7741
121747956 | F | LC | ETL.1820.POLE.NWOD | 45102856 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45102856 | 2014-09-20 | Light Duty Steel Pole | 3P SV - 3 Pole Single Vertical |  | Ceramic | Suspension |  |  |  |  | 0.023309 | 95.0515
121750401 | E | LC | ETL.6040.TOWR | 40873032 | MOSSLNDG | YOSEMITE | 2021-07-17 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Structure-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40873032 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 3.3648e-05
121756417 | F | LC | ETL.4050.POLE.WOOD | 45111378 | LAKEVLLE | HUMBOLDT | 2021-07-19 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45111378 | 2014-12-29 | Single Wood Pole | DDE - Double Dead End | 2014-12-29 | Polymer | Dead End | [5 empty] | 3880.585
121763135 | E | LC | ETL.2390.POLE.WDPS | 44391296 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391293 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 5.3331e-05 | 996.4046 | 0.05314
121786402 | B | LC | ETL.9240.TOWR | 43249851 | PISMOBCH | LOS PADRES | 2021-07-22 | 2021-08-09 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 43249851 |  | LATTICE STEEL TOWER | [9 empty] | 1475.0885
121805376 | B | LC | ETL.6290.POLE.WOOD | 40659857 | TABLEMTN | NORTH VALLEY | 2021-07-27 | 2021-10-27 | ETL.6290 | CARIBOU-PLUMAS JCT | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40659857 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1962-01-01 | Polymer | Post |  |  |  |  | 0.29874 | 47.5141
121806258 | E | LC | ETL.6070.INSL | 40687391 | TABLEMTN | NORTH VALLEY | 2021-07-26 |  | ETL.6070 | ROUND MTN-TABLE MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40657630 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1967-01-01 | Ceramic | Suspension |  |  |  |  | 0.010882 | 367.404 | 3.9981
121807598 | B | LC | ETL.6220.POLE.WOOD | 40824466 | EUREKA | HUMBOLDT | 2021-07-26 | 2021-09-30 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40824466 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.53266
121810220 | E | LC | ETL.5430.INSL.CERA | 44561546 | TABLEMTN | NORTH VALLEY | 2021-07-26 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560787 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.006291
121810220 | E | LC | ETL.5430.INSL.CERA | 44561546 | TABLEMTN | NORTH VALLEY | 2021-07-26 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560787 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.006291
121810589 | F | LC | ETL.6950.POLE.NWOD | 44174899 | SACTO | SIERRA | 2021-07-28 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44174899 |  | Fiberglass | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00039786 | 617.0629
121810759 | E | LC | ETL.1183.TOWR | 45098584 | LAKEVLLE | HUMBOLDT | 2021-07-26 | 2021-09-10 | ETL.1183 | CALPINE-WEST FORD FLAT | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45098584 |  | LATTICE STEEL TOWER | Unknown |  | Unknown | Unknown | [5 empty] | 206.3359
121810837 | F | LC | ETL.1440.POLE.WDPS | 44149441 | SACTO | SACRAMENTO | 2021-07-27 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44149440 | 2013-11-06 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0010788 | 15.8859
121822625 | E | LC | ETL.2540.POLE.WDPS | 44551368 | MOSSLNDG | CENTRAL COAST | 2021-07-29 |  | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44550898 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.010305 | 2455.0217 | 25.2998
121922036 | B | LC | ETL.6880.POLE.NWOD | 40751176 | LAKEVLLE | SONOMA | 2021-08-19 | 2021-08-24 | ETL.6880 | FULTON-CALISTOGA | Non-Routine Patrol | Investigate | [Air Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751176 |  | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 1.6173e-07 | 4321.8276
121951511 | F | LC | ETL.2395.POLE.WOOD | 44550083 | TABLEMTN | NORTH VALLEY | 2021-07-31 |  | ETL.2395 | GRIZZLY TAP | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550083 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | Dead End |  |  |  |  | 0.00026459 | 3021.0042 | 0.79934
122054878 | E | LC | ETL.4780.INSL.CERA | 40778736 | LAKEVLLE | SONOMA | 2021-09-15 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129174 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | [5 empty] | 0.00072269 | 2059.9019 | 1.4887
122057634 | E | LC | ETL.4780.INSL.NCER | 45128981 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129336 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 2.3059e-06 | 2534.3203 | 0.0058438
122057634 | E | LC | ETL.4780.INSL.NCER | 45128981 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129336 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 2.3059e-06 | 2534.3203 | 0.0058438
122068720 | B | LC | ETL.1420.SWIT | 40743224 | SACTO | SACRAMENTO | 2021-09-17 | 2021-09-27 | ETL.1420 | DRUM-RIO OSO #1 | Switch | Out of Adjustment | [Repair, Completed] | Tier3 |  |  | COMP | [8 empty] | Other | VACUUM INTERRUPTER (1 GAP) | Manual
118595206 | F | LC | ETL.5960.TOWR | 40581808 | PISMOBCH | LOS PADRES | 2020-03-02 |  | ETL.5960 | DIABLO-GATES #1 | FAA Lighting-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40581808 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-04-12 | Ceramic | Suspension |  |  |  |  | 2.6756e-08 | 777.0289
118753692 | E | LC | ETL.7510.POLE.WOOD | 40824954 | LAKEVLLE | SONOMA | 2020-03-27 | 2020-04-16 | ETL.7510 | MENDOCINO-HARTLEY | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824954 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 5.7659e-06 | 632.8055
118772779 | F | LC | ETL.1730.TOWR | 40758012 | MOSSLNDG | CENTRAL COAST | 2020-04-02 | 2020-04-14 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40758012 | 1954-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1972-01-01 | Porcelain | Suspension |  |  |  |  | 3.7377e-08 | 0.065147
118964152 | E | LC | ETL.1073.POLE.WDPS | 44774783 | VICTOR | YOSEMITE | 2020-04-30 | 2021-11-17 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [12 empty] | 0.065147
119016315 | E | LC | ETL.6980.POLE.WOOD | 40860960 | LAKEVLLE | SONOMA | 2020-04-24 | 2021-08-23 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860960 | 1979-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 1979-01-01 | Polymer | Suspension |  |  |  |  | 0.1189 | 792.0737
119032237 | E | LC | ETL.6720.POLE.WOOD | 42578841 | TABLEMTN | NORTH VALLEY | 2020-05-11 | 2020-06-29 | ETL.6720 | DESABLA-CENTERVILLE | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119035718 | E | LC | ETL.4750.TOWR | 41129172 | LAKEVLLE | SONOMA | 2020-05-08 | 2020-05-19 | ETL.4750 | GEYSERS #12-FULTON | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 41129172 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | Dead End |  |  |  |  | 0.00039529 | 1172.524
119051357 | F | LC | ETL.4220.POLE.WOOD | 40861995 | TABLEMTN | NORTH VALLEY | 2020-05-11 | 2020-07-01 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861995 | 1962-01-01 | Single Wood Pole | 3P DV - 3 Pole Double Vertical | 1962-01-01 | Ceramic | Other |  |  |  |  | 0.010066 | 1791.7156
119056331 | E | LC | ETL.1730.INSL.CERA | 40629104 | MOSSLNDG | CENTRAL COAST | 2020-05-14 | 2020-08-18 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119062244 | F | LC | ETL.6440.POLE.WOOD | 41144205 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-08-25 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41144205 |  | Single Wood Pole | T-1 - Tri Post | 2018-12-12 | Polymer | Post |  |  |  |  | 0.0040082 | 4658.5894
119066099 | B | LC | ETL.5930.TOWR | 40762009 | CONCORD | EAST BAY | 2020-05-26 | 2020-06-24 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40762009 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-26 | Glass | Suspension |  |  |  |  | 1.0344e-08 | 1553.9977
119066099 | B | LC | ETL.5930.TOWR | 40762009 | CONCORD | EAST BAY | 2020-05-26 | 2020-06-24 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40762009 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.0344e-08 | 1553.9977
119116183 | E | LC | ETL.1050.INSL.CERA | 40637995 | FRESNO | FRESNO | 2020-05-26 | 2021-04-26 | ETL.1050 | BALCH-SANGER | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119117184 | E | LC | ETL.7290.POLE.WOOD | 40771266 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-08-17 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40771266 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0028951 | 1744.4635
119117918 | E | LC | ETL.8170.INSL.CERA | 40837327 | EUREKA | HUMBOLDT | 2020-06-04 | 2021-08-03 | ETL.8170 | TRINITY-MAPLE CREEK | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40810498 |  | Single Wood Pole | Unknown |  | Ceramic | Unknown |  |  |  |  | 0.014663 | 348.0238
119119210 | E | LC | ETL.6770.POLE.WOOD | 40616113 | SACTO | SIERRA | 2020-06-04 | 2021-04-19 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119119336 | E | LC | ETL.8290.POLE.WOOD | 40660885 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-21 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119119370 | F | LC | ETL.6470.POLE.WOOD | 40693188 | SACTO | SIERRA | 2020-06-01 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40693188 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.06284 | 823.1843
119119383 | F | LC | ETL.7560.POLE.NWOD | 44263386 | SACTO | SIERRA | 2020-05-29 |  | ETL.7560 | WEIMAR #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44263386 |  | Light Duty Steel Pole | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.0075317 | 6059.3994
119119431 | F | LC | ETL.6330.POLE.NWOD | 40758713 | TABLEMTN | NORTH VALLEY | 2020-05-28 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40758713 | 1998-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Non Ceramic | Post |  |  |  |  | 1.1469e-06 | 375.2416
119120046 | E | LC | ETL.8170.POLE.WOOD | 40861543 | EUREKA | HUMBOLDT | 2020-06-03 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40861543 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.16712 | 79.1467 | 13.2272
119161608 | F | LC | ETL.1810.TOWR | 44321414 | EUREKA | HUMBOLDT | 2020-06-05 | 2021-01-19 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Marker (i.e. signs)-Steel | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44321414 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 0.00025994
119169511 | F | LC | ETL.6280.POLE.WOOD | 40656555 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40656555 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 4.9817e-06 | 411.289
119169543 | F | LC | ETL.3530.TOWR | 40585565 | PISMOBCH | LOS PADRES | 2020-06-15 | 2021-02-01 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585565 | 1952-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1952-01-01 | Porcelain | Dead End |  |  |  |  | 1.4285e-07 | 2972.0795
119177345 | F | LC | ETL.1400.POLE.STPS | 44382154 | VICTOR | YOSEMITE | 2020-06-12 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44382153 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.6153e-05 | 63.3763
119180961 | E | LC | ETL.7300.POLE.NWOD | 44836628 | TABLEMTN | NORTH VALLEY | 2020-06-16 | 2021-08-12 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44836628 | 2019-05-01 | Light Duty Steel Pole | T-1 - Tri Post | 2019-05-01 | Polymer | Post |  |  |  |  | 8.0459e-08 | 2843.664
119183263 | B | LC | ETL.1073.INSL.NCER | 44874785 | VICTOR | YOSEMITE | 2020-06-17 | 2020-08-12 | ETL.1073 | MI-WUK-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44871251 | 2019-12-03 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | 2019-12-03 | Glass | Double Dead End |  |  |  |  | 1.1103e-06
119183263 | B | LC | ETL.1073.INSL.NCER | 44874785 | VICTOR | YOSEMITE | 2020-06-17 | 2020-08-12 | ETL.1073 | MI-WUK-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44871251 | 2019-12-03 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | 2019-12-03 | Glass | Double Dead End |  |  |  |  | 1.1103e-06
119189091 | F | LC | ETL.6310.POLE.WOOD | 40759472 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40759472 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.3295e-05 | 5971.9565
119194362 | F | LC | ETL.7590.POLE.WOOD | 40678356 | MOSSLNDG | CENTRAL COAST | 2020-06-18 | 2021-01-12 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119205712 | F | LC | ETL.7180.POLE.WOOD | 40861610 | LAKEVLLE | NORTH BAY | 2020-06-24 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40861610 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper |  | Porcelain | [5 empty] | 7.3513e-06 | 1504.5828
119208370 | E | LC | ETL.7260.POLE.WOOD | 40592361 | TABLEMTN | NORTH VALLEY | 2020-06-24 | 2020-09-24 | ETL.7260 | KESWICK-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592361 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.0074855 | 522.4315
119210073 | F | LC | ETL.4950.TOWR | 40864660 | LAKEVLLE | SONOMA | 2020-06-25 | 2021-03-08 | ETL.4950 | FULTON-LAKEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40864660 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-04-08 | Glass | Suspension |  |  |  |  | 0.001109 | 5754.3889
119210073 | F | LC | ETL.4950.TOWR | 40864660 | LAKEVLLE | SONOMA | 2020-06-25 | 2021-03-08 | ETL.4950 | FULTON-LAKEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40864660 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-09-25 | Porcelain | Suspension |  |  |  |  | 0.001109 | 5754.3889
119213266 | E | LC | ETL.4392.INSL.CERA | 40833091 | LAKEVLLE |  | 2020-06-25 | 2021-08-16 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119220818 | E | LC | ETL.5140.POLE.WDPS | 44553582 | SACTO | SACRAMENTO | 2020-06-26 | 2021-01-25 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 3 | Within Both | DLFL | 44553225 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00046976 | 3733.8787
119221563 | E | LC | ETL.7180.POLE.WOOD | 40701427 | LAKEVLLE | SONOMA | 2020-06-26 | 2021-04-07 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | HFRA Removal | COMP | 40701427 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2013-01-30 | Ceramic | Post |  |  |  |  | 1.5852e-05 | 47.5251
119236509 | F | LC | ETL.7270.POLE.WOOD | 40908534 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908534 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0033248 | 4367.7598
119289759 | F | LC | ETL.6690.POLE.WOOD | 40611483 | SACTO | SACRAMENTO | 2020-06-30 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40611483 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.016808 | 110.8228
119294489 | F | LC | ETL.3740.TOWR | 44188772 | CONCORD | DIABLO | 2020-07-01 | 2021-04-22 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44188772 | 2008-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Polymer | Dead End |  |  |  |  | 0.076314 | 398.0443
119296188 | F | LC | ETL.6900.POLE.WOOD | 40804780 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 2 | Within Both | PEND | 40804780 | 1980-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 3.1552e-06 | 395.7669
119304811 | E | LC | ETL.8170.POLE.WDPS | 44565621 | EUREKA | HUMBOLDT | 2020-07-02 | 2021-06-08 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 44564174 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.033588 | 1174.8506
119311212 | E | LC | ETL.8170.INSL.CERA | 40628822 | EUREKA | HUMBOLDT | 2020-07-03 | 2021-06-17 | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119314600 | E | LC | ETL.8060.INSL.CERA | 40883825 | SACTO | SACRAMENTO | 2020-07-02 | 2021-06-01 | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119314880 | E | LC | ETL.1470.POLE.WOOD | 41176337 | LAKEVLLE | SONOMA | 2020-07-06 | 2021-03-15 | ETL.1470 | EAGLE ROCK-CORTINA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119314934 | E | LC | ETL.1440.POLE.WDPS | 44762505 | SACTO | SACRAMENTO | 2020-07-02 | 2021-06-29 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 784.8264
119315342 | F | LC | ETL.1470.POLE.WOOD | 41176333 | LAKEVLLE | SONOMA | 2020-07-06 | 2021-03-10 | ETL.1470 | EAGLE ROCK-CORTINA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41176333 | 1978-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1978-01-01 | Glass | Dead End |  |  |  |  | 0.029594 | 0.065149
119316894 | E | LC | ETL.1110.POLE.WDPS | 44424469 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-08-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424467 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00077317 | 2837.7712
119317703 | F | LC | ETL.7270.POLE.NWOD | 44649257 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44649257 | 2018-08-17 | Light Duty Steel Pole | T2N | 2018-08-17 | Polymer | Post |  |  |  |  | 0.00080941 | 1076.101
119329308 | F | LC | ETL.7270.POLE.WOOD | 40906121 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906121 |  | Single Wood Pole | T2N | 2017-12-20 | Polymer | Post |  |  |  |  | 0.0043435 | 1832.2993
119330088 | E | LC | ETL.1110.TOWR | 40814818 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-09-02 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier2 | Tier 2 | Within Both | DLFL | 40814818 | 1952-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-01-31 | Glass | Suspension |  |  |  |  | 0.0002786 | 26.9616
119330184 | E | LC | ETL.6280.POLE.WOOD | 40666805 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-08-02 | ETL.6280 | CARIBOU #2 | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40666805 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Pin |  |  |  |  | 3.0669e-05 | 490.3705
119336747 | F | LC | ETL.1480.TOWR | 40657360 | LAKEVLLE | HUMBOLDT | 2020-07-09 |  | ETL.1480 | EAGLE ROCK-REDBUD | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40657360 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Porcelain | Suspension |  |  |  |  | 0.0025384 | 1028.4229
119336747 | F | LC | ETL.1480.TOWR | 40657360 | LAKEVLLE | HUMBOLDT | 2020-07-09 |  | ETL.1480 | EAGLE ROCK-REDBUD | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40657360 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 0.0025384 | 1028.4229
119338554 | E | LC | ETL.7030.POLE.WOOD | 40667946 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119341235 | E | LC | ETL.6290.POLE.WOOD | 40589791 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40589791 | 1973-01-01 | Single Wood Pole | TCDE - Tap Construction Dead End | 1973-01-01 | Porcelain | Dead End |  |  |  |  | 0.019874 | 311.6891 | 6.1946
119353490 | E | LC | ETL.6980.POLE.WOOD | 40616622 | LAKEVLLE | SONOMA | 2020-07-10 | 2021-06-10 | ETL.6980 | FORT ROSS-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40616622 | 1986-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.12637 | 47.5538
119368178 | B | LC | ETL.1110.TOWR | 40644444 | EUREKA | HUMBOLDT | 2020-07-14 | 2020-08-06 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40644444 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Unknown |  |  |  |  | 9.4883e-05 | 166.2122
119379868 | E | LC | ETL.7340.POLE.WOOD | 40617288 | LAKEVLLE | SONOMA | 2020-07-16 | 2021-05-10 | ETL.7340 | LAKEVILLE #2 | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40617288 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Other |  |  |  |  | 0.0053456 | 1204.7117
119457454 | B | LC | ETL.6290.POLE.WOOD | 40861861 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2020-10-05 | ETL.6290 | CARIBOU-PLUMAS JCT | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861861 | 1962-01-01 | Single Wood Pole | T2N | 2020-09-30 | Polymer | Post |  |  |  |  | 0.51617 | 0.0778
119464089 | E | LC | ETL.6330.POLE.STPS | 44679451 | TABLEMTN | NORTH VALLEY | 2020-07-17 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Anchor-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 44673339 | 2018-11-14 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.3152e-05 | 3216.668 | 0.13881
119480014 | E | LC | ETL.9200.INSL | 40608203 | MIDWAY | KERN | 2020-07-21 |  | ETL.9200 | TAFT-CUYAMA #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40583998 | 1962-01-01 | Single Wood Pole | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.0213
119482204 | F | LC | ETL.9200.POLE.WOOD | 40654888 | MIDWAY | KERN | 2020-07-20 | 2021-04-29 | ETL.9200 | TAFT-CUYAMA #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40654888 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Ceramic | Pin |  |  |  |  | 0.0026321
119492156 | F | LC | ETL.1110.TOWR | 40596845 | TABLEMTN | HUMBOLDT | 2020-07-23 | 2021-04-06 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40596845 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-10-12 | Glass | Suspension |  |  |  |  | 1.1492e-06 | 284.8513
119495298 | E | LC | ETL.5140.POLE.STPS | 44416132 | SACTO | SACRAMENTO | 2020-07-23 | 2020-12-04 | ETL.5140 | MIDDLE FORK-GOLD HILL | Vegetation | Overgrown | [Remove, No Action Taken] |  | Tier 3 | Within Both | CNCL | 44416130 | 2018-09-07 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.8587e-06 | 189.9644
119510463 | E | LC | ETL.6880.POLE.NWOD | 44310678 | LAKEVLLE | SONOMA | 2020-07-27 | 2021-02-01 | ETL.6880 | FULTON-CALISTOGA | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44310678 | 2014-01-14 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2014-01-14 | Polymer | Dead End |  |  |  |  | 0.00093554 | 1330.0056
119514183 | F | LC | ETL.6280.POLE.NWOD | 44259102 | TABLEMTN | NORTH VALLEY | 2020-07-23 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44259102 | 2018-09-23 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2018-09-23 | Ceramic | Suspension |  |  |  |  | 8.6688e-11 | 348.0238
119515394 | F | LC | ETL.6290.POLE.WOOD | 40758620 | TABLEMTN | NORTH VALLEY | 2020-07-23 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758620 | 2010-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.058362 | 5556.3816
119554807 | E | LC | ETL.8170.POLE.WOOD | 40770502 | EUREKA | HUMBOLDT | 2020-08-03 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40770502 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.34886 | 79.1846 | 27.6241
119562454 | F | LC | ETL.7780.POLE.WOOD | 40876336 | LAKEVLLE | HUMBOLDT | 2020-08-05 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40876336 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 3.2575e-05 | 79.143
119566926 | E | LC | ETL.6300.INSL | 40885479 | TABLEMTN |  | 2020-08-05 |  | ETL.6300 | CARIBOU-WESTWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40862089 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Pin |  |  |  |  | 2.8391e-05 | 3036.7952 | 0.086218
119568267 | E | LC | ETL.6880.POLE.WOOD | 40912446 | LAKEVLLE | NORTH BAY | 2020-08-06 | 2021-06-15 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119575423 | E | LC | ETL.5650.TOWR | 40864681 | TABLEMTN | NORTH VALLEY | 2020-08-07 | 2021-04-12 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40864681 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.448e-06 | 1285.8232
119576408 | E | LC | ETL.7180.POLE.WOOD | 40588078 | LAKEVLLE | NORTH BAY | 2020-08-07 | 2021-04-21 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40588078 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Other |  |  |  |  | 6.925e-06 | 71.6461
119578370 | E | LC | ETL.7490.POLE.WOOD | 40662163 | EUREKA | HUMBOLDT | 2020-08-07 | 2021-08-11 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40662163 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-08-06 | Polymer | Dead End |  |  |  |  | 0.8777 | 0.065148
119578681 | E | LC | ETL.6222.POLE.WOOD | 40827187 | EUREKA | HUMBOLDT | 2020-08-07 |  | ETL.6222 | FORT SEWARD TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40827187 | 1952-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0027768
119599906 | E | LC | ETL.6520.POLE.WOOD | 40770754 | SACTO | SACRAMENTO | 2020-08-11 | 2021-05-10 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119600434 | E | LC | ETL.8210.POLE.WOOD | 40908318 | VICTOR | STOCKTON | 2020-08-11 | 2021-09-13 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0023343 | 3403.9211
119624514 | F | LC | ETL.8365.POLE.NWOD | 40906646 | EUREKA | HUMBOLDT | 2020-08-17 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40906646 | 2010-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.026583
119648495 | E | LC | ETL.2660.TOWR | 40822542 | SACTO | SACRAMENTO | 2020-08-21 | 2021-04-13 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Vegetation | Overgrown | [Trim, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822542 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Ceramic | Suspension |  |  |  |  | 6.928e-10 | 15.8963
119648495 | E | LC | ETL.2660.TOWR | 40822542 | SACTO | SACRAMENTO | 2020-08-21 | 2021-04-13 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Vegetation | Overgrown | [Trim, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822542 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 6.928e-10 | 15.8963
119663319 | F | LC | ETL.3020.TOWR | 40761971 | CONCORD | DIABLO | 2020-08-24 |  | ETL.3020 | NEWARK-JARVIS #1 | Structure-Tower | Anti-Climbing Guard | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40761971 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.9643e-07
119663319 | F | LC | ETL.3020.TOWR | 40761971 | CONCORD | DIABLO | 2020-08-24 |  | ETL.3020 | NEWARK-JARVIS #1 | Structure-Tower | Anti-Climbing Guard | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40761971 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-11-03 | Ceramic | Dead End |  |  |  |  | 1.9643e-07
119668492 | B | LC | ETL.1600.TOWR | 40861095 | LAKEVLLE | SONOMA | 2020-08-25 | 2020-10-19 | ETL.1600 | FULTON-PUEBLO | Other | Customer Issue | [Customer Refusal] | Tier3 | Tier 3 | Within Both | COMP | 40861095 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1997-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.3983e-05 | 965.4728
119706342 | E | LC | ETL.3960.TOWR | 40643127 | PISMOBCH | LOS PADRES | 2020-09-02 | 2021-02-02 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40643127 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-05-22 | Glass | Suspension |  |  |  |  | 2.6448e-08 | 6268.3306
119709849 | F | LC | ETL.5540.TOWR | 40866865 | TABLEMTN | NORTH VALLEY | 2020-08-29 | 2021-03-25 | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40866865 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 4.5433e-07 | 63.3704
119740911 | E | LC | ETL.6480.POLE.WOOD | 40824364 | SACTO | NORTH VALLEY | 2020-09-08 | 2021-06-29 | ETL.6480 | COLGATE-CHALLENGE | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119752712 | E | LC | ETL.6300.POLE.WDPS | 44989189 | TABLEMTN | NORTH VALLEY | 2020-08-12 | 2021-08-24 | ETL.6300 | CARIBOU-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42624216 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.002545 | 126.6209
119781278 | E | LC | ETL.7380.POLE.WOOD | 40827811 | MOSSLNDG | CENTRAL COAST | 2020-09-09 | 2021-08-19 | ETL.7380 | LAURELES-OTTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40827811 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.25369 | 221.4934
119785300 | B | LC | ETL.8410.POLE.WOOD | 40616695 | LAKEVLLE | HUMBOLDT | 2020-09-14 | 2020-12-04 | ETL.8410 | ELK-GUALALA | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | DLFL | 40616695 | 1960-01-01 | Single Wood Pole | T1-1A | 2020-11-23 | Polymer | Post |  |  |  |  | 0.12883 | 250.1485
119787190 | E | LC | ETL.8290.POLE.NWOD | 44911342 | TABLEMTN | NORTH VALLEY | 2020-09-16 | 2021-04-08 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44911342 | 2020-02-06 | Light Duty Steel Pole | T-1 - Tri Post | 2020-02-06 | Polymer | Post |  |  |  |  | 3.4156e-05 | 795.2646
119794908 | F | LC | ETL.1073.POLE.STPS | 44385275 | VICTOR | YOSEMITE | 2020-08-04 | 2020-11-10 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44385273 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.995e-06 | 15.88
119813336 | F | LC | ETL.1110.POLE.STPS | 44976183 | TABLEMTN | HUMBOLDT | 2020-08-27 | 2021-07-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42603428 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 6.4566e-05 | 585.4842
119816081 | F | LC | ETL.1400.POLE.WDPS | 44560756 | VICTOR | STOCKTON | 2020-08-29 | 2021-05-17 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119816384 | F | LC | ETL.3800.TOWR | 40590863 | CONCORD | EAST BAY | 2020-08-26 | 2021-04-19 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40590863 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-10-31 | Ceramic | Suspension |  |  |  |  | 7.6145e-08 | 1692.6119
119816387 | F | LC | ETL.7290.POLE.WOOD | 40617650 | TABLEMTN | NORTH VALLEY | 2020-08-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40617650 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | [5 empty] | 0.011841 | 31.7051
119821085 | F | LC | ETL.3960.TOWR | 40607920 | PISMOBCH | LOS PADRES | 2020-09-24 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40607920 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 6.9827e-08 | 5098.0332 | 0.00035598
119821085 | F | LC | ETL.3960.TOWR | 40607920 | PISMOBCH | LOS PADRES | 2020-09-24 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40607920 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 6.9827e-08 | 5098.0332 | 0.00035598
119821085 | F | LC | ETL.3960.TOWR | 40607920 | PISMOBCH | LOS PADRES | 2020-09-24 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40607920 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 6.9827e-08 | 5098.0332 | 0.00035598
119821085 | F | LC | ETL.3960.TOWR | 40607920 | PISMOBCH | LOS PADRES | 2020-09-24 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40607920 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 6.9827e-08 | 5098.0332 | 0.00035598
119835011 | E | LC | ETL.1110.TOWR | 40676702 | EUREKA | HUMBOLDT | 2020-09-30 | 2020-12-02 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676702 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Suspension |  |  |  |  | 0.00025839 | 79.1724
119835385 | F | LC | ETL.7820.POLE.WOOD | 40656746 | LAKEVLLE | HUMBOLDT | 2020-09-02 | 2021-09-30 | ETL.7820 | POTTER VALLEY-WILLITS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40656746 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | [5 empty] | 0.00032172 | 253.2372
119850446 | F | LC | ETL.1720.POLE.WDPS | 44513750 | MOSSLNDG | CENTRAL COAST | 2020-09-17 | 2021-07-07 | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | DLFL | 44512288 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00012425 | 189.9697
119890045 | E | LC | ETL.6030.TOWR | 40764251 | MIDWAY | KERN | 2020-10-08 | 2021-06-21 | ETL.6030 | MIDWAY-WHIRLWIND | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40764251 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 2.9771e-06 | 6222.8303
119896383 | E | LC | ETL.5220.INSL | 40611896 | METCALF | SAN JOSE | 2020-10-13 | 2021-03-10 | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119918396 | F | LC | ETL.5090.TOWR | 40659863 | MOSSLNDG | DE ANZA | 2020-08-29 | 2021-01-12 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40659863 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.029826 | 379.8559
119925486 | B | LC | ETL.1110.TOWR | 40756748 | TABLEMTN | HUMBOLDT | 2020-10-19 | 2020-12-31 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756748 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 0.00017737 | 19.0509
119936485 | B | LC | ETL.7572.INSL | 40898698 | METCALF | SAN JOSE | 2020-10-22 | 2020-12-08 | ETL.7572 | SAN BRUNO TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40874277 |  | Single Wood Pole | SUSP-A - Suspension Angle (TWR) |  | Ceramic | Other |  |  |  |  | 0.0031735 | 0.066432
119949210 | E | LC | ETL.5980.TOWR | 40664657 | PISMOBCH | LOS PADRES | 2020-10-26 | 2021-06-08 | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664657 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-10-17 | Glass Silicone Coated | Suspension |  |  |  |  | 6.0449e-12 | 1346.4261
119967578 | E | LC | ETL.2720.INSL.NCER | 45100597 | CONCORD | EAST BAY | 2020-08-28 | 2021-08-11 | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40580799 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 0.00043634 | 0.065152
119967578 | E | LC | ETL.2720.INSL.NCER | 45100597 | CONCORD | EAST BAY | 2020-08-28 | 2021-08-11 | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40580799 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-04 | Glass | Suspension |  |  |  |  | 0.00043634 | 0.065152
120126690 | F | LC | ETL.1650.POLE.WOOD | 40594053 | LAKEVLLE | SONOMA | 2020-10-07 | 2021-09-30 | ETL.1650 | GEYSERS #3-CLOVERDALE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40594053 | 1991-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1966-01-01 | Porcelain | Dead End |  |  |  |  | 0.00016287 | 3278.8411
120133582 | F | LC | ETL.3020.TOWR | 40804735 | CONCORD | MISSION | 2020-10-23 | 2021-03-22 | ETL.3020 | NEWARK-JARVIS #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40804735 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.5259e-07
120133582 | F | LC | ETL.3020.TOWR | 40804735 | CONCORD | MISSION | 2020-10-23 | 2021-03-22 | ETL.3020 | NEWARK-JARVIS #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40804735 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-11-03 | Ceramic | Suspension |  |  |  |  | 2.5259e-07
120133794 | F | LC | ETL.8170.POLE.WOOD | 40602117 | EUREKA | HUMBOLDT | 2020-08-03 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40602117 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.16116 | 269.0562
120139367 | E | LC | ETL.1110.TOWR | 40817268 | EUREKA | HUMBOLDT | 2020-12-05 | 2021-08-14 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817268 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.8334e-05 | 79.1724
120140904 | E | LC | ETL.2900.TOWR | 40761041 | MOSSLNDG | CENTRAL COAST | 2020-12-08 | 2020-12-09 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40761041 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1991-01-01 | Porcelain | Dead End |  |  |  |  | 0.0043859 | 4398.79
120140904 | E | LC | ETL.2900.TOWR | 40761041 | MOSSLNDG | CENTRAL COAST | 2020-12-08 | 2020-12-09 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40761041 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-11-05 | Glass Silicone Coated | Dead End |  |  |  |  | 0.0043859 | 4398.79
120150374 | F | LC | ETL.6280.POLE.WOOD | 40862063 | TABLEMTN | NORTH VALLEY | 2020-11-04 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | PEND | [11 empty] | 1.1916e-07 | 632.7172
120160592 | F | LC | ETL.8650.POLE.NWOD | 44420188 | FRESNO | FRESNO | 2020-12-09 | 2021-07-01 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420188 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0039923 | 5309.104
120228222 | E | LC | ETL.4100.TOWR | 40765438 | SACTO | SACRAMENTO | 2020-12-22 | 2021-01-26 | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40765438 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2018-05-29 | Glass Silicone Coated | Suspension |  |  |  |  | 9.1358e-07 | 5129.8823
120552902 | E | LC | ETL.5650.POLE.WDPS | 44765641 | TABLEMTN |  | 2021-02-18 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44765636 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.0587e-05 | 2836.814 | 0.17187
120564484 | E | LC | ETL.6660.POLE.WOOD | 44358493 | TABLEMTN | NORTH VALLEY | 2021-02-22 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44358493 | 2016-10-23 | Light Duty Steel Pole | T-1 - Tri Post | 2016-10-23 | Polymer | Post |  |  |  |  | 3.693e-11 | 3977.8811 | 1.469e-07
120653592 | F | LC | ETL.4920.TOWR | 40863473 | LAKEVLLE | SONOMA | 2021-03-17 |  | ETL.4920 | IGNACIO-SOBRANTE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40863473 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.00085664 | 284.7965 | 0.24397
120654921 | F | LC | ETL.4590.TOWR | 40910172 | TABLEMTN | NORTH VALLEY | 2021-03-17 | 2021-05-31 | ETL.4590 | CRESTA-RIO OSO | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910172 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 7.122e-06 | 15.8851
120658373 | E | LC | ETL.6950.POLE.WOOD | 40693026 | SACTO | SACRAMENTO | 2021-03-18 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40693026 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.0034179 | 3376.7928 | 11.5416
120663452 | B | LC | ETL.1350.POLE.WDPS | 44513800 | TABLEMTN | NORTH VALLEY | 2021-03-19 | 2021-04-05 | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44512296 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.008643 | 3880.9729
120678064 | B | LC | ETL.5140.INSL.NCER | 44690601 | SACTO | SIERRA | 2021-03-23 | 2021-04-01 | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44141450 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-10-29 | Glass | Suspension |  |  |  |  | 1.0846e-08
120678064 | B | LC | ETL.5140.INSL.NCER | 44690601 | SACTO | SIERRA | 2021-03-23 | 2021-04-01 | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44141450 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-10-29 | Glass | Suspension |  |  |  |  | 1.0846e-08
120685864 | E | LC | ETL.1440.POLE.WDPS | 44175616 | SACTO | SACRAMENTO | 2021-03-24 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44175614 | 2013-09-22 | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.0012183 | 411.4038 | 0.50122
120697902 | B | LC | ETL.9330.TOWR | 40815639 | FRESNO | FRESNO | 2021-03-26 | 2021-06-28 | ETL.9330 | WISHON-COPPERMINE | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40815639 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Polymer | [5 empty] | 0.0020092 | 6125.6431
120702010 | E | LC | ETL.7380.POLE.WOOD | 40771077 | MOSSLNDG | CENTRAL COAST | 2021-03-27 |  | ETL.7380 | LAURELES-OTTER | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40771077 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.43683 | 174.3987 | 76.1828
120708745 | E | LC | ETL.3830.INSL | 40703056 | VICTOR | STOCKTON | 2021-03-26 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40642841 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.7088e-07 | 6204.2363
120736394 | E | LC | ETL.8405.POLE.WOOD | 40822817 | SACTO | SACRAMENTO | 2021-04-02 | 2021-09-30 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822817 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2020-03-08 | Polymer | Dead End |  |  |  |  | 0.004133 | 1186.6189 | 4.9043
120737515 | F | LC | ETL.2540.POLE.WDPS | 44401444 | MOSSLNDG | CENTRAL COAST | 2021-04-02 | 2021-06-10 | ETL.2540 | METCALF-GREEN VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44401443 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.071232 | 57.0224
120738835 | F | LC | ETL.5960.TOWR | 40869378 | PISMOBCH | LOS PADRES | 2021-04-02 |  | ETL.5960 | DIABLO-GATES #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40869378 | 1997-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1997-01-01 | Ceramic | Suspension |  |  |  |  | 2.1802e-08 | 5493.7212
120744076 | E | LC | ETL.1650.INSL.NCER | 40577942 | LAKEVLLE | SONOMA | 2021-04-05 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40576031 | 1983-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1966-01-01 | Polymer | Dead End |  |  |  |  | 0.00031417 | 4022.6609 | 1.2638
120749113 | E | LC | ETL.2900.TOWR | 40593820 | MOSSLNDG | CENTRAL COAST | 2021-04-06 | 2021-07-12 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40593820 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Polymer | Suspension |  |  |  |  | 0.0093252 | 2216.3176
120755059 | F | LC | ETL.3830.TOWR | 40746921 | VICTOR | STOCKTON | 2021-03-31 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40746921 | 1971-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1989-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.2668e-09 | 3833.2197 | 4.8558e-06
120763547 | E | LC | ETL.4392.INSL.NCER | 41117765 | LAKEVLLE | SONOMA | 2021-04-08 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41102744 | 1999-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 7.1735e-05 | 4395.2046 | 0.31529
120770338 | E | LC | ETL.5510.TOWR | 40762219 | CONCORD | DIABLO | 2021-04-09 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762219 | 1961-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 2.0734e-07 | 4497.2598 | 0.00093247
120772775 | E | LC | ETL.6030.TOWR | 40749873 | MIDWAY | KERN | 2021-04-09 | 2021-10-19 | ETL.6030 | MIDWAY-WHIRLWIND | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40749873 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-12-09 | Glass Silicone Coated | Suspension |  |  |  |  | 2.9771e-06 | 6811.665
120794896 | E | LC | ETL.7360.POLE.NWOD | 44963429 | LAKEVLLE | SONOMA | 2021-04-12 |  | ETL.7360 | LAKEVILLE #1 | Anchor-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44963429 | 2020-08-10 | Light Duty Steel Pole | T-1 - Tri Post | 2020-08-10 | Polymer | Post |  |  |  |  | 0.00019139 | 1111.2394 | 0.21268
120805207 | E | LC | ETL.7290.POLE.WOOD | 41119880 | TABLEMTN | NORTH VALLEY | 2021-04-13 | 2021-06-23 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41119880 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | [7 empty] | 0.027624 | 2361.8477
120807227 | F | LC | ETL.5330.TOWR | 40818889 | MOSSLNDG | CENTRAL COAST | 2021-04-13 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40818889 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1969-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.0666e-06 | 238.11 | 0.00025396
120807227 | F | LC | ETL.5330.TOWR | 40818889 | MOSSLNDG | CENTRAL COAST | 2021-04-13 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40818889 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1969-01-01 | Ceramic | Other |  |  |  |  | 1.0666e-06 | 238.11 | 0.00025396
120808243 | E | LC | ETL.7590.POLE.WOOD | 40747197 | MOSSLNDG | CENTRAL COAST | 2021-04-13 |  | ETL.7590 | MONTA VISTA-BURNS | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40747197 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.80116 | 126.6368 | 101.4563
120812777 | E | LC | ETL.1252.INSL.NCER | 40776396 | FRESNO | FRESNO | 2021-04-08 |  | ETL.1252 | OAKHURST TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40748602 | 2005-01-01 | Light Duty Steel Pole | TPS - Tri Post & Susp (1-3) | 2005-01-01 | Polymer | Suspension |  |  |  |  | 3.2101e-06 | 47.5185 | 0.00015254
120820698 | E | LC | ETL.1530.INSL.CERA | 43704882 | SACTO | SIERRA | 2021-04-14 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40751922 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-11-10 | Ceramic | Dead End |  |  |  |  | 1.6992e-05 | 63.3518 | 0.0010764
120823065 | F | LC | ETL.5660.TOWR | 40607999 | CONCORD | DIABLO | 2021-04-15 |  | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40607999 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 9.9902e-07 | 1397.5155 | 0.0013961
120823065 | F | LC | ETL.5660.TOWR | 40607999 | CONCORD | DIABLO | 2021-04-15 |  | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40607999 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 9.9902e-07 | 1397.5155 | 0.0013961
120823065 | F | LC | ETL.5660.TOWR | 40607999 | CONCORD | DIABLO | 2021-04-15 |  | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40607999 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.9902e-07 | 1397.5155 | 0.0013961
120823065 | F | LC | ETL.5660.TOWR | 40607999 | CONCORD | DIABLO | 2021-04-15 |  | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40607999 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.9902e-07 | 1397.5155 | 0.0013961
120843539 | E | LC | ETL.8365.POLE.NWOD | 40906667 | EUREKA | HUMBOLDT | 2021-04-19 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Vegetation | Overgrown | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40906667 | 2011-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.010632
120845407 | F | LC | ETL.4440.TOWR | 40821153 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40821153 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 9.6576e-08 | 1332.8262 | 0.00012872
120848185 | E | LC | ETL.2760.INSL | 40724737 | CONCORD | DIABLO | 2021-04-19 |  | ETL.2760 | MORAGA-OAKLAND J | Damper-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40681828 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 9.9341e-08 | 0.065159 | 6.473e-09
120849705 | B | LC | ETL.8170.POLE.WOOD | 44190910 | EUREKA | HUMBOLDT | 2021-04-19 | 2021-06-09 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44190910 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | Post |  |  |  |  | 0.016631 | 110.8153
120879335 | E | LC | ETL.1810.POLE.WDPS | 44322222 | EUREKA | HUMBOLDT | 2021-04-23 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44322221 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 2.2141e-06 | 1118.868 | 0.0024773
120885811 | E | LC | ETL.3700.POLE.WOOD | 40878719 | PISMOBCH | LOS PADRES | 2021-04-09 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40878719 | 1989-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1989-01-01 | Porcelain | Unknown |  |  |  |  | 0.0036037 | 4037.8574 | 14.5511
120900337 | E | LC | ETL.4450.TOWR | 40867703 | CONCORD | DIABLO | 2021-04-29 |  | ETL.4450 | CASTRO VALLEY-NEWARK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40867703 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 0.00029058 | 2992.5576 | 0.86957
120910804 | E | LC | ETL.6470.POLE.WOOD | 40766592 | SACTO | SACRAMENTO | 2021-04-30 | 2021-07-22 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40766592 |  | Single Wood Pole | T2N | 2021-07-19 | Polymer | Post |  |  |  |  | 0.0041831 | 221.5243
120923648 | E | LC | ETL.2720.INSL | 40880144 | CONCORD | DIABLO | 2021-04-14 |  | ETL.2720 | MORAGA-OAKLAND #1 | Splice-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857637 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 5.7298e-05 | 0.065158 | 3.7334e-06
120923648 | E | LC | ETL.2720.INSL | 40880144 | CONCORD | DIABLO | 2021-04-14 |  | ETL.2720 | MORAGA-OAKLAND #1 | Splice-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857637 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 5.7298e-05 | 0.065158 | 3.7334e-06
120937673 | E | LC | ETL.8060.POLE.WOOD | 40593596 | SACTO | SACRAMENTO | 2021-05-05 | 2021-07-12 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40593596 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.059897 | 31.7066
120942385 | E | LC | ETL.2030.POLE.WOOD | 40687635 | FRESNO | FRESNO | 2021-05-06 |  | ETL.2030 | KINGS RIVER-SANGER-REEDLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40687635 | 1963-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1963-01-01 | Porcelain | Post |  |  |  |  | 1.7589e-05 | 4876.5371 | 0.085775
120949375 | E | LC | ETL.2720.INSL | 40671311 | CONCORD | DIABLO | 2021-04-19 |  | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40644194 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.00013462 | 0.065152 | 8.7705e-06
121067690 | E | LC | ETL.3820.TOWR | 40903772 | VICTOR | STOCKTON | 2021-04-16 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40903772 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 0.00013275 | 130.1517 | 0.017277
121192140 | E | LC | ETL.4590.TOWR | 40910174 | TABLEMTN | NORTH VALLEY | 2021-04-19 |  | ETL.4590 | CRESTA-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40910174 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-11-03 | Glass | Suspension |  |  |  |  | 1.0865e-05 | 2531.262 | 0.027503
121329749 | F | LC | ETL.2395.POLE.WOOD | 44550857 | TABLEMTN | NORTH VALLEY | 2021-05-13 | 2021-07-15 | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44550857 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.008922 | 300.6002
121330931 | E | LC | ETL.1530.INSL.CERA | 40630502 | SACTO | SIERRA | 2021-04-20 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | PEND
121344932 | E | LC | ETL.6890.POLE.NWOD | 44713005 | LAKEVLLE | SONOMA | 2021-04-28 |  | ETL.6890 | FULTON-HOPLAND | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44713005 | 2019-02-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-02-16 | Ceramic | Dead End |  |  |  |  | 1.1429e-06 | 2804.5479 | 0.0032054
121346766 | E | LC | ETL.5930.TOWR | 40676092 | LAKEVLLE | DIABLO | 2021-04-20 | 2021-11-15 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676092 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.9067e-08 | 143.0883 | 2.7282e-06
121346766 | E | LC | ETL.5930.TOWR | 40676092 | LAKEVLLE | DIABLO | 2021-04-20 | 2021-11-15 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676092 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.9067e-08 | 143.0883 | 2.7282e-06
121356745 | E | LC | ETL.5970.INSL | 40715243 | PISMOBCH | LOS PADRES | 2021-04-30 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40664596 | 1973-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1973-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.0224e-09 | 2137.2815 | 8.5969e-06
121367749 | F | LC | ETL.1250.POLE.NWOD | 40826108 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40826108 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 8.735e-09 | 5287.748
121370412 | E | LC | ETL.1250.POLE.WOOD | 40582999 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40582999 |  | Single Wood Pole | 3HP - 3 Horizontal Post |  | Ceramic | Post |  |  |  |  | 0.001001 | 6552.9849 | 6.5593
121377893 | F | LC | ETL.3700.POLE.WOOD | 40669525 | PISMOBCH | LOS PADRES | 2021-05-06 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40669525 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Porcelain | Post |  |  |  |  | 2.5632e-05 | 3263.2344
121378214 | F | LC | ETL.8640.POLE.NWOD | 44950377 | FRESNO | YOSEMITE | 2021-05-05 |  | ETL.8640 | EXCHEQUER-MARIPOSA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44950377 | 2020-05-22 | Light Duty Steel Pole | T-1 - Tri Post | 2020-05-22 | Polymer | Post |  |  |  |  | 6.1101e-10 | 6964.1582
121380368 | B | LC | ETL.4440.TOWR | 40815792 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-24 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40815792 | 1968-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1968-01-01 | Porcelain | Dead End |  |  |  |  | 2.4023e-07 | 5260.656
121384128 | E | LC | ETL.6640.POLE.WOOD | 40862384 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40862384 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.01347 | 933.8852 | 12.579
121384576 | F | LC | ETL.8000.POLE.NWOD | 44177828 | SACTO | SIERRA | 2021-05-11 |  | ETL.8000 | SMARTVILLE-NICOLAUS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44177828 | 2013-08-20 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2013-08-20 | Polymer | Post |  |  |  |  | 3.4745e-05 | 2646.7427
121385312 | F | LC | ETL.6760.POLE.WOOD | 40813449 | SACTO | SIERRA | 2021-05-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40813449 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.059867 | 110.8102
121385893 | E | LC | ETL.1650.POLE.WOOD | 40861029 | LAKEVLLE | SONOMA | 2021-05-12 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40861029 | 1966-01-01 | Single Wood Pole | WB - Wishbone | 2019-03-07 | Porcelain | Suspension |  |  |  |  | 0.0001512 | 3182.9705 | 0.48128
121388986 | E | LC | ETL.8250.POLE.WOOD | 40652661 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40652661 | 1995-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00027613 | 3320.7787 | 0.91697
121392067 | E | LC | ETL.1430.TOWR | 40814408 | SACTO | SIERRA | 2021-05-15 | 2021-06-22 | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40814408 | 1913-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-07-09 | Glass | Dead End |  |  |  |  | 0.003201 | 142.4642
121395986 | E | LC | ETL.6660.POLE.NWOD | 45086312 | TABLEMTN | NORTH VALLEY | 2021-05-18 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45086312 | 2021-03-04 | Light Duty Steel Pole | T2N | 2021-03-04 | Polymer | Post |  |  |  |  | 1.7733e-11 | 2235.968 | 3.9651e-08
121397702 | B | LC | ETL.6770.INSL.NCER | 44928329 | SACTO | SIERRA | 2021-05-19 | 2021-08-12 | ETL.6770 | DRUM-SPAULDING | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44928288 | 2020-05-20 | Light Duty Steel Pole | T-1 - Tri Post | 2020-05-20 | Polymer | Post |  |  |  |  | 0.0001909 | 411.4038
121418433 | E | LC | ETL.8290.POLE.WOOD | 40660889 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40660889 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.010728 | 398.6012 | 4.2763
121420198 | F | LC | ETL.6040.TOWR | 40664579 | MOSSLNDG | CENTRAL COAST | 2021-05-21 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40664579 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.7072e-06 | 2705.5906
121420640 | F | LC | ETL.6640.POLE.WOOD | 40769495 | TABLEMTN | NORTH VALLEY | 2021-05-21 | 2021-06-28 | ETL.6640 | COTTONWOOD-BENTON #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40769495 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.00074942 | 7591.7544
121436390 | B | LC | ETL.5140.POLE.WDPS | 44552446 | SACTO | SACRAMENTO | 2021-05-29 | 2021-08-16 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44551524 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.038841 | 4160.9766
121438684 | E | LC | ETL.4220.POLE.WDPS | 44557635 | TABLEMTN |  | 2021-05-26 |  | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44554025 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.055692 | 0.065151 | 0.0036284
121444489 | E | LC | ETL.6220.POLE.WOOD | 40769366 | EUREKA | HUMBOLDT | 2021-06-01 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40769366 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.045391 | 1460.0339 | 66.2728
121444489 | E | LC | ETL.6220.POLE.WOOD | 40769366 | EUREKA | HUMBOLDT | 2021-06-01 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40769366 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.045391 | 1460.0339 | 66.2728
121444704 | F | LC | ETL.1820.POLE.NWOD | 44976955 | EUREKA | HUMBOLDT | 2021-05-28 | 2021-07-29 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44976955 | 2020-03-09 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-03-09 | Glass | Suspension |  |  |  |  | 0.00044363 | 348.0238
121446065 | B | LC | ETL.1401.POLE.STPS | 44889241 | VICTOR | YOSEMITE | 2021-06-01 | 2021-07-22 | ETL.1401 | BEARDSLEY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44889223 | 2019-09-24 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.4675e-05 | 253.2337
121452139 | B | LC | ETL.5650.INSL | 40688928 | TABLEMTN | NORTH VALLEY | 2021-06-03 | 2021-07-08 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40658859 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 2.9117e-08 | 3391.8159
121453987 | F | LC | ETL.6470.POLE.WOOD | 40822630 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40822630 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.023921 | 727.8687
121482409 | B | LC | ETL.4350.INSL | 40774143 | FRESNO | FRESNO | 2021-06-05 | 2021-08-12 | ETL.4350 | BALCH-MCCALL | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40746512 | 1957-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1957-01-01 | Ceramic | Suspension |  |  |  |  | 2.493e-07 | 6331.5771
121482409 | B | LC | ETL.4350.INSL | 40774143 | FRESNO | FRESNO | 2021-06-05 | 2021-08-12 | ETL.4350 | BALCH-MCCALL | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40746512 | 1957-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1957-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.493e-07 | 6331.5771
121489353 | F | LC | ETL.8290.POLE.NWOD | 44911342 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.8290 | VOLTA-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44911342 | 2020-02-06 | Light Duty Steel Pole | T-1 - Tri Post | 2020-02-06 | Polymer | Post |  |  |  |  | 3.4156e-05 | 795.2646
121489384 | F | LC | ETL.5140.POLE.STPS | 45146368 | SACTO | SIERRA | 2021-05-29 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45146239 | 2020-10-12 | 2-Pole Non Wood | 2PS - 2 Pole SUSP
121514875 | E | LC | ETL.5390.TOWR | 40868154 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5390 | PIT #1-COTTONWOOD | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40868154 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 3.8552e-08 | 4405.1865 | 0.00016983
121516739 | F | LC | ETL.2790.TOWR | 40580825 | CONCORD | EAST BAY | 2021-06-04 | 2021-11-29 | ETL.2790 | MORAGA-SAN LEANDRO #3 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40580825 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-03-28 | Glass | Suspension |  |  |  |  | 2.4015e-06 | 0.065147
121516739 | F | LC | ETL.2790.TOWR | 40580825 | CONCORD | EAST BAY | 2021-06-04 | 2021-11-29 | ETL.2790 | MORAGA-SAN LEANDRO #3 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40580825 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-22 | Glass | Suspension |  |  |  |  | 2.4015e-06 | 0.065147
121518890 | F | LC | ETL.4440.TOWR | 40683796 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40683796 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 1.2223e-05 | 3638.1943 | 0.044469
121526204 | E | LC | ETL.5650.INSL | 40721290 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40675860 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.5197e-05 | 4674.3652 | 0.071034
121526349 | E | LC | ETL.1450.POLE.WDPS | 44549968 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44549505 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0024785 | 2056.7583 | 5.0976
121527602 | E | LC | ETL.9460.POLE.WDPS | 44275502 | VICTOR | STOCKTON | 2021-06-13 |  | ETL.9460 | VALLEY SPRINGS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44275499 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0019391 | 4766.6113 | 9.243
121532754 | F | LC | ETL.7260.POLE.WOOD | 44651531 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.7260 | KESWICK-CASCADE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44651531 | 2018-08-01 | Single Wood Pole | 3HP - 3 Horizontal Post | 2018-08-01 | Polymer | Post |  |  |  |  | 0.00030619 | 2437.969
121537506 | B | LC | ETL.1330.INSL | 40629332 | LAKEVLLE | SACRAMENTO | 2021-06-14 | 2021-08-24 | ETL.1330 | CORTINA-MENDOCINO #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587882 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.0038177 | 5288.4395
121537506 | B | LC | ETL.1330.INSL | 40629332 | LAKEVLLE | SACRAMENTO | 2021-06-14 | 2021-08-24 | ETL.1330 | CORTINA-MENDOCINO #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587882 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 0.0038177 | 5288.4395
121539521 | B | LC | ETL.6760.SWIT | 40743663 | SACTO | SACRAMENTO | 2021-06-15 | 2021-06-29 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Switch | Out of Adjustment | [Repair, Completed] | Tier2 |  |  | COMP | [8 empty] | SEECO | VACUUM INTERRUPTERS (3 GAPS) | SCADA Only
121541849 | F | LC | ETL.5650.TOWR | 40604759 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40604759 | 1942-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-02-15 | Glass | Dead End |  |  |  |  | 1.3147e-06 | 3105.6272 | 0.0040831
121543487 | F | LC | ETL.5390.TOWR | 40870705 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40870705 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 5.8846e-08 | 4682.2344
121543729 | F | LC | ETL.1820.POLE.NWOD | 44324174 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44324174 | 2015-12-01 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2015-12-01 | Ceramic | Suspension |  |  |  |  | 0.0085686 | 94.9939
121550425 | E | LC | ETL.7390.POLE.WOOD | 40750458 | LAKEVLLE | HUMBOLDT | 2021-06-13 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40750458 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.041781
121563061 | B | LC | ETL.4870.INSL | 40578603 | FRESNO | FRESNO | 2021-06-16 | 2021-07-27 | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40576624 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.8363e-08 | 5867.9263
121564513 | E | LC | ETL.6020.TOWR | 40817705 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40817705 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.7338e-07 | 158.2923 | 4.3274e-05
121564598 | F | LC | ETL.2395.POLE.WOOD | 44550083 | TABLEMTN | NORTH VALLEY | 2021-06-15 | 2021-07-12 | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44550083 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | Dead End |  |  |  |  | 0.00026459 | 3021.0042
121564735 | F | LC | ETL.1820.POLE.NWOD | 45014021 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45014021 | 2020-11-05 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-11-20 | Glass | Suspension |  |  |  |  | 0.0044244 | 4826.4807
121576648 | B | LC | ETL.1480.POLE.WOOD | 40669066 | LAKEVLLE | SONOMA | 2021-06-21 | 2021-06-30 | ETL.1480 | EAGLE ROCK-REDBUD | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40669066 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Porcelain | Post |  |  |  |  | 2.6924e-05 | 1155.7242
121578748 | E | LC | ETL.8960.POLE.WOOD | 40763868 | FRESNO | FRESNO | 2021-06-22 |  | ETL.8960 | LOS BANOS-PACHECO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40763868 | 1979-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 1979-01-01 | Porcelain | Dead End |  |  |  |  | 0.00031311
121580872 | B | LC | ETL.7550.INSL.NCER | 40779083 | LAKEVLLE |  | 2021-06-17 | 2021-07-28 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750980 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.00091359 | 15.8807
121584845 | F | LC | ETL.6690.POLE.WOOD | 40611471 | SACTO | SACRAMENTO | 2021-06-22 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40611471 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | [5 empty] | 0.03089 | 727.9573
121587936 | B | LC | ETL.8250.INSL.CERA | 40913754 | VICTOR | STOCKTON | 2021-06-22 | 2021-07-14 | ETL.8250 | CLAY-MARTEL | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40904148 |  | Single Wood Pole | T1DE - Tri Post Dead End 115 |  | Glass | Dead End |  |  |  |  | 0.022834 | 1362.709
121596707 | F | LC | ETL.8350.POLE.NWOD | 44891806 | VICTOR | STOCKTON | 2021-06-22 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44891806 | 2020-03-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-03-03 | Polymer | Dead End |  |  |  |  | 1.1881e-06 | 2332.3379
121596976 | F | LC | ETL.5630.TOWR | 40591370 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40591370 | 1950-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2018-09-18 | Ceramic | Double Dead End |  |  |  |  | 3.995e-06 | 218.3706 | 0.0008724
121598743 | E | LC | ETL.1440.POLE.WDPS | 44744315 | SACTO | SACRAMENTO | 2021-06-11 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40605256 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0064052 | 31.7066 | 0.20309
121603489 | F | LC | ETL.1182.TOWR | 45098590 | LAKEVLLE | SONOMA | 2021-06-25 | 2021-09-10 | ETL.1182 | BEAR CANYON TAP | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45098590 |  | LATTICE STEEL TOWER | Unknown |  | Unknown | Unknown | [5 empty] | 474.857
121605681 | E | LC | ETL.5463.INSL | 40829123 | CONCORD | EAST BAY | 2021-06-24 | 2021-11-15 | ETL.5463 | PITTSBURG-SAN MATEO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805055 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2001-01-01 | Non Ceramic | Dead End |  |  |  |  | 2.8582e-05 | 5213.9293 | 0.14903
121621085 | E | LC | ETL.1440.INSL.NCER | 44180225 | SACTO | SACRAMENTO | 2021-06-17 |  | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44180206 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.0058722
121621085 | E | LC | ETL.1440.INSL.NCER | 44180225 | SACTO | SACRAMENTO | 2021-06-17 |  | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44180206 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.0058722
121627684 | E | LC | ETL.6500.POLE.NWOD | 44153664 | SACTO | SACRAMENTO | 2021-06-28 |  | ETL.6500 | COLGATE-PALERMO | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44153664 |  | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | Suspension |  |  |  |  | 0.99984 | 428.1771 | 428.1084
121629018 | E | LC | ETL.7140.INSL.NCER | 45092648 | LAKEVLLE | NORTH BAY | 2021-06-29 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 41178108 |  | 2-Pole Non Wood | DE - Dead End | 2021-02-28 | Glass Silicone Coated | Dead End |  |  |  |  | 0.00050138
121629018 | E | LC | ETL.7140.INSL.NCER | 45092648 | LAKEVLLE | NORTH BAY | 2021-06-29 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 41178108 |  | 2-Pole Non Wood | DE - Dead End | 2021-02-28 | Glass Silicone Coated | Dead End |  |  |  |  | 0.00050138
121667832 | F | LC | ETL.6020.TOWR | 40601184 | TABLEMTN | NORTH VALLEY | 2021-07-06 | 2021-08-17 | ETL.6020 | MALIN-ROUND MTN #2 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40601184 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.2217e-08 | 174.1517
121668742 | E | LC | ETL.1730.POLE.WDPS | 44413369 | MOSSLNDG | CENTRAL COAST | 2021-06-29 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44413367 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.4632e-05 | 31.6948 | 0.00078071
121671609 | B | LC | ETL.4490.INSL | 40848545 | CONCORD | EAST BAY | 2021-07-06 | 2021-09-29 | ETL.4490 | CONTRA COSTA-DELTA SWITCHYARD | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
121675468 | F | LC | ETL.1730.POLE.WDPS | 44413336 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44413335 |  | 2-Pole Wood | 2P DDE-A - 2 Pole Double Dead End Angle | [7 empty] | 0.0018337 | 47.5096
121689786 | E | LC | ETL.5442.POLE.STPS | 44650663 | TABLEMTN |  | 2021-07-01 |  | ETL.5442 | PIT #7 TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44146176 | 2018-09-10 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 6.9087e-06 | 665.1749 | 0.0045955
121717853 | F | LC | ETL.1450.POLE.NWOD | 45090171 | SACTO | SIERRA | 2021-07-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45090171 | 2020-08-07 | Light Duty Steel Pole | 3P TRP D - 3 Pole Tramp Double Dead End | 2020-08-07 | Glass | Dead End |  |  |  |  | 1.6543e-06 | 118.9194
121721900 | B | LC | ETL.1820.INSL.NCER | 44768117 | EUREKA | HUMBOLDT | 2021-07-13 | 2021-08-04 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44768096 | 2019-05-02 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2019-05-02 | Polymer | Suspension |  |  |  |  | 7.7045e-05
121721900 | B | LC | ETL.1820.INSL.NCER | 44768117 | EUREKA | HUMBOLDT | 2021-07-13 | 2021-08-04 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44768096 | 2019-05-02 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2019-05-02 | Polymer | Suspension |  |  |  |  | 7.7045e-05
121723056 | B | LC | ETL.6020.INSL | 40635015 | TABLEMTN | NORTH VALLEY | 2021-07-12 | 2021-07-21 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601178 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 9.5082e-05 | 221.5655
121738464 | E | LC | ETL.1820.POLE.STPS | 44395183 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395182 | 2017-10-05 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.43154 | 142.4559 | 61.4753
121738873 | F | LC | ETL.1820.POLE.STPS | 44395402 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395401 | 2020-03-04 | 2-Pole Non Wood | Unknown | [7 empty] | 0.0017758 | 19.0509
121741138 | F | LC | ETL.4870.TOWR | 40597415 | FRESNO | FRESNO | 2021-07-14 |  | ETL.4870 | HELMS-GREGG #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40597415 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 3.448e-08
121744784 | F | LC | ETL.1820.POLE.WOOD | 45105741 | EUREKA | HUMBOLDT | 2021-07-15 | 2021-09-30 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 45105741 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Non Ceramic | Suspension | [5 empty] | 4084.9047
121747232 | F | LC | ETL.1820.POLE.NWOD | 45105736 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45105736 | 2020-03-04 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-03-04 | Ceramic | Suspension | [5 empty] | 0.065152
121750763 | F | LC | ETL.2390.POLE.WDPS | 44391280 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391279 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.1585e-05 | 5541.6973 | 0.3967
121769948 | B | LC | ETL.6280.POLE.WOOD | 44217538 | TABLEMTN | NORTH VALLEY | 2021-07-21 | 2021-10-06 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44217538 | 2014-11-25 | Single Wood Pole | T2N | 2014-11-25 | Non Ceramic | Post |  |  |  |  | 5.5609e-06 | 6616.2266
121781724 | E | LC | ETL.2390.POLE.WDPS | 44391055 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391054 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.7812e-05 | 1535.3563 | 0.088763
121781741 | E | LC | ETL.1810.POLE.WDPS | 44322297 | EUREKA | HUMBOLDT | 2021-07-20 | 2021-08-04 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | DLFL | 44322296 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00049591
121790566 | E | LC | ETL.9240.TOWR | 43249573 | PISMOBCH | LOS PADRES | 2021-07-24 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249573 |  | LATTICE STEEL TOWER | [9 empty] | 4402.5264
121791093 | E | LC | ETL.8365.INSL.NCER | 44856546 | EUREKA | HUMBOLDT | 2021-07-24 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44856544 | 2019-11-02 | Tubular Steel Pole | DDE - Double Dead End | 2019-11-24 | Polymer | Dead End |  |  |  |  | 0.0037776 | 284.8213 | 1.0759
121808094 | B | LC | ETL.4620.INSL.CERA | 44377887 | PISMOBCH | LOS PADRES | 2021-07-26 | 2021-09-14 | ETL.4620 | DIABLO-MESA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40810600 | 1969-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 2011-08-19 | Ceramic | Dead End |  |  |  |  | 2.2789e-06 | 618.0835
121812780 | B | LC | ETL.7060.POLE.WOOD | 40668120 | METCALF | PENINSULA | 2021-07-28 | 2021-10-06 | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40668120 |  | Single Wood Pole | 3P DV - 3 Pole Double Vertical |  | Non Ceramic | Other |  |  |  |  | 0.008435 | 1060.2281 | 8.943
121814350 | F | LC | ETL.6880.POLE.NWOD | 45074105 | LAKEVLLE | NORTH BAY | 2021-07-28 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45074105 | 2020-03-05 | Lattice Steel Pole | DC-DDE - Double Circuit Double Dead End | 2020-03-05 | Glass | Dead End |  |  |  |  | 2.6576e-07 | 31.7184
121934553 | E | LC | ETL.8170.POLE.WDPS | 44565312 | EUREKA | HUMBOLDT | 2021-08-22 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564200 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.01394 | 63.351 | 0.88313
122063937 | E | LC | ETL.4780.INSL | 40722920 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40678900 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 2.6944e-05 | 348.2342 | 0.009383
118390672 | E | LC | ETL.6500.POLE.WOOD | 40741817 | SACTO | SACRAMENTO | 2020-01-02 | 2020-09-03 | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118537085 | E | LC | ETL.1330.TOWR | 40813108 | SACTO | SACRAMENTO | 2020-02-14 | 2020-06-08 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40813108 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-05-04 | Glass | Dead End |  |  |  |  | 0.00017824 | 740.1464
118537085 | E | LC | ETL.1330.TOWR | 40813108 | SACTO | SACRAMENTO | 2020-02-14 | 2020-06-08 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40813108 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Porcelain | Dead End |  |  |  |  | 0.00017824 | 740.1464
118672051 | E | LC | ETL.6760.POLE.WOOD | 40913012 | SACTO | SACRAMENTO | 2020-03-10 | 2020-06-10 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Rotten | [Replace, Completed] | Tier3 |  |  | COMP
118763777 | E | LC | ETL.4392.INSL.CERA | 41129221 | LAKEVLLE |  | 2020-03-03 | 2020-05-29 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118782061 | F | LC | ETL.5250.TOWR | 40575733 | CONCORD | DIABLO | 2020-04-07 | 2020-05-13 | ETL.5250 | MORAGA-CASTRO VALLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40575733 | 1961-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1961-01-01 | Ceramic | Dead End |  |  |  |  | 9.8071e-08 | 31.6948
118782061 | F | LC | ETL.5250.TOWR | 40575733 | CONCORD | DIABLO | 2020-04-07 | 2020-05-13 | ETL.5250 | MORAGA-CASTRO VALLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40575733 | 1961-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 9.8071e-08 | 31.6948
118947957 | A | LC | ETL.1680.POLE.WOOD | 40809163 | LAKEVLLE | SONOMA | 2020-04-24 | 2020-05-01 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809163 | 1978-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1978-01-01 | Glass | Suspension |  |  |  |  | 0.00090066 | 5203.9238
118971994 | F | LC | ETL.6861.POLE.STPS | 44679459 | LAKEVLLE | HUMBOLDT | 2020-04-30 | 2021-08-17 | ETL.6861 | KONOCTI-EAGLE ROCK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] |  | Tier 3 | Within Both | COMP | 44679443 | 2018-10-25 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00011326 | 3532.2563
118992212 | F | LC | ETL.1470.POLE.NWOD | 40641852 | LAKEVLLE | SONOMA | 2020-05-06 | 2021-04-29 | ETL.1470 | EAGLE ROCK-CORTINA | Fence / Gate | Missing | [Install, Completed] | Tier2 |  |  | COMP
119028850 | F | LC | ETL.8405.POLE.WOOD | 40766784 | SACTO | SACRAMENTO | 2020-05-14 | 2021-10-26 | ETL.8405 | MIDDLE FORK #1 | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40766784 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0040394 | 2452.4026
119036216 | E | LC | ETL.1600.INSL.CERA | 40831855 | LAKEVLLE | SONOMA | 2020-05-12 | 2021-06-23 | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119058700 | F | LC | ETL.6440.POLE.WOOD | 41144134 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-08-25 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41144134 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 8.4543e-05 | 4057.0139
119064037 | E | LC | ETL.7510.POLE.WOOD | 40769749 | LAKEVLLE | HUMBOLDT | 2020-05-26 | 2020-07-16 | ETL.7510 | MENDOCINO-HARTLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40769749 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 3.4509e-06 | 4317.0959
119070259 | F | LC | ETL.7140.POLE.WOOD | 40657036 | LAKEVLLE | NORTH BAY | 2020-05-20 | 2020-07-09 | ETL.7140 | IGNACIO-BOLINAS #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 |  |  | COMP
119073585 | F | LC | ETL.7510.POLE.WOOD | 40862662 | LAKEVLLE | HUMBOLDT | 2020-05-26 | 2020-07-08 | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119082252 | F | LC | ETL.6760.POLE.WOOD | 40822654 | SACTO | SIERRA | 2020-05-28 | 2021-02-10 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40822654 |  | Single Wood Pole | T-1 - Tri Post | 2020-05-26 | Polymer | Post |  |  |  |  | 0.022195 | 110.8102
119084619 | E | LC | ETL.5250.TOWR | 40654420 | CONCORD | DIABLO | 2020-05-22 | 2021-02-22 | ETL.5250 | MORAGA-CASTRO VALLEY | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40654420 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 1.5041e-08 | 419.256
119104537 | F | LC | ETL.1710.POLE.WDPS | 44510604 | MOSSLNDG | CENTRAL COAST | 2020-05-20 | 2021-04-29 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44509653 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0022363 | 15.88
119108605 | F | LC | ETL.5140.POLE.WOOD | 42569894 | SACTO | SIERRA | 2020-05-21 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier3 |  |  | PEND
119110285 | F | LC | ETL.1710.POLE.WDPS | 44512082 | MOSSLNDG | CENTRAL COAST | 2020-05-20 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44510831 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0022426 | 15.88
119111090 | E | LC | ETL.4510.TOWR | 40690173 | CONCORD | DIABLO | 2020-05-21 | 2021-07-13 | ETL.4510 | CONTRA COSTA-LAS POSITAS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Non-HFTD | Non-HFRA | COMP | 40690173 | 1939-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2009-01-01 | Ceramic | Suspension |  |  |  |  | 9.095e-09
119114497 | E | LC | ETL.6220.POLE.WOOD | 40661833 | EUREKA | HUMBOLDT | 2020-05-27 | 2021-04-21 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40661833 |  | Single Wood Pole | DDE - Double Dead End | 2019-06-29 | Glass | Double Dead End |  |  |  |  | 0.080718 | 949.9796
119116067 | F | LC | ETL.6950.POLE.WOOD | 40768212 | SACTO | SIERRA | 2020-06-02 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40768212 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00076608 | 917.5387
119116520 | E | LC | ETL.6950.POLE.WOOD | 44207061 | SACTO | SIERRA | 2020-05-28 | 2021-10-13 | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44207061 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.0060754 | 538.1728 | 3.2696
119119520 | F | LC | ETL.4316.POLE.NWOD | 40758510 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-07 | ETL.4316 | PARADISE-TABLE MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40758510 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-07-31 | Glass | Double Dead End |  |  |  |  | 0.00052868 | 2045.7959
119127474 | F | LC | ETL.6280.POLE.NWOD | 40826325 | TABLEMTN | NORTH VALLEY | 2020-06-03 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40826325 |  | Light Duty Steel Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 3.0907e-06 | 174.0445
119161350 | E | LC | ETL.5140.POLE.WDPS | 45077520 | SACTO | SIERRA | 2020-06-01 | 2021-11-09 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40871784 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0096351 | 79.2067 | 0.76317
119163128 | F | LC | ETL.5440.POLE.WDPS | 44558269 | TABLEMTN |  | 2020-06-13 | 2020-08-17 | ETL.5440 | PIT #6 JCT-ROUND MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 |  |  | COMP
119169743 | E | LC | ETL.8170.POLE.STPS | 44271138 | EUREKA | HUMBOLDT | 2020-06-12 | 2021-08-02 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44271136 | 2013-07-27 | 3-Pole Non Wood | DDE - Double Dead End | [7 empty] | 0.00013383 | 1174.8506
119173593 | B | LC | ETL.5140.POLE.WDPS | 44552485 | SACTO | SACRAMENTO | 2020-05-20 | 2020-07-29 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119173593 | B | LC | ETL.5140.POLE.WDPS | 44552485 | SACTO | SACRAMENTO | 2020-05-20 | 2020-07-29 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119177708 | E | LC | ETL.8210.POLE.WOOD | 40908319 | VICTOR | STOCKTON | 2020-04-14 | 2021-06-17 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908319 | 1939-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0040402 | 3403.9211
119196219 | E | LC | ETL.6470.POLE.WOOD | 40817363 | SACTO | SIERRA | 2020-06-22 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.059999 | 110.8608
119197554 | E | LC | ETL.6470.POLE.WOOD | 40818495 | SACTO | SIERRA | 2020-06-22 | 2021-08-04 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.069484 | 142.5149
119198885 | F | LC | ETL.6480.POLE.WOOD | 40664527 | SACTO | SIERRA | 2020-06-22 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40664527 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.18722 | 316.5113
119198966 | F | LC | ETL.6480.POLE.WOOD | 40655133 | SACTO | SIERRA | 2020-06-22 | 2021-06-22 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40655133 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.14969 | 1139.0737
119199545 | E | LC | ETL.6470.POLE.WOOD | 40760745 | SACTO | SIERRA | 2020-06-23 | 2021-07-15 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760745 |  | Single Wood Pole | T2N | 2021-07-13 | Polymer | Post |  |  |  |  | 0.20217 | 158.2723
119222730 | E | LC | ETL.1240.POLE.STPS | 44200968 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2020-07-28 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44200966 |  | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 2.0219e-08 | 8091.4644
119235987 | E | LC | ETL.7290.POLE.WOOD | 44159603 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2020-11-06 | ETL.7290 | KILARC-CEDAR CREEK | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44159603 | 2014-06-02 | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.0090971 | 411.9666
119290524 | E | LC | ETL.1110.POLE.WDPS | 44424006 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-04-15 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44424005 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.003516 | 7234.6528
119291044 | F | LC | ETL.1110.POLE.WDPS | 44423356 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-07-06 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423354 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.003516 | 7925.0977
119292677 | E | LC | ETL.7780.POLE.WOOD | 40769166 | LAKEVLLE | SONOMA | 2020-07-01 | 2021-04-05 | ETL.7780 | PHILO JCT-ELK | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40769166 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Ceramic | [5 empty] | 0.0022113 | 158.2234
119300727 | E | LC | ETL.6220.POLE.WOOD | 40862532 | EUREKA | HUMBOLDT | 2020-07-02 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40862532 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.18913 | 585.2411 | 110.6855
119312488 | F | LC | ETL.8060.POLE.WOOD | 40751843 | SACTO | SIERRA | 2020-07-02 | 2021-05-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751843 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.017816 | 791.3312
119327325 | F | LC | ETL.1810.TOWR | 44321418 | EUREKA | HUMBOLDT | 2020-07-07 | 2021-10-11 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44321418 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 2.795e-06
119333780 | E | LC | ETL.8410.POLE.WOOD | 40616674 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-02-04 | ETL.8410 | ELK-GUALALA | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40616674 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Porcelain | Suspension |  |  |  |  | 0.17887 | 0.065148
119335266 | E | LC | ETL.7030.POLE.WOOD | 40600250 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-06-14 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600250 |  | Single Wood Pole | T2N | 2015-02-10 | Polymer | Post |  |  |  |  | 0.0065138 | 0.06515
119338557 | E | LC | ETL.6710.POLE.WOOD | 40769005 | MOSSLNDG | CENTRAL COAST | 2020-07-09 | 2021-06-15 | ETL.6710 | DEL MONTE-VIEJO | Vegetation | Overgrown | [Trim, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40769005 |  | Single Wood Pole | DV - Double Vertical | 2019-04-27 | Glass | Suspension |  |  |  |  | 0.59775 | 0.065148
119339919 | E | LC | ETL.7590.INSL.NCER | 44880487 | MOSSLNDG | CENTRAL COAST | 2020-07-09 | 2020-09-09 | ETL.7590 | MONTA VISTA-BURNS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767935 |  | Single Wood Pole | T-1 - Tri Post | 2020-01-21 | Polymer | Post |  |  |  |  | 0.088346 | 63.351
119355924 | F | LC | ETL.6280.POLE.NWOD | 44259109 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44259109 | 2018-09-21 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-09-21 | Polymer | Dead End - Suspension |  |  |  |  | 4.9518e-11 | 382.8197
119359029 | E | LC | ETL.1440.INSL.NCER | 44180231 | SACTO | SACRAMENTO | 2020-07-10 | 2021-06-23 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44180214 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.010399
119359029 | E | LC | ETL.1440.INSL.NCER | 44180231 | SACTO | SACRAMENTO | 2020-07-10 | 2021-06-23 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44180214 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.010399
119359029 | E | LC | ETL.1440.INSL.NCER | 44180231 | SACTO | SACRAMENTO | 2020-07-10 | 2021-06-23 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44180214 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.010399
119471070 | E | LC | ETL.7030.POLE.WOOD | 40770001 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-06-23 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770001 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.026253 | 63.4531
119473292 | F | LC | ETL.7160.POLE.WOOD | 44871200 | LAKEVLLE | NORTH BAY | 2020-07-20 |  | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871200 | 2019-09-19 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2019-09-19 | Glass | Suspension |  |  |  |  | 0.21406 | 286.616
119481059 | B | LC | ETL.4880.INSL | 40831633 | FRESNO | FRESNO | 2020-07-21 | 2020-09-15 | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40805402 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 3.448e-08
119481868 | E | LC | ETL.3720.INSL.CERA | 40704873 | CONCORD | EAST BAY | 2020-07-21 | 2021-03-24 | ETL.3720 | SOBRANTE-G #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119485735 | F | LC | ETL.8960.POLE.WOOD | 44231457 | FRESNO | FRESNO | 2020-07-22 | 2020-12-09 | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44231457 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.00067847
119492477 | E | LC | ETL.1110.POLE.WDPS | 44424601 | TABLEMTN | HUMBOLDT | 2020-07-22 | 2021-04-01 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 |  |  | COMP
119533783 | E | LC | ETL.7490.INSL | 40679298 | EUREKA | HUMBOLDT | 2020-07-30 | 2021-09-16 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119558746 | E | LC | ETL.6490.POLE.WOOD | 44190861 | SACTO | SACRAMENTO | 2020-08-04 | 2021-03-01 | ETL.6490 | COLGATE-GRASS VALLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44190861 |  | Single Wood Pole | Unknown | [7 empty] | 0.0088881 | 428.1771
119575887 | F | LC | ETL.5650.TOWR | 40668240 | TABLEMTN | NORTH VALLEY | 2020-08-07 | 2021-05-28 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40668240 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 3.5439e-07 | 1744.4635
119577887 | B | LC | ETL.6310.POLE.WOOD | 40676907 | TABLEMTN | NORTH VALLEY | 2020-08-07 | 2020-09-17 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [11 empty] | 1.1969e-05 | 4135.6346
119593107 | F | LC | ETL.7590.POLE.NWOD | 40824961 | MOSSLNDG | CENTRAL COAST | 2020-08-10 | 2021-01-12 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119595306 | E | LC | ETL.6480.POLE.NWOD | 44695500 | SACTO | SACRAMENTO | 2020-08-10 | 2021-06-14 | ETL.6480 | COLGATE-CHALLENGE | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44695500 | 2018-12-10 | Light Duty Steel Pole | T1-1A | 2018-12-10 | Polymer | Post |  |  |  |  | 0.04564 | 332.3298
119600617 | E | LC | ETL.7930.POLE.WOOD | 40875006 | MOSSLNDG | CENTRAL COAST | 2020-08-11 | 2021-03-18 | ETL.7930 | SALINAS-LAURELES | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40875006 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0033843 | 0.065147
119604860 | E | LC | ETL.6220.POLE.WOOD | 40650778 | EUREKA | HUMBOLDT | 2020-08-10 | 2021-02-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40650778 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.092658
119640156 | E | LC | ETL.9200.POLE.WDPS | 44976207 | MIDWAY | KERN | 2020-08-19 | 2021-08-17 | ETL.9200 | TAFT-CUYAMA #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 42696681 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.019248
119667739 | E | LC | ETL.1450.POLE.WDPS | 44558954 | SACTO | SACRAMENTO | 2020-08-19 | 2021-07-06 | ETL.1450 | DRUM-SUMMIT #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | DLFL | 44558463 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0019214 | 1260.556
119671998 | E | LC | ETL.1330.TOWR | 40587897 | LAKEVLLE | SONOMA | 2020-08-25 | 2021-04-01 | ETL.1330 | CORTINA-MENDOCINO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587897 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.01068 | 3323.7715
119675373 | E | LC | ETL.6979.POLE.WOOD | 40575977 | LAKEVLLE | SONOMA | 2020-08-26 | 2021-08-10 | ETL.6979 | MONTE RIO-FORT ROSS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119703538 | E | LC | ETL.7140.POLE.WOOD | 40742416 | LAKEVLLE | SONOMA | 2020-09-01 | 2021-09-30 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.01238 | 31.7201
119716433 | F | LC | ETL.7490.POLE.WOOD | 40602070 | EUREKA | HUMBOLDT | 2020-09-02 | 2021-08-02 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602070 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-08-07 | Glass | Dead End |  |  |  |  | 0.016357 | 348.0365
119718361 | B | LC | ETL.1430.INSL.NCER | 44926996 | SACTO | SACRAMENTO | 2020-09-04 | 2020-11-16 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119720840 | F | LC | ETL.8650.TOWR | 40748144 | FRESNO | YOSEMITE | 2020-07-27 |  | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40748144 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-12-17 | Glass | Suspension |  |  |  |  | 0.0012842 | 4099.8008
119723147 | F | LC | ETL.7490.POLE.NWOD | 44735712 | EUREKA | HUMBOLDT | 2020-08-10 | 2021-09-13 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44735712 | 2019-03-19 | Light Duty Steel Pole | 3P DV - 3 Pole Double Vertical | 2019-03-19 | Polymer | Post |  |  |  |  | 0.00020948 | 47.5141
119767310 | F | LC | ETL.1110.POLE.WDPS | 44423221 | TABLEMTN | HUMBOLDT | 2020-09-08 | 2021-02-10 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44423219 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0013667 | 4743.7998
119769307 | E | LC | ETL.1440.POLE.WDPS | 44762500 | SACTO | SACRAMENTO | 2020-07-01 | 2021-09-16 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 617.0731
119769307 | E | LC | ETL.1440.POLE.WDPS | 44762500 | SACTO | SACRAMENTO | 2020-07-01 | 2021-09-16 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 617.0731
119786455 | E | LC | ETL.8170.POLE.WOOD | 40906420 | EUREKA | HUMBOLDT | 2020-09-14 | 2021-06-21 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906420 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-06-04 | Glass | Dead End |  |  |  |  | 0.0055919 | 348.1371
119794957 | F | LC | ETL.3530.TOWR | 40870122 | PISMOBCH | LOS PADRES | 2020-08-05 | 2021-05-07 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40870122 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 1.3701e-06 | 1226.7673
119821029 | E | LC | ETL.3960.TOWR | 40751440 | PISMOBCH | LOS PADRES | 2020-09-22 | 2021-08-04 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751440 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Polymer | Suspension |  |  |  |  | 2.7574e-09 | 126.5838
119827599 | F | LC | ETL.5463.TOWR | 40681934 | CONCORD | DIABLO | 2020-09-29 | 2021-01-25 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40681934 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.2777e-09 | 1397.5155
119827599 | F | LC | ETL.5463.TOWR | 40681934 | CONCORD | DIABLO | 2020-09-29 | 2021-01-25 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40681934 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 1.2777e-09 | 1397.5155
119844200 | F | LC | ETL.6470.POLE.WOOD | 40874809 | SACTO | SIERRA | 2020-09-08 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40874809 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.015863 | 1598.1093
119891713 | F | LC | ETL.5650.POLE.STPS | 44971488 | TABLEMTN | NORTH VALLEY | 2020-10-12 | 2021-01-20 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Tier 3 | Within Both | DLFL | 40587070 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.2585e-06 | 1412.2946
119900270 | F | LC | ETL.7270.POLE.NWOD | 44164735 | TABLEMTN | NORTH VALLEY | 2020-10-07 | 2021-02-10 | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44164735 | 2014-08-15 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2014-08-15 | Ceramic | Dead End |  |  |  |  | 5.2443e-06 | 996.9431
119920588 | B | LC | ETL.8060.POLE.WOOD | 44156136 | SACTO | SIERRA | 2020-10-19 | 2020-11-19 | ETL.8060 | SPAULDING-SUMMIT | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44156136 | 2013-09-20 | Single Wood Pole | TH - TriAngle Post 70 | 2013-09-20 | Polymer | Post |  |  |  |  | 0.0087097 | 126.6309
119957960 | E | LC | ETL.7290.INSL | 40798661 | TABLEMTN | NORTH VALLEY | 2020-10-28 | 2021-03-15 | ETL.7290 | KILARC-CEDAR CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119973895 | A | LC | ETL.3960.INSL.NCER | 44837961 | PISMOBCH | LOS PADRES | 2020-11-02 | 2020-11-04 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40643114 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2019-09-03 | Glass | Suspension |  |  |  |  | 3.8886e-06 | 953.6552
120097004 | B | LC | ETL.6290.INSL.CERA | 40627379 | TABLEMTN |  | 2020-11-23 | 2020-12-16 | ETL.6290 | CARIBOU-PLUMAS JCT | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600690 | 1962-01-01 | Single Wood Pole | FDDE - Flat Dead End Construction | 1962-01-01 | Porcelain | Dead End |  |  |  |  | 0.15224 | 5538.7192
120126794 | F | LC | ETL.7270.POLE.NWOD | 44649296 | TABLEMTN | NORTH VALLEY | 2020-10-07 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44649296 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.00040956 | 0.065152
120150233 | E | LC | ETL.8650.POLE.NWOD | 44420177 | FRESNO | FRESNO | 2020-12-09 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44420177 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0026674 | 3305.365
120481179 | A | LC | ETL.7390.POLE.WOOD | 40648602 | LAKEVLLE | SONOMA | 2021-01-30 | 2021-02-02 | ETL.7390 | LAYTONVILLE-COVELO | Emergency | Storm Related | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648602 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Pin |  |  |  |  | 0.016292 | 412.5736
120612804 | E | LC | ETL.1480.INSL.CERA | 40815071 | LAKEVLLE |  | 2021-03-08 |  | ETL.1480 | EAGLE ROCK-REDBUD | Hardware-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40809073 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1978-01-01 | Glass | Dead End |  |  |  |  | 0.00023857 | 3050.2753 | 0.7277
120671503 | F | LC | ETL.4316.POLE.NWOD | 40702257 | TABLEMTN | NORTH VALLEY | 2021-03-16 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40702257 |  | Light Duty Steel Pole | DDE - Double Dead End | 2021-07-31 | Glass | Dead End |  |  |  |  | 0.00052868 | 2995.1147
120674463 | F | LC | ETL.5140.POLE.STPS | 44690699 | SACTO | SACRAMENTO | 2021-03-22 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44141449 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.1668e-09 | 98.503
120718968 | E | LC | ETL.7390.POLE.WDPS | 44412047 | LAKEVLLE | SONOMA | 2021-03-31 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44412044 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.015409
120719421 | F | LC | ETL.7390.POLE.WOOD | 40656700 | LAKEVLLE | SONOMA | 2021-03-31 | 2021-08-06 | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL | [11 empty] | 0.12666 | 461.1552
120743865 | E | LC | ETL.5960.TOWR | 40761222 | PISMOBCH | LOS PADRES | 2021-04-05 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40761222 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 3.6488e-08 | 5161.2417 | 0.00018832
120749055 | E | LC | ETL.5640.INSL | 40787494 | TABLEMTN | NORTH VALLEY | 2021-04-06 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758172 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 6.6115e-09 | 4167.8633 | 2.7556e-05
120749711 | E | LC | ETL.1730.POLE.WOOD | 40878200 | MOSSLNDG | CENTRAL COAST | 2021-04-06 | 2021-11-30 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Vegetation | Overgrown | [Trim, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40878200 | 1972-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1972-01-01 | Polymer | Dead End |  |  |  |  | 0.00055002 | 126.5838 | 0.069624
120756916 | E | LC | ETL.5310.INSL | 40782013 | PISMOBCH | LOS PADRES | 2021-04-07 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40753280 | 1960-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00089171 | 826.0043 | 0.73655
120763094 | E | LC | ETL.7540.POLE.WOOD | 41113147 | LAKEVLLE | SONOMA | 2021-04-07 |  | ETL.7540 | MENDOCINO-WILLITS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41113147 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00074997 | 1105.778 | 0.8293
120794430 | F | LC | ETL.5510.TOWR | 40810770 | CONCORD | DIABLO | 2021-04-12 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810770 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 2.1404e-07 | 4832.9663 | 0.0010344
120804292 | E | LC | ETL.6900.POLE.WOOD | 40759974 | LAKEVLLE | SONOMA | 2021-04-13 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40759974 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | Post |  |  |  |  | 0.00023663 | 1361.9498 | 0.32227
120812757 | F | LC | ETL.9100.POLE.WOOD | 44191862 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191862 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 5.0702e-06 | 2740.4846
120829196 | E | LC | ETL.6470.POLE.WOOD | 40767340 | SACTO | SACRAMENTO | 2021-04-16 | 2021-09-13 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40767340 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.014592 | 6094.7842
120839624 | E | LC | ETL.9330.POLE.NWOD | 44309743 | FRESNO | FRESNO | 2021-04-16 | 2021-07-08 | ETL.9330 | WISHON-COPPERMINE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44309743 |  | Lattice Steel Pole | SUSP - Suspension (TWR) | 2016-11-05 | Glass | Suspension |  |  |  |  | 0.00011316 | 6293.5435
120854891 | F | LC | ETL.4316.TOWR | 40871564 | TABLEMTN | NORTH VALLEY | 2021-04-12 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40871564 | 1921-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-23 | Glass | Suspension |  |  |  |  | 0.00065624 | 2092.6382
120883582 | E | LC | ETL.7270.POLE.WOOD | 40740667 | TABLEMTN | NORTH VALLEY | 2021-04-26 | 2021-09-01 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40740667 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.045345 | 1918.4999
120884556 | F | LC | ETL.6470.POLE.NWOD | 40679423 | SACTO | SACRAMENTO | 2021-04-26 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40679423 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00029384 | 1408.1655
120930229 | F | LC | ETL.1250.POLE.NWOD | 44327115 | FRESNO | FRESNO | 2021-05-04 | 2021-09-23 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44327115 |  | Lattice Steel Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 7.8833e-07 | 6932.1865
120932914 | E | LC | ETL.1820.INSL.NCER | 44395671 | EUREKA | HUMBOLDT | 2021-05-03 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395414 | 2020-03-03 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-03-03 | Glass | Suspension |  |  |  |  | 0.00053917
120932914 | E | LC | ETL.1820.INSL.NCER | 44395671 | EUREKA | HUMBOLDT | 2021-05-03 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395414 | 2020-03-03 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-03-03 | Glass | Suspension |  |  |  |  | 0.00053917
120953278 | E | LC | ETL.7610.POLE.WOOD | 40874039 | METCALF | SAN JOSE | 2021-05-08 |  | ETL.7610 | MONTA VISTA-LOS GATOS | Vegetation | Overgrown | [Trim] | Tier2 | Tier 2 | HFRA Removal | PEND | 40874039 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00019444 | 0.065147 | 1.2667e-05
121190401 | F | LC | ETL.2900.TOWR | 40810458 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810458 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.014032 | 777.9778 | 10.9163
121324237 | E | LC | ETL.2750.INSL.NCER | 40604486 | CONCORD | DIABLO | 2021-05-05 |  | ETL.2750 | MORAGA-OAKLAND #4 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | HFRA Removal | PEND | 40580805 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1960-01-01 | Polymer | Suspension |  |  |  |  | 6.9158e-06 | 0.065147 | 4.5054e-07
121338303 | E | LC | ETL.6220.POLE.WOOD | 40862505 | EUREKA | HUMBOLDT | 2021-05-13 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40862505 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.16726 | 1537.8777 | 257.2205
121339196 | E | LC | ETL.3500.INSL | 40603340 | VICTOR | STOCKTON | 2021-04-16 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40579794 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 0.0025252 | 1360.8871 | 3.4365
121341356 | F | LC | ETL.3742.POLE.NWOD | 41135473 | CONCORD | DIABLO | 2021-04-28 | 2021-09-30 | ETL.3742 | SOBRANTE-MORAGA | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 41135473 | 1947-01-01 | Lattice Steel Pole | DDE - Double Dead End | 1947-01-01 | Ceramic | Dead End |  |  |  |  | 3.4053e-08 | 332.4702
121344171 | F | LC | ETL.5540.TOWR | 40820395 | TABLEMTN | NORTH VALLEY | 2021-04-28 |  | ETL.5540 | POE-RIO OSO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40820395 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 1.0223e-07 | 4925.1411 | 0.00050348
121348804 | F | LC | ETL.4450.TOWR | 40814656 | CONCORD | MISSION | 2021-04-28 | 2021-09-16 | ETL.4450 | CASTRO VALLEY-NEWARK | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40814656 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.7005e-05 | 633.226
121348804 | F | LC | ETL.4450.TOWR | 40814656 | CONCORD | MISSION | 2021-04-28 | 2021-09-16 | ETL.4450 | CASTRO VALLEY-NEWARK | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40814656 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 2.7005e-05 | 633.226
121356964 | E | LC | ETL.4870.TOWR | 40576623 | FRESNO | FRESNO | 2021-05-18 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576623 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.9946e-08 | 4776.5884 | 0.00019081
121359598 | F | LC | ETL.4870.TOWR | 40576891 | FRESNO | FRESNO | 2021-05-19 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576891 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 2021-07-21 | Glass Silicone Coated | Double Dead End |  |  |  |  | 1.0799e-05 | 2957.7136 | 0.03194
121375324 | E | LC | ETL.4580.TOWR | 40601399 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40601399 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.1724e-05 | 4281.8581 | 0.050203
121379083 | F | LC | ETL.6320.POLE.NWOD | 45078155 | TABLEMTN | NORTH VALLEY | 2021-05-07 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45078155 | 2021-04-20 | Light Duty Steel Pole | T-1 - Tri Post | 2021-04-20 | Polymer | Post |  |  |  |  | 0.00035424 | 620.4225
121379587 | E | LC | ETL.3830.INSL.CERA | 40636300 | VICTOR | STOCKTON | 2021-05-21 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40604155 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 2.2414e-06 | 809.4304 | 0.0018143
121384578 | E | LC | ETL.6760.POLE.WOOD | 40611238 | SACTO | SIERRA | 2021-05-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40611238 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.087619 | 205.7564 | 18.0281
121392177 | E | LC | ETL.6760.POLE.WOOD | 40664702 | SACTO | SIERRA | 2021-05-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40664702 |  | Single Wood Pole | T-1 - Tri Post | 2020-05-08 | Polymer | Post |  |  |  |  | 0.026163 | 2515.499 | 65.8138
121405039 | F | LC | ETL.8405.POLE.NWOD | 44914342 | SACTO | SIERRA | 2021-05-20 | 2021-10-20 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44914342 | 2020-03-04 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-04 | Polymer | Post |  |  |  |  | 0.12525 | 4160.9766
121405148 | E | LC | ETL.8290.POLE.WOOD | 40656913 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40656913 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0015531 | 5431.645 | 8.4357
121420314 | F | LC | ETL.1400.POLE.STPS | 44384825 | VICTOR | STOCKTON | 2021-05-25 | 2021-06-11 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44384824 | 2019-06-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.023e-06 | 31.7081
121421263 | E | LC | ETL.7000.INSL.NCER | 40630424 | TABLEMTN |  | 2021-05-22 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40589865 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.044811 | 95.1115 | 4.2621
121429001 | F | LC | ETL.6470.POLE.WOOD | 40598660 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40598660 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.065397 | 1481.0322
121430520 | F | LC | ETL.1403.POLE.STPS | 44855803 | VICTOR | YOSEMITE | 2021-05-26 |  | ETL.1403 | SANDBAR TAP | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44855788 | 2019-11-21 | 2-Pole Non Wood | FSS - Field Switch Structure | [7 empty] | 6.1403e-05 | 1329.0924
121430693 | E | LC | ETL.6470.POLE.WOOD | 40611186 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40611186 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.06793 | 142.4516 | 9.6768
121435263 | E | LC | ETL.4220.INSL.CERA | 44388486 | TABLEMTN |  | 2021-05-29 |  | ETL.4220 | WOODLEAF-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44388389 | 2016-11-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2016-11-29 | Ceramic | Suspension |  |  |  |  | 0.0047621
121435263 | E | LC | ETL.4220.INSL.CERA | 44388486 | TABLEMTN |  | 2021-05-29 |  | ETL.4220 | WOODLEAF-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44388389 | 2016-11-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2016-11-29 | Ceramic | Suspension |  |  |  |  | 0.0047621
121449128 | F | LC | ETL.8560.POLE.WOOD | 40763014 | PISMOBCH | LOS PADRES | 2021-05-27 |  | ETL.8560 | CAYUCOS-CAMBRIA | Road | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40763014 |  | Single Wood Pole | FIG4DDE - Figure 4 Double Dead End | 2020-04-10 | Glass | Dead End |  |  |  |  | 0.0081218 | 303.4949
121475049 | F | LC | ETL.7540.POLE.WOOD | 40768578 | LAKEVLLE | HUMBOLDT | 2021-05-26 |  | ETL.7540 | MENDOCINO-WILLITS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40768578 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 3.0636e-05 | 1063.8021 | 0.03259
121486027 | F | LC | ETL.4316.POLE.STPS | 44559105 | TABLEMTN |  | 2021-05-26 | 2021-07-26 | ETL.4316 | PARADISE-TABLE MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44558928 | 2018-03-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00010802 | 3484.7625
121492691 | E | LC | ETL.4521.POLE.NWOD | 40593224 | CONCORD | MISSION | 2021-06-01 | 2021-09-29 | ETL.4521 | US WINDPOWER #3 TAP | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593224 | 2012-01-01 | Tubular Steel Pole | DV-DE - Double Vertical Dead End | 1984-01-01 | Ceramic | Other |  |  |  |  | 2.7713e-07 | 5466.0889
121492815 | F | LC | ETL.6890.POLE.WOOD | 42646238 | LAKEVLLE | HUMBOLDT | 2021-06-02 | 2021-07-12 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42646238 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00062187 | 3563.9871
121493297 | E | LC | ETL.1070.POLE.WDPS | 44387568 | VICTOR | STOCKTON | 2021-06-01 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44387567 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00028324 | 4947.8276 | 1.4014
121496453 | B | LC | ETL.1440.INSL | 40786965 | SACTO | SIERRA | 2021-06-08 | 2021-06-24 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756923 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0080375
121496453 | B | LC | ETL.1440.INSL | 40786965 | SACTO | SIERRA | 2021-06-08 | 2021-06-24 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756923 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0080375
121500041 | F | LC | ETL.5390.TOWR | 40593765 | TABLEMTN | NORTH VALLEY | 2021-06-03 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40593765 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 8.2541e-08 | 1871.8424
121512437 | F | LC | ETL.6320.POLE.NWOD | 44820192 | TABLEMTN | NORTH VALLEY | 2021-06-04 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44820192 | 2019-06-30 | Fiberglass | TPD - Tri Post Dead End Construction | 2019-06-30 | Glass | Dead End |  |  |  |  | 0.00035482 | 143.2547
121516252 | F | LC | ETL.6770.POLE.WOOD | 40759700 | SACTO | SIERRA | 2021-06-05 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40759700 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | Other |  |  |  |  | 0.022975 | 1344.8513
121519788 | E | LC | ETL.6880.POLE.NWOD | 44958692 | LAKEVLLE | NORTH BAY | 2021-06-07 |  | ETL.6880 | FULTON-CALISTOGA | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44958692 | 2020-05-19 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-19 | Glass | Dead End |  |  |  |  | 0.00018497 | 427.2245 | 0.079023
121523518 | F | LC | ETL.5640.TOWR | 40815317 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40815317 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 1.1666e-08 | 3772.0593 | 4.4005e-05
121525538 | B | LC | ETL.4430.INSL | 40899232 | TABLEMTN | NORTH VALLEY | 2021-06-11 | 2021-07-08 | ETL.4430 | BUCKS CREEK-ROCK CREEK-CRESTA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873468 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 2.4776e-05 | 6790.3833
121525838 | B | LC | ETL.4550.TOWR | 40817930 | TABLEMTN | NORTH VALLEY | 2021-06-11 | 2021-06-23 | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817930 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.8499e-05 | 2963.4478
121531674 | E | LC | ETL.5630.TOWR | 40656119 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40656119 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-08-10 | Glass | Suspension |  |  |  |  | 0.00030553 | 1537.5399 | 0.46977
121545304 | E | LC | ETL.4550.TOWR | 40605626 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40605626 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 0.00017603 | 4056.6345 | 0.71409
121547767 | E | LC | ETL.5400.INSL | 40687133 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5400 | PIT #3-PIT #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40657380 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1924-01-01 | Ceramic | Other |  |  |  |  | 0.011698 | 0.065152 | 0.00076217
121550709 | F | LC | ETL.5390.POLE.NWOD | 41184140 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5390 | PIT #1-COTTONWOOD | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41184140 |  | Lattice Steel Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | Suspension |  |  |  |  | 7.5638e-07 | 4131.7891
121561631 | E | LC | ETL.5780.TOWR | 40608528 | VICTOR | STOCKTON | 2021-06-15 |  | ETL.5780 | TIGER CREEK-ELECTRA | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40608528 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-05-22 | Glass Silicone Coated | Suspension |  |  |  |  | 3.1125e-06 | 126.8157 | 0.00039471
121561775 | F | LC | ETL.6230.POLE.NWOD | 45031497 | MOSSLNDG | CENTRAL COAST | 2021-06-15 |  | ETL.6230 | BURNS-LONE STAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45031497 | 2019-09-02 | Light Duty Steel Pole | T2N | 2019-09-02 | Polymer | Post |  |  |  |  | 0.061185 | 0.065152
121561802 | B | LC | ETL.4540.TOWR | 40757914 | SACTO | SACRAMENTO | 2021-06-15 | 2021-08-16 | ETL.4540 | CORTINA-VACA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40757914 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 2.6489e-05 | 3784.7144
121561921 | E | LC | ETL.6750.POLE.WDPS | 44374926 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44374924 | 2012-08-04 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0002611 | 205.744 | 0.05372
121568326 | E | LC | ETL.1400.POLE.WOOD | 44948149 | VICTOR | YOSEMITE | 2021-06-15 | 2021-11-08 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44948149 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.0013566 | 39.6314 | 0.053764
121572406 | F | LC | ETL.5390.POLE.STPS | 44378876 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44378875 | 2015-11-01 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0021728 | 1570.798
121574311 | E | LC | ETL.6330.POLE.WOOD | 40766983 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40766983 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0017658 | 269.1313 | 0.47524
121585474 | F | LC | ETL.1450.POLE.STPS | 45032865 | SACTO | SIERRA | 2021-06-17 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45032843 | 2020-06-13 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.000229 | 3069.2839
121589281 | B | LC | ETL.2720.TOWR | 40870714 | CONCORD | DIABLO | 2021-06-23 | 2021-07-15 | ETL.2720 | MORAGA-OAKLAND #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40870714 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-04 | Glass | Suspension |  |  |  |  | 4.3935e-06 | 1362.2408
121589281 | B | LC | ETL.2720.TOWR | 40870714 | CONCORD | DIABLO | 2021-06-23 | 2021-07-15 | ETL.2720 | MORAGA-OAKLAND #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40870714 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-01 | Glass | Suspension |  |  |  |  | 4.3935e-06 | 1362.2408
121608257 | E | LC | ETL.6050.TOWR | 40871207 | MOSSLNDG | SAN JOSE | 2021-06-17 |  | ETL.6050 | MOSS LANDING-METCALF | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40871207 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.8023e-08 | 490.6567 | 1.375e-05
121610463 | E | LC | ETL.1183.TOWR | 45098582 | LAKEVLLE | SONOMA | 2021-06-27 | 2021-09-16 | ETL.1183 | CALPINE-WEST FORD FLAT | Road | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45098582 |  | LATTICE STEEL TOWER | Unknown |  | Unknown | Unknown | [5 empty] | 47.5532
121637869 | E | LC | ETL.5390.INSL.NCER | 45114618 | TABLEMTN | NORTH VALLEY | 2021-06-23 |  | ETL.5390 | PIT #1-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40599952 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 5.0551e-08 | 5133.3115 | 0.00025949
121661281 | F | LC | ETL.8310.POLE.WDPS | 44564910 | MOSSLNDG | CENTRAL COAST | 2021-06-28 |  | ETL.8310 | WATSONVILLE-SALINAS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44564324 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0048062 | 601.2565
121675654 | B | LC | ETL.1372.POLE.WDPS | 44283685 | PISMOBCH | LOS PADRES | 2021-07-06 | 2021-10-06 | ETL.1372 | MANVILLE TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44283684 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00019582 | 1442.1754
121678090 | B | LC | ETL.6020.TOWR | 40605579 | TABLEMTN | NORTH VALLEY | 2021-07-06 | 2021-07-09 | ETL.6020 | MALIN-ROUND MTN #2 | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40605579 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.3177e-05 | 791.1504
121679430 | F | LC | ETL.2395.POLE.WOOD | 44403543 | TABLEMTN | NORTH VALLEY | 2021-07-02 |  | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44403543 | 2015-12-10 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2015-12-10 | Ceramic | Dead End |  |  |  |  | 0.0006639 | 79.1846
121679499 | E | LC | ETL.9240.TOWR | 43249539 | PISMOBCH | LOS PADRES | 2021-07-07 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 43249539 |  | LATTICE STEEL TOWER | [9 empty] | 524.6012
121685647 | E | LC | ETL.5140.INSL.CERA | 40775089 | SACTO | SIERRA | 2021-07-05 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44551630 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 7.2949e-05
121685647 | E | LC | ETL.5140.INSL.CERA | 40775089 | SACTO | SIERRA | 2021-07-05 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44551630 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 7.2949e-05
121687852 | E | LC | ETL.7640.POLE.WDPS | 44565389 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44564273 |  | 2-Pole Wood | TH - TriAngle Post 70 | [7 empty] | 6.7484e-05 | 3659.8687 | 0.24698
121706523 | B | LC | ETL.4040.INSL.CERA | 44784153 | TABLEMTN | NORTH VALLEY | 2021-07-07 | 2021-08-02 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553913 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 2019-07-14 | Ceramic | Suspension |  |  |  |  | 0.074947
121706523 | B | LC | ETL.4040.INSL.CERA | 44784153 | TABLEMTN | NORTH VALLEY | 2021-07-07 | 2021-08-02 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553913 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 2019-07-14 | Ceramic | Suspension |  |  |  |  | 0.074947
121707783 | E | LC | ETL.1680.INSL.CERA | 40578795 | LAKEVLLE | SONOMA | 2021-06-12 | 2021-09-17 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40576804 | 1972-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1972-01-01 | Porcelain | Dead End |  |  |  |  | 0.0017821 | 2708.3875
121729935 | E | LC | ETL.6470.POLE.WOOD | 40593278 | SACTO | SIERRA | 2021-07-14 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40593278 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.014554 | 5857.8857 | 85.2558
121731771 | E | LC | ETL.6750.POLE.WDPS | 44209117 | TABLEMTN |  | 2021-07-12 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44209114 | 2014-05-08 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.3657e-05 | 142.4582 | 0.0062192
121734490 | E | LC | ETL.1820.POLE.WOOD | 44553502 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44553502 |  | Single Wood Pole | SV-1B - Single Vertical Light Angle BR |  | Glass | Suspension |  |  |  |  | 0.24831 | 2753.0989 | 683.6172
121744351 | F | LC | ETL.1252.POLE.STPS | 44319947 | FRESNO | YOSEMITE | 2021-07-14 |  | ETL.1252 | OAKHURST TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44319946 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.9491e-05 | 3515.5505
121746385 | E | LC | ETL.3720.INSL.CERA | 40622425 | CONCORD | EAST BAY | 2021-07-13 |  | ETL.3720 | SOBRANTE-G #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40581861 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1968-01-01 | Porcelain | Suspension |  |  |  |  | 5.4333e-05 | 221.5946 | 0.01204
121762907 | F | LC | ETL.7040.POLE.WOOD | 45070796 | TABLEMTN | NORTH VALLEY | 2021-07-19 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45070796 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.13335 | 1981.5565
121779422 | E | LC | ETL.6510.POLE.WDPS | 44399442 | SACTO | SACRAMENTO | 2021-07-20 |  | ETL.6510 | COLGATE-SMARTVILLE #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44399440 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0006726 | 269.2076 | 0.18107
121781691 | F | LC | ETL.7390.POLE.NWOD | 40769312 | LAKEVLLE | HUMBOLDT | 2021-07-21 |  | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40769312 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | Dead End |  |  |  |  | 0.00080602 | 2203.6062
121783545 | E | LC | ETL.2390.POLE.WDPS | 44391248 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391247 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 7.1618e-05 | 6710.7031 | 0.48061
121800779 | B | LC | ETL.6280.POLE.WOOD | 44259130 | TABLEMTN | NORTH VALLEY | 2021-07-26 | 2021-09-21 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 4.1639e-06 | 382.8197
121803578 | E | LC | ETL.8365.POLE.NWOD | 40906673 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40906673 | 2011-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0028245
121807808 | E | LC | ETL.7390.POLE.WOOD | 40702874 | LAKEVLLE | HUMBOLDT | 2021-07-26 |  | ETL.7390 | LAYTONVILLE-COVELO | Hardware-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40702874 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-08-27 | Glass | Dead End |  |  |  |  | 0.35894
121810192 | E | LC | ETL.2540.POLE.WDPS | 44401581 | MOSSLNDG | CENTRAL COAST | 2021-07-28 | 2021-09-27 | ETL.2540 | METCALF-GREEN VALLEY | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 2455.0217
121810699 | E | LC | ETL.5420.POLE.WDPS | 44559089 | TABLEMTN | NORTH VALLEY | 2021-07-27 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44558532 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.016042 | 427.3329 | 6.8553
121812927 | E | LC | ETL.8630.POLE.WDPS | 44565581 | PISMOBCH | LOS PADRES | 2021-07-28 |  | ETL.8630 | DIVIDE-VANDENBERG #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564229 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0004801 | 2924.0354 | 1.4038
121815993 | B | LC | ETL.8365.INSL.NCER | 40922402 | EUREKA | HUMBOLDT | 2021-07-29 | 2021-08-19 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912593 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Pin |  |  |  |  | 0.089183
121816642 | F | LC | ETL.6500.POLE.STPS | 44984639 | SACTO | SIERRA | 2021-07-28 | 2021-08-02 | ETL.6500 | COLGATE-PALERMO | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44977501 | 2020-07-17 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.003757 | 2214.9285
121822010 | E | LC | ETL.2395.POLE.WOOD | 44550865 | TABLEMTN | NORTH VALLEY | 2021-07-30 |  | ETL.2395 | GRIZZLY TAP | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550865 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00077325 | 300.6002 | 0.23244
121824677 | E | LC | ETL.5630.POLE.NWOD | 44190825 | TABLEMTN | NORTH VALLEY | 2021-07-30 |  | ETL.5630 | ROCK CREEK-POE | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44190825 |  | Lattice Steel Pole | DDE - Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.00019408 | 1804.4395 | 0.35021
121953136 | E | LC | ETL.5230.INSL | 40782413 | METCALF | SAN JOSE | 2021-08-25 |  | ETL.5230 | MONTA VISTA-JEFFERSON #2 | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | PEND | 40753082 | 1963-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1963-01-01 | Ceramic | Suspension |  |  |  |  | 0.0062294 | 1234.1384 | 7.6879
122087353 | F | LC | ETL.8001.POLE.NWOD | 45128426 | SACTO | SIERRA | 2021-09-17 |  | ETL.8001 | BEALE AFB (WAPA) #1 TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45128426 | 2018-06-13 | Light Duty Steel Pole | SVDE - Single Vertical Dead End | 2018-06-13 | Polymer | Post | [5 empty] | 2125.1653
122133312 | E | LC | ETL.3160.INSL.NCER | 44914360 | CONCORD | EAST BAY | 2021-10-01 |  | ETL.3160 | OLEUM-G #2 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40581705 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-05-08 | Glass | Suspension |  |  |  |  | 0.00025605 | 443.3138 | 0.11351
122133312 | E | LC | ETL.3160.INSL.NCER | 44914360 | CONCORD | EAST BAY | 2021-10-01 |  | ETL.3160 | OLEUM-G #2 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40581705 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-20 | Glass | Dead End |  |  |  |  | 0.00025605 | 443.3138 | 0.11351
122232937 | E | LC | ETL.1110.TOWR | 40676706 | TABLEMTN | NORTH VALLEY | 2021-10-20 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40676706 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00030038 | 94.9939 | 0.028534
122232937 | E | LC | ETL.1110.TOWR | 40676706 | TABLEMTN | NORTH VALLEY | 2021-10-20 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40676706 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.00030038 | 94.9939 | 0.028534
118398861 | E | LC | ETL.6231.POLE.WOOD | 41142836 | MOSSLNDG | CENTRAL COAST | 2020-01-06 | 2020-01-21 | ETL.6231 | LONE STAR TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41142836 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.0066306 | 1760.0653
118499974 | F | LC | ETL.1330.TOWR | 40761521 | LAKEVLLE | SONOMA | 2020-02-05 |  | ETL.1330 | CORTINA-MENDOCINO #1 | Structure-Steel | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40761521 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0025231 | 6030.9009
118499974 | F | LC | ETL.1330.TOWR | 40761521 | LAKEVLLE | SONOMA | 2020-02-05 |  | ETL.1330 | CORTINA-MENDOCINO #1 | Structure-Steel | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40761521 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Dead End |  |  |  |  | 0.0025231 | 6030.9009
118522380 | E | LC | ETL.1330.TOWR | 40657091 | LAKEVLLE | SONOMA | 2020-02-10 | 2021-04-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40657091 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-02 | Glass | Suspension |  |  |  |  | 0.00012443 | 2171.0598
118522380 | E | LC | ETL.1330.TOWR | 40657091 | LAKEVLLE | SONOMA | 2020-02-10 | 2021-04-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40657091 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.00012443 | 2171.0598
118702918 | E | LC | ETL.6280.POLE.WOOD | 40599694 | TABLEMTN | NORTH VALLEY | 2020-03-13 | 2020-08-12 | ETL.6280 | CARIBOU #2 | Anchor-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118723646 | E | LC | ETL.6222.POLE.NWOD | 44815583 | EUREKA | HUMBOLDT | 2020-03-19 | 2020-09-03 | ETL.6222 | FORT SEWARD TAP | Crossarm-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | DLFL | 44815583 | 2019-05-31 | Light Duty Steel Pole | T-1 - Tri Post | 2020-02-25 | Polymer | Post |  |  |  |  | 4.8163e-08
118936241 | E | LC | ETL.3150.INSL.CERA | 43601234 | CONCORD | EAST BAY | 2020-04-21 | 2021-05-27 | ETL.3150 | OLEUM-G #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118938706 | E | LC | ETL.5440.POLE.WDPS | 44558235 | TABLEMTN |  | 2020-04-22 | 2020-06-09 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118939237 | E | LC | ETL.6330.POLE.WOOD | 40591786 | TABLEMTN | NORTH VALLEY | 2020-04-22 | 2021-10-18 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.00050003 | 1439.6834
118940192 | E | LC | ETL.3730.INSL.NCER | 40773243 | CONCORD | DIABLO | 2020-04-22 | 2021-04-05 | ETL.3730 | SOBRANTE-G #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118972150 | E | LC | ETL.6980.POLE.WOOD | 40616647 | LAKEVLLE | HUMBOLDT | 2020-04-30 | 2021-06-17 | ETL.6980 | FORT ROSS-GUALALA | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40616647 | 1953-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2010-01-01 | Polymer | Suspension |  |  |  |  | 0.20299 | 0.065147
118975688 | F | LC | ETL.2660.POLE.NWOD | 44515876 | SACTO | SIERRA | 2020-04-29 |  | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44515876 | 2018-02-13 | Tubular Steel Pole | DC-DDE-A - Double Circuit Double Dead End Angle | 2018-02-13 | Glass | Suspension |  |  |  |  | 2.5897e-09 | 1313.5581
119002747 | E | LC | ETL.1430.TOWR | 40805292 | SACTO | SIERRA | 2020-05-06 | 2020-06-10 | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40805292 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.0040895 | 158.3103
119005263 | E | LC | ETL.1420.TOWR | 40589593 | SACTO | SIERRA | 2020-05-06 | 2021-02-11 | ETL.1420 | DRUM-RIO OSO #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40589593 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm |  | Polymer | [5 empty] | 0.00059755 | 158.285
119041358 | A | LC | ETL.9100.POLE.WOOD | 42574227 | PISMOBCH | LOS PADRES | 2020-05-15 | 2020-06-17 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.0060663 | 2455.1978
119061222 | E | LC | ETL.1240.POLE.WDPS | 44386174 | TABLEMTN | NORTH VALLEY | 2020-05-18 | 2020-06-09 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44386174 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 2.2269e-06
119061222 | E | LC | ETL.1240.POLE.WDPS | 44386174 | TABLEMTN | NORTH VALLEY | 2020-05-18 | 2020-06-09 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44386174 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 2.2269e-06
119080200 | F | LC | ETL.7510.POLE.NWOD | 44652043 | LAKEVLLE | HUMBOLDT | 2020-05-26 | 2020-07-06 | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44652043 | 2018-07-31 | Light Duty Steel Pole | T-1 - Tri Post | 2018-07-31 | Polymer | Post |  |  |  |  | 4.5458e-09 | 2171.0598
119080320 | E | LC | ETL.1730.POLE.WDPS | 44601370 | MOSSLNDG | CENTRAL COAST | 2020-05-28 | 2020-09-24 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44601344 | 2017-09-25 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00050864 | 31.6948
119081615 | E | LC | ETL.6330.POLE.WOOD | 40656582 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2021-09-16 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40656582 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.015976 | 870.2589
119083872 | B | LC | ETL.1330.TOWR | 40587885 | LAKEVLLE | SONOMA | 2020-05-30 | 2020-06-11 | ETL.1330 | CORTINA-MENDOCINO #1 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587885 | 1951-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-11-20 | Polymer | Suspension |  |  |  |  | 0.00075317 | 6712.2544
119083872 | B | LC | ETL.1330.TOWR | 40587885 | LAKEVLLE | SONOMA | 2020-05-30 | 2020-06-11 | ETL.1330 | CORTINA-MENDOCINO #1 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587885 | 1951-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1951-01-01 | Polymer | Suspension |  |  |  |  | 0.00075317 | 6712.2544
119096462 | E | LC | ETL.6770.POLE.WOOD | 40810151 | SACTO | SACRAMENTO | 2020-06-02 | 2020-08-24 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0019685 | 632.957
119101064 | E | LC | ETL.8170.POLE.WOOD | 40906460 | EUREKA | HUMBOLDT | 2020-06-03 | 2021-09-23 | ETL.8170 | TRINITY-MAPLE CREEK | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40906460 |  | Single Wood Pole | T-1 - Tri Post | 2019-11-20 | Polymer | Post |  |  |  |  | 0.029289 | 664.5661
119103386 | E | LC | ETL.6950.POLE.WOOD | 40908722 | SACTO | SIERRA | 2020-05-18 | 2021-10-12 | ETL.6950 | GOLD HILL #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908722 | 2013-10-17 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2013-10-17 | Non Ceramic | Post |  |  |  |  | 0.0017461 | 1697.6278 | 2.9642
119109576 | F | LC | ETL.8240.POLE.WOOD | 40767359 | VICTOR | STOCKTON | 2020-06-02 | 2021-02-09 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40767359 | 1969-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0016219 | 2804.8376
119112036 | F | LC | ETL.3150.TOWR | 40746015 | CONCORD | EAST BAY | 2020-05-21 |  | ETL.3150 | OLEUM-G #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40746015 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 6.8331e-08 | 126.5956
119112424 | E | LC | ETL.6470.POLE.WOOD | 40767192 | SACTO | SIERRA | 2020-06-01 | 2020-07-07 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119113704 | F | LC | ETL.6330.POLE.NWOD | 44761244 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44761244 | 2019-05-08 | Light Duty Steel Pole | T2N | 2019-05-08 | Polymer | Pin |  |  |  |  | 3.9848e-06 | 862.7981
119116809 | E | LC | ETL.8405.POLE.WOOD | 42569704 | SACTO | SIERRA | 2020-05-28 | 2021-02-09 | ETL.8405 | MIDDLE FORK #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 42569704 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [6 empty] | 2531.4304
119118120 | F | LC | ETL.6690.POLE.WOOD | 40814225 | SACTO | SIERRA | 2020-05-29 | 2021-07-06 | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40814225 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.14874 | 142.4769
119118896 | F | LC | ETL.7300.POLE.NWOD | 44810003 | TABLEMTN | NORTH VALLEY | 2020-06-04 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44810003 | 2019-05-11 | Light Duty Steel Pole | T2N | 2019-05-11 | Polymer | Post |  |  |  |  | 1.9031e-05 | 301.3406
119120073 | F | LC | ETL.6490.POLE.WOOD | 40823693 | SACTO | SIERRA | 2020-06-03 |  | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40823693 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.010027 | 664.5627
119127395 | F | LC | ETL.7300.POLE.WOOD | 40876516 | TABLEMTN |  | 2020-06-03 | 2021-07-07 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876516 |  | Single Wood Pole | T2N | 2021-03-01 | Polymer | Post |  |  |  |  | 0.0024796 | 3707.2417
119128588 | E | LC | ETL.8360.POLE.WOOD | 40613352 | LAKEVLLE | SONOMA | 2020-06-09 | 2021-05-06 | ETL.8360 | LAYTONVILLE-WILLITS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119132429 | F | LC | ETL.4221.POLE.NWOD | 44820243 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2020-08-03 | ETL.4221 | SLY CREEK TAP | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44820243 | 2019-05-24 | Light Duty Steel Pole | DDE - Double Dead End | 2020-10-01 | Glass | Double Dead End |  |  |  |  | 2.0305e-05 | 348.1806
119169519 | F | LC | ETL.6280.POLE.WOOD | 40751734 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2021-09-14 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40751734 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 5.0586e-06 | 63.3304
119181822 | E | LC | ETL.6310.POLE.WOOD | 40600659 | TABLEMTN | NORTH VALLEY | 2020-06-18 | 2020-11-06 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40600659 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.2001e-05 | 4594.916
119182352 | F | LC | ETL.6310.POLE.WOOD | 40752055 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40752055 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 3.4949e-05 | 5290.9702
119183269 | E | LC | ETL.8210.POLE.WOOD | 40908249 | VICTOR | STOCKTON | 2020-06-16 | 2021-09-02 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908249 | 1984-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0022699 | 1303.8461
119188941 | E | LC | ETL.1600.TOWR | 40587744 | LAKEVLLE | SONOMA | 2020-06-18 |  | ETL.1600 | FULTON-PUEBLO | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40587744 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-06-20 | Glass | Suspension |  |  |  |  | 0.0072706 | 395.7428 | 2.8773
119193803 | F | LC | ETL.6310.POLE.WOOD | 40817326 | TABLEMTN | NORTH VALLEY | 2020-06-18 | 2020-07-30 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40817326 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 8.0326e-06 | 2218.8638
119196904 | E | LC | ETL.7515.INSL.NCER | 44929959 | LAKEVLLE | HUMBOLDT | 2020-06-22 |  | ETL.7515 | HARTLEY-CLEARLAKE | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44929936 | 2020-06-17 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2020-06-17 | Glass | Dead End |  |  |  |  | 1.1254e-05 | 5256.8892 | 0.059159
119198516 | F | LC | ETL.6470.POLE.WOOD | 40611145 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40611145 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.004324 | 126.6512
119199135 | E | LC | ETL.6470.POLE.WOOD | 40760456 | SACTO | SIERRA | 2020-06-23 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760456 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.10912 | 110.8608
119213304 | E | LC | ETL.4392.INSL.CERA | 40839420 | LAKEVLLE |  | 2020-06-25 | 2021-02-23 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119228752 | F | LC | ETL.7270.POLE.NWOD | 44685525 | TABLEMTN | NORTH VALLEY | 2020-06-29 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44685525 | 2018-11-26 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-26 | Polymer | Post |  |  |  |  | 1.0939e-05 | 1851.2888
119235475 | F | LC | ETL.7270.POLE.NWOD | 40577351 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2021-09-16 | ETL.7270 | KESWICK-TRINITY | Guy Wire Mark /Indic-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40577351 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.081449 | 317.8733
119237677 | E | LC | ETL.7270.POLE.WOOD | 40908530 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40908530 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-02-29 | Glass | Dead End |  |  |  |  | 0.0067097 | 4367.7598 | 29.3062
119293755 | E | LC | ETL.1370.POLE.WDPS | 44283614 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-06-23 | ETL.1370 | DIVIDE-CABRILLO #2 | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44283612 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.02188 | 2011.5979
119293822 | E | LC | ETL.1370.POLE.WDPS | 44283615 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-06-23 | ETL.1370 | DIVIDE-CABRILLO #2 | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44283612 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.02188 | 2011.5979
119296280 | E | LC | ETL.8170.POLE.STPS | 44820903 | EUREKA | HUMBOLDT | 2020-06-30 | 2021-06-02 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44812756 | 2019-08-03 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.3557e-05 | 126.5956
119304757 | E | LC | ETL.8170.POLE.WOOD | 40906441 | EUREKA | HUMBOLDT | 2020-07-02 | 2021-07-19 | ETL.8170 | TRINITY-MAPLE CREEK | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40906441 |  | Single Wood Pole | DDE - Double Dead End | 2021-06-05 | Glass | Dead End |  |  |  |  | 0.016594 | 110.8153
119308043 | B | LC | ETL.7140.POLE.STPS | 44874799 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] |  | Tier 3 | Within Both | COMP | 44870392 | 2019-05-10 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0031723 | 553.9316
119308099 | B | LC | ETL.7140.POLE.STPS | 44818544 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-26 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] |  | Tier 3 | Within Both | COMP | 44817633 | 2019-05-07 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0015726 | 4211.6216
119314480 | F | LC | ETL.7630.POLE.NWOD | 44768929 | LAKEVLLE | SONOMA | 2020-07-06 | 2020-10-30 | ETL.7630 | MONTE RIO-FULTON | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44768929 | 2019-05-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-05-03 | Polymer | Dead End - Post |  |  |  |  | 0.0020469 | 79.1651
119326597 | E | LC | ETL.7980.INSL.NCER | 44631855 | SACTO | SACRAMENTO | 2020-07-07 |  | ETL.7980 | SMARTVILLE-MARYSVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40602215 |  | Single Wood Pole | T-1 - Tri Post | 2018-07-12 | Polymer | Post |  |  |  |  | 0.0013348 | 4752.3833 | 6.3433
119327964 | E | LC | ETL.8170.POLE.WOOD | 40586383 | EUREKA | HUMBOLDT | 2020-07-07 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40586383 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.013841 | 0.065152 | 0.0009018
119329807 | F | LC | ETL.7270.POLE.WOOD | 40906090 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906090 |  | Single Wood Pole | T-1 - Tri Post | 2020-07-20 | Polymer | Post |  |  |  |  | 0.001545 | 142.6986
119330624 | F | LC | ETL.8060.POLE.WOOD | 40751889 | SACTO | SIERRA | 2020-07-07 | 2021-05-11 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire Mark /Indic-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751889 | 1996-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.008989 | 348.1462
119336754 | F | LC | ETL.6280.POLE.NWOD | 40868119 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40868119 |  | Light Duty Steel Pole | TP - Tri Pin |  | Non Ceramic | Pin |  |  |  |  | 0.00038805 | 2613.3357
119356099 | E | LC | ETL.6280.POLE.WOOD | 40875388 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40875388 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0069691 | 6679.6816 | 46.5513
119365234 | E | LC | ETL.1110.TOWR | 40821498 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-04-05 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40821498 | 1952-01-01 | LATTICE STEEL TOWER | SUSP-A - Suspension Angle (TWR) | 2021-05-28 | Ceramic | Suspension |  |  |  |  | 0.00019357 | 1408.2502
119369301 | B | LC | ETL.6880.POLE.WOOD | 40808995 | LAKEVLLE | SONOMA | 2020-07-14 | 2021-07-29 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Rotten | [Replace, Completed] | Tier3 |  |  | COMP
119374380 | F | LC | ETL.7030.POLE.WOOD | 40825584 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-07-13 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825584 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0047625 | 4765.3584
119377975 | F | LC | ETL.1430.TOWR | 40746578 | SACTO | SACRAMENTO | 2020-07-15 | 2021-02-22 | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746578 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-03-10 | Glass | Suspension |  |  |  |  | 0.0020207 | 205.7345
119380656 | E | LC | ETL.6222.POLE.WOOD | 40648567 | EUREKA | HUMBOLDT | 2020-07-16 |  | ETL.6222 | FORT SEWARD TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40648567 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0024429
119469566 | F | LC | ETL.7030.POLE.WOOD | 40816892 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40816892 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0063696
119469717 | E | LC | ETL.6290.POLE.WOOD | 40758604 | TABLEMTN | NORTH VALLEY | 2020-07-17 | 2021-09-02 | ETL.6290 | CARIBOU-PLUMAS JCT | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40758604 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.048047 | 1363.4305
119475468 | B | LC | ETL.7160.INSL.NCER | 44871240 | LAKEVLLE | NORTH BAY | 2020-07-20 | 2020-09-14 | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44871181 | 2019-09-19 | Single Wood Pole | 1VP - 1 Vertical | 2019-09-19 | Glass | Suspension |  |  |  |  | 0.23317 | 648.5276
119478881 | F | LC | ETL.9200.POLE.WOOD | 40586329 | MIDWAY | KERN | 2020-07-20 | 2021-07-19 | ETL.9200 | TAFT-CUYAMA #1 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40586329 | 1962-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.0041234
119485556 | F | LC | ETL.8170.POLE.NWOD | 44628449 | EUREKA | HUMBOLDT | 2020-07-21 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44628449 | 2018-06-11 | Light Duty Steel Pole | T2N | 2021-08-23 | Polymer | Post |  |  |  |  | 0.00010745 | 1646.483
119496446 | E | LC | ETL.1450.POLE.WDPS | 44557642 | SACTO | SACRAMENTO | 2020-07-22 | 2021-02-18 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
119497512 | F | LC | ETL.4040.POLE.STPS | 44328551 | TABLEMTN | NORTH VALLEY | 2020-07-23 | 2021-06-29 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44328548 | 2015-12-10 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 3.1333e-06 | 3563.1055
119509110 | E | LC | ETL.1110.INSL.CERA | 40796892 | TABLEMTN | HUMBOLDT | 2020-07-23 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424114 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0036505
119509110 | E | LC | ETL.1110.INSL.CERA | 40796892 | TABLEMTN | HUMBOLDT | 2020-07-23 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424114 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0036505
119515195 | F | LC | ETL.9200.POLE.WOOD | 40687920 | MIDWAY | KERN | 2020-07-23 |  | ETL.9200 | TAFT-CUYAMA #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40687920 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Ceramic | Pin |  |  |  |  | 0.019969
119515873 | F | LC | ETL.1110.POLE.NWOD | 42603425 | TABLEMTN | HUMBOLDT | 2020-07-22 | 2021-02-10 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42603425 |  | Lattice Steel Pole | DDE - Double Dead End | 2021-05-28 | Ceramic | Dead End |  |  |  |  | 0.00044445 | 221.5655
119523893 | E | LC | ETL.1420.TOWR | 40764900 | SACTO | SACRAMENTO | 2020-07-29 | 2021-03-05 | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40764900 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1913-01-01 | Porcelain | Dead End |  |  |  |  | 0.00051203 | 15.8837
119523893 | E | LC | ETL.1420.TOWR | 40764900 | SACTO | SACRAMENTO | 2020-07-29 | 2021-03-05 | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40764900 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2019-05-03 | Glass | Dead End |  |  |  |  | 0.00051203 | 15.8837
119528408 | F | LC | ETL.6220.POLE.WOOD | 40586738 | EUREKA | HUMBOLDT | 2020-07-30 | 2021-02-09 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40586738 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.054815 | 618.2028
119535567 | F | LC | ETL.6310.POLE.WOOD | 40592300 | TABLEMTN | NORTH VALLEY | 2020-07-30 | 2020-11-06 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40592300 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 1.5358e-06 | 5020.748
119559587 | F | LC | ETL.8365.POLE.WOOD | 40912646 | EUREKA | HUMBOLDT | 2020-08-04 | 2021-02-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40912646 | 2010-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.061817
119559606 | F | LC | ETL.8365.POLE.WOOD | 40912646 | EUREKA | HUMBOLDT | 2020-08-04 | 2021-03-31 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912646 | 2010-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.061817
119574454 | F | LC | ETL.3190.TOWR | 40910259 | TABLEMTN | NORTH VALLEY | 2020-08-06 |  | ETL.3190 | CARIBOU-PALERMO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40910259 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.0011585 | 31.6978 | 0.036721
119577567 | E | LC | ETL.8365.POLE.WOOD | 40750497 | EUREKA | HUMBOLDT | 2020-08-07 | 2021-05-03 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Jumper-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40750497 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-04-28 | Glass | Dead End |  |  |  |  | 0.050769 | 1046.2505
119596021 | F | LC | ETL.8210.POLE.WOOD | 40908248 | VICTOR | STOCKTON | 2020-08-10 |  | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908248 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0023697 | 1364.3922
119625083 | E | LC | ETL.1450.POLE.WDPS | 44549993 | SACTO | SACRAMENTO | 2020-08-17 | 2021-11-17 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44549454 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00011058 | 0.065152 | 7.2045e-06
119629261 | F | LC | ETL.6870.POLE.WOOD | 40693697 | SACTO | SIERRA | 2020-08-17 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40693697 | 1966-01-01 | Single Wood Pole | T2N | 2020-05-29 | Polymer | Post |  |  |  |  | 0.052236 | 60.2092
119636061 | F | LC | ETL.6710.POLE.WOOD | 40589419 | MOSSLNDG | CENTRAL COAST | 2020-08-18 | 2021-04-07 | ETL.6710 | DEL MONTE-VIEJO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40589419 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.13671 | 0.065148
119637560 | F | LC | ETL.1330.TOWR | 40762067 | LAKEVLLE | SONOMA | 2020-08-19 | 2021-03-22 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40762067 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.5179e-05 | 1369.4505
119637560 | F | LC | ETL.1330.TOWR | 40762067 | LAKEVLLE | SONOMA | 2020-08-19 | 2021-03-22 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40762067 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Ceramic | Dead End |  |  |  |  | 4.5179e-05 | 1369.4505
119640211 | E | LC | ETL.9200.POLE.WOOD | 40873192 | MIDWAY | KERN | 2020-08-19 | 2020-09-16 | ETL.9200 | TAFT-CUYAMA #1 | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40873192 | 1962-01-01 | Single Wood Pole | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.023036
119648114 | E | LC | ETL.4392.INSL.NCER | 40831849 | LAKEVLLE | SONOMA | 2020-08-20 | 2021-04-17 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119666097 | B | LC | ETL.6880.POLE.WOOD | 40912476 | LAKEVLLE | SONOMA | 2020-08-24 | 2021-08-03 | ETL.6880 | FULTON-CALISTOGA | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40912476 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-07-08 | Glass | Dead End |  |  |  |  | 0.0032095 | 696.472
119677766 | F | LC | ETL.7780.POLE.WOOD | 40660590 | LAKEVLLE | HUMBOLDT | 2020-08-25 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40660590 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Ceramic | [5 empty] | 0.0017249 | 121.845
119696502 | E | LC | ETL.9090.POLE.WOOD | 40813825 | PISMOBCH | LOS PADRES | 2020-05-05 | 2021-03-18 | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40813825 |  | Single Wood Pole | FIG4W - Wood X Arm | 2013-03-18 | Non Ceramic | Suspension |  |  |  |  | 0.0006234 | 427.1542
119699442 | B | LC | ETL.7212.INSL.NCER | 44405294 | METCALF | PENINSULA | 2020-08-27 | 2020-12-01 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119713123 | F | LC | ETL.1450.POLE.WOOD | 40876971 | SACTO | SACRAMENTO | 2020-09-03 | 2021-04-26 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876971 |  | Light Duty Steel Pole | 3P SV - 3 Pole Single Vertical | 1948-01-01 | Ceramic | Suspension |  |  |  |  | 5.0469e-06 | 63.348
119716896 | E | LC | ETL.7820.POLE.WOOD | 40876422 | LAKEVLLE | HUMBOLDT | 2020-09-02 | 2021-07-22 | ETL.7820 | POTTER VALLEY-WILLITS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40876422 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | [5 empty] | 5.5155e-05 | 300.718
119719360 | F | LC | ETL.4440.TOWR | 40663299 | TABLEMTN | NORTH VALLEY | 2020-09-04 | 2021-04-12 | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40663299 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 2.1569e-06 | 4463.6655
119723748 | F | LC | ETL.8650.POLE.NWOD | 44420202 | FRESNO | YOSEMITE | 2020-08-06 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44420202 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.010754 | 2214.1416
119756374 | F | LC | ETL.7390.POLE.NWOD | 40666668 | LAKEVLLE | SONOMA | 2020-09-12 | 2021-05-31 | ETL.7390 | LAYTONVILLE-COVELO | Road | Brush Fuel | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40666668 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0015499
119770538 | E | LC | ETL.2060.POLE.WOOD | 45078148 | LAKEVLLE | HUMBOLDT | 2020-08-14 | 2021-08-12 | ETL.2060 | FORT BRAGG-ELK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45078148 | 2016-12-08 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2016-12-08 | Ceramic | Dead End |  |  |  |  | 0.12871 | 79.143
119771224 | E | LC | ETL.5960.TOWR | 40650979 | PISMOBCH | LOS PADRES | 2020-09-16 | 2021-04-05 | ETL.5960 | DIABLO-GATES #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650979 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-08-06 | Glass | Suspension |  |  |  |  | 3.8922e-07 | 5113.772
119783864 | E | LC | ETL.6280.POLE.WOOD | 40600640 | TABLEMTN | NORTH VALLEY | 2020-09-14 |  | ETL.6280 | CARIBOU #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40600640 |  | Single Wood Pole | LB - Line and Buck |  | Polymer | Dead End |  |  |  |  | 0.00031501 | 1914.1288 | 0.60298
119785036 | E | LC | ETL.6220.POLE.WOOD | 40769398 | EUREKA | HUMBOLDT | 2020-09-14 | 2021-10-24 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40769398 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.033369 | 1537.8777 | 51.3179
119789700 | E | LC | ETL.5933.INSL.CERA | 44358900 | PISMOBCH | LOS PADRES | 2020-07-29 | 2021-04-05 | ETL.5933 | MORRO BAY-TEMPLETON | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40591874 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2016-08-27 | Ceramic | Dead End |  |  |  |  | 1.3607e-07 | 2151.1479
119790885 | E | LC | ETL.8410.SWIT | 40744207 | LAKEVLLE | SONOMA | 2020-09-21 | 2021-07-22 | ETL.8410 | ELK-GUALALA | Switch | Out of Adjustment | [Repair, Completed] | Tier2 |  |  | COMP | [8 empty] | SEECO | HIGH VELOCITY INTERRUPTER | SCADA Only
119810345 | F | LC | ETL.6280.POLE.WOOD | 44259130 | TABLEMTN | NORTH VALLEY | 2020-08-13 | 2021-07-08 | ETL.6280 | CARIBOU #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [11 empty] | 4.1639e-06 | 382.8197
119816122 | F | LC | ETL.6220.POLE.WOOD | 40769345 | EUREKA | HUMBOLDT | 2020-09-25 | 2021-02-09 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40769345 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.034956 | 2151.1467
119818185 | F | LC | ETL.8060.POLE.WOOD | 40602288 | SACTO | SIERRA | 2020-08-28 | 2021-02-12 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40602288 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.077567 | 95.0021
119829967 | B | LC | ETL.6880.POLE.WOOD | 40877288 | LAKEVLLE | NORTH BAY | 2020-09-29 | 2020-10-15 | ETL.6880 | FULTON-CALISTOGA | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119857627 | A | LC | ETL.6880.POLE.WOOD | 40912462 | LAKEVLLE | SONOMA | 2020-10-06 | 2020-10-20 | ETL.6880 | FULTON-CALISTOGA | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40912462 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0084065 | 734.6977
119889906 | F | LC | ETL.8365.POLE.NWOD | 40906686 | EUREKA | HUMBOLDT | 2020-10-09 | 2021-08-05 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] |  | Non-HFTD | HFRA Addition | DLFL | 40906686 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.024237
119898188 | F | LC | ETL.7270.POLE.NWOD | 44649280 | TABLEMTN | NORTH VALLEY | 2020-10-07 | 2021-02-10 | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44649280 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.00074886 | 1819.5953
119917459 | F | LC | ETL.6950.POLE.NWOD | 44186627 | SACTO | SIERRA | 2020-06-02 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44186627 | 2017-04-10 | Light Duty Steel Pole | T-1 - Tri Post | 2017-04-10 | Polymer | Post |  |  |  |  | 2.2319e-05 | 2453.718
119947045 | B | LC | ETL.1721.INSL.CERA | 40835272 | MOSSLNDG | CENTRAL COAST | 2020-10-23 | 2020-11-13 | ETL.1721 | METCALF-SALINAS #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 44414523 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | [5 empty] | 1.7215e-08
119947045 | B | LC | ETL.1721.INSL.CERA | 40835272 | MOSSLNDG | CENTRAL COAST | 2020-10-23 | 2020-11-13 | ETL.1721 | METCALF-SALINAS #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 44414523 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Non Ceramic | Suspension |  |  |  |  | 1.7215e-08
119947045 | B | LC | ETL.1721.INSL.CERA | 40835272 | MOSSLNDG | CENTRAL COAST | 2020-10-23 | 2020-11-13 | ETL.1721 | METCALF-SALINAS #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 44414523 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 1.7215e-08
119971934 | F | LC | ETL.6230.POLE.WOOD | 40611075 | MOSSLNDG | CENTRAL COAST | 2020-10-28 | 2021-04-28 | ETL.6230 | BURNS-LONE STAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40611075 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.1462 | 126.6368
120129585 | F | LC | ETL.7490.POLE.NWOD | 44145878 | EUREKA | HUMBOLDT | 2020-10-19 |  | ETL.7490 | MAPLE CREEK-HOOPA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44145878 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.00169 | 838.3292
120133331 | F | LC | ETL.8960.POLE.NWOD | 40764175 | FRESNO | YOSEMITE | 2020-10-27 | 2021-01-04 | ETL.8960 | LOS BANOS-PACHECO | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40764175 |  | Tubular Steel Pole | SS1 - Susp. Steel Single. CIR | 1974-01-01 | Polymer | Suspension |  |  |  |  | 3.8288e-07
120162035 | E | LC | ETL.1050.TOWR | 40751497 | FRESNO | FRESNO | 2020-12-10 | 2021-07-26 | ETL.1050 | BALCH-SANGER | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751497 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1923-01-01 | Porcelain | Dead End |  |  |  |  | 0.0051312 | 6221.439
120436039 | E | LC | ETL.8060.POLE.WOOD | 40586099 | SACTO | SACRAMENTO | 2021-01-16 | 2021-08-05 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586099 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Polymer | [5 empty] | 0.0046114 | 63.348
120627766 | E | LC | ETL.2390.POLE.WDPS | 44391060 | VICTOR | STOCKTON | 2021-03-10 | 2021-05-21 | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
120672120 | E | LC | ETL.2540.INSL.CERA | 40630109 | MOSSLNDG | SAN JOSE | 2021-03-16 | 2021-08-03 | ETL.2540 | METCALF-GREEN VALLEY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40589076 | 1952-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1952-01-01 | Porcelain | Double Dead End |  |  |  |  | 0.0039637 | 2452.0347
120680234 | E | LC | ETL.5140.POLE.STPS | 44377476 | SACTO | SACRAMENTO | 2021-03-23 | 2021-06-14 | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44377474 | 2011-10-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.0382e-05 | 4053.9558
120681479 | F | LC | ETL.1710.POLE.WDPS | 44513679 | MOSSLNDG | CENTRAL COAST | 2021-03-23 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44512237 |  | 2-Pole Wood | DE - Dead End | [7 empty] | 2.5173e-05 | 34.8578
120687141 | F | LC | ETL.4392.TOWR | 41129385 | LAKEVLLE | SONOMA | 2021-03-24 | 2021-03-29 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 41129385 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.00086104 | 411.5694
120687141 | F | LC | ETL.4392.TOWR | 41129385 | LAKEVLLE | SONOMA | 2021-03-24 | 2021-03-29 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 41129385 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.00086104 | 411.5694
120690566 | E | LC | ETL.1710.POLE.WOOD | 42567494 | MOSSLNDG | CENTRAL COAST | 2021-03-25 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42567494 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Ceramic | Double Dead End |  |  |  |  | 0.00026243 | 31.6948 | 0.0083175
120695515 | E | LC | ETL.1710.POLE.WDPS | 44512099 | MOSSLNDG | CENTRAL COAST | 2021-03-26 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44510837 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0007611 | 31.6948 | 0.024123
120696346 | E | LC | ETL.1070.INSL.NCER | 40852076 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40822920 | 1998-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1957-01-01 | Polymer | Dead End |  |  |  |  | 9.448e-06 | 3279.5457 | 0.030985
120700321 | E | LC | ETL.6890.POLE.WOOD | 40667715 | LAKEVLLE | SONOMA | 2021-03-27 | 2021-08-11 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
120715990 | E | LC | ETL.5330.TOWR | 40662585 | MOSSLNDG | CENTRAL COAST | 2021-03-30 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40662585 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 5.2484e-06 | 224.0817 | 0.0011761
120725900 | E | LC | ETL.3700.POLE.WOOD | 40826937 | PISMOBCH | LOS PADRES | 2021-04-01 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40826937 | 1989-01-01 | Single Wood Pole | T1DE - Tri Post Dead End 115 | 1989-01-01 | Porcelain | Dead End |  |  |  |  | 9.6194e-05 | 4037.8574 | 0.38842
120740263 | E | LC | ETL.2660.POLE.NWOD | 44515811 | SACTO | SACRAMENTO | 2021-04-03 | 2021-04-09 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44515811 | 2018-02-13 | Tubular Steel Pole | DC-DDE - Double Circuit Double Dead End | 2018-02-13 | Glass | Suspension |  |  |  |  | 7.8254e-08 | 6282.2275
120743844 | B | LC | ETL.3830.TOWR | 40803330 | VICTOR | STOCKTON | 2021-03-31 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803330 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.4229e-05 | 2741.7422
120745442 | E | LC | ETL.8365.POLE.WOOD | 40912694 | EUREKA | HUMBOLDT | 2021-04-05 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40912694 |  | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 2021-04-27 | Glass | Dead End |  |  |  |  | 0.048093 | 5040.4707 | 242.4129
120757446 | E | LC | ETL.1350.POLE.STPS | 44993145 | TABLEMTN | NORTH VALLEY | 2021-04-07 | 2021-06-30 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993113 | 2020-06-04 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.5698e-05 | 0.065152
120758525 | A | LC | ETL.5310.INSL | 40885424 | PISMOBCH | LOS PADRES | 2021-04-07 | 2021-04-12 | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Emergency | Storm Related | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863089 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.016726 | 982.0776
120759292 | E | LC | ETL.8220.POLE.WOOD | 40613669 | VICTOR | STOCKTON | 2021-04-07 |  | ETL.8220 | VALLEY SPRINGS-CALAVERAS CEMENT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40613669 | 1991-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 2.713e-05 | 2066.6564 | 0.056068
120763178 | E | LC | ETL.7140.POLE.WOOD | 40809050 | LAKEVLLE | SONOMA | 2021-04-08 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40809050 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | [5 empty] | 0.039971 | 1711.6168 | 68.4148
120767254 | B | LC | ETL.5091.INSL | 41122514 | MOSSLNDG | CENTRAL COAST | 2021-04-08 | 2021-05-20 | ETL.5091 | METCALF-MONTA VISTA #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40753073 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0071317 | 316.4942
120794500 | F | LC | ETL.3830.TOWR | 40804665 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40804665 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.6507e-05 | 95.2198 | 0.002524
120794760 | E | LC | ETL.8250.INSL.CERA | 40918588 | VICTOR | STOCKTON | 2021-04-10 | 2021-11-30 | ETL.8250 | CLAY-MARTEL | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908869 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00098857 | 2742.4761 | 2.7111
120811454 | F | LC | ETL.9100.POLE.WOOD | 44191332 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191332 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 9.8e-05 | 1440.5813
120815978 | E | LC | ETL.3500.TOWR | 40803570 | VICTOR | STOCKTON | 2021-04-14 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40803570 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 3.4208e-06 | 94.9894 | 0.00032494
120833301 | F | LC | ETL.3830.TOWR | 40642837 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40642837 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 3.6767e-06 | 5476.1846
120835005 | E | LC | ETL.1890.TOWR | 40748482 | FRESNO | FRESNO | 2021-04-17 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40748482 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 8.2375e-07 | 5129.5869 | 0.0042255
120843862 | E | LC | ETL.5970.INSL.NCER | 45009334 | PISMOBCH | LOS PADRES | 2021-04-19 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40587683 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-02-23 | Glass Silicone Coated | Suspension |  |  |  |  | 2.0268e-07 | 2614.7756 | 0.00052996
120845956 | E | LC | ETL.1110.INSL.NCER | 45082495 | TABLEMTN | NORTH VALLEY | 2021-04-19 | 2021-06-25 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45082463 | 2021-04-12 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2021-04-12 | Glass | Dead End |  |  |  |  | 0.0058906
120845956 | E | LC | ETL.1110.INSL.NCER | 45082495 | TABLEMTN | NORTH VALLEY | 2021-04-19 | 2021-06-25 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45082463 | 2021-04-12 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2021-04-12 | Glass | Dead End |  |  |  |  | 0.0058906
120845956 | E | LC | ETL.1110.INSL.NCER | 45082495 | TABLEMTN | NORTH VALLEY | 2021-04-19 | 2021-06-25 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45082463 | 2021-04-12 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2021-04-12 | Glass | Dead End |  |  |  |  | 0.0058906
120851556 | E | LC | ETL.4316.TOWR | 40758414 | TABLEMTN | NORTH VALLEY | 2021-04-13 | 2021-05-24 | ETL.4316 | PARADISE-TABLE MTN | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758414 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-11-18 | Glass | Suspension |  |  |  |  | 0.0016314 | 4386.7925
120858169 | E | LC | ETL.3500.TOWR | 40643401 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40643401 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 8.4322e-05 | 553.8282 | 0.0467
120859880 | F | LC | ETL.1820.POLE.STPS | 44918942 | EUREKA | HUMBOLDT | 2021-04-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Right of Way | Encroachment | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44918840 | 2019-04-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014233 | 63.3274
120860997 | B | LC | ETL.4870.TOWR | 40858327 | FRESNO | FRESNO | 2021-04-20 | 2021-06-17 | ETL.4870 | HELMS-GREGG #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40858327 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 7.7361e-09 | 4812.7461
120860997 | B | LC | ETL.4870.TOWR | 40858327 | FRESNO | FRESNO | 2021-04-20 | 2021-06-17 | ETL.4870 | HELMS-GREGG #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40858327 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-31 | Glass | Dead End |  |  |  |  | 7.7361e-09 | 4812.7461
120875180 | E | LC | ETL.1440.POLE.WDPS | 45078141 | SACTO | SIERRA | 2021-04-23 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40913110 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0018212 | 648.7145 | 1.1815
120880325 | F | LC | ETL.5463.POLE.NWOD | 41136385 | CONCORD | DIABLO | 2021-04-24 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41136385 | 2002-01-01 | Tubular Steel Pole | SVDE - Single Vertical Dead End | 2001-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 1.1484e-07 | 5654.4177 | 0.00064934
120882521 | E | LC | ETL.3740.INSL.CERA | 40781526 | CONCORD | EAST BAY | 2021-04-24 | 2021-09-01 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40752436 | 1922-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1991-01-01 | Porcelain | Suspension |  |  |  |  | 0.044312 | 11.1359
120904697 | E | LC | ETL.5980.TOWR | 40818896 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40818896 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 6.8749e-07 | 1298.0298 | 0.00089239
120907585 | F | LC | ETL.3700.POLE.WOOD | 40659141 | PISMOBCH | LOS PADRES | 2021-04-27 | 2021-09-27 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40659141 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Polymer | Dead End |  |  |  |  | 0.00050525 | 4164.8696
120931391 | E | LC | ETL.7550.POLE.WOOD | 40649118 | LAKEVLLE | SONOMA | 2021-05-04 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | PEND | 40649118 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 2.4501e-06 | 79.143 | 0.00019391
120946486 | B | LC | ETL.6470.POLE.WOOD | 40905841 | SACTO | SACRAMENTO | 2021-05-06 | 2021-07-29 | ETL.6470 | COLGATE-ALLEGHANY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40905841 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.4954 | 129.8254
121322557 | F | LC | ETL.4850.TOWR | 40813995 | FRESNO | FRESNO | 2021-04-21 |  | ETL.4850 | HAAS-MCCALL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40813995 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1957-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.1188e-09 | 9201.1709 | 5.63e-05
121328940 | F | LC | ETL.5452.TOWR | 40593856 | CONCORD | DIABLO | 2021-04-24 |  | ETL.5452 | CONTRA COSTA-MORAGA #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40593856 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-01-01 | Ceramic | Suspension |  |  |  |  | 6.5674e-09 | 15.8815
121330760 | E | LC | ETL.5330.INSL | 40631256 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591782 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 2.2461e-05 | 871.2979 | 0.01957
121330760 | E | LC | ETL.5330.INSL | 40631256 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591782 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 2.2461e-05 | 871.2979 | 0.01957
121347644 | E | LC | ETL.1820.POLE.WDPS | 44557452 | EUREKA | HUMBOLDT | 2021-05-17 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44553968 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.026804 | 63.351 | 1.6981
121356845 | E | LC | ETL.1420.TOWR | 40762307 | SACTO | SIERRA | 2021-04-28 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40762307 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.0022604 | 3564.2905 | 8.0568
121370261 | F | LC | ETL.6950.POLE.WOOD | 40666285 | SACTO | SIERRA | 2021-05-01 | 2021-09-28 | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40666285 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.0014042 | 5506.1968
121378645 | F | LC | ETL.8350.POLE.NWOD | 44911340 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44911340 | 2020-03-03 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-03 | Polymer | Post |  |  |  |  | 2.2437e-06 | 2376.6802
121380402 | B | LC | ETL.4440.TOWR | 40758275 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-29 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758275 | 1968-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1968-01-01 | Porcelain | Dead End |  |  |  |  | 1.5447e-05 | 3463.8922
121380451 | E | LC | ETL.8350.POLE.NWOD | 44918821 | VICTOR | STOCKTON | 2021-05-08 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44918821 | 2020-03-03 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-03 | Polymer | Post |  |  |  |  | 1.3873e-06 | 2265.8246 | 0.0031433
121384952 | F | LC | ETL.6500.POLE.WOOD | 40866242 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40866242 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | Pin |  |  |  |  | 0.0080463 | 4139.2256
121390304 | F | LC | ETL.1600.TOWR | 40810362 | LAKEVLLE | SONOMA | 2021-05-24 |  | ETL.1600 | FULTON-PUEBLO | Road | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810362 | 1946-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.9364e-06 | 2346.1775
121390304 | F | LC | ETL.1600.TOWR | 40810362 | LAKEVLLE | SONOMA | 2021-05-24 |  | ETL.1600 | FULTON-PUEBLO | Road | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810362 | 1946-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1946-01-01 | Ceramic | Dead End |  |  |  |  | 3.9364e-06 | 2346.1775
121394870 | E | LC | ETL.7550.POLE.WOOD | 40809258 | LAKEVLLE | HUMBOLDT | 2021-05-15 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40809258 |  | Single Wood Pole | SV-PJ-90 - Single Vertical Post Jumper 90 |  | Porcelain | [5 empty] | 3.198e-05 | 854.2646 | 0.027319
121398078 | F | LC | ETL.6770.POLE.NWOD | 44928254 | SACTO | SIERRA | 2021-05-19 |  | ETL.6770 | DRUM-SPAULDING | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44928254 | 2020-05-21 | Light Duty Steel Pole | T2N | 2020-05-21 | Polymer | Post |  |  |  |  | 0.00025635 | 3069.2839
121398936 | E | LC | ETL.2760.INSL | 40724733 | CONCORD | EAST BAY | 2021-05-19 |  | ETL.2760 | MORAGA-OAKLAND J | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40681824 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.8573e-08 | 458.8659 | 1.3111e-05
121400875 | E | LC | ETL.1650.POLE.STPS | 44258749 | LAKEVLLE |  | 2021-05-25 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44258746 | 2017-09-21 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 6.1728e-07 | 2786.7917 | 0.0017202
121404666 | F | LC | ETL.6640.POLE.NWOD | 40660651 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40660651 |  | Tubular Steel Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.00028517 | 2807.3894
121405084 | F | LC | ETL.1073.POLE.WOOD | 40803728 | VICTOR | YOSEMITE | 2021-05-19 | 2021-06-10 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40803728 | 1991-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1956-01-01 | Non Ceramic | Other |  |  |  |  | 0.00027917 | 31.7081
121408429 | E | LC | ETL.7290.POLE.WOOD | 40701722 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40701722 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.051716 | 142.5082 | 7.3699
121444196 | E | LC | ETL.1350.TOWR | 40752216 | TABLEMTN | NORTH VALLEY | 2021-06-01 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40752216 | 1944-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.00068397 | 0.066048 | 4.5174e-05
121446699 | F | LC | ETL.1720.POLE.STPS | 44401056 | MOSSLNDG | CENTRAL COAST | 2021-05-28 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44401055 |  | 2-Pole Non Wood | 2P DDE-A - 2 Pole Double Dead End Angle | [7 empty] | 3.8993e-09 | 2708.2156
121452400 | B | LC | ETL.4392.INSL.CERA | 41129232 | LAKEVLLE | SONOMA | 2021-06-02 | 2021-07-13 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41129340 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.00010865 | 3423.9121
121452400 | B | LC | ETL.4392.INSL.CERA | 41129232 | LAKEVLLE | SONOMA | 2021-06-02 | 2021-07-13 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41129340 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.00010865 | 3423.9121
121455413 | F | LC | ETL.1720.POLE.STPS | 44304398 | MOSSLNDG | CENTRAL COAST | 2021-05-28 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44304396 | 2015-07-02 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.3765e-09 | 3183.5676
121470338 | E | LC | ETL.2700.INSL.CERA | 45114370 | CONCORD | DIABLO | 2021-06-03 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45114356 |  | Lattice Steel Pole |  |  | Ceramic | Suspension | [5 empty] | 1568.8029
121475441 | E | LC | ETL.1250.INSL.NCER | 40776324 | FRESNO | FRESNO | 2021-05-28 | 2021-06-30 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44319506 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 7.2086e-06
121475441 | E | LC | ETL.1250.INSL.NCER | 40776324 | FRESNO | FRESNO | 2021-05-28 | 2021-06-30 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44319506 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 7.2086e-06
121475441 | E | LC | ETL.1250.INSL.NCER | 40776324 | FRESNO | FRESNO | 2021-05-28 | 2021-06-30 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44319506 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 7.2086e-06
121485768 | E | LC | ETL.6980.POLE.WOOD | 40825488 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40825488 | 1968-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.47074 | 0.065147 | 0.030667
121494885 | F | LC | ETL.2770.TOWR | 40609137 | CONCORD | EAST BAY | 2021-06-03 |  | ETL.2770 | MORAGA-SAN LEANDRO #1 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40609137 | 1925-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Dead End |  |  |  |  | 1.1606e-05 | 0.065147 | 7.5609e-07
121494885 | F | LC | ETL.2770.TOWR | 40609137 | CONCORD | EAST BAY | 2021-06-03 |  | ETL.2770 | MORAGA-SAN LEANDRO #1 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40609137 | 1925-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.1606e-05 | 0.065147 | 7.5609e-07
121498951 | E | LC | ETL.6981.INSL.NCER | 42737667 | LAKEVLLE |  | 2021-06-01 |  | ETL.6981 | SALMON CREEK TAP | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42737663 | 2012-01-01 | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper |  | Non Ceramic | [5 empty] | 0.00054743 | 1803.7023 | 0.9874
121499844 | E | LC | ETL.5640.TOWR | 40598920 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40598920 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 7.6775e-09 | 3407.9209 | 2.6164e-05
121518338 | F | LC | ETL.4880.TOWR | 40740037 | FRESNO | FRESNO | 2021-06-07 |  | ETL.4880 | HELMS-GREGG #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Zone 1 | HFRA Removal | PEND | 40740037 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 9.3078e-06
121526674 | E | LC | ETL.5650.INSL | 40884933 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40862809 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 6.317e-05 | 207.066 | 0.01308
121540194 | F | LC | ETL.7820.POLE.WOOD | 40824417 | LAKEVLLE | HUMBOLDT | 2021-06-14 | 2021-07-01 | ETL.7820 | POTTER VALLEY-WILLITS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
121543066 | F | LC | ETL.6760.POLE.WOOD | 40598590 | SACTO | SIERRA | 2021-06-10 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40598590 |  | Light Duty Steel Pole | LB - Line and Buck |  | Non Ceramic | Post |  |  |  |  | 0.0089537 | 205.7564
121547470 | F | LC | ETL.6220.POLE.NWOD | 44855784 | EUREKA | HUMBOLDT | 2021-06-15 | 2021-09-30 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire Mark /Indic-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44855784 | 2019-09-17 | Light Duty Steel Pole | T2N | 2019-09-17 | Polymer | Post |  |  |  |  | 0.0027498 | 832.1305
121550103 | B | LC | ETL.1660.POLE.WDPS | 44298610 | LAKEVLLE |  | 2021-06-15 | 2021-08-05 | ETL.1660 | GEYSERS #3-EAGLE ROCK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121556526 | F | LC | ETL.6020.TOWR | 40805303 | TABLEMTN | NORTH VALLEY | 2021-06-15 | 2021-10-08 | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40805303 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 7.4055e-09 | 428.4714
121557028 | B | LC | ETL.4960.INSL | 40705321 | CONCORD |  | 2021-06-16 | 2021-07-07 | ETL.4960 | LAKEVILLE-SOBRANTE #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40646731 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.00085333 | 762.1324
121563290 | B | LC | ETL.6370.INSL.NCER | 44878270 | CONCORD | DIABLO | 2021-06-18 | 2021-08-05 | ETL.6370 | CHRISTIE-WILLOW PASS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44878253 | 2019-09-22 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | 2019-09-22 | Polymer | Dead End |  |  |  |  | 0.11101
121563290 | B | LC | ETL.6370.INSL.NCER | 44878270 | CONCORD | DIABLO | 2021-06-18 | 2021-08-05 | ETL.6370 | CHRISTIE-WILLOW PASS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44878253 | 2019-09-22 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | 2019-09-22 | Polymer | Dead End |  |  |  |  | 0.11101
121563290 | B | LC | ETL.6370.INSL.NCER | 44878270 | CONCORD | DIABLO | 2021-06-18 | 2021-08-05 | ETL.6370 | CHRISTIE-WILLOW PASS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44878253 | 2019-09-22 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | 2019-09-22 | Polymer | Dead End |  |  |  |  | 0.11101
121568052 | E | LC | ETL.6981.POLE.WOOD | 40860827 | LAKEVLLE | SONOMA | 2021-06-14 |  | ETL.6981 | SALMON CREEK TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40860827 | 1988-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Suspension |  |  |  |  | 0.0022185 | 1012.2208 | 2.2456
121572348 | E | LC | ETL.1403.POLE.NWOD | 44855787 | VICTOR | YOSEMITE | 2021-06-15 |  | ETL.1403 | SANDBAR TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44855787 | 2019-11-21 | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2019-11-21 | Glass | Double Dead End |  |  |  |  | 8.2482e-05 | 1329.0924 | 0.10963
121584846 | E | LC | ETL.3740.INSL.CERA | 40622386 | CONCORD | EAST BAY | 2021-06-22 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40581836 | 1958-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2021-03-16 | Glass | Dead End |  |  |  |  | 0.04122 | 126.6897 | 5.2222
121584846 | E | LC | ETL.3740.INSL.CERA | 40622386 | CONCORD | EAST BAY | 2021-06-22 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40581836 | 1958-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.04122 | 126.6897 | 5.2222
121590880 | B | LC | ETL.7270.INSL.NCER | 44649426 | TABLEMTN |  | 2021-06-23 | 2021-07-22 | ETL.7270 | KESWICK-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44649275 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.00066879 | 142.5468
121596497 | F | LC | ETL.6650.POLE.WDPS | 44386947 | TABLEMTN | NORTH VALLEY | 2021-06-23 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44386944 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0012209 | 0.065157 | 7.9549e-05
121608016 | B | LC | ETL.7550.POLE.WOOD | 40666590 | LAKEVLLE | HUMBOLDT | 2021-06-17 | 2021-07-28 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40666590 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00030804 | 4117.8877
121637538 | E | LC | ETL.4316.INSL.NCER | 42567098 | TABLEMTN |  | 2021-06-22 |  | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42567096 | 2011-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | Unknown |  |  |  |  | 0.012867 | 238.4023 | 3.0676
121658239 | E | LC | ETL.6330.POLE.WOOD | 40599735 | TABLEMTN | NORTH VALLEY | 2021-06-26 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40599735 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 0.00392 | 1091.8842 | 4.2802
121658479 | F | LC | ETL.6750.POLE.STPS | 44562150 | TABLEMTN | NORTH VALLEY | 2021-07-02 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44561585 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 6.7918e-07 | 0.066431
121705980 | B | LC | ETL.6020.TOWR | 40677654 | TABLEMTN | NORTH VALLEY | 2021-07-09 | 2021-07-21 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40677654 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 5.3658e-12 | 3534.1289
121716515 | E | LC | ETL.4050.POLE.WDPS | 44558388 | LAKEVLLE |  | 2021-07-06 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44557895 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00012225 | 2187.8147 | 0.26747
121716686 | E | LC | ETL.1680.POLE.WOOD | 40741737 | LAKEVLLE | SONOMA | 2021-07-12 | 2021-09-10 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40741737 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | Dead End |  |  |  |  | 0.001782 | 2708.3875
121716686 | E | LC | ETL.1680.POLE.WOOD | 40741737 | LAKEVLLE | SONOMA | 2021-07-12 | 2021-09-10 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40741737 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | Dead End |  |  |  |  | 0.001782 | 2708.3875
121717516 | F | LC | ETL.6500.POLE.WOOD | 40866232 | SACTO | NORTH VALLEY | 2021-07-08 |  | ETL.6500 | COLGATE-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40866232 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | Pin |  |  |  |  | 0.033563 | 857.2685 | 28.7722
121732372 | E | LC | ETL.5400.TOWR | 40657330 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.5400 | PIT #3-PIT #1 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40657330 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2017-11-01 | Ceramic | Suspension |  |  |  |  | 0.08683 | 4935.4473 | 428.5442
121742485 | E | LC | ETL.1820.POLE.STPS | 44395177 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395176 | 2017-09-15 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.063019 | 94.9585 | 5.9842
121742485 | E | LC | ETL.1820.POLE.STPS | 44395177 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395176 | 2017-09-15 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.063019 | 94.9585 | 5.9842
121748476 | F | LC | ETL.6240.POLE.WOOD | 40695106 | MOSSLNDG | CENTRAL COAST | 2021-07-16 |  | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40695106 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.45578 | 31.7081
121748565 | F | LC | ETL.5140.POLE.STPS | 45146346 | SACTO | SIERRA | 2021-07-13 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45146222 | 2020-10-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP
121748661 | F | LC | ETL.1820.POLE.WOOD | 45089722 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45089722 | 2020-03-12 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2020-03-12 | Glass | Dead End |  |  |  |  | 0.025163 | 2753.0989
121755514 | F | LC | ETL.2540.POLE.WOOD | 45109412 | METCALF | SAN JOSE | 2021-07-19 |  | ETL.2540 | METCALF-GREEN VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45109412 | 2020-04-22 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2020-04-22 | Glass | Suspension | [5 empty] | 47.5295
121767690 | F | LC | ETL.6760.POLE.WOOD | 40598599 | SACTO | SIERRA | 2021-07-19 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40598599 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.017558 | 31.7022
121785063 | E | LC | ETL.6470.INSL.CERA | 40731114 | SACTO | SACRAMENTO | 2021-07-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40693271 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.17399 | 269.0426 | 46.8097
121790047 | E | LC | ETL.6040.INSL | 40774590 | MOSSLNDG | YOSEMITE | 2021-07-24 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40746828 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 4.2414e-05 | 807.9712 | 0.034269
121813064 | B | LC | ETL.6280.POLE.NWOD | 40861857 | TABLEMTN | NORTH VALLEY | 2021-07-29 | 2021-09-21 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 4.4028e-05 | 632.7172
121816140 | E | LC | ETL.6220.POLE.WOOD | 40862857 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40862857 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.46828
121822282 | E | LC | ETL.2730.INSL | 40878732 | CONCORD | DIABLO | 2021-07-28 |  | ETL.2730 | MORAGA-OAKLAND #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857632 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.00026973 | 1.796 | 0.00048443
121822282 | E | LC | ETL.2730.INSL | 40878732 | CONCORD | DIABLO | 2021-07-28 |  | ETL.2730 | MORAGA-OAKLAND #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857632 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-01 | Glass | Suspension |  |  |  |  | 0.00026973 | 1.796 | 0.00048443
121823222 | E | LC | ETL.7631.INSL.NCER | 45108097 | LAKEVLLE | SONOMA | 2021-07-30 | 2021-08-09 | ETL.7631 | WOHLER TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 45107531 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post | [5 empty] | 1094.5327
121854886 | E | LC | ETL.4316.TOWR | 40599191 | TABLEMTN | NORTH VALLEY | 2021-08-06 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40599191 | 1921-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1986-01-01 | Porcelain | Suspension |  |  |  |  | 0.00049332 | 2721.2283 | 1.3424
122065238 | E | LC | ETL.4780.INSL | 40620236 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40594211 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.001387 | 665.4853 | 0.923
122104028 | E | LC | ETL.7140.POLE.WOOD | 40742416 | LAKEVLLE | SONOMA | 2021-09-27 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | PEND | [11 empty] | 0.01238 | 31.7201 | 0.39268
122163027 | E | LC | ETL.4392.INSL.NCER | 40629188 | LAKEVLLE | SONOMA | 2021-10-07 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Emergency | Storm Related | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40587750 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 1.9486e-07 | 1140.1291 | 0.00022216
122185501 | F | LC | ETL.6480.POLE.NWOD | 45120517 | SACTO | NORTH VALLEY | 2021-10-08 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45120517 | 2021-06-30 | Light Duty Steel Pole | T-1 - Tri Post | 2021-06-30 | Polymer | Post | [5 empty] | 458.8146
122186581 | E | LC | ETL.1450.INSL.NCER | 45164650 | SACTO | SIERRA | 2021-10-11 |  | ETL.1450 | DRUM-SUMMIT #2 | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45164639 | 2021-09-21 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2021-09-21 | Glass | Suspension
122196781 | E | LC | ETL.6290.POLE.WOOD | 42721921 | TABLEMTN | NORTH VALLEY | 2021-10-02 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 42721921 |  | Single Wood Pole | TCDE - Tap Construction Dead End | 2018-11-06 | Polymer | Post |  |  |  |  | 0.039714 | 2404.1431 | 95.4774
118442092 | A | LC | ETL.6222.POLE.NWOD | 44815583 | EUREKA | HUMBOLDT | 2020-01-17 | 2020-02-07 | ETL.6222 | FORT SEWARD TAP | Vegetation | Overgrown | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44815583 | 2019-05-31 | Light Duty Steel Pole | T-1 - Tri Post | 2020-02-25 | Polymer | Post |  |  |  |  | 4.8163e-08
118576243 | E | LC | ETL.5930.INSL | 40713873 | CONCORD |  | 2020-02-25 | 2021-06-14 | ETL.5930 | PARKWAY-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662572 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-03-03 | Glass | Suspension |  |  |  |  | 4.3933e-07 | 1395.4297
118576243 | E | LC | ETL.5930.INSL | 40713873 | CONCORD |  | 2020-02-25 | 2021-06-14 | ETL.5930 | PARKWAY-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662572 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 4.3933e-07 | 1395.4297
118730734 | A | LC | ETL.6690.POLE.WOOD | 40818994 | SACTO | SACRAMENTO | 2020-03-17 | 2020-07-15 | ETL.6690 | DEER CREEK-DRUM | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118912486 | E | LC | ETL.4590.TOWR | 40910178 | TABLEMTN | NORTH VALLEY | 2020-04-11 | 2021-09-09 | ETL.4590 | CRESTA-RIO OSO | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910178 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-08-28 | Glass | Suspension |  |  |  |  | 6.4375e-11 | 2499.6221
118916791 | F | LC | ETL.6880.POLE.NWOD | 40667682 | LAKEVLLE | SONOMA | 2020-04-14 | 2020-11-10 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 |  |  | DLFL
118927409 | E | LC | ETL.2770.TOWR | 40646045 | CONCORD | DIABLO | 2020-04-16 | 2021-01-19 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40646045 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-08-23 | Glass | Suspension |  |  |  |  | 1.9484e-06 | 0.065159
118927409 | E | LC | ETL.2770.TOWR | 40646045 | CONCORD | DIABLO | 2020-04-16 | 2021-01-19 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40646045 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 1.9484e-06 | 0.065159
118940537 | E | LC | ETL.6330.POLE.WOOD | 40585921 | TABLEMTN | NORTH VALLEY | 2020-04-22 | 2021-10-06 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40585921 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Pin |  |  |  |  | 0.00044132 | 237.5546
118940784 | E | LC | ETL.6220.POLE.WOOD | 40661837 | EUREKA | HUMBOLDT | 2020-04-22 | 2020-06-18 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40661837 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.14168 | 332.2581
118948278 | E | LC | ETL.6220.POLE.WOOD | 40591068 | EUREKA | HUMBOLDT | 2020-04-24 | 2021-10-25 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40591068 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.29274 | 332.2834 | 97.2721
118989231 | B | LC | ETL.1650.INSL.CERA | 43680381 | LAKEVLLE |  | 2020-04-28 | 2020-07-14 | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44298326 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Other |  |  |  |  | 0.00015364
118989231 | B | LC | ETL.1650.INSL.CERA | 43680381 | LAKEVLLE |  | 2020-04-28 | 2020-07-14 | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44298326 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Other |  |  |  |  | 0.00015364
118989231 | B | LC | ETL.1650.INSL.CERA | 43680381 | LAKEVLLE |  | 2020-04-28 | 2020-07-14 | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44298326 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Other |  |  |  |  | 0.00015364
118990684 | E | LC | ETL.1450.POLE.WOOD | 42572859 | SACTO | SACRAMENTO | 2020-05-06 | 2020-11-12 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119017208 | E | LC | ETL.7780.POLE.WOOD | 40820713 | LAKEVLLE | HUMBOLDT | 2020-04-30 | 2021-01-12 | ETL.7780 | PHILO JCT-ELK | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40820713 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Non Ceramic | [5 empty] | 0.00013522 | 411.3464
119030458 | E | LC | ETL.1470.INSL.CERA | 40676859 | LAKEVLLE | HUMBOLDT | 2020-05-12 | 2021-07-14 | ETL.1470 | EAGLE ROCK-CORTINA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119030589 | F | LC | ETL.8410.POLE.WOOD | 40601573 | LAKEVLLE | HUMBOLDT | 2020-05-05 |  | ETL.8410 | ELK-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40601573 | 1960-01-01 | Single Wood Pole | TPSR - Tri Post & Susp Light | 1960-01-01 | Polymer | Suspension |  |  |  |  | 0.10256 | 174.0364
119047693 | E | LC | ETL.5650.TOWR | 40588925 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2021-07-19 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40588925 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 7.6899e-06 | 968.9049
119059348 | E | LC | ETL.3750.TOWR | 40857800 | CONCORD | DIABLO | 2020-05-22 | 2021-03-24 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Insulator | Contaminated | [Ground Wash, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857800 | 1932-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Dead End |  |  |  |  | 3.9536e-05 | 0.065158
119083788 | E | LC | ETL.6980.POLE.WOOD | 40750323 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-06-22 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750323 | 1953-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2010-01-01 | Polymer | Suspension |  |  |  |  | 0.2651 | 47.5118
119095027 | E | LC | ETL.8290.POLE.WOOD | 40615924 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-21 | ETL.8290 | VOLTA-DESCHUTES | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119096920 | F | LC | ETL.1650.POLE.WOOD | 40657192 | LAKEVLLE |  | 2020-05-27 | 2021-03-16 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40657192 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 0.00023871 | 4151.2271
119110486 | F | LC | ETL.1050.POLE.NWOD | 43218943 | FRESNO | FRESNO | 2020-05-26 | 2021-07-08 | ETL.1050 | BALCH-SANGER | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 43218943 |  | Lattice Steel Pole | DDE - Double Dead End |  | Glass | [5 empty] | 0.0061011 | 4149.042
119113356 | E | LC | ETL.1401.POLE.WOOD | 40760580 | VICTOR | YOSEMITE | 2020-05-26 | 2021-04-15 | ETL.1401 | BEARDSLEY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760580 |  | Single Wood Pole | DE - Dead End |  | Porcelain | Dead End |  |  |  |  | 0.0039103 | 2246.7366
119114742 | E | LC | ETL.7380.POLE.NWOD | 40601872 | MOSSLNDG | CENTRAL COAST | 2020-05-29 | 2021-08-23 | ETL.7380 | LAURELES-OTTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40601872 | 2009-01-01 | Light Duty Steel Pole | DV - Double Vertical |  | Ceramic | [5 empty] | 0.087009 | 237.6766
119117049 | E | LC | ETL.6470.POLE.WOOD | 40760705 | SACTO | SIERRA | 2020-06-01 | 2020-07-23 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119117384 | F | LC | ETL.1400.POLE.NWOD | 44384140 | VICTOR | YOSEMITE | 2020-05-27 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44384140 | 2017-08-17 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 4.7361e-05 | 965.199
119119278 | E | LC | ETL.6520.POLE.WOOD | 40580265 | SACTO | SIERRA | 2020-06-03 | 2021-06-09 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40580265 |  | Single Wood Pole | T-1 - Tri Post | 2019-06-29 | Polymer | Post |  |  |  |  | 0.0038209 | 4905.0928
119131404 | E | LC | ETL.3750.INSL.CERA | 42582067 | CONCORD | EAST BAY | 2020-06-05 | 2021-03-31 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119167340 | F | LC | ETL.6280.POLE.NWOD | 44414597 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | PEND | 44414597 | 2014-08-27 | Light Duty Steel Pole | T-1 - Tri Post | 2014-08-27 | Polymer | Post |  |  |  |  | 1.1729e-05 | 5950.0312
119175059 | F | LC | ETL.6890.POLE.NWOD | 44713011 | LAKEVLLE | SONOMA | 2020-06-15 | 2020-11-10 | ETL.6890 | FULTON-HOPLAND | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44713011 | 2019-02-16 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-02-16 | Ceramic | Suspension |  |  |  |  | 2.0237e-07 | 1631.0891
119184328 | E | LC | ETL.6310.POLE.WOOD | 40816324 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-08-26 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816324 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 2.6822e-05 | 6462.6191
119194212 | B | LC | ETL.6470.INSL.NCER | 40723264 | SACTO | SACRAMENTO | 2020-06-19 | 2020-07-06 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40679456 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.28593 | 95.0148
119196401 | E | LC | ETL.9340.POLE.NWOD | 44844653 | FRESNO | FRESNO | 2020-06-22 | 2020-08-06 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 44844653 | 2019-09-29 | Light Duty Steel Pole | T-1 - Tri Post | 2019-09-29 | Polymer | Post |  |  |  |  | 0.0021836 | 4654.8892
119197831 | F | LC | ETL.6470.POLE.WOOD | 40658308 | SACTO | SIERRA | 2020-06-22 | 2021-07-13 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40658308 |  | Single Wood Pole | T2N | 2021-07-13 | Polymer | Post |  |  |  |  | 0.051935 | 79.2067
119198369 | E | LC | ETL.1710.POLE.WDPS | 44696024 | MOSSLNDG | CENTRAL COAST | 2020-06-22 | 2021-04-19 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | DLFL | 42567456 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00018818 | 23.8246
119200775 | F | LC | ETL.6470.POLE.WOOD | 40598563 | SACTO | SIERRA | 2020-06-23 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40598563 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.21419 | 110.8481
119202529 | B | LC | ETL.4220.POLE.STPS | 44762694 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-07-15 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue] |  | Tier 2 | Within Both | DLFL | 44762533 | 2019-05-01 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.2164e-05 | 174.0849
119222770 | E | LC | ETL.8290.POLE.WOOD | 40877081 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2020-12-01 | ETL.8290 | VOLTA-DESCHUTES | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40877081 |  | Single Wood Pole | T-1 - Tri Post | 2019-06-08 | Polymer | Post |  |  |  |  | 0.0022405 | 4102.7412
119233503 | E | LC | ETL.6060.TOWR | 40820727 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2020-11-10 | ETL.6060 | ROUND MTN-TABLE MTN #1 | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40820727 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.2846e-05 | 174.1355
119290855 | F | LC | ETL.7270.POLE.NWOD | 44649279 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44649279 | 2018-08-17 | Light Duty Steel Pole | T2N | 2018-08-17 | Polymer | Post |  |  |  |  | 0.00054417 | 142.4582
119295341 | E | LC | ETL.8170.POLE.WDPS | 44565322 | EUREKA | HUMBOLDT | 2020-07-01 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564177 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.028619 | 553.6737 | 15.8455
119304964 | F | LC | ETL.7030.POLE.WOOD | 40701303 | TABLEMTN | NORTH VALLEY | 2020-07-02 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40701303 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0043392
119308620 | E | LC | ETL.1400.POLE.WDPS | 44770783 | VICTOR | STOCKTON | 2020-07-01 | 2021-05-17 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40803711 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0078569 | 31.7207
119309017 | E | LC | ETL.7780.POLE.WOOD | 40762789 | LAKEVLLE | SONOMA | 2020-07-03 | 2021-04-15 | ETL.7780 | PHILO JCT-ELK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119317602 | F | LC | ETL.7270.POLE.WOOD | 42621534 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 42621534 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0041585 | 838.6274
119326545 | E | LC | ETL.1710.TOWR | 40816121 | MOSSLNDG | CENTRAL COAST | 2020-07-07 | 2020-12-16 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40816121 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-04-23 | Glass | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147
119326545 | E | LC | ETL.1710.TOWR | 40816121 | MOSSLNDG | CENTRAL COAST | 2020-07-07 | 2020-12-16 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40816121 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147
119326584 | E | LC | ETL.6300.POLE.WOOD | 40810067 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-10-04 | ETL.6300 | CARIBOU-WESTWOOD | Vegetation | Overgrown | [Trim] | Tier2 | Tier 2 | Within Both | DLFL | 40810067 |  | Single Wood Pole | TH - TriAngle Post 70 | 2014-11-07 | Non Ceramic | Post |  |  |  |  | 1.2874e-05 | 36.5692
119329512 | E | LC | ETL.8170.POLE.WDPS | 44565314 | EUREKA | HUMBOLDT | 2020-07-07 | 2021-09-01 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564293 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.015544 | 0.065152
119329901 | F | LC | ETL.6300.POLE.WOOD | 44190973 | TABLEMTN | NORTH VALLEY | 2020-07-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44190973 |  | Single Wood Pole | TH - TriAngle Post 70 | [7 empty] | 1.3022e-05 | 38.0243
119336228 | E | LC | ETL.7980.POLE.WOOD | 40817050 | SACTO | SIERRA | 2020-07-07 | 2021-01-15 | ETL.7980 | SMARTVILLE-MARYSVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
119355152 | E | LC | ETL.1450.POLE.WDPS | 44561220 | SACTO | SACRAMENTO | 2020-07-08 | 2021-04-27 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44559162 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00045731 | 79.1687
119357385 | E | LC | ETL.7030.POLE.WOOD | 40827577 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-05-14 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827577 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.046195 | 63.381
119359691 | F | LC | ETL.7030.POLE.WOOD | 40616865 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2020-08-07 | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | DLFL
119359996 | F | LC | ETL.2500.TOWR | 40815156 | METCALF | SAN JOSE | 2020-07-02 |  | ETL.2500 | METCALF-EL PATIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40815156 | 1957-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2003-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0056657 | 1519.5542 | 8.6094
119364309 | E | LC | ETL.7030.POLE.WOOD | 40825581 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-06-14 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825581 |  | Single Wood Pole | T2N | 2021-06-01 | Polymer | Post |  |  |  |  | 0.0051885 | 0.06515
119371607 | E | LC | ETL.8170.POLE.WDPS | 44420632 | EUREKA | HUMBOLDT | 2020-07-14 | 2021-06-14 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420630 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0042142 | 177.2654
119373667 | F | LC | ETL.7030.POLE.WOOD | 40667959 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40667959 |  | Single Wood Pole | T2N | 2015-02-10 | Polymer | Post |  |  |  |  | 0.0065138 | 0.06515
119382132 | E | LC | ETL.6220.POLE.WOOD | 40826263 | EUREKA | HUMBOLDT | 2020-07-15 | 2021-11-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40826263 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.080547
119473255 | E | LC | ETL.3190.TOWR | 40910310 | TABLEMTN | NORTH VALLEY | 2020-07-20 |  | ETL.3190 | CARIBOU-PALERMO | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40910310 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 0.09773 | 2111.5416 | 206.3599
119475560 | F | LC | ETL.8960.POLE.WOOD | 40652905 | FRESNO | FRESNO | 2020-07-20 | 2021-07-19 | ETL.8960 | LOS BANOS-PACHECO | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40652905 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1974-01-01 | Porcelain | Dead End |  |  |  |  | 0.00044346
119475560 | F | LC | ETL.8960.POLE.WOOD | 40652905 | FRESNO | FRESNO | 2020-07-20 | 2021-07-19 | ETL.8960 | LOS BANOS-PACHECO | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40652905 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1974-01-01 | Porcelain | Dead End |  |  |  |  | 0.00044346
119480699 | E | LC | ETL.7780.POLE.WOOD | 40768482 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-04-20 | ETL.7780 | PHILO JCT-ELK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119489205 | E | LC | ETL.6450.POLE.NWOD | 44915222 | TABLEMTN | NORTH VALLEY | 2020-07-22 | 2020-10-29 | ETL.6450 | COLEMAN-SOUTH | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44915222 | 2020-05-19 | Light Duty Steel Pole | T-1 - Tri Post | 2020-05-19 | Polymer | Post |  |  |  |  | 7.1345e-09 | 4848.4707
119498369 | E | LC | ETL.7820.POLE.WOOD | 40577247 | LAKEVLLE | SONOMA | 2020-07-24 | 2021-07-03 | ETL.7820 | POTTER VALLEY-WILLITS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119512994 | E | LC | ETL.9460.POLE.WOOD | 40907554 | VICTOR | STOCKTON | 2020-07-27 | 2021-09-09 | ETL.9460 | VALLEY SPRINGS #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0011978 | 2520.3257
119515885 | F | LC | ETL.6280.POLE.WOOD | 44191316 | TABLEMTN | NORTH VALLEY | 2020-07-23 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44191316 |  | Single Wood Pole | BDE - Buck Dead End | [7 empty] | 1.05e-05 | 3115.8767
119515934 | F | LC | ETL.8060.POLE.WDPS | 44565382 | SACTO | SACRAMENTO | 2020-07-28 | 2021-08-25 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564290 |  | 3-Pole Wood | FSS - Field Switch Structure | [7 empty] | 0.02873 | 1131.3246
119533787 | E | LC | ETL.4050.POLE.WOOD | 43250126 | LAKEVLLE | SONOMA | 2020-07-30 | 2021-04-17 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43250126 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00026654
119533787 | E | LC | ETL.4050.POLE.WOOD | 43250126 | LAKEVLLE | SONOMA | 2020-07-30 | 2021-04-17 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43250126 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00026654
119577136 | F | LC | ETL.8365.POLE.WOOD | 40912648 | EUREKA | HUMBOLDT | 2020-08-07 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40912648 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.059526
119578265 | E | LC | ETL.7490.POLE.WOOD | 40770516 | EUREKA | HUMBOLDT | 2020-08-07 | 2021-01-26 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL | [11 empty] | 0.97858 | 0.065148
119603985 | F | LC | ETL.6222.POLE.WOOD | 40770373 | EUREKA | HUMBOLDT | 2020-08-10 |  | ETL.6222 | FORT SEWARD TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40770373 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0014108
119628291 | E | LC | ETL.6870.POLE.NWOD | 44837823 | SACTO | SIERRA | 2020-08-17 | 2021-04-29 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44837823 | 2019-06-05 | Light Duty Steel Pole | T2N | 2019-06-05 | Polymer | Post |  |  |  |  | 0.0019311 | 0.065152
119637869 | E | LC | ETL.1450.POLE.WDPS | 44561221 | SACTO | SACRAMENTO | 2020-08-18 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44559165 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00039739 | 118.9194 | 0.047257
119665774 | F | LC | ETL.1110.TOWR | 40676710 | EUREKA | HUMBOLDT | 2020-08-20 | 2021-01-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676710 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Unknown |  |  |  |  | 0.0005928 | 221.4934
119667991 | E | LC | ETL.5930.TOWR | 40592029 | CONCORD | DIABLO | 2020-08-25 | 2021-06-21 | ETL.5930 | PARKWAY-MORAGA | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40592029 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-27 | Glass | Dead End |  |  |  |  | 1.731e-06 | 47.5494
119667991 | E | LC | ETL.5930.TOWR | 40592029 | CONCORD | DIABLO | 2020-08-25 | 2021-06-21 | ETL.5930 | PARKWAY-MORAGA | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40592029 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.731e-06 | 47.5494
119704201 | E | LC | ETL.3500.TOWR | 40744662 | VICTOR | STOCKTON | 2020-09-02 | 2021-06-28 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40744662 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 3.9961e-05 | 95.0148
119722477 | E | LC | ETL.1240.POLE.WDPS | 44386117 | TABLEMTN | NORTH VALLEY | 2020-07-31 |  | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44386116 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.165e-05 | 3390.7913 | 0.039503
119742490 | E | LC | ETL.5960.TOWR | 40688638 | FRESNO | FRESNO | 2020-09-10 |  | ETL.5960 | DIABLO-GATES #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40688638 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 8.2355e-05
119754952 | E | LC | ETL.9460.INSL.CERA | 40917200 | VICTOR | STOCKTON | 2020-06-22 | 2021-09-13 | ETL.9460 | VALLEY SPRINGS #2 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40907497 | 1991-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0010028 | 3801.7695
119764487 | E | LC | ETL.7030.INSL.NCER | 44685343 | TABLEMTN | NORTH VALLEY | 2020-09-08 | 2021-06-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119767809 | F | LC | ETL.5933.TOWR | 40753141 | PISMOBCH | LOS PADRES | 2020-08-13 | 2021-02-03 | ETL.5933 | MORRO BAY-TEMPLETON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40753141 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 9.1046e-08 | 4194.9302
119767809 | F | LC | ETL.5933.TOWR | 40753141 | PISMOBCH | LOS PADRES | 2020-08-13 | 2021-02-03 | ETL.5933 | MORRO BAY-TEMPLETON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40753141 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.1046e-08 | 4194.9302
119772897 | F | LC | ETL.6470.POLE.WOOD | 40593285 | SACTO | SIERRA | 2020-09-08 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40593285 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0092617 | 2784.1987
119780954 | B | LC | ETL.1110.POLE.WDPS | 44423352 | EUREKA | HUMBOLDT | 2020-09-12 | 2020-11-05 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423351 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00066907 | 261.0341
119781233 | E | LC | ETL.7030.POLE.WOOD | 40817131 | TABLEMTN | NORTH VALLEY | 2020-09-12 | 2021-09-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817131 |  | Single Wood Pole | T2N | 2018-11-28 | Polymer | Post |  |  |  |  | 0.0040477 | 887.2656
119781274 | E | LC | ETL.1730.POLE.WDPS | 44413416 | MOSSLNDG | CENTRAL COAST | 2020-09-11 | 2020-11-10 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44413415 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.8091e-05 | 47.5096
119785793 | E | LC | ETL.1370.INSL.NCER | 42574079 | PISMOBCH | LOS PADRES | 2020-09-15 | 2021-06-28 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44283612 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 0.02188
119785793 | E | LC | ETL.1370.INSL.NCER | 42574079 | PISMOBCH | LOS PADRES | 2020-09-15 | 2021-06-28 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44283612 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 0.02188
119785793 | E | LC | ETL.1370.INSL.NCER | 42574079 | PISMOBCH | LOS PADRES | 2020-09-15 | 2021-06-28 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44283612 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 0.02188
119800241 | F | LC | ETL.7300.POLE.NWOD | 44809983 | TABLEMTN | NORTH VALLEY | 2020-09-22 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44809983 | 2019-05-23 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2019-05-23 | Polymer | Post |  |  |  |  | 2.1551e-07 | 2520.2751
119809864 | F | LC | ETL.6620.TOWR | 40910985 | TABLEMTN | NORTH VALLEY | 2020-08-13 |  | ETL.6620 | COTTONWOOD #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40910985 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 0.00013107 | 4816.6782
119816623 | F | LC | ETL.8410.POLE.WOOD | 40876120 | LAKEVLLE | HUMBOLDT | 2020-09-09 |  | ETL.8410 | ELK-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40876120 | 1960-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1960-01-01 | Polymer | Suspension |  |  |  |  | 0.27069 | 189.852
119819593 | F | LC | ETL.6280.POLE.WOOD | 40824586 | TABLEMTN | NORTH VALLEY | 2020-09-15 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40824586 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 0.00013001 | 5538.7192
119831589 | A | LC | ETL.1110.POLE.WDPS | 44424483 | TABLEMTN | HUMBOLDT | 2020-09-28 | 2020-10-13 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP
119834605 | F | LC | ETL.7270.POLE.WOOD | 40906105 | TABLEMTN | NORTH VALLEY | 2020-09-29 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906105 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0031997 | 996.9431
119836440 | F | LC | ETL.6490.POLE.WOOD | 40825247 | SACTO | SIERRA | 2020-09-15 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40825247 |  | Single Wood Pole | T-1 - Tri Post | 2019-07-20 | Polymer | Post |  |  |  |  | 0.012953 | 2926.5906
119864718 | E | LC | ETL.8405.POLE.NWOD | 44979005 | SACTO | SIERRA | 2020-10-07 | 2021-04-12 | ETL.8405 | MIDDLE FORK #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44979005 | 2020-09-27 | Light Duty Steel Pole | LB - Line and Buck | 2020-09-27 | Glass | Dead End |  |  |  |  | 0.0068696 | 189.9644
119893531 | E | LC | ETL.7590.POLE.WOOD | 44320359 | MOSSLNDG | DE ANZA | 2020-10-07 | 2021-03-24 | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44320359 | 2018-07-22 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-07-22 | Non Ceramic | Dead End |  |  |  |  | 0.26003 | 47.5295
119893708 | E | LC | ETL.7150.POLE.WOOD | 40663594 | LAKEVLLE | NORTH BAY | 2020-10-06 |  | ETL.7150 | IGNACIO-ALTO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40663594 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.015531 | 0.066431 | 0.0010318
119909398 | F | LC | ETL.8170.POLE.NWOD | 44846600 | EUREKA | HUMBOLDT | 2020-10-07 | 2021-09-07 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44846600 | 2019-05-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-05-11 | Glass | Dead End |  |  |  |  | 0.00071289 | 47.5295
119909398 | F | LC | ETL.8170.POLE.NWOD | 44846600 | EUREKA | HUMBOLDT | 2020-10-07 | 2021-09-07 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44846600 | 2019-05-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-05-11 | Glass | Dead End |  |  |  |  | 0.00071289 | 47.5295
119978700 | F | LC | ETL.8960.POLE.STPS | 44236982 | FRESNO | FRESNO | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44236981 |  | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 8.9733e-06
120012106 | F | LC | ETL.1350.POLE.STPS | 44998015 | TABLEMTN | NORTH VALLEY | 2020-11-11 |  | ETL.1350 | CRAG VIEW-CASCADE | Right of Way | Encroachment | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44997966 | 2020-06-01 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00060713 | 3960.7385
120044885 | F | LC | ETL.7780.POLE.WOOD | 40824299 | LAKEVLLE | HUMBOLDT | 2020-10-07 |  | ETL.7780 | PHILO JCT-ELK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40824299 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.00011954 | 411.3464
120191444 | F | LC | ETL.1450.POLE.WDPS | 44550020 | SACTO | SACRAMENTO | 2020-12-11 | 2021-02-16 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44549456 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 8.6548e-05 | 2056.7583
120423687 | E | LC | ETL.4050.POLE.NWOD | 45099348 | LAKEVLLE | SONOMA | 2021-01-12 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45099348 | 2019-06-05 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-06-05 | Glass | Suspension |  |  |  |  | 6.3773e-09 | 2138.6487 | 1.3639e-05
120527426 | E | LC | ETL.1810.INSL.CERA | 44378027 | EUREKA | HUMBOLDT | 2021-02-11 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44322540 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-10-18 | Ceramic | Suspension |  |  |  |  | 1.5174e-06
120527426 | E | LC | ETL.1810.INSL.CERA | 44378027 | EUREKA | HUMBOLDT | 2021-02-11 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44322540 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-10-18 | Ceramic | Suspension |  |  |  |  | 1.5174e-06
120601444 | E | LC | ETL.6280.POLE.WOOD | 40600609 | TABLEMTN | NORTH VALLEY | 2021-03-04 | 2021-09-24 | ETL.6280 | CARIBOU #2 | Anchor-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40600609 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Ceramic | Pin |  |  |  |  | 9.8091e-05 | 5270.2847
120693169 | E | LC | ETL.3700.INSL.NCER | 44386996 | PISMOBCH | LOS PADRES | 2021-03-25 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44385259 | 2018-04-08 | Light Duty Steel Pole | T1DE - Tri Post Dead End 115 | 2018-04-08 | Polymer | Post |  |  |  |  | 1.5989e-08 | 4781.6733 | 7.6456e-05
120718563 | E | LC | ETL.1350.POLE.STPS | 44994609 | TABLEMTN | NORTH VALLEY | 2021-03-31 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44993924 | 2020-06-16 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 5.1506e-05 | 411.4229
120724726 | E | LC | ETL.5980.TOWR | 40651883 | PISMOBCH | LOS PADRES | 2021-04-01 | 2021-05-10 | ETL.5980 | DIABLO-MIDWAY #3 | Vegetation-Tower | Overgrown | [Cage Clearing, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40651883 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-04-12 | Ceramic | Dead End |  |  |  |  | 2.8292e-11 | 2137.2815
120724765 | E | LC | ETL.7390.POLE.NWOD | 44965313 | LAKEVLLE | SONOMA | 2021-04-01 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44965313 | 2020-08-28 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-08-28 | Glass | Suspension |  |  |  |  | 0.0044222
120727389 | E | LC | ETL.1070.INSL.NCER | 40693227 | VICTOR | STOCKTON | 2021-04-01 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40662358 | 1957-01-01 | Single Wood Pole | WB - Wishbone | 1957-01-01 | Polymer | Suspension |  |  |  |  | 1.8664e-05 | 3617.2195 | 0.067511
120734700 | E | LC | ETL.4040.POLE.STPS | 44647086 | TABLEMTN | NORTH VALLEY | 2021-04-02 | 2021-09-11 | ETL.4040 | TRINITY-COTTONWOOD | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44646910 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00021353 | 541.2549
120740283 | E | LC | ETL.7390.POLE.NWOD | 44837755 | LAKEVLLE | SONOMA | 2021-04-03 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44837755 | 2019-07-30 | Light Duty Steel Pole | T-1 - Tri Post | 2019-07-30 | Polymer | Post |  |  |  |  | 0.080593
120770675 | E | LC | ETL.7140.POLE.WDPS | 45096570 | LAKEVLLE | NORTH BAY | 2021-04-08 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41111803 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.28751 | 680.8114 | 195.7384
120786851 | E | LC | ETL.9250.POLE.WOOD | 40765140 | MIDWAY | KERN | 2021-04-10 | 2021-11-17 | ETL.9250 | TEJON-LEBEC | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40765140 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Non Ceramic | Post |  |  |  |  | 0.051387 | 4848.7817 | 249.1637
120787883 | F | LC | ETL.4750.TOWR | 40865687 | LAKEVLLE | SONOMA | 2021-04-10 |  | ETL.4750 | GEYSERS #12-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40865687 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 0.094426 | 2868.3489 | 270.847
120787883 | F | LC | ETL.4750.TOWR | 40865687 | LAKEVLLE | SONOMA | 2021-04-10 |  | ETL.4750 | GEYSERS #12-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40865687 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2019-12-16 | Glass | Dead End |  |  |  |  | 0.094426 | 2868.3489 | 270.847
120792974 | B | LC | ETL.3830.INSL | 40603083 | VICTOR | STOCKTON | 2021-04-09 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40579573 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.6363e-07 | 6204.2363
120819624 | B | LC | ETL.2720.INSL | 40624130 | CONCORD | DIABLO | 2021-04-14 | 2021-04-27 | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40583040 | 1931-01-01 | LATTICE STEEL TOWER | Unknown |  | Non Ceramic | Suspension |  |  |  |  | 0.0029658 | 0.065156
120840126 | E | LC | ETL.1600.INSL.CERA | 40630962 | LAKEVLLE | SONOMA | 2021-04-09 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591169 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 1.1269e-07 | 174.2787 | 1.964e-05
120849832 | E | LC | ETL.1730.INSL.CERA | 40892093 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40867612 | 1954-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1972-01-01 | Porcelain | Suspension |  |  |  |  | 6.2196e-08 | 0.066432 | 4.1318e-09
120850507 | E | LC | ETL.4100.TOWR | 40611977 | LAKEVLLE | SACRAMENTO | 2021-04-12 |  | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40611977 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-05-28 | Glass | Suspension |  |  |  |  | 7.9261e-07 | 5700.4204 | 0.0045182
120853397 | E | LC | ETL.8365.POLE.NWOD | 40906627 | EUREKA | HUMBOLDT | 2021-04-20 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Vegetation | Overgrown | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40906627 | 2010-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0022984
120858682 | F | LC | ETL.5400.POLE.NWOD | 44445547 | TABLEMTN | NORTH VALLEY | 2021-04-21 |  | ETL.5400 | PIT #3-PIT #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44445547 | 2017-10-03 | Tubular Steel Pole | DV-DE - Double Vertical Dead End | 2017-10-03 | Non Ceramic | Dead End |  |  |  |  | 0.00026099 | 4706.947
120863233 | F | LC | ETL.3720.TOWR | 40746161 | CONCORD | DIABLO | 2021-04-21 |  | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40746161 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-09-26 | Polymer | Suspension |  |  |  |  | 5.2399e-05 | 474.6866 | 0.024873
120863233 | F | LC | ETL.3720.TOWR | 40746161 | CONCORD | DIABLO | 2021-04-21 |  | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40746161 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-11-19 | Polymer | Suspension |  |  |  |  | 5.2399e-05 | 474.6866 | 0.024873
120872961 | E | LC | ETL.3820.TOWR | 40587253 | VICTOR | STOCKTON | 2021-04-23 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587253 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 9.0525e-06 | 5823.2505 | 0.052715
120879853 | E | LC | ETL.3830.TOWR | 40744432 | VICTOR | STOCKTON | 2021-04-24 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40744432 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 0.00034817 | 3195.5342 | 1.1126
120880350 | E | LC | ETL.5463.TOWR | 40746307 | CONCORD | DIABLO | 2021-04-24 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40746307 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 9.6682e-07 | 3898.1736 | 0.0037688
120888582 | E | LC | ETL.2740.TOWR | 40745871 | CONCORD | DIABLO | 2021-04-27 |  | ETL.2740 | MORAGA-OAKLAND #3 | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40745871 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-01-29 | Polymer | Suspension |  |  |  |  | 9.9567e-06 | 1362.2408 | 0.013563
120888582 | E | LC | ETL.2740.TOWR | 40745871 | CONCORD | DIABLO | 2021-04-27 |  | ETL.2740 | MORAGA-OAKLAND #3 | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40745871 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-07-24 | Ceramic | Suspension |  |  |  |  | 9.9567e-06 | 1362.2408 | 0.013563
120894135 | E | LC | ETL.1250.INSL.NCER | 40615851 | FRESNO | FRESNO | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40590407 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 7.9337e-05 | 5619.8403 | 0.44586
120894791 | E | LC | ETL.3960.TOWR | 40643127 | PISMOBCH | LOS PADRES | 2021-04-28 | 2021-06-02 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40643127 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-05-22 | Glass | Suspension |  |  |  |  | 2.6448e-08 | 6268.3306
120894900 | E | LC | ETL.5340.INSL | 40835807 | MOSSLNDG | CENTRAL COAST | 2021-04-13 |  | ETL.5340 | MOSS LANDING-LAS AGUILAS SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810761 | 1949-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1949-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.197e-06 | 47.5223 | 0.00010441
120911414 | E | LC | ETL.5930.TOWR | 40863055 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40863055 | 1946-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-04-28 | Glass | Suspension |  |  |  |  | 4.5296e-06 | 175.917 | 0.00079683
120911414 | E | LC | ETL.5930.TOWR | 40863055 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40863055 | 1946-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 4.5296e-06 | 175.917 | 0.00079683
120914640 | E | LC | ETL.6470.POLE.WOOD | 40679443 | SACTO | SACRAMENTO | 2021-05-01 | 2021-08-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40679443 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.015338 | 474.7878
120930816 | B | LC | ETL.4550.TOWR | 40816835 | TABLEMTN | NORTH VALLEY | 2021-05-04 | 2021-07-07 | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816835 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 3.929e-07 | 5006.2686
120931381 | B | LC | ETL.7550.POLE.NWOD | 44968851 | LAKEVLLE | SONOMA | 2021-05-04 | 2021-06-01 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44968851 | 2020-09-10 | Light Duty Steel Pole | T-1 - Tri Post | 2020-09-10 | Polymer | Post |  |  |  |  | 6.5735e-11 | 79.143
120935253 | F | LC | ETL.3830.POLE.NWOD | 45080510 | VICTOR | STOCKTON | 2021-05-05 | 2021-08-10 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 45080510 | 2015-11-02 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 2.9193e-07 | 5476.1846
121130236 | E | LC | ETL.7550.POLE.WOOD | 40614289 | LAKEVLLE | SONOMA | 2021-05-08 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40614289 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 9.176e-05 | 850.9427 | 0.078082
121130239 | B | LC | ETL.7550.POLE.WOOD | 40750973 | LAKEVLLE | SONOMA | 2021-05-08 | 2021-06-01 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750973 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0001416 | 602.6383
121189196 | F | LC | ETL.8250.POLE.WOOD | 40908853 | VICTOR | STOCKTON | 2021-05-11 | 2021-09-23 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908853 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.018395 | 754.7912
121320135 | E | LC | ETL.1820.POLE.WDPS | 44562714 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Hardware-Wood | Missing | [Install] | Tier2 |  |  | PEND
121322377 | E | LC | ETL.7490.POLE.WDPS | 44743796 | EUREKA | HUMBOLDT | 2021-05-12 | 2021-06-08 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL | [12 empty] | 0.065148
121328802 | E | LC | ETL.7560.POLE.WOOD | 40759714 | SACTO | SIERRA | 2021-04-23 |  | ETL.7560 | WEIMAR #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40759714 |  | Single Wood Pole | TPSRD - Tramp Double Dead End | 2014-05-07 | Porcelain | Post |  |  |  |  | 0.083197 | 2056.6992 | 171.1112
121336988 | E | LC | ETL.2395.POLE.WOOD | 45019101 | TABLEMTN | NORTH VALLEY | 2021-05-14 | 2021-08-23 | ETL.2395 | GRIZZLY TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 45019101 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0052286 | 79.1846
121337017 | E | LC | ETL.2395.POLE.WOOD | 44550104 | TABLEMTN | NORTH VALLEY | 2021-05-14 |  | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44550104 |  | Single Wood Pole | DV - Double Vertical |  | Ceramic | Dead End |  |  |  |  | 0.091441 | 189.8861 | 17.3634
121344731 | F | LC | ETL.2790.TOWR | 40804667 | CONCORD | DIABLO | 2021-04-23 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40804667 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.3891e-07 | 15.8932 | 1.0154e-05
121363924 | F | LC | ETL.5980.TOWR | 40587698 | PISMOBCH | LOS PADRES | 2021-04-30 |  | ETL.5980 | DIABLO-MIDWAY #3 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40587698 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.4537e-10 | 2856.3857
121365258 | E | LC | ETL.6870.INSL | 40854208 | SACTO | SACRAMENTO | 2021-05-19 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40824947 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.12533 | 332.3381 | 41.6511
121373520 | F | LC | ETL.9340.POLE.NWOD | 43680873 | FRESNO | YOSEMITE | 2021-05-03 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 43680873 | 2015-06-15 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2016-06-15 | Polymer | Post |  |  |  |  | 0.0027999 | 5664.3166
121373658 | E | LC | ETL.4570.INSL | 40795902 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4570 | COTTONWOOD-LOGAN CREEK | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40765238 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.2232e-07 | 3559.869 | 0.00043546
121381814 | F | LC | ETL.6470.POLE.WOOD | 40665786 | SACTO | SIERRA | 2021-05-11 | 2021-06-30 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
121383304 | F | LC | ETL.6500.POLE.WOOD | 40866823 | SACTO | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40866823 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.001994 | 2250.7314
121385602 | E | LC | ETL.4590.INSL.NCER | 45174424 | TABLEMTN | NORTH VALLEY | 2021-05-12 |  | ETL.4590 | CRESTA-RIO OSO | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40910142 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-14 | Glass | Suspension |  |  |  |  | 0.00028729 | 254.0199 | 0.072976
121392012 | E | LC | ETL.3770.TOWR | 40662371 | CONCORD | DIABLO | 2021-05-17 |  | ETL.3770 | SOBRANTE-R #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | PEND | 40662371 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-08-29 | Glass | Suspension |  |  |  |  | 9.6193e-05 | 0.065147 | 6.2667e-06
121404484 | F | LC | ETL.7550.POLE.WOOD | 40585219 | LAKEVLLE | HUMBOLDT | 2021-05-21 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40585219 |  | Single Wood Pole | SV-DE-90 - Single Vertical Dead End 90 |  | Polymer | [5 empty] | 1.2985e-06 | 2930.8291
121404748 | F | LC | ETL.8290.POLE.NWOD | 44949907 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44949907 | 2019-06-10 | Light Duty Steel Pole | T2N | 2019-06-10 | Polymer | Post |  |  |  |  | 8.6568e-07 | 3010.644
121405085 | E | LC | ETL.7290.INSL.NCER | 44175367 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.7290 | KILARC-CEDAR CREEK | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44175302 | 2014-10-15 | Single Wood Pole | TPA - Tri Pin Arm |  | Polymer | Post |  |  |  |  | 0.081238 | 158.265 | 12.8572
121408568 | F | LC | ETL.3750.TOWR | 40581839 | CONCORD | DIABLO | 2021-05-21 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40581839 | 1922-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 3.1983e-08 | 31.8352
121420586 | E | LC | ETL.1420.TOWR | 40756300 | SACTO | SIERRA | 2021-05-26 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40756300 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-12 | Glass | Suspension |  |  |  |  | 7.7421e-06 | 142.4516 | 0.0011029
121421109 | F | LC | ETL.7040.POLE.WOOD | 40598804 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40598804 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.12116 | 1428.0112
121428642 | E | LC | ETL.8365.POLE.WOOD | 40587720 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587720 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0030116 | 587.0327 | 1.7679
121430077 | B | LC | ETL.7550.INSL.NCER | 40800797 | LAKEVLLE |  | 2021-05-28 | 2021-06-14 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40769233 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0061693 | 3608.3047
121430934 | F | LC | ETL.1402.POLE.STPS | 44915907 | VICTOR | YOSEMITE | 2021-05-25 | 2021-07-12 | ETL.1402 | SPRING GAP TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44915845 | 2019-11-18 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.2541e-05 | 174.1264
121466213 | E | LC | ETL.1350.TOWR | 40810512 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810512 | 1944-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064043 | 174.1138 | 0.11151
121466213 | E | LC | ETL.1350.TOWR | 40810512 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810512 | 1944-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-12-15 | Glass | Dead End |  |  |  |  | 0.00064043 | 174.1138 | 0.11151
121468949 | E | LC | ETL.4950.INSL | 41129288 | LAKEVLLE |  | 2021-05-27 |  | ETL.4950 | FULTON-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40592327 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Ceramic | Suspension |  |  |  |  | 4.2814e-07 | 1790.5603 | 0.00076662
121473645 | F | LC | ETL.2395.POLE.WDPS | 44549956 | TABLEMTN |  | 2021-06-04 |  | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44549423 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0056682 | 79.1846
121474553 | F | LC | ETL.6979.POLE.WOOD | 40750318 | LAKEVLLE | SONOMA | 2021-06-03 |  | ETL.6979 | MONTE RIO-FORT ROSS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40750318 | 1984-01-01 | Single Wood Pole | TPSR - Tri Post & Susp Light | 2010-01-01 | Polymer | Other |  |  |  |  | 0.023969 | 364.1447 | 8.7284
121475447 | F | LC | ETL.4392.TOWR | 41129338 | LAKEVLLE | SONOMA | 2021-05-28 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41129338 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 2.4608e-05 | 3818.9065 | 0.093976
121475447 | F | LC | ETL.4392.TOWR | 41129338 | LAKEVLLE | SONOMA | 2021-05-28 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41129338 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 2.4608e-05 | 3818.9065 | 0.093976
121480438 | E | LC | ETL.6470.POLE.WOOD | 40658320 | SACTO | SIERRA | 2021-06-07 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40658320 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.41914 | 174.1689 | 73.0007
121490245 | F | LC | ETL.1440.POLE.WDPS | 45109408 | SACTO | SIERRA | 2021-05-29 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40605259 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.002663 | 3274.9534
121493127 | E | LC | ETL.4440.TOWR | 40595024 | TABLEMTN | NORTH VALLEY | 2021-06-01 |  | ETL.4440 | CARIBOU-TABLE MTN | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40595024 | 1968-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1968-01-01 | Ceramic | Suspension |  |  |  |  | 6.0021e-05 | 6537.3096 | 0.39238
121499934 | E | LC | ETL.5390.TOWR | 40856775 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40856775 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 9.8989e-06 | 47.7038 | 0.00047221
121517164 | E | LC | ETL.5390.TOWR | 40603380 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40603380 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 0.00016138 | 920.8503 | 0.14861
121521704 | E | LC | ETL.1600.INSL.CERA | 40636602 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40604783 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-08-20 | Ceramic | Suspension |  |  |  |  | 0.00011362 | 1205.4454 | 0.13697
121521704 | E | LC | ETL.1600.INSL.CERA | 40636602 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40604783 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 0.00011362 | 1205.4454 | 0.13697
121522300 | F | LC | ETL.5650.TOWR | 40761289 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40761289 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 4.1899e-06 | 271.3708 | 0.001137
121523642 | E | LC | ETL.6760.POLE.WOOD | 40589523 | SACTO | SIERRA | 2021-06-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40589523 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-03-04 | Glass | Dead End |  |  |  |  | 0.10682 | 126.6688 | 13.5308
121535197 | E | LC | ETL.8060.POLE.WDPS | 44565382 | SACTO | SIERRA | 2021-06-09 |  | ETL.8060 | SPAULDING-SUMMIT | Ground Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44564290 |  | 3-Pole Wood | FSS - Field Switch Structure | [7 empty] | 0.02873 | 1131.3246 | 32.5035
121535939 | F | LC | ETL.6470.POLE.WOOD | 40602514 | SACTO | SIERRA | 2021-06-09 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40602514 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.063664 | 1598.1093
121543158 | F | LC | ETL.6500.POLE.NWOD | 45099313 | SACTO | NORTH VALLEY | 2021-06-12 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45099313 | 2020-08-08 | Light Duty Steel Pole | T-1 - Tri Post | 2020-08-08 | Polymer | Post |  |  |  |  | 1.5217e-05 | 2140.1382
121550784 | E | LC | ETL.5650.TOWR | 40765415 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40765415 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 8.6622e-07 | 1634.3816 | 0.0014157
121550846 | E | LC | ETL.5970.TOWR | 40603146 | PISMOBCH | LOS PADRES | 2021-06-16 |  | ETL.5970 | DIABLO-MIDWAY #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40603146 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-09-26 | Glass Silicone Coated | Suspension |  |  |  |  | 3.01e-08 | 2580.0969 | 7.766e-05
121553842 | E | LC | ETL.6050.INSL | 40715165 | MOSSLNDG | CENTRAL COAST | 2021-06-17 |  | ETL.6050 | MOSS LANDING-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40664431 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 5.8997e-05 | 2858.7448 | 0.16866
121557684 | B | LC | ETL.6380.INSL.NCER | 44667867 | LAKEVLLE |  | 2021-06-16 | 2021-07-01 | ETL.6380 | KONOCTI-MIDDLETOWN | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44667812 | 2018-10-31 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-10-31 | Polymer | Dead End |  |  |  |  | 2.2505e-07 | 4893.2662
121588545 | B | LC | ETL.4460.TOWR | 40809796 | MOSSLNDG | CENTRAL COAST | 2021-06-23 | 2021-06-24 | ETL.4460 | COBURN-LAS AGUILAS SW STA | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809796 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 1.6468e-07 | 460.7576
121594444 | E | LC | ETL.4950.TOWR | 40818219 | LAKEVLLE | SONOMA | 2021-06-24 |  | ETL.4950 | FULTON-LAKEVILLE | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40818219 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-04-01 | Glass | Suspension |  |  |  |  | 0.00045217 | 351.5916 | 0.15898
121594444 | E | LC | ETL.4950.TOWR | 40818219 | LAKEVLLE | SONOMA | 2021-06-24 |  | ETL.4950 | FULTON-LAKEVILLE | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40818219 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00045217 | 351.5916 | 0.15898
121600503 | E | LC | ETL.1440.POLE.WDPS | 45096564 | SACTO | SACRAMENTO | 2021-06-25 |  | ETL.1440 | DRUM-SUMMIT #1 | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40913112 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0011089 | 0.065152 | 7.2248e-05
121600652 | E | LC | ETL.7390.POLE.NWOD | 42813768 | LAKEVLLE | SONOMA | 2021-06-25 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42813768 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.00012497 | 1093.7991 | 0.1367
121609832 | E | LC | ETL.4440.TOWR | 40758287 | TABLEMTN | NORTH VALLEY | 2021-06-23 |  | ETL.4440 | CARIBOU-TABLE MTN | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758287 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 7.8333e-05 | 1170.4968 | 0.091689
121609852 | E | LC | ETL.4316.POLE.WOOD | 40591575 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40591575 | 1999-01-01 | Single Wood Pole | 3WV-T - Three Way Vertical Tap | 2021-07-26 | Glass | Double Dead End |  |  |  |  | 0.039898 | 2531.262 | 100.9925
121620662 | E | LC | ETL.7130.POLE.WDPS | 44837692 | EUREKA | HUMBOLDT | 2021-06-27 | 2021-07-12 | ETL.7130 | HUMBOLDT-MAPLE CREEK | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40601317 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.46935 | 94.9585
121620678 | E | LC | ETL.7130.POLE.WDPS | 44837691 | EUREKA | HUMBOLDT | 2021-06-27 |  | ETL.7130 | HUMBOLDT-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40601317 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.46935 | 94.9585 | 44.5688
121622637 | F | LC | ETL.6760.POLE.WOOD | 44964260 | SACTO | SIERRA | 2021-06-22 | 2021-09-30 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44964260 | 2019-08-14 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-08-14 | Glass | Dead End |  |  |  |  | 0.0061744 | 901.7202
121622648 | B | LC | ETL.6070.TOWR | 40869100 | TABLEMTN | NORTH VALLEY | 2021-06-27 | 2021-07-19 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40869100 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-17 | Glass Silicone Coated | Suspension |  |  |  |  | 2.8124e-06 | 2613.4871
121624280 | E | LC | ETL.8250.POLE.WOOD | 40904145 | VICTOR | STOCKTON | 2021-06-28 |  | ETL.8250 | CLAY-MARTEL | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40904145 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.021549 | 808.7196 | 17.4274
121632963 | B | LC | ETL.1810.INSL.NCER | 44836648 | EUREKA | HUMBOLDT | 2021-06-28 | 2021-08-17 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44836588 | 2019-08-31 | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2019-08-31 | Glass | Double Dead End - Post |  |  |  |  | 6.674e-09 | 253.1893
121633035 | B | LC | ETL.4392.INSL.CERA | 41129278 | LAKEVLLE | SONOMA | 2021-06-27 | 2021-09-14 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129386 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.005784 | 411.5694
121633035 | B | LC | ETL.4392.INSL.CERA | 41129278 | LAKEVLLE | SONOMA | 2021-06-27 | 2021-09-14 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129386 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.005784 | 411.5694
121647135 | E | LC | ETL.6890.POLE.WOOD | 40808479 | LAKEVLLE | HUMBOLDT | 2021-06-28 |  | ETL.6890 | FULTON-HOPLAND | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40808479 | 1932-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Other |  |  |  |  | 0.00076724 | 3896.4792 | 2.9895
121648426 | E | LC | ETL.3500.INSL | 40828045 | VICTOR | STOCKTON | 2021-06-17 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40804238 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0042916 | 110.8228 | 0.47561
121648531 | E | LC | ETL.6240.POLE.WOOD | 40593140 | MOSSLNDG | CENTRAL COAST | 2021-07-01 | 2021-08-09 | ETL.6240 | BURNS-LONE STAR #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593140 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.55457 | 110.8153
121655674 | F | LC | ETL.7820.POLE.NWOD | 45037610 | LAKEVLLE | SONOMA | 2021-07-02 |  | ETL.7820 | POTTER VALLEY-WILLITS | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45037610 | 2021-02-04 | Light Duty Steel Pole | T-1 - Tri Post | 2021-02-04 | Polymer | Post |  |  |  |  | 8.5441e-07 | 3785.6865
121683896 | A | LC | ETL.1220.INSL | 40788250 | MOSSLNDG | CENTRAL COAST | 2021-07-08 | 2021-07-13 | ETL.1220 | CAMP EVERS-PAUL SWEET | Emergency-Steel | Other | [Replace, Completed, Completed] | Tier3 |  |  | COMP
121687627 | F | LC | ETL.5934.TOWR | 40582305 | PISMOBCH | FRESNO | 2021-07-06 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40582305 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 1.5575e-05 | 4046.0034 | 0.063015
121687627 | F | LC | ETL.5934.TOWR | 40582305 | PISMOBCH | FRESNO | 2021-07-06 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40582305 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-08-09 | Ceramic | Suspension |  |  |  |  | 1.5575e-05 | 4046.0034 | 0.063015
121689309 | F | LC | ETL.7640.POLE.WDPS | 44565379 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564270 |  | 2-Pole Wood | TH - TriAngle Post 70 | [7 empty] | 7.5087e-06 | 3880.9729
121705167 | E | LC | ETL.6760.POLE.WOOD | 44261255 | SACTO | SIERRA | 2021-07-06 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44261255 | 2016-05-04 | Single Wood Pole | FDDE - Flat Dead End Construction | 2016-05-04 | Porcelain | Pin |  |  |  |  | 0.11315 | 2233.9502 | 252.7812
121706524 | E | LC | ETL.6470.POLE.WOOD | 40693267 | SACTO | SIERRA | 2021-07-07 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40693267 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.24726 | 110.8355 | 27.4047
121730341 | B | LC | ETL.4880.INSL | 40620436 | FRESNO | FRESNO | 2021-07-13 | 2021-10-04 | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40594350 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 3.5471e-06
121731059 | E | LC | ETL.6280.POLE.NWOD | 40868117 | TABLEMTN | NORTH VALLEY | 2021-07-14 |  | ETL.6280 | CARIBOU #2 | Anchor-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40868117 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Non Ceramic | Pin |  |  |  |  | 0.00032849 | 4683.9302 | 1.5386
121731565 | B | LC | ETL.1820.INSL.NCER | 44395577 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44395130 | 2020-03-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-03-09 | Glass | Suspension |  |  |  |  | 0.0071523
121731565 | B | LC | ETL.1820.INSL.NCER | 44395577 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44395130 | 2020-03-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-03-09 | Glass | Suspension |  |  |  |  | 0.0071523
121733741 | E | LC | ETL.7640.POLE.WDPS | 44565507 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564292 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0035575 | 506.6299 | 1.8023
121744174 | F | LC | ETL.5420.POLE.STPS | 44400003 | TABLEMTN |  | 2021-07-14 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44400001 | 2017-11-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.3435e-05 | 63.351
121747355 | F | LC | ETL.1710.POLE.STPS | 45102161 | MOSSLNDG | CENTRAL COAST | 2021-07-15 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45102109 | 2021-06-11 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [8 empty] | 47.5096
121748550 | F | LC | ETL.1820.POLE.WOOD | 44395487 | EUREKA | HUMBOLDT | 2021-07-16 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395487 | 2020-03-12 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2020-03-12 | Glass | Dead End |  |  |  |  | 0.02557 | 2753.0989
121770349 | B | LC | ETL.2390.INSL.CERA | 44195296 | VICTOR | STOCKTON | 2021-07-20 | 2021-09-09 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44390965 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 2013-09-19 | Porcelain | Dead End |  |  |  |  | 8.3378e-05
121770349 | B | LC | ETL.2390.INSL.CERA | 44195296 | VICTOR | STOCKTON | 2021-07-20 | 2021-09-09 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44390965 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 2013-09-19 | Porcelain | Dead End |  |  |  |  | 8.3378e-05
121783805 | B | LC | ETL.9240.TOWR | 43249715 | PISMOBCH | LOS PADRES | 2021-07-22 | 2021-10-11 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249715 |  | LATTICE STEEL TOWER | [9 empty] | 2470.1736
121793187 | B | LC | ETL.8365.POLE.NWOD | 40906678 | EUREKA | HUMBOLDT | 2021-07-24 | 2021-08-18 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906678 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.012954
121797204 | F | LC | ETL.4316.POLE.STPS | 45083343 | TABLEMTN | NORTH VALLEY | 2021-07-22 | 2021-08-25 | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 45083299 | 2021-04-23 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.9749e-05 | 1365.8254
121800504 | E | LC | ETL.7100.POLE.WOOD | 40614693 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.7100 | HUMBOLDT BAY-RIO DELL JCT | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40614693 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.07444 | 237.2987 | 17.6644
121806397 | E | LC | ETL.4040.POLE.WDPS | 45099494 | TABLEMTN | NORTH VALLEY | 2021-07-21 |  | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42622417 | 1949-01-01 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.039381 | 1851.2888 | 72.9064
121814678 | F | LC | ETL.7130.POLE.WOOD | 44947427 | EUREKA | HUMBOLDT | 2021-07-28 | 2021-08-17 | ETL.7130 | HUMBOLDT-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | DLFL | 44947427 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.15806
121822987 | F | LC | ETL.7060.POLE.WOOD | 42564715 | METCALF | PENINSULA | 2021-07-30 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 42564715 |  | Single Wood Pole | DV - Double Vertical |  | Ceramic | [5 empty] | 0.0044503 | 1060.2281
121825087 | B | LC | ETL.7970.SWIT | 40744064 | SACTO | SACRAMENTO | 2021-07-31 | 2021-08-03 | ETL.7970 | SMARTVILLE-CAMP FAR WEST | Switch | Out of Adjustment | [Repair, Completed] | Tier2 |  |  | COMP | [8 empty] | TCO | VACUUM INTERRUPTER (3 GAP) | SCADA Only
121829442 | B | LC | ETL.3830.TOWR | 40761542 | VICTOR | STOCKTON | 2021-08-02 | 2021-10-24 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Switch | Out of Adjustment | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761542 | 1962-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Other |  |  |  |  | 7.658e-08 | 1679.8154 | 0.00012864
121837480 | E | LC | ETL.8250.POLE.WOOD | 40691770 | VICTOR | STOCKTON | 2021-08-03 |  | ETL.8250 | CLAY-MARTEL | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40691770 | 1957-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00071708 | 1838.3271 | 1.3182
122017765 | E | LC | ETL.6750.POLE.WOOD | 42611957 | TABLEMTN | NORTH VALLEY | 2021-09-08 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 42611957 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 1.5412e-05 | 79.1724 | 0.0012202
118537866 | E | LC | ETL.8170.POLE.WDPS | 44752436 | EUREKA | HUMBOLDT | 2020-02-14 |  | ETL.8170 | TRINITY-MAPLE CREEK | Anchor-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | PEND | 40861547 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.2659 | 284.7712 | 75.7197
118897631 | F | LC | ETL.4392.TOWR | 41129393 | LAKEVLLE | SONOMA | 2020-04-08 | 2021-06-30 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41129393 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.00023066 | 114.0854
118926078 | E | LC | ETL.4440.TOWR | 40674583 | TABLEMTN | NORTH VALLEY | 2020-04-16 | 2021-04-12 | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40674583 | 1968-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1968-01-01 | Porcelain | Dead End |  |  |  |  | 0.00018762 | 5962.8364
118926586 | E | LC | ETL.6440.POLE.WOOD | 40660622 | TABLEMTN | NORTH VALLEY | 2020-04-16 | 2020-05-28 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118961074 | E | LC | ETL.6220.POLE.WOOD | 40661824 | EUREKA | HUMBOLDT | 2020-04-29 | 2021-04-07 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Idle | [Remove, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40661824 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.043999 | 839.2908
118964768 | E | LC | ETL.7590.POLE.WOOD | 41124289 | MOSSLNDG | CENTRAL COAST | 2020-04-30 | 2020-10-28 | ETL.7590 | MONTA VISTA-BURNS | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41124289 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 0.12505 | 1361.0769
118967657 | E | LC | ETL.7590.POLE.WOOD | 42565750 | MOSSLNDG | CENTRAL COAST | 2020-05-01 | 2020-07-22 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
118972217 | E | LC | ETL.4750.INSL.CERA | 40620228 | LAKEVLLE |  | 2020-05-01 | 2021-08-30 | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118983633 | E | LC | ETL.3450.INSL | 41170017 | SACTO | SACRAMENTO | 2020-05-05 |  | ETL.3450 | RIO OSO-WEST SACRAMENTO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Non-HFTD | Non-HFRA | PEND | 40908368 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 1.8345e-06
118993444 | E | LC | ETL.1350.POLE.WDPS | 44512133 | TABLEMTN |  | 2020-05-06 | 2020-10-21 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119005193 | E | LC | ETL.2700.TOWR | 40645976 | CONCORD | DIABLO | 2020-05-06 | 2021-02-22 | ETL.2700 | MORAGA-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40645976 | 1944-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1944-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00017343 | 1568.8029
119005193 | E | LC | ETL.2700.TOWR | 40645976 | CONCORD | DIABLO | 2020-05-06 | 2021-02-22 | ETL.2700 | MORAGA-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40645976 | 1944-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1944-01-01 | Ceramic | Dead End |  |  |  |  | 0.00017343 | 1568.8029
119026720 | F | LC | ETL.8650.POLE.NWOD | 44420135 | FRESNO | YOSEMITE | 2020-05-08 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44420135 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.010175 | 2977.8208
119030254 | E | LC | ETL.8250.POLE.WOOD | 40812116 | VICTOR | STOCKTON | 2020-03-16 | 2021-03-16 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40812116 | 1957-01-01 | Single Wood Pole | SV-DE-90 - Single Vertical Dead End 90 |  | Porcelain | [5 empty] | 8.8823e-05 | 1665.905
119030323 | E | LC | ETL.3160.INSL.CERA | 44377341 | CONCORD | EAST BAY | 2020-05-12 | 2021-05-18 | ETL.3160 | OLEUM-G #2 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | HFRA Removal | COMP | 40804791 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1931-01-01 | Ceramic | Dead End |  |  |  |  | 9.2939e-06 | 47.5096
119030323 | E | LC | ETL.3160.INSL.CERA | 44377341 | CONCORD | EAST BAY | 2020-05-12 | 2021-05-18 | ETL.3160 | OLEUM-G #2 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | HFRA Removal | COMP | 40804791 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-02-06 | Ceramic | Dead End |  |  |  |  | 9.2939e-06 | 47.5096
119075270 | E | LC | ETL.1240.POLE.WDPS | 44386222 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-07-07 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44386221 |  | 2-Pole Wood | 2PS TRP - 2 Pole SUSP. Transposition | [7 empty] | 1.6734e-05 | 2218.8638
119075454 | B | LC | ETL.2750.INSL.CERA | 40604483 | CONCORD | EAST BAY | 2020-05-26 | 2020-06-16 | ETL.2750 | MORAGA-OAKLAND #4 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40580804 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | Suspension |  |  |  |  | 0.0003026 | 0.065158
119078252 | E | LC | ETL.7510.POLE.WOOD | 40769747 | LAKEVLLE | HUMBOLDT | 2020-05-26 | 2020-07-07 | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119097520 | F | LC | ETL.1402.POLE.STPS | 44161081 | VICTOR | STOCKTON | 2020-05-04 | 2021-09-28 | ETL.1402 | SPRING GAP TAP | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44161079 | 2016-11-15 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.2682e-05 | 1329.0924
119116518 | E | LC | ETL.4223.POLE.WOOD | 42567887 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2020-09-28 | ETL.4223 | KANAKA TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42567887 | 2013-01-01 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 9.2986e-08
119116518 | E | LC | ETL.4223.POLE.WOOD | 42567887 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2020-09-28 | ETL.4223 | KANAKA TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42567887 | 2020-06-27 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 9.2986e-08
119116518 | E | LC | ETL.4223.POLE.WOOD | 42567887 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2020-09-28 | ETL.4223 | KANAKA TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42567887 | 2013-01-01 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 9.2986e-08
119117715 | E | LC | ETL.8290.POLE.WOOD | 40660889 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-26 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660889 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.010728 | 398.6012
119130144 | F | LC | ETL.7270.POLE.WOOD | 40752197 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-07-29 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40752197 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-08-24 | Glass | Double Dead End |  |  |  |  | 0.097273 | 1918.4999
119132174 | F | LC | ETL.6520.POLE.WOOD | 40602850 | SACTO | SIERRA | 2020-06-02 | 2021-06-10 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602850 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.0058328 | 1711.8802
119142241 | F | LC | ETL.7270.POLE.WOOD | 40827877 | TABLEMTN | NORTH VALLEY | 2020-06-04 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40827877 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.030881 | 2552.6013
119146834 | E | LC | ETL.1370.INSL.CERA | 40856114 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-09-14 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119169747 | F | LC | ETL.1422.TOWR | 40825405 | SACTO | SIERRA | 2020-06-12 | 2020-11-12 | ETL.1422 | BRUNSWICK #1 TAP | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40825405 | 1975-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.739e-06 | 427.1649
119178054 | F | LC | ETL.1400.POLE.STPS | 44384144 | VICTOR | YOSEMITE | 2020-06-12 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44384142 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.2217e-05 | 965.199
119180510 | E | LC | ETL.6220.POLE.WDPS | 44402613 | EUREKA | HUMBOLDT | 2020-06-15 | 2021-02-04 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44402612 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.14499
119183512 | E | LC | ETL.6310.POLE.WOOD | 40867946 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2020-11-09 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119187519 | F | LC | ETL.7212.POLE.WOOD | 40599236 | METCALF | PENINSULA | 2020-06-19 | 2021-04-26 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40599236 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.2411 | 760.1513
119197005 | E | LC | ETL.1240.POLE.STPS | 44923938 | TABLEMTN | NORTH VALLEY | 2020-06-22 | 2020-08-04 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44923854 | 2020-03-25 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.4222e-09 | 3831.3433
119199194 | F | LC | ETL.6480.POLE.WOOD | 40576333 | SACTO | SIERRA | 2020-06-22 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40576333 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.070574 | 316.448
119199514 | E | LC | ETL.6470.INSL.NCER | 44686508 | SACTO | SACRAMENTO | 2020-06-23 | 2021-08-05 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664647 |  | Single Wood Pole | T2N | 2018-11-28 | Polymer | Post |  |  |  |  | 0.092534 | 110.8608
119208041 | E | LC | ETL.1450.POLE.WDPS | 44549891 | SACTO | SACRAMENTO | 2020-06-03 | 2020-09-02 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119232884 | E | LC | ETL.1240.POLE.WDPS | 44386218 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2020-07-27 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119233757 | E | LC | ETL.9330.TOWR | 40597310 | FRESNO | FRESNO | 2020-06-29 | 2021-06-29 | ETL.9330 | WISHON-COPPERMINE | Hardware-Tower | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | DLFL | 40597310 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 6.962e-05
119293678 | E | LC | ETL.8480.POLE.WOOD | 40868874 | PISMOBCH | LOS PADRES | 2020-07-01 |  | ETL.8480 | ATASCADERO-CAYUCOS | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40868874 | 1954-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1954-01-01 | Polymer | Suspension |  |  |  |  | 0.00015758 | 964.8711 | 0.15204
119293716 | E | LC | ETL.6880.POLE.WOOD | 40905744 | LAKEVLLE | SONOMA | 2020-07-01 | 2021-10-18 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40905744 |  | Single Wood Pole | T-1 - Tri Post | 2014-07-17 | Polymer | Post |  |  |  |  | 0.00041035 | 4800.3047 | 1.9698
119296274 | E | LC | ETL.6900.POLE.WOOD | 40746031 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | PEND | 40746031 | 1980-01-01 | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 1.6716e-06 | 395.7669 | 0.00066156
119299955 | E | LC | ETL.9100.POLE.WOOD | 44191410 | PISMOBCH | LOS PADRES | 2020-07-01 | 2020-11-23 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL | [11 empty] | 0.00041678 | 1281.5726
119300877 | F | LC | ETL.8060.POLE.WOOD | 40660186 | SACTO | SIERRA | 2020-06-29 | 2021-02-11 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40660186 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.056014 | 221.5552
119301497 | B | LC | ETL.8650.POLE.NWOD | 44859209 | FRESNO | FRESNO | 2020-07-02 | 2020-12-08 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44859209 | 2019-11-18 | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-11-18 | Glass | Suspension |  |  |  |  | 0.0063222 | 6869.2563
119305447 | F | LC | ETL.1440.POLE.STPS | 44338123 | SACTO | SIERRA | 2020-07-01 | 2020-07-27 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44338120 | 2018-09-06 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 1.4929e-06 | 3069.2839
119308044 | E | LC | ETL.1440.POLE.WOOD | 42572734 | SACTO | SIERRA | 2020-07-01 | 2020-08-20 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42572734 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 0.0015643 | 110.9493
119308062 | E | LC | ETL.1073.POLE.WDPS | 44771104 | VICTOR | YOSEMITE | 2020-07-01 | 2021-10-04 | ETL.1073 | MI-WUK-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40579929 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00019849 | 0.065147
119308342 | F | LC | ETL.8060.POLE.WOOD | 40809675 | SACTO | SIERRA | 2020-07-02 | 2021-02-11 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40809675 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0052244 | 291.1663
119310769 | B | LC | ETL.8170.POLE.WOOD | 40602117 | EUREKA | HUMBOLDT | 2020-07-03 | 2020-10-27 | ETL.8170 | TRINITY-MAPLE CREEK | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602117 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.16116 | 269.0562
119336168 | E | LC | ETL.6710.POLE.WOOD | 40768967 | MOSSLNDG | CENTRAL COAST | 2020-07-09 | 2021-03-11 | ETL.6710 | DEL MONTE-VIEJO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40768967 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.056873 | 0.066432
119341257 | E | LC | ETL.6890.POLE.WOOD | 40692989 | LAKEVLLE | SONOMA | 2020-07-09 | 2021-10-04 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.007966 | 2548.5022
119357440 | F | LC | ETL.7270.POLE.WOOD | 40827881 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40827881 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.061573 | 743.7872
119360007 | F | LC | ETL.6280.POLE.WOOD | 40675427 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40675427 |  | Single Wood Pole | T-1 - Tri Post | 2019-05-23 | Polymer | Post |  |  |  |  | 5.9377e-06 | 363.8401
119378315 | E | LC | ETL.7030.POLE.WOOD | 40825652 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2020-10-07 | ETL.7030 | HAT CREEK #1-WESTWOOD | Vegetation | Overgrown | [Trim, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40825652 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0032511 | 6268.4326
119467009 | E | LC | ETL.7030.POLE.WOOD | 40667969 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-06-14 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40667969 |  | Single Wood Pole | T2N | 2017-08-16 | Polymer | Post |  |  |  |  | 0.0002252 | 904.5289
119496204 | F | LC | ETL.1110.POLE.STPS | 44424640 | EUREKA | HUMBOLDT | 2020-07-22 | 2021-01-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424637 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.6692e-06 | 657.3666
119497668 | F | LC | ETL.1710.POLE.WDPS | 44510571 | MOSSLNDG | CENTRAL COAST | 2020-07-24 | 2021-04-07 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 3 | Within Both | DLFL | 44509647 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0024739 | 47.5096
119510410 | F | LC | ETL.5250.TOWR | 40756483 | CONCORD | DIABLO | 2020-07-27 | 2021-02-17 | ETL.5250 | MORAGA-CASTRO VALLEY | Hardware-Tower | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756483 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.9686e-08 | 333.6693
119516237 | E | LC | ETL.5353.TOWR | 40871124 | METCALF | SAN JOSE | 2020-07-28 |  | ETL.5353 | LOS ESTEROS-METCALF | Road | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40871124 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Ceramic | Suspension |  |  |  |  | 6.2172e-07 | 2900.4739
119537320 | E | LC | ETL.1470.POLE.WOOD | 41176302 | LAKEVLLE | HUMBOLDT | 2020-07-30 | 2021-06-21 | ETL.1470 | EAGLE ROCK-CORTINA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41176302 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Porcelain | Post |  |  |  |  | 0.0025093 | 3846.4539
119560346 | E | LC | ETL.7180.POLE.WOOD | 40750722 | LAKEVLLE | NORTH BAY | 2020-08-04 | 2021-04-22 | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750722 |  | Single Wood Pole | TP - Tri Pin |  | Non Ceramic | Pin |  |  |  |  | 9.7939e-06 | 126.9887
119566619 | F | LC | ETL.6280.POLE.WOOD | 40769569 | TABLEMTN | NORTH VALLEY | 2020-08-05 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40769569 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Other |  |  |  |  | 0.00028184 | 4065.6267
119567840 | E | LC | ETL.5140.POLE.WDPS | 44553582 | SACTO | SACRAMENTO | 2020-08-06 | 2021-12-02 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44553225 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00046976 | 3733.8787 | 1.754
119574023 | F | LC | ETL.1073.POLE.STPS | 44797109 | VICTOR | STOCKTON | 2020-08-06 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44797087 | 2019-07-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.7295e-06 | 15.88
119609925 | B | LC | ETL.1470.POLE.WOOD | 41176401 | LAKEVLLE | HUMBOLDT | 2020-05-09 | 2020-09-30 | ETL.1470 | EAGLE ROCK-CORTINA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119611256 | F | LC | ETL.5463.TOWR | 40805061 | CONCORD | DIABLO | 2020-08-13 | 2021-04-22 | ETL.5463 | PITTSBURG-SAN MATEO | Hardware-Tower | Missing | [Install, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805061 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 8.6383e-09 | 2709.8901
119611256 | F | LC | ETL.5463.TOWR | 40805061 | CONCORD | DIABLO | 2020-08-13 | 2021-04-22 | ETL.5463 | PITTSBURG-SAN MATEO | Hardware-Tower | Missing | [Install, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805061 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 8.6383e-09 | 2709.8901
119615520 | E | LC | ETL.1810.POLE.STPS | 44322742 | EUREKA | HUMBOLDT | 2020-08-14 | 2021-07-29 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Crossarm-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322740 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.6539e-08 | 0.066432
119628420 | F | LC | ETL.6870.POLE.WOOD | 40611468 | SACTO | SIERRA | 2020-08-17 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40611468 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post | 2019-05-05 | Polymer | Post |  |  |  |  | 0.20551 | 0.065152
119643325 | B | LC | ETL.8650.POLE.NWOD | 44420174 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44420174 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0021672 | 3305.365
119649511 | F | LC | ETL.2660.TOWR | 40660285 | SACTO | SACRAMENTO | 2020-08-21 | 2021-03-15 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | GO95 / Anti Climb | Ground / Clearance | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660285 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Ceramic | Suspension |  |  |  |  | 1.6919e-08 | 2452.9336
119649511 | F | LC | ETL.2660.TOWR | 40660285 | SACTO | SACRAMENTO | 2020-08-21 | 2021-03-15 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | GO95 / Anti Climb | Ground / Clearance | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660285 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Porcelain | Suspension |  |  |  |  | 1.6919e-08 | 2452.9336
119658765 | A | LC | ETL.6240.POLE.WOOD | 40875350 | MOSSLNDG | CENTRAL COAST | 2020-08-22 | 2020-09-19 | ETL.6240 | BURNS-LONE STAR #2 | Emergency-Wood | Other | [Replace, Completed] | Tier3 |  |  | COMP
119708063 | F | LC | ETL.8060.POLE.WOOD | 40862178 | SACTO | SIERRA | 2020-08-28 | 2021-02-12 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | DLFL | [11 empty] | 0.077628 | 125.0488
119723444 | E | LC | ETL.5540.INSL.CERA | 40615879 | TABLEMTN | NORTH VALLEY | 2020-08-07 | 2021-06-22 | ETL.5540 | POE-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119723774 | E | LC | ETL.8300.POLE.WOOD | 40601124 | TABLEMTN | NORTH VALLEY | 2020-08-05 |  | ETL.8300 | VOLTA-SOUTH | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40601124 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.016699 | 4102.6147 | 68.5103
119754037 | E | LC | ETL.8350.POLE.WOOD | 40643843 | VICTOR | STOCKTON | 2020-08-31 | 2021-05-05 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40643843 | 1993-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Glass | [5 empty] | 1.1268e-05 | 4759.0768
119756345 | F | LC | ETL.6380.POLE.WOOD | 44370570 | LAKEVLLE | HUMBOLDT | 2020-08-18 | 2021-03-09 | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44370570 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2021-07-29 | Glass | Suspension |  |  |  |  | 1.9318e-06 | 5892.4917
119765917 | E | LC | ETL.1110.POLE.WDPS | 44510608 | EUREKA | HUMBOLDT | 2020-08-17 | 2021-07-21 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44509665 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0028372 | 1888.7225
119769300 | E | LC | ETL.4220.POLE.NWOD | 44923808 | TABLEMTN | NORTH VALLEY | 2020-08-17 | 2021-04-15 | ETL.4220 | WOODLEAF-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119770304 | F | LC | ETL.8170.POLE.WOOD | 44271128 | EUREKA | HUMBOLDT | 2020-08-18 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44271128 |  | Single Wood Pole | DDE - Double Dead End | 2013-07-27 | Ceramic | Dead End |  |  |  |  | 0.013769 | 0.065148
119779266 | E | LC | ETL.1400.POLE.WDPS | 44774107 | VICTOR | STOCKTON | 2020-09-11 | 2021-05-17 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40803719 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0073248 | 31.7334
119781214 | E | LC | ETL.6290.INSL.CERA | 40640486 | TABLEMTN | NORTH VALLEY | 2020-09-12 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40614940 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.048683 | 126.5956 | 6.1631
119789607 | E | LC | ETL.1440.POLE.STPS | 44963252 | SACTO | SIERRA | 2020-09-18 | 2021-06-28 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44961228 | 2020-06-03 | 3-Pole Non Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 1.4832e-06 | 58.6018
119795101 | E | LC | ETL.8580.TOWR | 40609546 | FRESNO | FRESNO | 2020-09-21 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | PEND | 40609546 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-12-12 | Glass | Suspension |  |  |  |  | 0.00014799
119819458 | F | LC | ETL.7140.POLE.WOOD | 44310139 | LAKEVLLE | NORTH BAY | 2020-09-14 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44310139 | 2016-09-22 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2016-09-22 | Ceramic | Suspension |  |  |  |  | 0.0039949 | 728.338
119850143 | F | LC | ETL.5540.POLE.STPS | 44383632 | TABLEMTN | NORTH VALLEY | 2020-09-08 | 2021-07-19 | ETL.5540 | POE-RIO OSO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44383630 |  | 2-Pole Non Wood | 2P DDE-A - 2 Pole Double Dead End Angle | [7 empty] | 2.8476e-08 | 63.3704
119856587 | F | LC | ETL.7030.POLE.WOOD | 40770727 | TABLEMTN | NORTH VALLEY | 2020-10-02 | 2021-01-22 | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40770727 |  | Single Wood Pole | T2N | 2021-08-18 | Polymer | Post |  |  |  |  | 0.029677 | 0.065151
119930655 | F | LC | ETL.7212.POLE.WOOD | 40656244 | METCALF | PENINSULA | 2020-10-20 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40656244 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.78567 | 1345.4139
119932695 | E | LC | ETL.5970.INSL | 40793027 | PISMOBCH | LOS PADRES | 2020-10-21 | 2021-06-29 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119988047 | E | LC | ETL.8580.TOWR | 40748097 | FRESNO | FRESNO | 2020-11-04 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | PEND | 40748097 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Porcelain | [5 empty] | 0.00026534
120045487 | F | LC | ETL.6979.POLE.NWOD | 44917323 | LAKEVLLE | SONOMA | 2020-10-07 |  | ETL.6979 | MONTE RIO-FORT ROSS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44917323 | 2020-04-23 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-04-23 | Glass | Dead End |  |  |  |  | 0.00055286 | 31.7242
120097143 | E | LC | ETL.3180.INSL.NCER | 44190117 | CONCORD | EAST BAY | 2020-11-16 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 41196301 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Non Ceramic | Suspension |  |  |  |  | 0.0013122 | 16.3369 | 0.021437
120117451 | A | LC | ETL.8210.POLE.WOOD | 44230880 | VICTOR | STOCKTON | 2020-12-02 | 2020-12-04 | ETL.8210 | VALLEY SPRINGS #1 | Emergency | Storm Related | [Replace, Completed] | Tier2 |  |  | COMP
120130594 | F | LC | ETL.7180.POLE.NWOD | 40809522 | LAKEVLLE | NORTH BAY | 2020-10-20 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40809522 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 9.2218e-08 | 253.482
120132233 | F | LC | ETL.3150.TOWR | 40869889 | CONCORD | EAST BAY | 2020-12-04 |  | ETL.3150 | OLEUM-G #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40869889 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.2931e-07 | 79.7793 | 2.6272e-05
120132233 | F | LC | ETL.3150.TOWR | 40869889 | CONCORD | EAST BAY | 2020-12-04 |  | ETL.3150 | OLEUM-G #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40869889 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-14 | Glass | Suspension |  |  |  |  | 3.2931e-07 | 79.7793 | 2.6272e-05
120133317 | F | LC | ETL.1110.POLE.NWOD | 44891804 | TABLEMTN | NORTH VALLEY | 2020-10-19 | 2021-02-10 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44891804 | 2019-09-19 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2019-09-19 | Glass | Dead End |  |  |  |  | 1.2505e-05 | 4641.2573
120144027 | E | LC | ETL.8650.INSL.CERA | 40637221 | FRESNO | FRESNO | 2020-12-08 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40606162 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0044388 | 6995.4082
120149917 | E | LC | ETL.8650.POLE.WDPS | 44245517 | FRESNO | FRESNO | 2020-12-09 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Guy Pole-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | DLFL | 44245516 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.054091 | 5503.6265
120176776 | F | LC | ETL.5630.POLE.NWOD | 43249829 | TABLEMTN | NORTH VALLEY | 2020-12-10 | 2021-04-05 | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 43249829 |  | Lattice Steel Pole | Unknown |  | Ceramic | Dead End |  |  |  |  | 0.00022526 | 6035.9935
120229460 | F | LC | ETL.3180.TOWR | 40804775 | CONCORD | EAST BAY | 2020-11-18 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40804775 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-03-15 | Glass | Suspension |  |  |  |  | 2.228e-08 | 16.4761 | 3.6709e-07
120229460 | F | LC | ETL.3180.TOWR | 40804775 | CONCORD | EAST BAY | 2020-11-18 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40804775 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-03-14 | Glass | Dead End - Suspension |  |  |  |  | 2.228e-08 | 16.4761 | 3.6709e-07
120232933 | F | LC | ETL.3020.TOWR | 40644301 | CONCORD | MISSION | 2020-12-23 |  | ETL.3020 | NEWARK-JARVIS #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40644301 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.7919e-06
120232933 | F | LC | ETL.3020.TOWR | 40644301 | CONCORD | MISSION | 2020-12-23 |  | ETL.3020 | NEWARK-JARVIS #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40644301 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-11-03 | Ceramic | Dead End |  |  |  |  | 3.7919e-06
120305438 | F | LC | ETL.1820.POLE.STPS | 44395140 | EUREKA | HUMBOLDT | 2020-12-23 | 2021-07-26 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44395139 | 2020-03-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00025589 | 63.351
120499459 | A | LC | ETL.8405.POLE.WOOD | 40660036 | SACTO | SACRAMENTO | 2021-02-04 | 2021-02-10 | ETL.8405 | MIDDLE FORK #1 | Emergency-Wood | Other | [Replace, Completed, Completed] | Tier3 |  |  | COMP
120554638 | E | LC | ETL.5650.POLE.WDPS | 44765642 | TABLEMTN |  | 2021-02-18 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44765636 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.0587e-05 | 2836.814 | 0.17187
120653228 | F | LC | ETL.4920.TOWR | 40602309 | LAKEVLLE | SONOMA | 2021-03-17 |  | ETL.4920 | IGNACIO-SOBRANTE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40602309 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 5.1954e-05 | 822.7153 | 0.042744
120661907 | F | LC | ETL.4392.TOWR | 41129390 | LAKEVLLE | SONOMA | 2021-03-17 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41129390 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.0011045 | 996.9683 | 1.1012
120667415 | E | LC | ETL.6910.POLE.WOOD | 40659325 | LAKEVLLE | SONOMA | 2021-03-20 |  | ETL.6910 | FULTON-MOLINO-COTATI | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40659325 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Polymer | [5 empty] | 0.00016765 | 443.6687 | 0.074381
120680793 | F | LC | ETL.5790.TOWR | 40762383 | VICTOR | STOCKTON | 2021-03-22 |  | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40762383 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 3.9909e-05 | 237.591
120685927 | E | LC | ETL.5960.TOWR | 40592889 | PISMOBCH | LOS PADRES | 2021-03-24 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40592889 | 1973-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 2.4525e-06 | 1170.3627 | 0.0028703
120687144 | B | LC | ETL.5630.TOWR | 40815391 | TABLEMTN | NORTH VALLEY | 2021-03-24 | 2021-04-30 | ETL.5630 | ROCK CREEK-POE | Other | Land/Enviro Issue | [Access Issue] | Tier2 | Tier 2 | Within Both | COMP | 40815391 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 0.0091457 | 2497.7503
120736896 | E | LC | ETL.4040.POLE.STPS | 44647082 | TABLEMTN | NORTH VALLEY | 2021-04-02 | 2021-09-12 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44646903 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0017929 | 427.7504
120740461 | F | LC | ETL.2900.TOWR | 40870251 | MOSSLNDG | CENTRAL COAST | 2021-04-03 | 2021-07-26 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870251 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0068992 | 3623.5847
120748993 | E | LC | ETL.1350.POLE.NWOD | 44993097 | TABLEMTN | NORTH VALLEY | 2021-04-06 | 2021-06-24 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993097 | 2020-06-04 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-04 | Glass | Dead End |  |  |  |  | 0.00035246 | 15.8866
120758526 | E | LC | ETL.5310.INSL | 40885424 | PISMOBCH | LOS PADRES | 2021-04-07 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40863089 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.016726 | 982.0776 | 16.4262
120767070 | F | LC | ETL.8250.POLE.WOOD | 40908803 | VICTOR | STOCKTON | 2021-04-08 |  | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40908803 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00054043 | 5094.106
120805138 | E | LC | ETL.7140.POLE.WOOD | 40617125 | LAKEVLLE | SONOMA | 2021-04-13 | 2021-08-16 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40617125 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | [5 empty] | 0.052478 | 47.5223
120812769 | E | LC | ETL.8650.TOWR | 40873716 | FRESNO | YOSEMITE | 2021-04-07 | 2021-08-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40873716 | 1929-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0035639 | 5678.02
120814514 | F | LC | ETL.4950.TOWR | 40864243 | LAKEVLLE | SONOMA | 2021-04-07 |  | ETL.4950 | FULTON-LAKEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40864243 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 4.5306e-05 | 110.8617 | 0.0050227
120833608 | E | LC | ETL.9250.POLE.WOOD | 40749367 | MIDWAY | KERN | 2021-04-17 | 2021-09-02 | ETL.9250 | TEJON-LEBEC | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40749367 | 1967-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Other |  |  |  |  | 0.11262 | 9424.9238
120842138 | E | LC | ETL.1610.INSL.CERA | 40878329 | LAKEVLLE | SONOMA | 2021-04-12 |  | ETL.1610 | SILVERADO-FULTON JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40857285 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 3.8128e-05 | 8417.8564 | 0.32096
120842138 | E | LC | ETL.1610.INSL.CERA | 40878329 | LAKEVLLE | SONOMA | 2021-04-12 |  | ETL.1610 | SILVERADO-FULTON JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40857285 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 3.8128e-05 | 8417.8564 | 0.32096
120860042 | E | LC | ETL.1530.POLE.WOOD | 40586137 | SACTO | SIERRA | 2021-04-13 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40586137 | 1980-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1980-01-01 | Ceramic | Dead End |  |  |  |  | 0.00043594 | 665.5124 | 0.29012
120860645 | F | LC | ETL.6690.POLE.NWOD | 44919741 | SACTO | SACRAMENTO | 2021-04-21 | 2021-08-09 | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44919741 | 2020-05-02 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-02 | Glass | Dead End |  |  |  |  | 0.01219 | 63.348
120895878 | E | LC | ETL.5540.TOWR | 40590789 | TABLEMTN | NORTH VALLEY | 2021-04-14 |  | ETL.5540 | POE-RIO OSO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40590789 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 3.5652e-07 | 4276.2046 | 0.0015245
120909944 | E | LC | ETL.6020.TOWR | 40868386 | TABLEMTN | NORTH VALLEY | 2021-04-30 |  | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40868386 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Dead End |  |  |  |  | 9.1248e-10 | 1347.8633 | 1.2299e-06
120931770 | E | LC | ETL.1820.POLE.WDPS | 44562793 | EUREKA | HUMBOLDT | 2021-05-04 |  | ETL.1820 | HUMBOLDT-TRINITY | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562388 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.097027 | 237.3869 | 23.033
121322255 | E | LC | ETL.1110.POLE.WDPS | 44561160 | TABLEMTN | HUMBOLDT | 2021-05-12 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44515859 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0020157 | 5129.4224 | 10.3395
121322972 | E | LC | ETL.3960.TOWR | 40744760 | PISMOBCH | LOS PADRES | 2021-04-21 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40744760 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 8.1427e-09 | 4512.897 | 3.6747e-05
121322972 | E | LC | ETL.3960.TOWR | 40744760 | PISMOBCH | LOS PADRES | 2021-04-21 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40744760 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 8.1427e-09 | 4512.897 | 3.6747e-05
121336914 | E | LC | ETL.3500.TOWR | 40745438 | VICTOR | STOCKTON | 2021-04-26 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40745438 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 0.00076387 | 142.4769 | 0.10883
121340370 | A | LC | ETL.5091.INSL | 41122484 | MOSSLNDG | CENTRAL COAST | 2021-05-15 | 2021-05-18 | ETL.5091 | METCALF-MONTA VISTA #3 | Emergency | Storm Related | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40753099 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.015096 | 459.1403
121358580 | E | LC | ETL.6130.TOWR | 40753763 | VICTOR | YOSEMITE | 2021-04-30 |  | ETL.6130 | TRACY-LOS BANOS | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753763 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Glass | Suspension |  |  |  |  | 7.138e-08 | 1984.5067 | 0.00014165
121364092 | F | LC | ETL.6880.POLE.WOOD | 40588914 | LAKEVLLE | NORTH BAY | 2021-05-01 |  | ETL.6880 | FULTON-CALISTOGA | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40588914 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0024277 | 3387.7546
121369105 | F | LC | ETL.4870.TOWR | 40576606 | FRESNO | FRESNO | 2021-05-20 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576606 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 1.2652e-07 | 5393.4243 | 0.00068235
121374361 | E | LC | ETL.9250.INSL | 40777417 | MIDWAY | KERN | 2021-05-05 | 2021-08-06 | ETL.9250 | TEJON-LEBEC | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40749552 |  | Single Wood Pole | DV - Double Vertical |  | Ceramic | [5 empty] | 0.04857 | 4334.67
121376130 | E | LC | ETL.6760.POLE.WOOD | 40664724 | SACTO | SIERRA | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40664724 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.062731 | 649.2313 | 40.7268
121381065 | E | LC | ETL.1600.INSL | 40835236 | LAKEVLLE | SONOMA | 2021-05-08 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810362 | 1946-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.9364e-06 | 2346.1775 | 0.0092354
121381065 | E | LC | ETL.1600.INSL | 40835236 | LAKEVLLE | SONOMA | 2021-05-08 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810362 | 1946-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1946-01-01 | Ceramic | Dead End |  |  |  |  | 3.9364e-06 | 2346.1775 | 0.0092354
121381412 | E | LC | ETL.9250.POLE.WOOD | 40764570 | MIDWAY | KERN | 2021-05-05 | 2021-08-06 | ETL.9250 | TEJON-LEBEC | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40764570 |  | Single Wood Pole | DV - Double Vertical |  | Ceramic | [5 empty] | 0.039954 | 3692.9529
121383168 | E | LC | ETL.1400.INSL | 40771678 | VICTOR | YOSEMITE | 2021-05-12 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40744506 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010038
121383168 | E | LC | ETL.1400.INSL | 40771678 | VICTOR | YOSEMITE | 2021-05-12 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40744506 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010038
121384138 | E | LC | ETL.6470.POLE.WOOD | 40593276 | SACTO | SIERRA | 2021-05-11 |  | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40593276 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.066377 | 4700.8066 | 312.025
121385733 | F | LC | ETL.5452.TOWR | 40581897 | CONCORD | DIABLO | 2021-05-12 |  | ETL.5452 | CONTRA COSTA-MORAGA #1 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40581897 | 1950-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | 2013-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.5278e-06 | 111.0323 | 0.00028067
121395556 | E | LC | ETL.1420.INSL.CERA | 40890230 | SACTO | SACRAMENTO | 2021-05-15 |  | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40866009 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 8.8165e-05 | 269.0173 | 0.023718
121402937 | F | LC | ETL.8290.POLE.WOOD | 40817155 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40817155 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.0028988 | 3057.9141
121404141 | F | LC | ETL.8405.POLE.WOOD | 40873829 | SACTO | SIERRA | 2021-05-20 |  | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40873829 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.031982 | 205.7471
121405233 | E | LC | ETL.7290.POLE.WOOD | 40817416 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.7290 | KILARC-CEDAR CREEK | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40817416 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.0032429 | 556.7504 | 1.8055
121405577 | E | LC | ETL.8290.POLE.NWOD | 44949900 | TABLEMTN | NORTH VALLEY | 2021-05-20 | 2021-06-11 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44949900 | 2019-06-11 | Light Duty Steel Pole | T2N | 2019-06-11 | Polymer | Post |  |  |  |  | 1.3088e-06 | 5431.645
121418162 | E | LC | ETL.1070.POLE.WOOD | 40804219 | VICTOR | STOCKTON | 2021-05-20 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40804219 | 1998-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1957-01-01 | Polymer | Dead End |  |  |  |  | 9.9639e-05 | 2171.9446 | 0.21641
121419779 | F | LC | ETL.6470.POLE.WOOD | 40874834 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40874834 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.25669 | 221.5931
121453938 | E | LC | ETL.1350.POLE.WDPS | 44513795 | TABLEMTN |  | 2021-05-29 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44512283 | 2012-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0019596 | 3880.9729 | 7.6052
121468848 | B | LC | ETL.2823.INSL.CERA | 41130042 | LAKEVLLE |  | 2021-06-03 | 2021-06-21 | ETL.2823 | FULTON-LAKEVILLE-IGNACIO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818221 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 7.7858e-05 | 31.7169
121470333 | A | LC | ETL.4950.INSL.CERA | 44942639 | LAKEVLLE | SONOMA | 2021-06-04 | 2021-06-10 | ETL.4950 | FULTON-LAKEVILLE | Emergency-Steel | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129395 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-10-14 | Glass | Dead End |  |  |  |  | 0.0021741 | 345.1107
121470333 | A | LC | ETL.4950.INSL.CERA | 44942639 | LAKEVLLE | SONOMA | 2021-06-04 | 2021-06-10 | ETL.4950 | FULTON-LAKEVILLE | Emergency-Steel | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129395 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2021-02-28 | Glass | Dead End |  |  |  |  | 0.0021741 | 345.1107
121470333 | A | LC | ETL.4950.INSL.CERA | 44942639 | LAKEVLLE | SONOMA | 2021-06-04 | 2021-06-10 | ETL.4950 | FULTON-LAKEVILLE | Emergency-Steel | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129395 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2018-04-04 | Ceramic | Double Dead End |  |  |  |  | 0.0021741 | 345.1107
121482724 | B | LC | ETL.6750.INSL.NCER | 40628928 | TABLEMTN |  | 2021-06-04 | 2021-09-02 | ETL.6750 | DELTA-MTN GATE JCT | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121491804 | E | LC | ETL.5140.POLE.WDPS | 44552344 | SACTO | SACRAMENTO | 2021-05-28 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44551554 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.019937 | 4160.9766 | 82.9591
121493435 | F | LC | ETL.7610.POLE.WOOD | 40823285 | METCALF | DE ANZA | 2021-06-01 |  | ETL.7610 | MONTA VISTA-LOS GATOS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | HFRA Removal | PEND | 40823285 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00010353 | 0.065147
121513966 | E | LC | ETL.1820.POLE.WDPS | 44565583 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564230 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.90741 | 79.1467 | 71.8186
121516719 | F | LC | ETL.1450.POLE.WDPS | 44552263 | SACTO | SACRAMENTO | 2021-06-04 | 2021-07-12 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | DLFL | 44551549 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00043839 | 3069.2839
121518208 | B | LC | ETL.5390.INSL.NCER | 45114445 | TABLEMTN | NORTH VALLEY | 2021-06-10 | 2021-08-17 | ETL.5390 | PIT #1-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40817903 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.0648e-05 | 4476.4062
121518256 | E | LC | ETL.8590.POLE.WDPS | 44307725 | FRESNO | FRESNO | 2021-06-11 |  | ETL.8590 | COPPERMINE-TIVY VALLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44307724 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0020924 | 4623.4492 | 9.6741
121538988 | E | LC | ETL.5630.INSL.NCER | 45102904 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.5630 | ROCK CREEK-POE | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40867803 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-05-27 | Glass | Suspension |  |  |  |  | 0.0091457 | 2507.2401 | 22.9304
121554566 | E | LC | ETL.5970.INSL | 40848803 | PISMOBCH | LOS PADRES | 2021-06-15 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40820141 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 6.0391e-08 | 1552.8336 | 9.3778e-05
121581549 | E | LC | ETL.5463.INSL | 40885264 | CONCORD | EAST BAY | 2021-06-22 |  | ETL.5463 | PITTSBURG-SAN MATEO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40861880 | 1964-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0016499 | 5304.291 | 8.7515
121582599 | A | LC | ETL.3780.INSL | 40622445 | CONCORD | DIABLO | 2021-06-22 | 2021-06-24 | ETL.3780 | SOBRANTE-R #2 | Emergency-Steel | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581870 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1923-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.013745 | 253.126
121596223 | B | LC | ETL.8170.INSL | 40780543 | EUREKA | HUMBOLDT | 2021-06-23 | 2021-09-29 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752256 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.013685 | 6206.8564
121600556 | E | LC | ETL.7390.POLE.NWOD | 42813768 | LAKEVLLE | SONOMA | 2021-06-25 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42813768 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.00012497 | 1093.7991 | 0.1367
121601328 | F | LC | ETL.1182.TOWR | 45098591 | LAKEVLLE | SONOMA | 2021-06-25 | 2021-09-10 | ETL.1182 | BEAR CANYON TAP | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45098591 |  | LATTICE STEEL TOWER | Unknown |  | Unknown | Unknown | [5 empty] | 158.4936
121609376 | F | LC | ETL.1070.POLE.WOOD | 40645009 | VICTOR | YOSEMITE | 2021-06-22 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40645009 | 1957-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 1957-01-01 | Polymer | Dead End |  |  |  |  | 0.00023215 | 2390.8503 | 0.55503
121617091 | E | LC | ETL.5970.TOWR | 40817723 | PISMOBCH | LOS PADRES | 2021-06-26 |  | ETL.5970 | DIABLO-MIDWAY #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40817723 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-30 | Glass | Suspension |  |  |  |  | 1.1437e-07 | 286.2883 | 3.2742e-05
121617099 | B | LC | ETL.6060.INSL | 40789070 | TABLEMTN | NORTH VALLEY | 2021-06-22 | 2021-09-16 | ETL.6060 | ROUND MTN-TABLE MTN #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40759734 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.0080073 | 190.8412
121622897 | B | LC | ETL.6720.POLE.NWOD | 40700298 | TABLEMTN | NORTH VALLEY | 2021-06-27 | 2021-07-13 | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40700298 | 1998-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 4.2449e-05 | 0.065151
121623176 | E | LC | ETL.1450.POLE.NWOD | 45125369 | SACTO | SIERRA | 2021-06-28 |  | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45125369 | 2020-07-25 | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper | 2020-07-25 | Glass | Double Dead End | [5 empty] | 648.7145
121624667 | B | LC | ETL.6320.INSL.NCER | 40617301 | TABLEMTN |  | 2021-06-28 | 2021-07-13 | ETL.6320 | CENTERVILLE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591722 | 1999-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Non Ceramic | Pin |  |  |  |  | 0.031679 | 2662.146
121630614 | E | LC | ETL.7490.POLE.WOOD | 40586855 | EUREKA | HUMBOLDT | 2021-06-15 |  | ETL.7490 | MAPLE CREEK-HOOPA | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40586855 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-07-30 | Polymer | Dead End |  |  |  |  | 0.46676 | 126.5956 | 59.0899
121647767 | E | LC | ETL.2395.POLE.WOOD | 45019107 | TABLEMTN | NORTH VALLEY | 2021-06-26 |  | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45019107 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.0066717 | 6679.8335 | 44.5656
121655659 | E | LC | ETL.5430.POLE.WDPS | 44561504 | TABLEMTN | NORTH VALLEY | 2021-07-01 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560803 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.004144 | 665.1749 | 2.7565
121660333 | E | LC | ETL.1720.POLE.STPS | 44893479 | MOSSLNDG | SAN JOSE | 2021-06-29 | 2021-10-04 | ETL.1720 | GREEN VALLEY-LLAGAS | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44893446 | 2019-11-07 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.245e-08 | 1134.4898 | 3.6814e-05
121661530 | E | LC | ETL.8350.POLE.WOOD | 40579948 | VICTOR | STOCKTON | 2021-07-01 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40579948 |  | Single Wood Pole | T2N | 2021-03-24 | Polymer | Post |  |  |  |  | 0.0014061 | 110.7947 | 0.15579
121684561 | E | LC | ETL.1110.POLE.NWOD | 42603444 | TABLEMTN | NORTH VALLEY | 2021-07-08 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42603444 |  | Lattice Steel Pole | DDE - Double Dead End | 2020-10-12 | Glass | Dead End |  |  |  |  | 1.6842e-05 | 126.6368 | 0.0021329
121684823 | B | LC | ETL.9240.TOWR | 43249512 | PISMOBCH | LOS PADRES | 2021-07-08 | 2021-07-27 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249512 |  | LATTICE STEEL TOWER | [9 empty] | 158.4262
121713139 | E | LC | ETL.3700.POLE.WDPS | 44296823 | PISMOBCH | LOS PADRES | 2021-06-30 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44296821 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0001621 | 4054.1909 | 0.65717
121715528 | E | LC | ETL.1820.INSL.NCER | 40886476 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-05 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
121717994 | F | LC | ETL.4040.POLE.WDPS | 44561244 | TABLEMTN | NORTH VALLEY | 2021-07-07 | 2021-07-26 | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 3 | Within Both | DLFL | 44552618 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.046673 | 2249.5164
121725584 | E | LC | ETL.4220.POLE.STPS | 44907405 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44907379 | 2020-04-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.004815 | 142.5462 | 0.68637
121727923 | E | LC | ETL.1162.INSL.CERA | 45070798 | CONCORD | EAST BAY | 2021-07-01 | 2021-10-19 | ETL.1162 | BRIGHTON-OLEUM JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
121729536 | B | LC | ETL.6511.POLE.WDPS | 44926560 | SACTO | SIERRA | 2021-07-14 | 2021-07-26 | ETL.6511 | NARROWS #1 TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44926560 | 2020-06-06 | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2020-06-06 | Glass | Dead End
121729536 | B | LC | ETL.6511.POLE.WDPS | 44926560 | SACTO | SIERRA | 2021-07-14 | 2021-07-26 | ETL.6511 | NARROWS #1 TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44926560 | 2020-06-06 | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2020-06-06 | Glass | Dead End
121729536 | B | LC | ETL.6511.POLE.WDPS | 44926560 | SACTO | SIERRA | 2021-07-14 | 2021-07-26 | ETL.6511 | NARROWS #1 TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44926560 | 2020-06-06 | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2020-06-06 | Glass | Dead End
121729737 | F | LC | ETL.4393.POLE.NWOD | 44984412 | SACTO | SIERRA | 2021-06-13 |  | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44984412 |  | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2016-08-08 | Ceramic | Dead End |  |  |  |  | 6.2622e-07 | 349.6656
121737631 | F | LC | ETL.5420.POLE.STPS | 44400035 | TABLEMTN |  | 2021-07-09 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44400034 | 2017-11-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.7171e-05 | 3338.3914
121741239 | E | LC | ETL.1820.POLE.STPS | 44395439 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44395438 | 2020-03-04 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.009475 | 6300.0015 | 59.6926
121744929 | F | LC | ETL.4393.POLE.NWOD | 45078753 | SACTO | SIERRA | 2021-07-15 |  | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45078753 | 2020-09-02 | Light Duty Steel Pole | DDE - Double Dead End | 2020-09-02 | Glass | Double Dead End |  |  |  |  | 0.00032628 | 2056.7583
121745234 | E | LC | ETL.8350.POLE.WDPS | 44405874 | VICTOR | STOCKTON | 2021-07-14 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44405871 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.1034e-05 | 1075.7365 | 0.01187
121749929 | F | LC | ETL.1810.POLE.STPS | 44395988 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44395987 | 2017-08-23 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.1557e-07
121750406 | E | LC | ETL.6220.POLE.WOOD | 40614568 | EUREKA | HUMBOLDT | 2021-07-17 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40614568 |  | Single Wood Pole | TPSRD - Tri Post & Susp Dead End |  | Porcelain | [5 empty] | 0.16322
121753138 | B | LC | ETL.8365.INSL.NCER | 45021966 | EUREKA | HUMBOLDT | 2021-07-19 | 2021-08-21 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 45021957 | 2020-12-21 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-12-21 | Polymer | Post |  |  |  |  | 0.00057876
121767883 | F | LC | ETL.5510.TOWR | 40651295 | CONCORD | DIABLO | 2021-07-19 |  | ETL.5510 | PITTSBURG-TESLA #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40651295 | 1953-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1953-01-01 | Ceramic | Dead End |  |  |  |  | 6.427e-06 | 5592.7007 | 0.035944
121780991 | F | LC | ETL.5463.POLE.NWOD | 41136388 | CONCORD | DIABLO | 2021-07-21 | 2021-08-09 | ETL.5463 | PITTSBURG-SAN MATEO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 41136388 | 2002-01-01 | Tubular Steel Pole | SVDE - Single Vertical Dead End | 2001-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 9.2245e-08 | 5624.2686
121784512 | E | LC | ETL.6760.POLE.WOOD | 40874793 | SACTO | SIERRA | 2021-07-23 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40874793 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.01305 | 33.284 | 0.43436
121785384 | E | LC | ETL.5934.TOWR | 40805225 | FRESNO | FRESNO | 2021-07-22 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40805225 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.0020904
121791328 | B | LC | ETL.8365.POLE.WOOD | 40750497 | EUREKA | HUMBOLDT | 2021-07-24 | 2021-08-19 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40750497 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-04-28 | Glass | Dead End |  |  |  |  | 0.050769 | 1046.2505
121811002 | E | LC | ETL.6950.POLE.NWOD | 44174898 | SACTO | SIERRA | 2021-07-28 |  | ETL.6950 | GOLD HILL #1 | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44174898 |  | Fiberglass | TPA - Tri Pin Arm |  | Porcelain | Post |  |  |  |  | 0.002947 | 982.2551 | 2.8947
121816141 | F | LC | ETL.6220.POLE.WOOD | 40862857 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40862857 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.46828
121816153 | E | LC | ETL.5510.TOWR | 40603574 | CONCORD | DIABLO | 2021-07-29 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40603574 | 1953-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Dead End |  |  |  |  | 7.1063e-09 | 4670.9731 | 3.3193e-05
121820539 | F | LC | ETL.6480.POLE.NWOD | 45120503 | SACTO | NORTH VALLEY | 2021-07-29 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45120503 | 2021-06-30 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-06-30 | Glass | Dead End | [5 empty] | 458.8146
121822001 | E | LC | ETL.2395.POLE.WDPS | 44551439 | TABLEMTN | NORTH VALLEY | 2021-07-30 |  | ETL.2395 | GRIZZLY TAP | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550861 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0081083 | 300.6002 | 2.4374
121902790 | E | LC | ETL.4040.INSL.CERA | 40615410 | TABLEMTN |  | 2021-07-07 |  | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553989 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.006721
121902790 | E | LC | ETL.4040.INSL.CERA | 40615410 | TABLEMTN |  | 2021-07-07 |  | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553989 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.006721
121942699 | E | LC | ETL.9460.POLE.WOOD | 40907556 | VICTOR | STOCKTON | 2021-08-23 |  | ETL.9460 | VALLEY SPRINGS #2 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40907556 | 1991-01-01 | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Porcelain | [5 empty] | 0.0023355 | 2520.3257 | 5.8862
122020448 | E | LC | ETL.4440.POLE.NWOD | 44190874 | TABLEMTN | NORTH VALLEY | 2021-09-02 |  | ETL.4440 | CARIBOU-TABLE MTN | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44190874 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 0.00032474 | 6034.1842 | 1.9596
122408931 | E | LC | ETL.8180.POLE.WOOD | 40761056 | LAKEVLLE | SONOMA | 2021-11-23 |  | ETL.8180 | TULUCAY-NAPA #1 | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40761056 | 1967-01-01 | Single Wood Pole | WB - Wishbone | 2020-08-25 | Glass | Suspension |  |  |  |  | 0.033962 | 3863.3413 | 131.2083
118575966 | E | LC | ETL.5930.INSL | 40611760 | CONCORD |  | 2020-02-25 | 2020-07-20 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 |  |  | COMP
118681702 | E | LC | ETL.7212.POLE.WOOD | 40599243 | METCALF | SAN JOSE | 2020-03-11 | 2021-04-26 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40599243 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.20004 | 791.4469
118738297 | E | LC | ETL.1200.INSL.NCER | 40790778 | PISMOBCH | LOS PADRES | 2020-03-23 | 2020-07-29 | ETL.1200 | CABRILLO-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761093 | 2010-01-01 | Light Duty Steel Pole | T-1 - Tri Post | 1989-01-01 | Polymer | Dead End |  |  |  |  | 1.7853e-08 | 5097.3877
118793698 | E | LC | ETL.8210.POLE.WOOD | 40908269 | VICTOR | STOCKTON | 2020-04-07 | 2021-07-06 | ETL.8210 | VALLEY SPRINGS #1 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908269 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0018677 | 1221.7842
118910104 | F | LC | ETL.4590.TOWR | 40911298 | TABLEMTN | NORTH VALLEY | 2020-04-10 |  | ETL.4590 | CRESTA-RIO OSO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40911298 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.7573e-06 | 0.090455
118911603 | F | LC | ETL.2770.TOWR | 40594276 | CONCORD | DIABLO | 2020-04-10 | 2021-01-19 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594276 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 7.8578e-07 | 15.8932
118911603 | F | LC | ETL.2770.TOWR | 40594276 | CONCORD | DIABLO | 2020-04-10 | 2021-01-19 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594276 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 7.8578e-07 | 15.8932
118921769 | E | LC | ETL.7270.POLE.WOOD | 40617597 | TABLEMTN | NORTH VALLEY | 2020-04-15 |  | ETL.7270 | KESWICK-TRINITY | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40617597 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.25873 | 3563.1055 | 921.8974
118927308 | E | LC | ETL.2770.INSL | 40704861 | CONCORD | EAST BAY | 2020-04-16 | 2021-08-26 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118948207 | F | LC | ETL.4392.TOWR | 41129397 | LAKEVLLE | SONOMA | 2020-04-24 | 2021-06-30 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | DLFL | 41129397 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.0034723 | 3141.8581
118957182 | E | LC | ETL.6980.POLE.WOOD | 40648473 | LAKEVLLE | SONOMA | 2020-04-27 | 2021-06-23 | ETL.6980 | FORT ROSS-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648473 | 1985-01-01 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 1953-01-01 | Polymer | Dead End |  |  |  |  | 0.32716 | 71.2319
118964040 | E | LC | ETL.2060.POLE.WOOD | 40648270 | LAKEVLLE | SONOMA | 2020-04-30 | 2020-05-01 | ETL.2060 | FORT BRAGG-ELK | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648270 | 1961-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2020-07-14 | Glass | Suspension |  |  |  |  | 0.28156 | 15.8807
118969168 | F | LC | ETL.4782.TOWR | 40809008 | LAKEVLLE | SONOMA | 2020-04-30 | 2021-03-22 | ETL.4782 | SANTA FE GEOTHERMAL TAP | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809008 | 1982-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End | [5 empty] | 349.3637
118976710 | E | LC | ETL.1330.TOWR | 40657061 | LAKEVLLE | HUMBOLDT | 2020-04-23 | 2021-05-11 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40657061 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.0019291 | 5381.2715
118976713 | F | LC | ETL.5463.TOWR | 40805087 | CONCORD | MISSION | 2020-04-20 | 2021-01-19 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805087 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Ceramic | Dead End |  |  |  |  | 6.6954e-08 | 3154.5959
118976713 | F | LC | ETL.5463.TOWR | 40805087 | CONCORD | MISSION | 2020-04-20 | 2021-01-19 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805087 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.6954e-08 | 3154.5959
118983896 | E | LC | ETL.7490.POLE.WDPS | 45099461 | EUREKA | HUMBOLDT | 2020-05-05 |  | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40668473 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.50943 | 142.4498 | 72.568
118985393 | E | LC | ETL.7950.POLE.WDPS | 44307304 | METCALF | SAN JOSE | 2020-05-05 | 2021-04-19 | ETL.7950 | SAN MATEO-HILLSDALE JCT | Guy Wire-Wood | Missing | [Install] | Tier2 | Tier 2 | HFRA Removal | DLFL | 44307303 | 2015-05-29 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0080061 | 0.065147
118997054 | F | LC | ETL.1530.POLE.NWOD | 44722642 | SACTO | SIERRA | 2020-05-01 | 2021-01-14 | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44722642 | 2018-11-10 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2018-11-10 | Ceramic | Suspension |  |  |  |  | 1.4741e-07 | 1344.6511
119004773 | F | LC | ETL.8650.POLE.NWOD | 44420172 | FRESNO | YOSEMITE | 2020-05-05 | 2021-09-15 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44420172 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0016024 | 3210.4758
119063050 | F | LC | ETL.7140.POLE.WOOD | 40750704 | LAKEVLLE | NORTH BAY | 2020-05-20 | 2021-08-31 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750704 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.063834 | 680.8114
119094084 | F | LC | ETL.7300.POLE.WOOD | 40826004 | TABLEMTN | NORTH VALLEY | 2020-06-02 | 2020-07-29 | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL
119094332 | E | LC | ETL.5390.TOWR | 40744731 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2021-03-24 | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40744731 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 8.3904e-07 | 809.5917
119096921 | E | LC | ETL.1430.TOWR | 40655126 | SACTO | SIERRA | 2020-05-19 | 2021-03-08 | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40655126 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-03-16 | Glass | Suspension |  |  |  |  | 0.002459 | 3797.0496
119097621 | E | LC | ETL.1110.POLE.WDPS | 44423873 | TABLEMTN | HUMBOLDT | 2020-05-19 | 2021-04-12 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423872 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00083534 | 4088.4016
119102348 | F | LC | ETL.1720.POLE.STPS | 44076661 | MOSSLNDG | CENTRAL COAST | 2020-05-20 | 2021-09-29 | ETL.1720 | GREEN VALLEY-LLAGAS | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44076659 | 2017-04-27 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.3965e-09 | 2341.6399
119111105 | F | LC | ETL.5290.TOWR | 40746359 | PISMOBCH | LOS PADRES | 2020-05-26 | 2021-01-20 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40746359 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Other |  |  |  |  | 6.3577e-07 | 619.4626
119111105 | F | LC | ETL.5290.TOWR | 40746359 | PISMOBCH | LOS PADRES | 2020-05-26 | 2021-01-20 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40746359 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 6.3577e-07 | 619.4626
119114898 | E | LC | ETL.1430.TOWR | 40913104 | SACTO | SIERRA | 2020-05-19 | 2021-03-11 | ETL.1430 | DRUM-RIO OSO #2 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119116869 | F | LC | ETL.6760.POLE.WOOD | 40813455 | SACTO | SIERRA | 2020-05-28 | 2021-02-10 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40813455 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.081467 | 949.3081
119117606 | F | LC | ETL.5290.TOWR | 40862866 | PISMOBCH | LOS PADRES | 2020-05-26 | 2021-01-19 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862866 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.6467e-08 | 3405.4033
119118909 | E | LC | ETL.6520.POLE.WOOD | 40878152 | SACTO | SIERRA | 2020-06-03 | 2021-06-09 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40878152 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.003367 | 5479.3975
119119072 | E | LC | ETL.6520.POLE.WOOD | 40745238 | SACTO | SIERRA | 2020-06-03 | 2021-06-09 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40745238 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 0.0063084 | 5336.644
119119375 | F | LC | ETL.6950.POLE.NWOD | 44174898 | SACTO | SIERRA | 2020-05-28 | 2021-08-03 | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44174898 |  | Fiberglass | TPA - Tri Pin Arm |  | Porcelain | Post |  |  |  |  | 0.002947 | 982.2551
119129967 | F | LC | ETL.7300.POLE.WOOD | 44141993 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-03-24 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44141993 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.00025131 | 6050.8618
119130807 | F | LC | ETL.7300.POLE.WOOD | 40602047 | TABLEMTN |  | 2020-06-03 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40602047 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0012412 | 996.3953
119160768 | F | LC | ETL.6470.POLE.WOOD | 40760435 | SACTO | SIERRA | 2020-06-11 | 2021-07-27 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760435 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.015604 | 411.5556
119160839 | F | LC | ETL.6440.POLE.WOOD | 40601047 | TABLEMTN | NORTH VALLEY | 2020-06-09 | 2020-08-27 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601047 |  | Single Wood Pole | T-1 - Tri Post | 2013-01-18 | Polymer | Post |  |  |  |  | 0.00040884 | 2131.4695
119162037 | F | LC | ETL.6470.POLE.WOOD | 40598558 | SACTO | SIERRA | 2020-06-10 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40598558 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.020278 | 474.7878
119163139 | B | LC | ETL.1112.INSL.CERA | 40621832 | FRESNO | YOSEMITE | 2020-06-04 | 2021-10-19 | ETL.1112 | INDIAN FLAT-YOSEMITE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40595495 | 1930-01-01 | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR | 1929-01-01 | Porcelain | Suspension |  |  |  |  | 0.0023453 | 4306.9175
119173537 | F | LC | ETL.7490.POLE.WOOD | 44935739 | EUREKA | HUMBOLDT | 2020-06-15 |  | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44935739 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.57287 | 0.065148
119179528 | F | LC | ETL.6280.POLE.WOOD | 40758806 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758806 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0001326 | 6569.0815
119180127 | E | LC | ETL.7300.POLE.WOOD | 40617709 | TABLEMTN |  | 2020-06-16 | 2021-03-11 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119185340 | B | LC | ETL.6310.POLE.WOOD | 40676976 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2020-09-17 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676976 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.4514e-05 | 5385.2025
119187540 | E | LC | ETL.6280.POLE.NWOD | 45121211 | TABLEMTN | NORTH VALLEY | 2020-06-18 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45121211 | 2020-02-25 | Light Duty Steel Pole | T2N | 2020-02-25 | Polymer | Post | [5 empty] | 63.3304
119189283 | F | LC | ETL.6310.POLE.WOOD | 40867968 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40867968 |  | Single Wood Pole | T-1 - Tri Post | 2018-10-10 | Polymer | Post |  |  |  |  | 2.3031e-05 | 5436.8481
119194509 | F | LC | ETL.1240.POLE.STPS | 44200947 | TABLEMTN | NORTH VALLEY | 2020-06-22 | 2020-07-30 | ETL.1240 | CASCADE-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Tier 2 | Within Both | COMP | 44200944 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 3.2742e-09 | 5687.9312
119194764 | E | LC | ETL.6470.INSL.CERA | 40696054 | SACTO | SACRAMENTO | 2020-06-22 | 2021-08-10 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664742 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.25187 | 221.5931
119199046 | F | LC | ETL.6480.POLE.WOOD | 40824180 | SACTO | SIERRA | 2020-06-22 | 2021-01-25 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119206450 | F | LC | ETL.4680.TOWR | 40651563 | LAKEVLLE | SONOMA | 2020-06-24 | 2021-03-02 | ETL.4680 | FULTON-IGNACIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40651563 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.7576e-07 | 15.891
119222772 | E | LC | ETL.8290.POLE.WOOD | 40600274 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2020-12-01 | ETL.8290 | VOLTA-DESCHUTES | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40600274 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.0048702 | 3232.478
119223953 | B | LC | ETL.7321.POLE.WOOD | 40769967 | MOSSLNDG | CENTRAL COAST | 2020-06-27 | 2021-05-20 | ETL.7321 | JOLON TAP | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40769967 |  | Single Wood Pole | DV - Double Vertical |  | Ceramic | Other |  |  |  |  | 0.0008407 | 808.3414
119238737 | E | LC | ETL.7300.POLE.WOOD | 40867878 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2021-03-12 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40867878 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0021228 | 1218.3302
119293972 | B | LC | ETL.8060.INSL.CERA | 40902958 | SACTO | SACRAMENTO | 2020-06-29 | 2021-05-06 | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119302470 | F | LC | ETL.7300.POLE.WOOD | 40759119 | TABLEMTN | NORTH VALLEY | 2020-07-02 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40759119 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0063285 | 16.0306
119303780 | B | LC | ETL.8060.POLE.WOOD | 40751901 | SACTO | SIERRA | 2020-07-02 | 2020-09-30 | ETL.8060 | SPAULDING-SUMMIT | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751901 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.023973 | 221.6944
119304351 | E | LC | ETL.8170.POLE.WOOD | 40602091 | EUREKA | HUMBOLDT | 2020-07-02 | 2021-11-22 | ETL.8170 | TRINITY-MAPLE CREEK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602091 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-04-21 | Polymer | Dead End |  |  |  |  | 0.019222 | 15.8815 | 0.30527
119310705 | F | LC | ETL.8060.POLE.WOOD | 40761669 | SACTO | SIERRA | 2020-07-02 | 2021-08-23 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761669 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.008691 | 1131.3246
119314528 | E | LC | ETL.1110.POLE.WDPS | 44550736 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44550081 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0011098 | 5651.1868
119316085 | E | LC | ETL.1470.POLE.WOOD | 41176327 | LAKEVLLE | SONOMA | 2020-07-06 | 2021-03-08 | ETL.1470 | EAGLE ROCK-CORTINA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41176327 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Non Ceramic | Post |  |  |  |  | 0.0057865 | 0.065149
119317599 | E | LC | ETL.6290.POLE.WOOD | 40614982 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-09-14 | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40614982 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.024313 | 1202.1041
119317719 | F | LC | ETL.7270.POLE.WOOD | 40906095 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906095 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0026062 | 759.5581
119325262 | E | LC | ETL.6950.POLE.WOOD | 40661281 | SACTO | SACRAMENTO | 2020-07-07 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40661281 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.013406 | 1534.4731 | 20.5708
119328882 | E | LC | ETL.7030.POLE.WOOD | 40815888 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-07-06 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119332426 | B | LC | ETL.6980.POLE.WOOD | 40584664 | LAKEVLLE | SONOMA | 2020-07-08 | 2020-08-03 | ETL.6980 | FORT ROSS-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40584664 | 1953-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.49356 | 0.065147
119335411 | F | LC | ETL.4040.POLE.STPS | 44647159 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-04-01 | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44646920 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00010378 | 2223.9963
119335751 | F | LC | ETL.6770.POLE.NWOD | 44874803 | SACTO | SIERRA | 2020-07-07 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44874803 | 2019-04-24 | Light Duty Steel Pole | T-1 - Tri Post | 2019-04-24 | Polymer | Post |  |  |  |  | 0.00026903 | 506.3281
119339204 | E | LC | ETL.8060.POLE.WOOD | 40770653 | SACTO | SACRAMENTO | 2020-07-09 | 2021-08-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770653 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0047152 | 95.1488
119339948 | F | LC | ETL.6900.POLE.WOOD | 40823370 | LAKEVLLE | SONOMA | 2020-07-09 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40823370 | 1986-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Polymer | Suspension |  |  |  |  | 1.2496e-06 | 1613.9003
119355923 | F | LC | ETL.6280.POLE.WOOD | 40864711 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Non-HFTD | Non-HFRA | PEND | 40864711 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Other |  |  |  |  | 1.6147e-05 | 4020.1462
119357830 | E | LC | ETL.7270.POLE.WOOD | 44649313 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44649313 | 2018-08-17 | Single Wood Pole | T2N | 2018-08-17 | Polymer | Post |  |  |  |  | 0.0011677 | 379.78 | 0.44345
119367911 | F | LC | ETL.6280.POLE.WOOD | 40824643 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-07-01 | ETL.6280 | CARIBOU #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119374939 | F | LC | ETL.1820.POLE.NWOD | 44789678 | EUREKA | HUMBOLDT | 2020-07-14 | 2021-01-19 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44789678 | 2019-04-29 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-04-29 | Glass | Suspension |  |  |  |  | 0.19564 | 189.8987
119374965 | F | LC | ETL.1820.POLE.NWOD | 44789694 | EUREKA | HUMBOLDT | 2020-07-14 | 2021-01-19 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44789694 | 2019-04-29 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-04-29 | Glass | Suspension |  |  |  |  | 0.19564 | 189.8987
119378298 | F | LC | ETL.7030.POLE.WOOD | 40671148 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2020-12-23 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119379763 | F | LC | ETL.6220.POLE.WOOD | 40824448 | EUREKA | HUMBOLDT | 2020-07-15 | 2021-02-01 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40824448 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 0.081232 | 5040.4707
119462210 | E | LC | ETL.6380.POLE.NWOD | 44262517 | LAKEVLLE | SONOMA | 2020-07-16 | 2021-04-26 | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119462211 | E | LC | ETL.6380.POLE.WOOD | 40615068 | LAKEVLLE | SONOMA | 2020-07-16 | 2021-03-11 | ETL.6380 | KONOCTI-MIDDLETOWN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40615068 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Other |  |  |  |  | 1.1033e-08 | 1901.5002
119478997 | E | LC | ETL.1110.INSL | 40611005 | EUREKA | HUMBOLDT | 2020-07-20 | 2021-08-04 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586445 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.323e-05 | 0.065152
119492483 | E | LC | ETL.1450.POLE.WDPS | 44553916 | SACTO | SIERRA | 2020-07-22 | 2021-01-20 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44553916 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0021418
119492483 | E | LC | ETL.1450.POLE.WDPS | 44553916 | SACTO | SIERRA | 2020-07-22 | 2021-01-20 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44553916 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0021418
119504624 | F | LC | ETL.1890.TOWR | 40646713 | FRESNO | FRESNO | 2020-07-23 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40646713 | 1982-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1982-01-01 | Porcelain | Suspension |  |  |  |  | 1.0711e-07
119522774 | F | LC | ETL.7490.POLE.WDPS | 44779053 | EUREKA | HUMBOLDT | 2020-07-29 |  | ETL.7490 | MAPLE CREEK-HOOPA | Animal Guard-Wood | Missing | [Install] | Tier2 |  |  | PEND
119533931 | F | LC | ETL.1470.POLE.WOOD | 41176415 | LAKEVLLE | HUMBOLDT | 2020-07-30 | 2021-02-16 | ETL.1470 | EAGLE ROCK-CORTINA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 41176415 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Porcelain | Post |  |  |  |  | 0.0026941 | 5079.5444
119536962 | F | LC | ETL.6380.POLE.WOOD | 40860828 | LAKEVLLE | HUMBOLDT | 2020-07-31 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40860828 |  | Single Wood Pole | T2N | 2018-09-29 | Polymer | Post |  |  |  |  | 3.3377e-05 | 5177.0571
119537216 | E | LC | ETL.6760.POLE.WOOD | 40756212 | SACTO | SACRAMENTO | 2020-07-31 | 2020-09-09 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119542898 | A | LC | ETL.6480.POLE.NWOD | 44695497 | SACTO | SACRAMENTO | 2020-08-01 | 2020-08-13 | ETL.6480 | COLGATE-CHALLENGE | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44695497 | 2018-12-10 | Light Duty Steel Pole | T2N | 2018-12-10 | Polymer | Post |  |  |  |  | 0.021949 | 348.1483
119551391 | F | LC | ETL.4392.TOWR | 41129373 | LAKEVLLE | SONOMA | 2020-08-03 | 2021-11-15 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129373 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.00033265 | 740.6124
119551391 | F | LC | ETL.4392.TOWR | 41129373 | LAKEVLLE | SONOMA | 2020-08-03 | 2021-11-15 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129373 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.00033265 | 740.6124
119560382 | B | LC | ETL.7180.POLE.WOOD | 40825705 | LAKEVLLE | NORTH BAY | 2020-08-04 | 2020-11-06 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40825705 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 4.9099e-05 | 411.2508
119566866 | F | LC | ETL.6980.POLE.WOOD | 40808288 | LAKEVLLE | SONOMA | 2020-08-06 |  | ETL.6980 | FORT ROSS-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40808288 | 1969-01-01 | Single Wood Pole | 3HP - 3 Horizontal Post | 1953-01-01 | Polymer | Suspension |  |  |  |  | 0.46354 | 158.3606
119600640 | F | LC | ETL.9210.POLE.WOOD | 40822442 | MIDWAY | KERN | 2020-08-11 |  | ETL.9210 | TAFT-CUYAMA #2 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40822442 | 1946-01-01 | Single Wood Pole | T-1 - Tri Post | 1946-01-01 | Polymer | Post |  |  |  |  | 0.045162
119603403 | F | LC | ETL.1073.POLE.WDPS | 44774780 | VICTOR | STOCKTON | 2020-08-12 | 2021-02-09 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Wood | Missing | [Install] |  | Tier 3 | Within Both | DLFL | 40803732 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00038544 | 15.88
119612463 | B | LC | ETL.8650.TOWR | 40819683 | FRESNO | FRESNO | 2020-08-13 | 2020-12-09 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40819683 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1929-01-01 | Porcelain | Suspension |  |  |  |  | 0.0020352 | 6915.5117
119643328 | B | LC | ETL.8650.TOWR | 40595489 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40595489 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1929-01-01 | Ceramic | Suspension |  |  |  |  | 0.0044596 | 3210.4758
119674087 | B | LC | ETL.5780.TOWR | 40811161 | VICTOR | STOCKTON | 2020-08-26 | 2020-12-04 | ETL.5780 | TIGER CREEK-ELECTRA | Other | Customer Issue | [Customer Refusal, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40811161 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1931-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.7899e-06 | 79.1577
119682358 | E | LC | ETL.1420.TOWR | 40873409 | SACTO | SACRAMENTO | 2020-08-27 | 2020-12-04 | ETL.1420 | DRUM-RIO OSO #1 | Vegetation-Tower | Overgrown | [Cage Clearing, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40873409 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2016-08-08 | Ceramic | Suspension |  |  |  |  | 8.4891e-07 | 775.2733
119692813 | F | LC | ETL.7270.POLE.NWOD | 44649255 | TABLEMTN | NORTH VALLEY | 2020-08-29 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44649255 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.0017832 | 1550.618
119722872 | E | LC | ETL.6470.POLE.WOOD | 40824250 | SACTO | SIERRA | 2020-08-10 | 2021-07-29 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40824250 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.016711 | 395.6266
119741795 | E | LC | ETL.5960.TOWR | 40746867 | FRESNO | FRESNO | 2020-09-10 | 2021-07-15 | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40746867 | 1973-01-01 | LATTICE STEEL TOWER | SUSP-A - Suspension Angle (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 0.0008001
119743373 | B | LC | ETL.6770.INSL.NCER | 40610585 | SACTO | SIERRA | 2020-09-10 | 2020-11-30 | ETL.6770 | DRUM-SPAULDING | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119783561 | A | LC | ETL.4220.POLE.WOOD | 40649821 | TABLEMTN | NORTH VALLEY | 2020-09-18 | 2020-10-15 | ETL.4220 | WOODLEAF-PALERMO | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119796427 | F | LC | ETL.1330.TOWR | 40869584 | LAKEVLLE | SONOMA | 2020-09-22 |  | ETL.1330 | CORTINA-MENDOCINO #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40869584 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 9.5653e-05 | 2171.0598
119797298 | F | LC | ETL.6950.POLE.WOOD | 40654868 | SACTO | SIERRA | 2020-08-04 |  | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40654868 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00070172 | 4006.7029
119814364 | E | LC | ETL.8300.POLE.WOOD | 40615921 | TABLEMTN | NORTH VALLEY | 2020-09-25 | 2021-07-22 | ETL.8300 | VOLTA-SOUTH | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40615921 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.016682 | 4039.3728
119816229 | F | LC | ETL.3742.POLE.WOOD | 41135443 | CONCORD | DIABLO | 2020-08-29 |  | ETL.3742 | SOBRANTE-MORAGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41135443 | 1969-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1999-01-01 | Non Ceramic | Post |  |  |  |  | 4.9854e-05 | 79.1467
119826466 | B | LC | ETL.6880.POLE.WOOD | 40809007 | LAKEVLLE | NORTH BAY | 2020-09-28 | 2020-10-20 | ETL.6880 | FULTON-CALISTOGA | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119847347 | F | LC | ETL.1110.POLE.WDPS | 44561134 | TABLEMTN | HUMBOLDT | 2020-09-08 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44515892 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00058003 | 5302.9683
119887555 | F | LC | ETL.7030.POLE.WOOD | 40868430 | TABLEMTN | NORTH VALLEY | 2020-10-05 | 2021-05-11 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40868430 |  | Single Wood Pole | T2N | 2021-05-03 | Polymer | Post |  |  |  |  | 0.0068951 | 6157.7817
119915805 | F | LC | ETL.6980.POLE.WDPS | 44312250 | LAKEVLLE | SONOMA | 2020-10-16 | 2021-02-10 | ETL.6980 | FORT ROSS-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | DLFL
119921260 | E | LC | ETL.6380.POLE.WOOD | 40768970 | LAKEVLLE | HUMBOLDT | 2020-10-16 | 2021-03-03 | ETL.6380 | KONOCTI-MIDDLETOWN | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768970 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Other |  |  |  |  | 6.4333e-05 | 6683.7227
119928063 | E | LC | ETL.5970.TOWR | 40753873 | PISMOBCH | LOS PADRES | 2020-10-20 | 2021-04-29 | ETL.5970 | DIABLO-MIDWAY #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40753873 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 4.7466e-11 | 2533.0825
119931787 | E | LC | ETL.4309.POLE.WOOD | 41104278 | LAKEVLLE | SONOMA | 2020-10-20 |  | ETL.4309 | SANTA ROSA-CORONA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41104278 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Non Ceramic | Post |  |  |  |  | 0.0045384 | 174.3384 | 0.79122
119995953 | F | LC | ETL.7270.POLE.NWOD | 44649319 | TABLEMTN | NORTH VALLEY | 2020-10-07 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44649319 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.0020151 | 126.6494
119997131 | F | LC | ETL.2090.TOWR | 40871076 | METCALF | SAN JOSE | 2020-11-08 |  | ETL.2090 | LAWRENCE-MONTA VISTA | Road | Brush Fuel | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40871076 | 1942-01-01 | LATTICE STEEL TOWER | DE - Dead End | 1998-01-01 | Porcelain | Dead End |  |  |  |  | 1.1341e-08 | 1140.4965
120001872 | E | LC | ETL.6020.INSL | 40845626 | TABLEMTN | NORTH VALLEY | 2020-11-09 | 2021-06-15 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40817711 | 1993-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 8.1949e-08 | 142.4835
120026559 | E | LC | ETL.1450.POLE.WDPS | 44557672 | SACTO | SACRAMENTO | 2020-11-12 | 2021-09-28 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44554054 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.05406 | 1123.6396
120110853 | F | LC | ETL.8365.POLE.NWOD | 40912547 | EUREKA | HUMBOLDT | 2020-11-20 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40912547 | 2010-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Dead End |  |  |  |  | 0.00036579
120120687 | E | LC | ETL.6720.POLE.STPS | 44949090 | TABLEMTN | NORTH VALLEY | 2020-11-30 | 2021-03-02 | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44860100 | 2019-12-06 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 6.04e-07 | 15.8851
120125425 | F | LC | ETL.8365.POLE.WDPS | 44403643 | EUREKA | HUMBOLDT | 2020-11-30 | 2021-02-01 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44403643 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle |  | Polymer | Suspension |  |  |  |  | 0.047823
120125425 | F | LC | ETL.8365.POLE.WDPS | 44403643 | EUREKA | HUMBOLDT | 2020-11-30 | 2021-02-01 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44403643 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle |  | Polymer | Suspension |  |  |  |  | 0.047823
120125425 | F | LC | ETL.8365.POLE.WDPS | 44403643 | EUREKA | HUMBOLDT | 2020-11-30 | 2021-02-01 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44403643 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle |  | Polymer | Suspension |  |  |  |  | 0.047823
120161428 | E | LC | ETL.1050.TOWR | 40816899 | FRESNO | FRESNO | 2020-12-10 | 2021-08-04 | ETL.1050 | BALCH-SANGER | Connector | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816899 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1923-01-01 | Porcelain | Suspension |  |  |  |  | 0.0012174 | 6854.0659
120226019 | E | LC | ETL.2410.SWIT | 41119845 | LAKEVLLE | SONOMA | 2020-12-21 | 2021-11-16 | ETL.2410 | MENDOCINO-REDBUD | Switch | Out of Adjustment | [Repair, Completed] | Tier2 |  |  | COMP | [8 empty] | Other | ARCING HORNS ONLY | Manual
120672439 | E | LC | ETL.7630.INSL.CERA | 40676329 | LAKEVLLE |  | 2021-03-22 |  | ETL.7630 | MONTE RIO-FULTON | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40648449 | 1952-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.17945 | 94.985 | 17.0454
120696294 | B | LC | ETL.1530.POLE.NWOD | 44196531 | SACTO | SACRAMENTO | 2021-03-26 | 2021-05-13 | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44196531 | 2015-05-19 | Light Duty Steel Pole | T-1 - Tri Post | 2015-05-19 | Polymer | Post |  |  |  |  | 4.0649e-07 | 126.6259
120718012 | E | LC | ETL.2900.TOWR | 40595227 | MOSSLNDG | CENTRAL COAST | 2021-03-31 | 2021-06-02 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Raptor Guard-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40595227 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0011156 | 860.535
120734924 | E | LC | ETL.4040.INSL.CERA | 44646949 | TABLEMTN | NORTH VALLEY | 2021-04-02 | 2021-10-06 | ETL.4040 | TRINITY-COTTONWOOD | Damper-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44646909 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | 2018-08-17 | Ceramic | Suspension |  |  |  |  | 0.00094373
120734924 | E | LC | ETL.4040.INSL.CERA | 44646949 | TABLEMTN | NORTH VALLEY | 2021-04-02 | 2021-10-06 | ETL.4040 | TRINITY-COTTONWOOD | Damper-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44646909 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | 2018-08-17 | Ceramic | Suspension |  |  |  |  | 0.00094373
120750551 | E | LC | ETL.3840.INSL.CERA | 40896340 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40872232 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 0.00022251 | 5666.2915 | 1.2608
120750621 | F | LC | ETL.7040.POLE.WOOD | 40758225 | TABLEMTN | NORTH VALLEY | 2021-04-06 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758225 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.044774 | 1364.1134
120760109 | F | LC | ETL.8350.POLE.WOOD | 40579960 | VICTOR | STOCKTON | 2021-04-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40579960 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 2.4547e-05 | 571.9987
120786978 | E | LC | ETL.8250.POLE.WOOD | 40607075 | VICTOR | STOCKTON | 2021-04-10 | 2021-08-11 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120787316 | E | LC | ETL.6030.TOWR | 40648028 | MIDWAY | KERN | 2021-04-10 | 2021-04-23 | ETL.6030 | MIDWAY-WHIRLWIND | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40648028 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-12-09 | Glass Silicone Coated | Suspension |  |  |  |  | 4.1916e-06 | 6906.6963
120796694 | E | LC | ETL.7270.POLE.WOOD | 40701679 | TABLEMTN | NORTH VALLEY | 2021-04-12 |  | ETL.7270 | KESWICK-TRINITY | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40701679 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0034973 | 2708.5825 | 9.4727
120812345 | E | LC | ETL.5300.INSL | 40781981 | PISMOBCH | LOS PADRES | 2021-04-14 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40753265 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 6.2352e-06 | 984.3804 | 0.0061379
120812408 | F | LC | ETL.9100.POLE.WOOD | 44191867 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191867 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 4.4177e-06 | 2581.5518
120816155 | E | LC | ETL.5660.TOWR | 40761885 | CONCORD | DIABLO | 2021-04-14 |  | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40761885 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Dead End |  |  |  |  | 1.7671e-08 | 2709.8901 | 4.7887e-05
120851704 | E | LC | ETL.4393.INSL.NCER | 45076991 | SACTO | SIERRA | 2021-04-20 |  | ETL.4393 | DRUM-HIGGINS | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45076977 | 2021-04-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2021-04-10 | Glass | Suspension |  |  |  |  | 2.8175e-10
120851704 | E | LC | ETL.4393.INSL.NCER | 45076991 | SACTO | SIERRA | 2021-04-20 |  | ETL.4393 | DRUM-HIGGINS | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45076977 | 2021-04-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2021-04-10 | Glass | Suspension |  |  |  |  | 2.8175e-10
120857762 | B | LC | ETL.2910.INSL.CERA | 40781989 | MOSSLNDG | CENTRAL COAST | 2021-04-20 | 2021-05-06 | ETL.2910 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752787 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1963-01-01 | Porcelain | Dead End |  |  |  |  | 0.08739 | 841.4142
120861281 | E | LC | ETL.4316.TOWR | 40599217 | TABLEMTN | NORTH VALLEY | 2021-04-21 | 2021-07-27 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40599217 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-18 | Glass | Suspension |  |  |  |  | 0.0011241 | 2883.9575
120863031 | F | LC | ETL.1400.POLE.NWOD | 44948151 | VICTOR | STOCKTON | 2021-04-21 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44948151 | 2019-09-25 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-09-25 | Glass | Suspension |  |  |  |  | 4.736e-05 | 31.7081
120864195 | E | LC | ETL.1400.POLE.WDPS | 44774095 | VICTOR | STOCKTON | 2020-07-01 | 2021-06-01 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120865687 | E | LC | ETL.6470.POLE.WOOD | 40817325 | SACTO | SACRAMENTO | 2021-04-22 | 2021-08-12 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817325 |  | Single Wood Pole | T2N | 2018-11-28 | Polymer | Post |  |  |  |  | 0.012402 | 1060.0317
120871008 | E | LC | ETL.5780.TOWR | 40811159 | VICTOR | STOCKTON | 2021-04-22 |  | ETL.5780 | TIGER CREEK-ELECTRA | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40811159 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 0.00068133 | 1202.2845 | 0.81916
120873332 | E | LC | ETL.3770.TOWR | 40746171 | CONCORD | DIABLO | 2021-04-23 |  | ETL.3770 | SOBRANTE-R #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40746171 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1923-01-01 | Ceramic | Suspension |  |  |  |  | 2.1426e-05 | 269.6005 | 0.0057764
120875570 | E | LC | ETL.6890.POLE.WOOD | 40601451 | LAKEVLLE | SONOMA | 2021-04-23 | 2021-10-14 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.00036652 | 1094.799 | 0.40127
120892597 | F | LC | ETL.1530.TOWR | 40660260 | SACTO | SIERRA | 2021-04-13 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40660260 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-07-30 | Ceramic | Dead End |  |  |  |  | 4.109e-05 | 166.4406
120892597 | F | LC | ETL.1530.TOWR | 40660260 | SACTO | SIERRA | 2021-04-13 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40660260 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-07-11 | Ceramic | Dead End |  |  |  |  | 4.109e-05 | 166.4406
120893709 | F | LC | ETL.4850.TOWR | 40858211 | FRESNO | FRESNO | 2021-04-26 | 2021-05-20 | ETL.4850 | HAAS-MCCALL | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40858211 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1957-01-01 | Ceramic | Suspension |  |  |  |  | 1.2163e-08 | 9201.1709
120909451 | B | LC | ETL.6110.INSL | 40631696 | METCALF | SAN JOSE | 2021-04-30 | 2021-06-17 | ETL.6110 | TESLA-METCALF | Insulator | Contaminated | [Ground Wash, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592653 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 7.9354e-08 | 2711.6123
120953396 | E | LC | ETL.7060.POLE.NWOD | 44185659 | METCALF | SAN JOSE | 2021-05-08 | 2021-08-30 | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | HFRA Removal | COMP | 44185659 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | [5 empty] | 1.8682e-07 | 665.295
121047827 | E | LC | ETL.2910.INSL.NCER | 40835360 | MOSSLNDG | CENTRAL COAST | 2021-04-15 |  | ETL.2910 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810462 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2008-01-01 | Polymer | Suspension |  |  |  |  | 0.1197 | 475.4211 | 56.9067
121190098 | E | LC | ETL.8250.POLE.WOOD | 40912849 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40912849 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00018015 | 2931.7273 | 0.52816
121190538 | F | LC | ETL.4440.TOWR | 40760920 | TABLEMTN | NORTH VALLEY | 2021-05-11 |  | ETL.4440 | CARIBOU-TABLE MTN | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40760920 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-12-22 | Ceramic | Suspension |  |  |  |  | 3.2163e-07 | 1012.8475
121190615 | E | LC | ETL.1820.POLE.WDPS | 44562227 | EUREKA | HUMBOLDT | 2021-05-11 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591243 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.87148 | 395.7131 | 344.8554
121192083 | F | LC | ETL.2740.TOWR | 40581563 | CONCORD | DIABLO | 2021-04-20 |  | ETL.2740 | MORAGA-OAKLAND #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40581563 | 1931-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1960-01-01 | Polymer | Dead End |  |  |  |  | 5.2737e-06 | 0.065147 | 3.4356e-07
121322508 | F | LC | ETL.5330.TOWR | 40810755 | MOSSLNDG | CENTRAL COAST | 2021-04-21 | 2021-10-11 | ETL.5330 | MOSS LANDING-COBURN | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40810755 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 1.1371e-05 | 585.2392
121322508 | F | LC | ETL.5330.TOWR | 40810755 | MOSSLNDG | CENTRAL COAST | 2021-04-21 | 2021-10-11 | ETL.5330 | MOSS LANDING-COBURN | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40810755 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.1371e-05 | 585.2392
121322728 | E | LC | ETL.5540.TOWR | 40866649 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.5540 | POE-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40866649 | 1950-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 3.6886e-08 | 269.2704 | 9.9324e-06
121331942 | F | LC | ETL.2900.TOWR | 40871092 | MOSSLNDG | CENTRAL COAST | 2021-04-21 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40871092 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0051024 | 743.9189 | 3.7957
121351035 | E | LC | ETL.6020.TOWR | 40868974 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40868974 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00022946 | 126.6368 | 0.029058
121378060 | E | LC | ETL.1820.POLE.WDPS | 44563015 | EUREKA | HUMBOLDT | 2021-05-21 | 2021-06-21 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562382 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.020917 | 94.963
121383207 | F | LC | ETL.8000.POLE.NWOD | 44177596 | SACTO | SIERRA | 2021-05-11 | 2021-08-26 | ETL.8000 | SMARTVILLE-NICOLAUS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44177596 | 2013-08-20 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2013-08-20 | Polymer | Post |  |  |  |  | 6.8084e-05 | 3229.2878
121383290 | E | LC | ETL.6500.INSL.NCER | 40639061 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40610897 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 1.3365e-06 | 2473.1323 | 0.0033054
121384189 | F | LC | ETL.8250.POLE.WOOD | 40908800 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908800 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.00090309 | 5094.106
121394068 | F | LC | ETL.8060.POLE.WOOD | 40590044 | SACTO | SIERRA | 2021-05-17 |  | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40590044 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.077758 | 784.8264
121397764 | F | LC | ETL.8060.POLE.WOOD | 40817684 | SACTO | SIERRA | 2021-05-18 | 2021-06-30 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40817684 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.079387 | 617.0731
121399341 | E | LC | ETL.1650.POLE.WOOD | 40771906 | LAKEVLLE | SONOMA | 2021-05-26 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40771906 | 1966-01-01 | Single Wood Pole | WB - Wishbone | 1966-01-01 | Ceramic | Other |  |  |  |  | 0.00011366 | 4860.2104 | 0.55241
121399517 | E | LC | ETL.6950.POLE.WOOD | 40768214 | SACTO | SIERRA | 2021-05-26 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40768214 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0032325 | 1379.443 | 4.459
121405156 | E | LC | ETL.6870.POLE.WOOD | 40768420 | SACTO | SIERRA | 2021-05-19 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40768420 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.042506 | 79.2067 | 3.3668
121422521 | E | LC | ETL.7380.POLE.WOOD | 40617408 | MOSSLNDG | CENTRAL COAST | 2021-05-26 |  | ETL.7380 | LAURELES-OTTER | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40617408 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.93701 | 31.6978 | 29.7012
121425038 | E | LC | ETL.6050.TOWR | 40811346 | MOSSLNDG | CENTRAL COAST | 2021-05-28 |  | ETL.6050 | MOSS LANDING-METCALF | Vegetation | Overgrown | [Trim] | Tier2 | Tier 2 | Within Both | PEND | 40811346 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 2019-08-29 | Glass | Suspension |  |  |  |  | 8.087e-09 | 2595.8459 | 2.0993e-05
121427329 | F | LC | ETL.1420.POLE.STPS | 44415577 | SACTO | SACRAMENTO | 2021-05-26 | 2021-07-26 | ETL.1420 | DRUM-RIO OSO #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44415576 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.2253e-06 | 269.0173
121436017 | E | LC | ETL.9250.INSL | 40608182 | MIDWAY | KERN | 2021-05-21 | 2021-11-02 | ETL.9250 | TEJON-LEBEC | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40583977 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | [5 empty] | 0.014842 | 3692.9529
121436977 | B | LC | ETL.6160.INSL.NCER | 41170692 | CONCORD | EAST BAY | 2021-06-01 | 2021-07-26 | ETL.6160 | LONE TREE-CAYETANO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40586463 | 1995-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2009-01-01 | Non Ceramic | Dead End |  |  |  |  | 2.9168e-08 | 5466.0889
121436977 | B | LC | ETL.6160.INSL.NCER | 41170692 | CONCORD | EAST BAY | 2021-06-01 | 2021-07-26 | ETL.6160 | LONE TREE-CAYETANO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40586463 | 1995-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2009-01-01 | Non Ceramic | Suspension |  |  |  |  | 2.9168e-08 | 5466.0889
121455433 | E | LC | ETL.8350.INSL.NCER | 45082478 | VICTOR | STOCKTON | 2021-06-03 | 2021-08-25 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45082459 | 2021-03-25 | Light Duty Steel Pole | TPS1D - Tri Post & Susp DDE 115 KV | 2021-03-25 | Glass | Dead End |  |  |  |  | 0.00014466 | 1075.7617
121468640 | B | LC | ETL.5630.INSL | 40712411 | TABLEMTN | NORTH VALLEY | 2021-06-02 | 2021-06-14 | ETL.5630 | ROCK CREEK-POE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40659993 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 9.4966e-06 | 4523.73
121485412 | F | LC | ETL.7100.POLE.NWOD | 44768925 | EUREKA | HUMBOLDT | 2021-05-29 |  | ETL.7100 | HUMBOLDT BAY-RIO DELL JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44768925 | 2019-05-23 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2019-05-23 | Polymer | Post |  |  |  |  | 0.0033314 | 205.6675
121485876 | F | LC | ETL.4040.POLE.WDPS | 44558369 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44557904 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.01271 | 253.2084
121486060 | E | LC | ETL.4770.INSL.CERA | 40844705 | LAKEVLLE |  | 2021-05-29 |  | ETL.4770 | GEYSERS #17-FULTON | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40818368 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 7.8025e-08 | 2501.0085 | 0.00019514
121493523 | F | LC | ETL.7610.POLE.WOOD | 40612224 | METCALF | DE ANZA | 2021-06-01 |  | ETL.7610 | MONTA VISTA-LOS GATOS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | HFRA Removal | PEND | 40612224 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00010354 | 0.065147
121495635 | E | LC | ETL.7000.INSL.CERA | 40617442 | TABLEMTN |  | 2021-06-08 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591864 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00048424 | 0.065148 | 3.1547e-05
121500236 | E | LC | ETL.5400.INSL.NCER | 40893357 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5400 | PIT #3-PIT #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40868836 | 1924-01-01 | LATTICE STEEL TOWER | TRP SUSP - Tramp Susp | 1924-01-01 | Glass | Suspension |  |  |  |  | 0.19552 | 94.9939 | 18.5728
121511425 | E | LC | ETL.1450.POLE.WDPS | 44553508 | SACTO | SACRAMENTO | 2021-06-10 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553098 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00019861 | 63.348 | 0.012582
121516043 | E | LC | ETL.1600.POLE.NWOD | 44866799 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44866799 | 2019-10-05 | Light Duty Steel Pole | DDE - Double Dead End | 2019-10-05 | Glass | Dead End |  |  |  |  | 7.6048e-07 | 2406.1555 | 0.0018298
121516118 | E | LC | ETL.4040.POLE.STPS | 44784268 | TABLEMTN | NORTH VALLEY | 2021-06-04 |  | ETL.4040 | TRINITY-COTTONWOOD | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44784124 | 2019-07-14 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00021446 | 5212.1279 | 1.1178
121516369 | E | LC | ETL.6130.INSL | 40680722 | VICTOR | STOCKTON | 2021-06-05 |  | ETL.6130 | TRACY-LOS BANOS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40651827 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.2038e-09 | 2022.4012 | 4.4569e-06
121520243 | E | LC | ETL.1450.POLE.WDPS | 44212222 | SACTO | SACRAMENTO | 2021-06-04 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44212221 | 2013-09-30 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012705 | 30.1245 | 0.038273
121520390 | F | LC | ETL.1600.TOWR | 40862873 | LAKEVLLE | NORTH BAY | 2021-06-07 | 2021-09-30 | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40862873 | 1946-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2019-12-16 | Glass | Dead End |  |  |  |  | 2.3549e-07 | 775.2442
121536504 | F | LC | ETL.6852.POLE.WOOD | 40615113 | LAKEVLLE | HUMBOLDT | 2021-06-09 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40615113 |  | Single Wood Pole | T2N | 2018-11-01 | Polymer | Post |  |  |  |  | 0.061166 | 6506.4966
121540463 | E | LC | ETL.7800.POLE.WOOD | 40820912 | SACTO | SACRAMENTO | 2021-06-15 |  | ETL.7800 | PLACER-DEL MAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | PEND | [11 empty] | 1.3176e-05 | 2677.1912 | 0.035274
121541157 | B | LC | ETL.1710.INSL.NCER | 45100581 | MOSSLNDG | CENTRAL COAST | 2021-06-15 | 2021-08-11 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Other | Customer Issue | [Customer Refusal] | Tier3 | Tier 3 | Within Both | DLFL | 40815170 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-06 | Glass | Double Dead End |  |  |  |  | 2.2668e-06 | 0.065147
121541157 | B | LC | ETL.1710.INSL.NCER | 45100581 | MOSSLNDG | CENTRAL COAST | 2021-06-15 | 2021-08-11 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Other | Customer Issue | [Customer Refusal] | Tier3 | Tier 3 | Within Both | DLFL | 40815170 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-05 | Glass | Dead End |  |  |  |  | 2.2668e-06 | 0.065147
121544147 | E | LC | ETL.5390.TOWR | 40817582 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40817582 | 1938-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2019-08-15 | Glass | Suspension |  |  |  |  | 0.000394 | 221.4934 | 0.087268
121562497 | E | LC | ETL.4050.POLE.WDPS | 44558228 | LAKEVLLE | SONOMA | 2021-06-18 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44557942 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.0949e-05 | 4923.8599 | 0.20163
121564171 | E | LC | ETL.9200.POLE.WDPS | 44976208 | MIDWAY | KERN | 2021-06-18 |  | ETL.9200 | TAFT-CUYAMA #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 42696681 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.019248
121573576 | E | LC | ETL.1070.POLE.WOOD | 40580416 | VICTOR | YOSEMITE | 2021-06-17 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40580416 | 1957-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1957-01-01 | Porcelain | Dead End |  |  |  |  | 0.00019139 | 5127.0312 | 0.98128
121588398 | B | LC | ETL.7060.POLE.WOOD | 40599222 | METCALF | SAN JOSE | 2021-06-23 | 2021-06-29 | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Other | Vegetation Overgrown | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40599222 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 2.3137e-05 | 422.9651
121590882 | F | LC | ETL.1070.POLE.WOOD | 40804201 | VICTOR | STOCKTON | 2021-06-22 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40804201 | 1998-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1998-01-01 | Polymer | Post |  |  |  |  | 0.00013004 | 2029.6281 | 0.26393
121596096 | E | LC | ETL.5970.TOWR | 40592846 | PISMOBCH | LOS PADRES | 2021-06-22 |  | ETL.5970 | DIABLO-MIDWAY #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40592846 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 4.5689e-10 | 1236.6721 | 5.6502e-07
121609444 | E | LC | ETL.6762.INSL | 40780191 | SACTO | SACRAMENTO | 2021-06-18 |  | ETL.6762 | ROLLINS TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40751945 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.00056676 | 110.7947 | 0.062794
121609585 | E | LC | ETL.5960.TOWR | 40762971 | PISMOBCH | LOS PADRES | 2021-06-26 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762971 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 3.9808e-06 | 619.6523 | 0.0024667
121628392 | E | LC | ETL.6650.INSL.CERA | 40722802 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44386769 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0031248
121628392 | E | LC | ETL.6650.INSL.CERA | 40722802 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44386769 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0031248
121646841 | F | LC | ETL.4040.POLE.WOOD | 40910717 | TABLEMTN | NORTH VALLEY | 2021-06-30 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40910717 | 1949-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 1949-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.022484 | 443.6022
121653590 | B | LC | ETL.1400.INSL | 40772112 | VICTOR | YOSEMITE | 2021-07-02 | 2021-09-23 | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40744852 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.009221
121653590 | B | LC | ETL.1400.INSL | 40772112 | VICTOR | YOSEMITE | 2021-07-02 | 2021-09-23 | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40744852 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.009221
121655250 | A | LC | ETL.1350.POLE.WDPS | 44549999 | TABLEMTN |  | 2021-07-01 | 2021-07-08 | ETL.1350 | CRAG VIEW-CASCADE | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
121662426 | B | LC | ETL.5730.INSL | 40630914 | CONCORD | EAST BAY | 2021-07-02 | 2021-08-19 | ETL.5730 | TESLA-RAVENSWOOD | Insulator | Contaminated | [Ground Wash, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591031 | 1971-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 2.4413e-07 | 3421.4727
121683939 | E | LC | ETL.9240.TOWR | 43249683 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Structure-Tower | Anti-Climbing Guard | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249683 |  | LATTICE STEEL TOWER | [9 empty] | 1569.4222
121684006 | E | LC | ETL.9240.TOWR | 43249549 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249549 |  | LATTICE STEEL TOWER | [9 empty] | 1143.0077
121685576 | F | LC | ETL.4393.POLE.STPS | 45074198 | SACTO | SIERRA | 2021-07-06 |  | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45074120 | 2021-03-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.1074e-05 | 2056.7583
121690642 | F | LC | ETL.6870.POLE.WOOD | 40873849 | SACTO | SIERRA | 2021-07-06 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40873849 | 1966-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 0.075952 | 0.065152
121705753 | F | LC | ETL.1450.POLE.WOOD | 45018603 | SACTO | SIERRA | 2021-06-27 | 2021-09-29 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 45018603 | 2013-09-30 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2013-09-30 | Ceramic | Suspension |  |  |  |  | 0.00071104 | 427.3257
121707075 | F | LC | ETL.6650.POLE.WDPS | 44561490 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44559156 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0036053 | 903.6237
121714644 | E | LC | ETL.5970.TOWR | 40658618 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.5970 | DIABLO-MIDWAY #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40658618 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-10-03 | Glass | Suspension |  |  |  |  | 4.4879e-07 | 3582.1601 | 0.0016076
121724782 | E | LC | ETL.1820.INSL.CERA | 40781155 | EUREKA | HUMBOLDT | 2021-07-13 | 2021-09-13 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121731695 | F | LC | ETL.9250.POLE.NWOD | 40583839 | MIDWAY | KERN | 2021-07-14 |  | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40583839 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Other |  |  |  |  | 0.028537 | 4896.4937
121731747 | E | LC | ETL.4393.INSL.NCER | 42550110 | SACTO | SACRAMENTO | 2021-06-12 |  | ETL.4393 | DRUM-HIGGINS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42550109 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Polymer | [5 empty] | 0.0022466 | 94.9894 | 0.2134
121733637 | B | LC | ETL.2540.POLE.WDPS | 44551349 | MOSSLNDG | CENTRAL COAST | 2021-07-14 | 2021-08-27 | ETL.2540 | METCALF-GREEN VALLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [12 empty] | 1190.7595
121735236 | F | LC | ETL.1820.POLE.STPS | 44395349 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-10-13 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44395348 | 2020-03-04 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0035393 | 1613.8785
121738385 | F | LC | ETL.1400.POLE.WDPS | 45095802 | VICTOR | YOSEMITE | 2021-07-07 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40579917 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0013675 | 36.4773
121738989 | E | LC | ETL.6750.POLE.WDPS | 44374927 | TABLEMTN | NORTH VALLEY | 2021-07-09 | 2021-07-30 | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44374927 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 2019-04-12 | Glass | Dead End - Suspension |  |  |  |  | 0.00026446
121738989 | E | LC | ETL.6750.POLE.WDPS | 44374927 | TABLEMTN | NORTH VALLEY | 2021-07-09 | 2021-07-30 | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44374927 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 2019-04-12 | Glass | Dead End - Suspension |  |  |  |  | 0.00026446
121741222 | F | LC | ETL.6280.POLE.NWOD | 45021377 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45021377 | 2018-11-07 | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2018-11-07 | Ceramic | Dead End |  |  |  |  | 2.0134e-07 | 1619.6546
121741224 | F | LC | ETL.6240.POLE.WOOD | 40767333 | MOSSLNDG | CENTRAL COAST | 2021-07-13 |  | ETL.6240 | BURNS-LONE STAR #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40767333 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.19872 | 0.065152
121741820 | E | LC | ETL.1420.TOWR | 40756296 | SACTO | SIERRA | 2021-07-13 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40756296 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 0.00052042 | 1234.2582 | 0.64233
121746936 | B | LC | ETL.9340.SWIT | 40625976 | FRESNO | YOSEMITE | 2021-07-15 | 2021-08-21 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP | [8 empty] | KPF | ARCING HORNS ONLY | Manual
121749048 | F | LC | ETL.6500.POLE.WOOD | 40655078 | SACTO | NORTH VALLEY | 2021-07-15 |  | ETL.6500 | COLGATE-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40655078 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2015-08-19 | Ceramic | Dead End - Suspension |  |  |  |  | 0.0021968 | 2947.1846 | 6.4743
121758807 | E | LC | ETL.6280.POLE.WOOD | 40862051 | TABLEMTN | NORTH VALLEY | 2021-07-19 |  | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40862051 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-05-23 | Ceramic | Dead End |  |  |  |  | 3.4543e-05 | 2072.0388 | 0.071575
121767694 | E | LC | ETL.6660.POLE.NWOD | 45084717 | TABLEMTN | NORTH VALLEY | 2021-07-19 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45084717 | 2021-03-04 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-04 | Polymer | Post |  |  |  |  | 1.3879e-10 | 4785.126 | 6.6412e-07
121770919 | F | LC | ETL.2390.POLE.WDPS | 44391139 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44391138 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.1733e-05 | 727.6107
121778156 | E | LC | ETL.1810.POLE.STPS | 45146339 | EUREKA | HUMBOLDT | 2021-07-20 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 45146219 | 2021-05-09 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle
121803870 | E | LC | ETL.5960.TOWR | 40753920 | PISMOBCH | LOS PADRES | 2021-07-26 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40753920 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-11-05 | Glass | Dead End |  |  |  |  | 8.0528e-06 | 79.1393 | 0.00063729
121818179 | E | LC | ETL.5390.TOWR | 40744749 | TABLEMTN | NORTH VALLEY | 2021-07-29 |  | ETL.5390 | PIT #1-COTTONWOOD | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40744749 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-01-13 | Glass | Suspension |  |  |  |  | 3.2509e-07 | 2012.1138 | 0.00065411
121864718 | E | LC | ETL.5410.INSL.NCER | 45128520 | TABLEMTN | NORTH VALLEY | 2021-08-09 |  | ETL.5410 | CARBERRY SW STA-ROUND MTN | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40594855 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-09 | Glass | Suspension |  |  |  |  | 1.5331e-05 | 1745.0076 | 0.026752
121919975 | E | LC | ETL.7575.POLE.WDPS | 44384744 | METCALF | SAN JOSE | 2021-08-18 |  | ETL.7575 | SNEATH LANE-PACIFICA | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44384743 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.36816 | 396.2583 | 145.8879
121985932 | F | LC | ETL.8210.POLE.WOOD | 44372042 | VICTOR | YOSEMITE | 2021-09-01 | 2021-09-16 | ETL.8210 | VALLEY SPRINGS #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44372042 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.011315 | 5638.3501
122105242 | E | LC | ETL.6280.POLE.WOOD | 40651990 | TABLEMTN | NORTH VALLEY | 2021-09-27 |  | ETL.6280 | CARIBOU #2 | Guy Wire-Wood | Missing | [Install] | Tier2 |  |  | PEND | [11 empty] | 1.5033e-05 | 47.5141 | 0.00071428
122232869 | E | LC | ETL.1110.TOWR | 40592241 | TABLEMTN | NORTH VALLEY | 2021-10-20 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40592241 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.00023553 | 94.9939 | 0.022374
118606093 | E | LC | ETL.9090.POLE.WDPS | 44565529 | PISMOBCH | LOS PADRES | 2020-03-04 | 2021-05-27 | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118684206 | E | LC | ETL.6280.POLE.NWOD | 40656532 | TABLEMTN | NORTH VALLEY | 2020-03-12 | 2020-08-25 | ETL.6280 | CARIBOU #2 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40656532 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-01-07 | Polymer | Dead End |  |  |  |  | 2.0885e-05 | 1898.3378
118709423 | A | LC | ETL.1540.INSL | 40712532 | SACTO | SACRAMENTO | 2020-03-16 | 2020-03-17 | ETL.1540 | EL DORADO-MISSOURI FLAT #2 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660247 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 0.0001293 | 704.0812
118917010 | E | LC | ETL.3770.TOWR | 40646639 | CONCORD | EAST BAY | 2020-04-14 | 2021-04-12 | ETL.3770 | SOBRANTE-R #1 | Structure-Steel | Anti-Climbing Guard | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40646639 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-08-29 | Glass | Suspension |  |  |  |  | 1.6303e-06 | 474.6866
118917013 | F | LC | ETL.3770.TOWR | 40646639 | CONCORD | EAST BAY | 2020-04-14 | 2021-01-25 | ETL.3770 | SOBRANTE-R #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40646639 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-08-29 | Glass | Suspension |  |  |  |  | 1.6303e-06 | 474.6866
118917305 | B | LC | ETL.1600.TOWR | 40645129 | LAKEVLLE | NORTH BAY | 2020-04-14 | 2020-04-24 | ETL.1600 | FULTON-PUEBLO | Damper-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40645129 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-06-20 | Glass | Suspension |  |  |  |  | 4.8183e-09 | 79.1687
118917305 | B | LC | ETL.1600.TOWR | 40645129 | LAKEVLLE | NORTH BAY | 2020-04-14 | 2020-04-24 | ETL.1600 | FULTON-PUEBLO | Damper-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40645129 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 4.8183e-09 | 79.1687
118947157 | E | LC | ETL.8290.POLE.WOOD | 40827011 | TABLEMTN | NORTH VALLEY | 2020-04-24 | 2020-05-08 | ETL.8290 | VOLTA-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40827011 |  | Single Wood Pole | T2N | 2019-06-06 | Polymer | Post |  |  |  |  | 6.3744e-05 | 2911.8145
118956964 | F | LC | ETL.6220.INSL.CERA | 40899732 | EUREKA | HUMBOLDT | 2020-04-28 | 2021-04-21 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Jumper-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
118989050 | E | LC | ETL.3770.INSL | 40830932 | CONCORD | EAST BAY | 2020-04-21 | 2021-05-06 | ETL.3770 | SOBRANTE-R #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119004606 | B | LC | ETL.1430.INSL.NCER | 44305001 | SACTO | SACRAMENTO | 2020-05-06 | 2020-08-05 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119030250 | E | LC | ETL.8250.POLE.WOOD | 40588353 | VICTOR | STOCKTON | 2020-03-31 | 2021-03-16 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40588353 | 1957-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | [5 empty] | 6.8241e-05 | 3343.1924
119036385 | B | LC | ETL.8411.POLE.WOOD | 40601567 | LAKEVLLE | HUMBOLDT | 2020-05-14 | 2020-06-08 | ETL.8411 | GARCIA TAP | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601567 | 1961-01-01 | Single Wood Pole | Unknown | [7 empty] | 0.0025679 | 738.6521
119044419 | B | LC | ETL.6980.INSL.NCER | 40710433 | LAKEVLLE |  | 2020-05-15 | 2020-06-04 | ETL.6980 | FORT ROSS-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656433 | 1986-01-01 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.17899 | 47.5118
119047571 | E | LC | ETL.6890.POLE.WOOD | 40648705 | LAKEVLLE | SONOMA | 2020-04-28 | 2021-04-28 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119062816 | B | LC | ETL.7140.INSL | 40779557 | LAKEVLLE | NORTH BAY | 2020-05-20 | 2020-05-27 | ETL.7140 | IGNACIO-BOLINAS #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40750704 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.063834 | 680.8114
119072990 | E | LC | ETL.8300.POLE.WOOD | 40667418 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2021-08-26 | ETL.8300 | VOLTA-SOUTH | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119084547 | F | LC | ETL.8405.POLE.WOOD | 40669382 | SACTO | SIERRA | 2020-05-28 | 2021-10-05 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40669382 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0051828 | 6723.8696
119094123 | E | LC | ETL.3960.TOWR | 40856781 | PISMOBCH | LOS PADRES | 2020-05-15 | 2021-08-03 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40856781 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-07-21 | Glass | Suspension |  |  |  |  | 9.8126e-09 | 4765.5547
119096822 | E | LC | ETL.5250.INSL | 40786488 | CONCORD | EAST BAY | 2020-05-22 | 2021-06-14 | ETL.5250 | MORAGA-CASTRO VALLEY | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756555 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-29 | Glass | Suspension |  |  |  |  | 6.1219e-08 | 174.0283
119096822 | E | LC | ETL.5250.INSL | 40786488 | CONCORD | EAST BAY | 2020-05-22 | 2021-06-14 | ETL.5250 | MORAGA-CASTRO VALLEY | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756555 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 6.1219e-08 | 174.0283
119102114 | E | LC | ETL.1430.TOWR | 40765123 | SACTO | SIERRA | 2020-05-19 | 2021-02-24 | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40765123 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.0029323 | 63.3607
119102714 | F | LC | ETL.6750.POLE.WDPS | 44561473 | TABLEMTN |  | 2020-05-19 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44560763 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0011939 | 522.173
119104215 | F | LC | ETL.6230.POLE.WDPS | 44561479 | MOSSLNDG | CENTRAL COAST | 2020-05-20 | 2020-11-12 | ETL.6230 | BURNS-LONE STAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119113517 | E | LC | ETL.7140.POLE.WOOD | 40584912 | LAKEVLLE | NORTH BAY | 2020-05-29 | 2021-05-24 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119113975 | E | LC | ETL.6760.POLE.WOOD | 40813457 | SACTO | SIERRA | 2020-05-28 | 2021-03-29 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119116258 | F | LC | ETL.6760.POLE.WOOD | 40598631 | SACTO | SIERRA | 2020-05-28 | 2021-03-22 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40598631 |  | Single Wood Pole | T2N | 2021-06-15 | Polymer | Post |  |  |  |  | 0.023086 | 110.8102
119116741 | F | LC | ETL.5490.TOWR | 40581140 | CONCORD | DIABLO | 2020-05-22 | 2021-04-01 | ETL.5490 | PITTSBURG-SAN RAMON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581140 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 0.00030112 | 4357.1626
119118775 | E | LC | ETL.6950.POLE.WOOD | 40768224 | SACTO | SIERRA | 2020-06-02 | 2021-10-13 | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768224 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0011951 | 538.1728 | 0.64319
119119033 | E | LC | ETL.6720.POLE.WOOD | 40751713 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40751713 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00019085 | 79.2789 | 0.01513
119119385 | F | LC | ETL.7290.POLE.WOOD | 40677193 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40677193 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.019895 | 968.9049
119125753 | E | LC | ETL.7490.POLE.WOOD | 44645848 | EUREKA | HUMBOLDT | 2020-05-29 | 2021-08-05 | ETL.7490 | MAPLE CREEK-HOOPA | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44645848 | 2018-08-09 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2018-08-09 | Ceramic | Suspension |  |  |  |  | 0.098731 | 838.3292
119130951 | F | LC | ETL.7300.POLE.WOOD | 44141994 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-03-23 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44141994 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.00020911 | 6446.7676
119144481 | F | LC | ETL.6770.POLE.WOOD | 40700279 | SACTO | SIERRA | 2020-06-04 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND | [11 empty] | 0.02869 | 1344.8513
119148118 | F | LC | ETL.9100.POLE.NWOD | 44772564 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-31 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 5.8782e-07 | 2024.7844
119155623 | E | LC | ETL.6440.POLE.WOOD | 40809847 | TABLEMTN | NORTH VALLEY | 2020-06-09 | 2020-08-27 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809847 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Post |  |  |  |  | 0.0013667 | 2123.7271
119156754 | E | LC | ETL.8170.POLE.WDPS | 44771070 | EUREKA | HUMBOLDT | 2020-06-12 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 2 | Within Both | PEND | 40861539 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.32484 | 79.1467 | 25.7098
119181756 | E | LC | ETL.1420.TOWR | 40588546 | SACTO | SIERRA | 2020-06-11 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40588546 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 4.3744e-06 | 1360.4569 | 0.0059512
119181757 | E | LC | ETL.6470.POLE.WOOD | 40874813 | SACTO | SIERRA | 2020-06-17 | 2021-07-27 | ETL.6470 | COLGATE-ALLEGHANY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40874813 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 0.21774 | 110.8481
119190312 | F | LC | ETL.6310.POLE.WOOD | 40759474 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40759474 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0002549 | 5196.2129
119201238 | E | LC | ETL.1370.INSL.CERA | 40634062 | PISMOBCH | LOS PADRES | 2020-06-23 | 2021-06-29 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119221984 | E | LC | ETL.6770.POLE.WOOD | 40601226 | SACTO | SACRAMENTO | 2020-06-26 | 2021-07-21 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.00037938 | 617.1616
119229114 | B | LC | ETL.6720.POLE.NWOD | 44860101 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2020-07-10 | ETL.6720 | DESABLA-CENTERVILLE | Other | Customer Issue | [Access Issue] | Tier3 |  |  | DLFL
119305163 | F | LC | ETL.7270.POLE.WOOD | 40909429 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-08-25 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40909429 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-10-30 | Glass | Dead End |  |  |  |  | 0.017 | 0.15372
119332921 | E | LC | ETL.7212.POLE.WDPS | 44384407 | METCALF | PENINSULA | 2020-07-07 | 2021-04-22 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44384405 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.041629 | 712.3272
119333893 | F | LC | ETL.6280.POLE.WOOD | 40666797 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-07-29 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40666797 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 4.661e-06 | 0.065148
119334531 | E | LC | ETL.7030.POLE.WOOD | 40827513 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-06-11 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40827513 |  | Single Wood Pole | T2N | 2021-06-08 | Polymer | Post |  |  |  |  | 0.0085347
119334969 | F | LC | ETL.8170.POLE.WOOD | 40604695 | EUREKA | HUMBOLDT | 2020-07-08 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40604695 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.0031364 | 63.351
119337065 | F | LC | ETL.5660.TOWR | 40607999 | CONCORD | DIABLO | 2020-07-09 |  | ETL.5660 | SAN RAMON-MORAGA | Road | Brush Fuel | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40607999 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 9.9902e-07 | 1397.5155
119337065 | F | LC | ETL.5660.TOWR | 40607999 | CONCORD | DIABLO | 2020-07-09 |  | ETL.5660 | SAN RAMON-MORAGA | Road | Brush Fuel | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40607999 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 9.9902e-07 | 1397.5155
119337065 | F | LC | ETL.5660.TOWR | 40607999 | CONCORD | DIABLO | 2020-07-09 |  | ETL.5660 | SAN RAMON-MORAGA | Road | Brush Fuel | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40607999 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.9902e-07 | 1397.5155
119337065 | F | LC | ETL.5660.TOWR | 40607999 | CONCORD | DIABLO | 2020-07-09 |  | ETL.5660 | SAN RAMON-MORAGA | Road | Brush Fuel | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40607999 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.9902e-07 | 1397.5155
119341110 | F | LC | ETL.7030.POLE.WOOD | 40769966 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Other | Other | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40769966 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.016869 | 698.4329
119354766 | E | LC | ETL.7930.POLE.WOOD | 40768296 | MOSSLNDG | CENTRAL COAST | 2020-07-10 |  | ETL.7930 | SALINAS-LAURELES | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40768296 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0043074 | 31.6948 | 0.13652
119356583 | B | LC | ETL.6290.INSL.NCER | 40899936 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2020-09-01 | ETL.6290 | CARIBOU-PLUMAS JCT | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 43250179 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | [5 empty] | 0.024172 | 15.8815
119356820 | E | LC | ETL.6900.POLE.WOOD | 41119964 | LAKEVLLE | SONOMA | 2020-07-10 | 2021-02-12 | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Vegetation | Overgrown | [Trim, Completed] |  | Tier 2 | Within Both | COMP | 41119964 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | [7 empty] | 4.5594e-06 | 395.7669
119359809 | E | LC | ETL.1880.TOWR | 43218143 | FRESNO | FRESNO | 2020-07-13 |  | ETL.1880 | KERCKHOFF #1-KERCKHOFF #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 43218143 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-03-03 | Ceramic | Suspension |  |  |  |  | 1.1923e-06 | 5176.9556 | 0.0061724
119360871 | E | LC | ETL.7030.POLE.WOOD | 40770817 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-05-24 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770817 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0032511 | 6015.0806
119364163 | E | LC | ETL.8060.POLE.WOOD | 40590007 | SACTO | SACRAMENTO | 2020-07-13 | 2021-05-11 | ETL.8060 | SPAULDING-SUMMIT | Hardware-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40590007 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.055376 | 38.0425
119375829 | F | LC | ETL.7030.POLE.WOOD | 40867822 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40867822 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0096552 | 64.0224
119378968 | E | LC | ETL.6220.POLE.WOOD | 40666736 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40666736 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.016993
119470215 | F | LC | ETL.7030.POLE.WOOD | 40861885 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-02-11 | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40861885 |  | Single Wood Pole | T2N | 2021-06-09 | Polymer | Post |  |  |  |  | 0.0029953
119475630 | F | LC | ETL.7160.POLE.WOOD | 44871181 | LAKEVLLE | NORTH BAY | 2020-07-20 |  | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871181 | 2019-09-19 | Single Wood Pole | 1VP - 1 Vertical | 2019-09-19 | Glass | Suspension |  |  |  |  | 0.23317 | 648.5276
119476423 | E | LC | ETL.8405.POLE.WOOD | 40598771 | SACTO | SACRAMENTO | 2020-07-20 | 2021-04-27 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40598771 |  | Single Wood Pole | T2N | 2020-12-16 | Polymer | Post |  |  |  |  | 0.17721 | 1708.8922
119476585 | F | LC | ETL.1110.TOWR | 40765779 | EUREKA | HUMBOLDT | 2020-07-20 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier2 | Tier 2 | Within Both | PEND | 40765779 | 1952-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2020-07-02 | Glass | Suspension |  |  |  |  | 1.4168e-06 | 126.6368 | 0.00017942
119477444 | E | LC | ETL.3742.TOWR | 41135455 | CONCORD | DIABLO | 2020-07-20 |  | ETL.3742 | SOBRANTE-MORAGA | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41135455 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | [5 empty] | 9.7431e-08 | 0.066432 | 6.4725e-09
119485929 | E | LC | ETL.2170.INSL.CERA | 40638245 | SACTO | SACRAMENTO | 2020-07-21 |  | ETL.2170 | MADISON-VACA | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Non-HFTD | Non-HFRA | PEND | 40608770 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.00013148
119489416 | F | LC | ETL.8060.POLE.WOOD | 40770710 | SACTO | SIERRA | 2020-07-22 | 2021-05-13 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Zone 1 | HFRA Removal | COMP | 40770710 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.013322 | 1212.3663
119497885 | F | LC | ETL.6880.POLE.WOOD | 40658395 | LAKEVLLE | SONOMA | 2020-07-23 | 2021-08-02 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40658395 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.019301 | 569.8757
119505009 | F | LC | ETL.8170.POLE.WOOD | 40906361 | EUREKA | HUMBOLDT | 2020-07-21 | 2021-09-01 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40906361 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.01727 | 2469.0088
119516425 | F | LC | ETL.6520.POLE.WOOD | 40826819 | SACTO | SIERRA | 2020-07-23 | 2021-10-07 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826819 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.014522 | 2214.9285
119558739 | F | LC | ETL.7490.POLE.WOOD | 44735744 | EUREKA | HUMBOLDT | 2020-08-04 |  | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44735744 | 2019-03-30 | Single Wood Pole | T-1 - Tri Post | 2019-03-30 | Polymer | Post |  |  |  |  | 0.005304 | 142.4245 | 0.75542
119563670 | E | LC | ETL.7490.POLE.WOOD | 44837836 | EUREKA | HUMBOLDT | 2020-08-05 |  | ETL.7490 | MAPLE CREEK-HOOPA | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44837836 | 2019-09-21 | Single Wood Pole | T2N | 2019-09-21 | Polymer | Post |  |  |  |  | 0.0027724 | 118.7697 | 0.32928
119566665 | E | LC | ETL.1110.INSL.CERA | 40789516 | TABLEMTN | HUMBOLDT | 2020-08-05 | 2021-04-05 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759372 | 1952-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Porcelain | [5 empty] | 0.00022697 | 0.065152
119592623 | F | LC | ETL.8350.POLE.NWOD | 45015285 | VICTOR | STOCKTON | 2020-08-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45015285 | 2020-05-07 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-07 | Glass | Dead End |  |  |  |  | 7.9582e-05 | 537.8945
119612461 | B | LC | ETL.8650.TOWR | 40871008 | FRESNO | FRESNO | 2020-08-13 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871008 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1929-01-01 | Porcelain | Suspension |  |  |  |  | 0.0024058 | 6915.5117
119638441 | B | LC | ETL.8365.POLE.WOOD | 40912494 | EUREKA | HUMBOLDT | 2020-08-19 | 2020-11-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912494 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.069511
119643320 | B | LC | ETL.8650.TOWR | 40584417 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40584417 | 1929-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0049941 | 459.3026
119676494 | E | LC | ETL.3500.TOWR | 40580454 | VICTOR | STOCKTON | 2020-08-26 | 2021-04-12 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40580454 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 8.3699e-05 | 553.8282
119692412 | A | LC | ETL.7590.POLE.WOOD | 40767270 | MOSSLNDG | CENTRAL COAST | 2020-08-30 | 2020-09-19 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119695284 | B | LC | ETL.2720.TOWR | 40805690 | CONCORD | EAST BAY | 2020-08-29 | 2020-11-22 | ETL.2720 | MORAGA-OAKLAND #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805690 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-03 | Polymer | Suspension |  |  |  |  | 6.1461e-05 | 0.065158
119695284 | B | LC | ETL.2720.TOWR | 40805690 | CONCORD | EAST BAY | 2020-08-29 | 2020-11-22 | ETL.2720 | MORAGA-OAKLAND #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805690 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-01 | Polymer | Suspension |  |  |  |  | 6.1461e-05 | 0.065158
119710143 | E | LC | ETL.1120.TOWR | 40645853 | CONCORD | DIABLO | 2020-08-29 | 2021-01-26 | ETL.1120 | BRIGHTON-CLAYTON #1 | Spacer-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40645853 | 1909-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-05-21 | Glass | Suspension |  |  |  |  | 8.2116e-07 | 5588.4961
119712408 | E | LC | ETL.1450.INSL.CERA | 40918353 | SACTO | SACRAMENTO | 2020-08-27 | 2020-10-02 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44551579 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.000107
119712408 | E | LC | ETL.1450.INSL.CERA | 40918353 | SACTO | SACRAMENTO | 2020-08-27 | 2020-10-02 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44551579 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.000107
119720137 | E | LC | ETL.6440.POLE.WOOD | 41144114 | TABLEMTN | NORTH VALLEY | 2020-09-03 | 2021-04-22 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119721047 | A | LC | ETL.6230.POLE.WDPS | 40602886 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-10-13 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602886 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.21807
119721047 | A | LC | ETL.6230.POLE.WDPS | 40602886 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-10-13 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602886 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.21807
119721047 | A | LC | ETL.6230.POLE.WDPS | 40602886 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-10-13 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602886 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.21807
119723406 | E | LC | ETL.8170.INSL.NCER | 40916038 | EUREKA | HUMBOLDT | 2020-08-07 | 2021-06-21 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906369 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.017358 | 2009.6299
119752482 | F | LC | ETL.7270.POLE.WOOD | 40674320 | TABLEMTN | NORTH VALLEY | 2020-08-13 | 2021-08-30 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40674320 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.044288 | 3233.4868
119755180 | F | LC | ETL.8410.POLE.WOOD | 40605935 | LAKEVLLE | HUMBOLDT | 2020-08-25 |  | ETL.8410 | ELK-GUALALA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40605935 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Porcelain | Suspension |  |  |  |  | 0.18933 | 15.8807
119756357 | F | LC | ETL.7390.POLE.WOOD | 44412208 | LAKEVLLE | SONOMA | 2020-09-12 | 2021-09-28 | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44412208 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.087892
119778944 | E | LC | ETL.4070.TOWR | 40608756 | SACTO | SACRAMENTO | 2020-09-17 | 2021-02-11 | ETL.4070 | VACA-SUISUN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40608756 | 1922-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1922-01-01 | Porcelain | Dead End |  |  |  |  | 7.5613e-09 | 9772.5527
119778944 | E | LC | ETL.4070.TOWR | 40608756 | SACTO | SACRAMENTO | 2020-09-17 | 2021-02-11 | ETL.4070 | VACA-SUISUN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40608756 | 1922-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1922-01-01 | Porcelain | Dead End |  |  |  |  | 7.5613e-09 | 9772.5527
119779750 | E | LC | ETL.9090.POLE | 40653422 | PISMOBCH | LOS PADRES | 2020-09-10 | 2021-05-20 | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 40653422 |  | Single Wood Pole | FIG4W - Wood X Arm | 2013-03-18 | Non Ceramic | Suspension |  |  |  |  | 0.0071269 | 1728.2214
119785935 | F | LC | ETL.6220.POLE.WOOD | 40752634 | EUREKA | HUMBOLDT | 2020-09-14 | 2021-02-09 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40752634 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | Dead End |  |  |  |  | 0.0075902 | 682.5942
119789514 | F | LC | ETL.6861.POLE.NWOD | 42754341 | LAKEVLLE | HUMBOLDT | 2020-07-29 |  | ETL.6861 | KONOCTI-EAGLE ROCK | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 42754341 | 2011-01-01 | Tubular Steel Pole | DV-DE - Double Vertical Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 3.892e-07 | 4447.7559
119790511 | F | LC | ETL.7590.POLE.WOOD | 40645493 | MOSSLNDG | DE ANZA | 2020-07-31 |  | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40645493 |  | Single Wood Pole | 3P DDE-A - 3 Pole Double Dead End Angle |  | Non Ceramic | Double Dead End |  |  |  |  | 0.973 | 126.6368
119796706 | F | LC | ETL.3960.TOWR | 40751434 | PISMOBCH | LOS PADRES | 2020-08-04 | 2021-01-12 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751434 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 7.9823e-09 | 1871.3141
119796706 | F | LC | ETL.3960.TOWR | 40751434 | PISMOBCH | LOS PADRES | 2020-08-04 | 2021-01-12 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751434 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 7.9823e-09 | 1871.3141
119808345 | F | LC | ETL.1440.POLE.WOOD | 40814122 | SACTO | SIERRA | 2020-08-12 | 2021-07-06 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40814122 | 1956-01-01 | Single Wood Pole | 3P DV - 3 Pole Double Vertical | 1956-01-01 | Ceramic | Dead End |  |  |  |  | 0.021336 | 1260.556
119834215 | F | LC | ETL.2395.POLE.WDPS | 44403545 | TABLEMTN |  | 2020-09-08 |  | ETL.2395 | GRIZZLY TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
119838774 | E | LC | ETL.8060.POLE.WOOD | 40618256 | SACTO | SIERRA | 2020-10-01 | 2021-02-12 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40618256 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Polymer | Dead End - Pin |  |  |  |  | 0.0046114 | 63.348
119871717 | E | LC | ETL.7030.POLE.WOOD | 40598392 | TABLEMTN | NORTH VALLEY | 2020-10-02 | 2021-06-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40598392 |  | Single Wood Pole | T2N | 2021-05-05 | Polymer | Post |  |  |  |  | 0.0043939 | 6268.4326
119898451 | E | LC | ETL.6520.POLE.WOOD | 40828234 | SACTO | SIERRA | 2020-10-07 | 2021-06-09 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40828234 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 0.083521 | 744.7016
119912621 | B | LC | ETL.5933.TOWR | 40762765 | PISMOBCH | LOS PADRES | 2020-10-09 | 2020-11-05 | ETL.5933 | MORRO BAY-TEMPLETON | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40762765 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 9.3179e-07 | 142.5251
119917367 | F | LC | ETL.6330.POLE.WOOD | 44191939 | TABLEMTN | NORTH VALLEY | 2020-09-21 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
119932172 | F | LC | ETL.1073.POLE.WOOD | 40643758 | VICTOR | STOCKTON | 2020-10-20 | 2021-04-23 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40643758 | 1956-01-01 | Single Wood Pole | 3P TRP D - 3 Pole Tramp Double Dead End | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00058615 | 31.7081
119992576 | B | LC | ETL.8960.POLE.WOOD | 40588558 | FRESNO | YOSEMITE | 2020-11-03 | 2021-06-24 | ETL.8960 | LOS BANOS-PACHECO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40588558 | 1979-01-01 | Single Wood Pole | SUSP - Suspension (TWR) | 1979-01-01 | Glass | Suspension |  |  |  |  | 0.00016239
119995945 | F | LC | ETL.6760.POLE.WOOD | 40611285 | SACTO | SIERRA | 2020-10-06 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40611285 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.019375 | 31.7022
120069638 | E | LC | ETL.6060.TOWR | 40759985 | TABLEMTN | NORTH VALLEY | 2020-11-18 | 2021-06-14 | ETL.6060 | ROUND MTN-TABLE MTN #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40759985 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 9.9515e-05 | 190.8412
120139393 | F | LC | ETL.6280.POLE.WOOD | 40861867 | TABLEMTN | NORTH VALLEY | 2020-10-29 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40861867 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Other |  |  |  |  | 0.0001481 | 1376.0835
120233471 | E | LC | ETL.1600.POLE.NWOD | 44865397 | LAKEVLLE | SACRAMENTO | 2020-12-24 | 2021-06-30 | ETL.1600 | FULTON-PUEBLO | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44865397 | 2019-12-16 | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 2019-12-16 | Glass | Suspension |  |  |  |  | 1.7521e-07 | 3143.4478
120658285 | F | LC | ETL.4223.POLE.WDPS | 45099511 | TABLEMTN | NORTH VALLEY | 2021-03-18 | 2021-07-29 | ETL.4223 | KANAKA TAP | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42567883 | 1964-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0013958 | 743.6169
120667406 | F | LC | ETL.4222.POLE.NWOD | 44383496 | TABLEMTN | NORTH VALLEY | 2021-03-20 |  | ETL.4222 | FORBESTOWN TAP | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44383496 | 2017-09-16 | Light Duty Steel Pole | 3P DDE - 3 Pole Double Dead End | 2017-09-16 | Polymer | Dead End |  |  |  |  | 3.397e-06 | 537.9951
120671518 | F | LC | ETL.4920.TOWR | 40872696 | LAKEVLLE | SONOMA | 2021-03-22 |  | ETL.4920 | IGNACIO-SOBRANTE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40872696 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 5.3248e-05 | 1427.1888 | 0.075995
120689677 | F | LC | ETL.5330.TOWR | 40752941 | MOSSLNDG | CENTRAL COAST | 2021-03-24 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40752941 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 4.8912e-06 | 790.9332 | 0.0038686
120689677 | F | LC | ETL.5330.TOWR | 40752941 | MOSSLNDG | CENTRAL COAST | 2021-03-24 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40752941 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 4.8912e-06 | 790.9332 | 0.0038686
120696477 | E | LC | ETL.1710.POLE.WDPS | 44513715 | MOSSLNDG | CENTRAL COAST | 2021-03-26 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44512284 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 7.3951e-05 | 31.6948 | 0.0023439
120700517 | F | LC | ETL.3770.TOWR | 40746173 | CONCORD | DIABLO | 2021-03-27 |  | ETL.3770 | SOBRANTE-R #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | PEND | 40746173 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-08-29 | Glass | Suspension |  |  |  |  | 8.9435e-06 | 0.066432 | 5.9413e-07
120706186 | F | LC | ETL.4316.POLE.NWOD | 44674850 | TABLEMTN | NORTH VALLEY | 2021-03-25 |  | ETL.4316 | PARADISE-TABLE MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44674850 | 2018-11-15 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-18 | Polymer | Post |  |  |  |  | 0.00017026 | 2867.8025
120712758 | E | LC | ETL.1650.POLE.STPS | 44298349 | LAKEVLLE | SONOMA | 2021-03-30 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44298348 | 2018-05-16 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 8.372e-08 | 3610.0372 | 0.00030223
120751317 | E | LC | ETL.1530.POLE.NWOD | 40861985 | SACTO | SIERRA | 2021-03-29 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Hardware-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40861985 | 1980-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 2.0808e-06 | 0.066432 | 1.3823e-07
120764479 | E | LC | ETL.5090.INSL | 40885036 | MOSSLNDG | CENTRAL COAST | 2021-04-08 |  | ETL.5090 | MONTA VISTA-COYOTE SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40862880 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0025847 | 15.8866 | 0.041061
120770567 | E | LC | ETL.6880.POLE.NWOD | 44928868 | LAKEVLLE | SONOMA | 2021-04-09 | 2021-07-22 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44928868 | 2020-06-07 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-06-07 | Glass | Dead End |  |  |  |  | 1.8099e-06 | 3025.6633
120773734 | E | LC | ETL.6390.POLE.NWOD | 45073094 | LAKEVLLE | HUMBOLDT | 2021-04-09 |  | ETL.6390 | CLEAR LAKE-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45073094 | 2021-03-24 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-24 | Polymer | Post |  |  |  |  | 4.1142e-09 | 1354.7244 | 5.5736e-06
120794361 | E | LC | ETL.8250.INSL.NCER | 44194070 | VICTOR | STOCKTON | 2021-04-12 | 2021-08-10 | ETL.8250 | CLAY-MARTEL | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44194067 | 2014-05-08 | Single Wood Pole | TH - TriAngle Post 70 | 2014-05-08 | Polymer | Post |  |  |  |  | 2.7283e-05 | 1036.1259
120799241 | F | LC | ETL.8365.POLE.WOOD | 40912593 | EUREKA | HUMBOLDT | 2021-04-12 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Vegetation | Overgrown | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40912593 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Pin |  |  |  |  | 0.089183
120824616 | A | LC | ETL.2390.POLE.WDPS | 44391058 | VICTOR | STOCKTON | 2021-04-15 | 2021-04-21 | ETL.2390 | MELONES-CURTIS | Emergency | Storm Related | [Replace, Completed] | Tier2 |  |  | COMP
120842134 | F | LC | ETL.3820.TOWR | 40811284 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40811284 | 1910-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post |  | Polymer | Post |  |  |  |  | 1.1622e-06 | 4067.2603
120842134 | F | LC | ETL.3820.TOWR | 40811284 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40811284 | 1910-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post |  | Polymer | [5 empty] | 1.1622e-06 | 4067.2603
120859484 | F | LC | ETL.5300.TOWR | 40576866 | PISMOBCH | LOS PADRES | 2021-04-12 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576866 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00012409 | 748.8279 | 0.092919
120859776 | F | LC | ETL.5330.TOWR | 40762313 | MOSSLNDG | CENTRAL COAST | 2021-04-13 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762313 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 3.5349e-06 | 284.7448 | 0.0010065
120859870 | F | LC | ETL.1820.POLE.STPS | 44918942 | EUREKA | HUMBOLDT | 2021-04-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44918840 | 2019-04-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014233 | 63.3274
120860719 | E | LC | ETL.8640.POLE.WOOD | 40651790 | FRESNO | FRESNO | 2021-04-21 |  | ETL.8640 | EXCHEQUER-MARIPOSA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40651790 | 1976-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1976-01-01 | Porcelain | Post |  |  |  |  | 2.0143e-05 | 6742.4971 | 0.13582
120861462 | F | LC | ETL.2700.TOWR | 40580781 | CONCORD | DIABLO | 2021-04-21 | 2021-06-14 | ETL.2700 | MORAGA-CLAREMONT #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 |  |  | DLFL
120868548 | F | LC | ETL.4000.INSL.NCER | 44959578 | VICTOR | YOSEMITE | 2021-04-21 |  | ETL.4000 | TESLA-SALADO-MANTECA | Conductor-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40912750 | 1925-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2020-08-12 | Glass | Suspension |  |  |  |  | 0.059533 | 1840.5094
120896825 | E | LC | ETL.3820.TOWR | 40579634 | VICTOR | STOCKTON | 2021-04-28 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40579634 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 2.7344e-07 | 47.5096 | 1.2991e-05
120931763 | F | LC | ETL.1820.POLE.WDPS | 44557449 | EUREKA | HUMBOLDT | 2021-05-04 | 2021-06-23 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44553938 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.022029 | 237.3869
120936533 | E | LC | ETL.7000.POLE.WOOD | 40867615 | TABLEMTN | NORTH VALLEY | 2021-05-05 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40867615 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00026671 | 31.6978 | 0.0084541
120949855 | E | LC | ETL.2900.TOWR | 40821198 | MOSSLNDG | CENTRAL COAST | 2021-04-19 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40821198 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1963-01-01 | Porcelain | Dead End |  |  |  |  | 0.0033937 | 1013.5428 | 3.4396
121191213 | F | LC | ETL.7820.POLE.WOOD | 44815075 | LAKEVLLE | SONOMA | 2021-05-11 |  | ETL.7820 | POTTER VALLEY-WILLITS | Right of Way | Encroachment | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44815075 | 2019-07-12 | Single Wood Pole | T2N | 2019-07-12 | Polymer | Post |  |  |  |  | 0.00016882 | 537.983
121191948 | F | LC | ETL.5140.TOWR | 40765402 | SACTO | SIERRA | 2021-04-01 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40765402 | 1965-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.0516e-05 | 2949.7161
121323026 | E | LC | ETL.4590.TOWR | 40910179 | TABLEMTN | NORTH VALLEY | 2021-04-19 |  | ETL.4590 | CRESTA-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40910179 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.9608e-09 | 2499.6221 | 4.9012e-06
121330764 | F | LC | ETL.2790.TOWR | 40808549 | CONCORD | DIABLO | 2021-04-19 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40808549 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.379e-06 | 31.6978 | 0.00010711
121331051 | F | LC | ETL.3500.TOWR | 40643013 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40643013 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.00086079 | 5128.1152 | 4.4142
121336900 | E | LC | ETL.5330.INSL | 40636645 | MOSSLNDG | CENTRAL COAST | 2021-04-15 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40604865 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 4.3075e-05 | 205.6706 | 0.0088593
121336970 | E | LC | ETL.2395.POLE.WOOD | 45019101 | TABLEMTN | NORTH VALLEY | 2021-05-14 | 2021-05-28 | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45019101 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0052286 | 79.1846
121346802 | E | LC | ETL.5930.TOWR | 40656836 | LAKEVLLE | DIABLO | 2021-04-20 | 2021-11-15 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656836 | 1946-01-01 | LATTICE STEEL TOWER | TRP SUSP - Tramp Susp | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 7.568e-09 | 143.0883 | 1.0829e-06
121347662 | E | LC | ETL.3741.INSL | 40740801 | CONCORD | EAST BAY | 2021-04-23 |  | ETL.3741 | MORAGA-LAKEWOOD | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40739975 | 1947-01-01 | Lattice Steel Pole | DDE - Double Dead End | 1947-01-01 | Ceramic | Other |  |  |  |  | 2.2998e-08 | 458.8659 | 1.0553e-05
121355537 | E | LC | ETL.4620.TOWR | 40597245 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.4620 | DIABLO-MESA | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40597245 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2011-08-19 | Ceramic | Dead End |  |  |  |  | 3.8974e-09 | 174.0536 | 6.7836e-07
121381022 | F | LC | ETL.8350.POLE.NWOD | 44920064 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44920064 | 2020-01-15 | Light Duty Steel Pole | T-1 - Tri Post | 2020-01-15 | Polymer | Post |  |  |  |  | 4.939e-07 | 95.3431
121383156 | F | LC | ETL.1430.TOWR | 40757312 | SACTO | SIERRA | 2021-05-21 |  | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40757312 | 1913-01-01 | LATTICE STEEL TOWER | Unknown | 2016-11-14 | Non Ceramic | Post |  |  |  |  | 0.00013487 | 1507.6083 | 0.20333
121384450 | E | LC | ETL.6470.POLE.WOOD | 40598540 | SACTO | SIERRA | 2021-05-11 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40598540 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0051009 | 3211.3491 | 16.3807
121385681 | F | LC | ETL.6760.POLE.WOOD | 40598585 | SACTO | SIERRA | 2021-05-13 | 2021-06-25 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40598585 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.098262 | 332.3255
121391804 | E | LC | ETL.6050.TOWR | 40811352 | MOSSLNDG | SAN JOSE | 2021-05-17 |  | ETL.6050 | MOSS LANDING-METCALF | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40811352 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 6.3011e-08 | 3026.9094 | 0.00019073
121397738 | F | LC | ETL.6660.POLE.NWOD | 40909595 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40909595 | 1998-01-01 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-04 | Polymer | Post |  |  |  |  | 6.5637e-08 | 1902.7744
121422700 | E | LC | ETL.1073.POLE.WDPS | 44774768 | VICTOR | YOSEMITE | 2021-05-25 | 2021-10-28 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40580216 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0037556 | 15.8866 | 0.059663
121423875 | F | LC | ETL.1402.POLE.STPS | 44779621 | VICTOR | STOCKTON | 2021-05-25 | 2021-06-25 | ETL.1402 | SPRING GAP TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44779601 | 2019-06-24 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.6187e-06 | 174.1264
121424893 | F | LC | ETL.5220.TOWR | 40761467 | METCALF | PENINSULA | 2021-05-27 |  | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40761467 | 1963-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1963-01-01 | Ceramic | Suspension |  |  |  |  | 0.084848 | 933.5308 | 79.2079
121427943 | F | LC | ETL.8290.POLE.WOOD | 40615883 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.8290 | VOLTA-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40615883 |  | Single Wood Pole | T-1 - Tri Post | 2018-03-30 | Polymer | Post |  |  |  |  | 0.00058205 | 795.0117
121450584 | E | LC | ETL.6110.INSL | 40715132 | METCALF | SAN JOSE | 2021-06-02 |  | ETL.6110 | TESLA-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40664359 | 1966-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.8887e-06 | 1548.3909 | 0.015312
121455708 | E | LC | ETL.6290.POLE.WOOD | 40768874 | TABLEMTN | NORTH VALLEY | 2021-05-29 | 2021-08-06 | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL | [11 empty] | 0.027745 | 3115.8767
121466144 | E | LC | ETL.3830.INSL.NCER | 40669667 | VICTOR | STOCKTON | 2021-06-03 | 2021-06-24 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40642796 | 1927-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1999-01-01 | Polymer | Dead End |  |  |  |  | 6.6813e-07 | 6093.292
121467250 | E | LC | ETL.1600.INSL.CERA | 40614408 | LAKEVLLE |  | 2021-06-04 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40589189 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 1.097e-07 | 1190.6113 | 0.0001306
121475222 | F | LC | ETL.7490.POLE.WOOD | 40771305 | EUREKA | HUMBOLDT | 2021-05-28 | 2021-10-11 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40771305 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.72389 | 0.065148
121484896 | F | LC | ETL.4316.POLE.STPS | 44838832 | TABLEMTN |  | 2021-05-29 | 2021-08-12 | ETL.4316 | PARADISE-TABLE MTN | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44838787 | 2018-12-10 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00053669 | 4196.3833
121487718 | E | LC | ETL.4550.TOWR | 40657704 | TABLEMTN | NORTH VALLEY | 2021-06-01 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40657704 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.3254e-07 | 2789.5828 | 0.00036974
121493359 | E | LC | ETL.6220.POLE.WOOD | 40600519 | EUREKA | HUMBOLDT | 2021-05-27 | 2021-06-17 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40600519 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.44526 | 710.0929
121493503 | F | LC | ETL.1430.TOWR | 40590518 | SACTO | SIERRA | 2021-06-01 |  | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40590518 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.0011591 | 316.4733 | 0.36682
121494546 | B | LC | ETL.1450.INSL | 40629345 | SACTO | SACRAMENTO | 2021-06-08 | 2021-08-31 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602591 | 1955-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | 1955-01-01 | Ceramic | Dead End |  |  |  |  | 4.3035e-06 | 348.1462
121498568 | E | LC | ETL.2700.TOWR | 44188761 | CONCORD | DIABLO | 2021-06-01 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44188761 | 2008-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 6.2736e-09 | 445.731 | 2.7963e-06
121512719 | F | LC | ETL.6852.POLE.NWOD | 45100505 | LAKEVLLE | HUMBOLDT | 2021-06-10 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45100505 | 2021-05-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-05-11 | Glass | Dead End |  |  |  |  | 0.011737 | 6378.4995
121513429 | E | LC | ETL.1450.POLE.WDPS | 44552405 | SACTO | SACRAMENTO | 2021-06-10 |  | ETL.1450 | DRUM-SUMMIT #2 | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44551583 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0023913 | 411.4417 | 0.98387
121516099 | F | LC | ETL.6880.POLE.WOOD | 40912462 | LAKEVLLE | NORTH BAY | 2021-06-05 |  | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40912462 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0084065 | 734.6977
121516534 | E | LC | ETL.6760.POLE.WOOD | 40874725 | SACTO | SIERRA | 2021-06-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40874725 |  | Single Wood Pole | T1DE - Tri Post Dead End 115 |  | Polymer | [5 empty] | 0.22157 | 47.5526 | 10.5363
121516991 | F | LC | ETL.1450.TOWR | 40671557 | SACTO | SIERRA | 2021-06-01 |  | ETL.1450 | DRUM-SUMMIT #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40671557 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Dead End |  |  |  |  | 0.00059742 | 1123.6396 | 0.67129
121517022 | F | LC | ETL.7575.POLE.WDPS | 44384736 | METCALF | SAN FRANCISCO | 2021-06-04 | 2021-07-12 | ETL.7575 | SNEATH LANE-PACIFICA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44384735 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.24712 | 760.1513
121518988 | E | LC | ETL.1810.POLE.WDPS | 44322597 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44322596 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.056277 | 142.4559 | 8.017
121519269 | E | LC | ETL.4440.INSL | 40796906 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40765547 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 2.4871e-05 | 6458.0005 | 0.16062
121522129 | B | LC | ETL.5390.INSL.NCER | 45114523 | TABLEMTN | NORTH VALLEY | 2021-06-11 | 2021-08-17 | ETL.5390 | PIT #1-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40758860 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.4981e-06 | 3248.3611
121523915 | E | LC | ETL.1820.INSL.CERA | 40853376 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560134 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.72788
121523915 | E | LC | ETL.1820.INSL.CERA | 40853376 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560134 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.72788
121523915 | E | LC | ETL.1820.INSL.CERA | 40853376 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560134 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.72788
121536538 | F | LC | ETL.5390.TOWR | 40821480 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40821480 | 1938-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 0.00096601 | 743.6465 | 0.71837
121536790 | E | LC | ETL.1600.POLE.WOOD | 40585161 | LAKEVLLE | NORTH BAY | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40585161 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 1977-01-01 | Porcelain | Dead End |  |  |  |  | 4.4628e-05 | 553.7645 | 0.024713
121543007 | F | LC | ETL.7990.POLE.NWOD | 44676875 | SACTO | SIERRA | 2021-06-12 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44676875 | 2018-08-23 | Light Duty Steel Pole | T-1 - Tri Post | 2018-08-23 | Polymer | Post |  |  |  |  | 5.227e-06 | 3449.7656
121543603 | F | LC | ETL.5650.TOWR | 40819294 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40819294 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.0513e-08 | 4626.835 | 4.8641e-05
121544073 | F | LC | ETL.5390.TOWR | 40868861 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40868861 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 5.1614e-05 | 1597.7395 | 0.082466
121550349 | E | LC | ETL.5980.TOWR | 40592864 | PISMOBCH | LOS PADRES | 2021-06-15 |  | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40592864 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.3605e-05 | 31.6948 | 0.00043122
121550840 | F | LC | ETL.7990.POLE.WOOD | 40908936 | SACTO | SIERRA | 2021-06-12 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908936 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | [5 empty] | 2.2211e-05 | 3564.1165
121557212 | B | LC | ETL.9061.INSL | 40623241 | FRESNO | FRESNO | 2021-06-16 | 2021-08-24 | ETL.9061 | DUNLAP TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40596826 |  | Light Duty Steel Pole | TAP - Tri Arm Post | 1964-01-01 | Non Ceramic | Other |  |  |  |  | 1.5114e-06 | 6331.5015
121557525 | E | LC | ETL.7550.POLE.WOOD | 40750955 | LAKEVLLE | HUMBOLDT | 2021-06-12 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40750955 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.00031622 | 110.7947 | 0.035035
121586870 | E | LC | ETL.5960.TOWR | 40664705 | PISMOBCH | LOS PADRES | 2021-06-22 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40664705 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 1.2964e-05 | 31.6948 | 0.00041091
121590844 | E | LC | ETL.8310.POLE.WOOD | 40858662 | MOSSLNDG | CENTRAL COAST | 2021-06-22 | 2021-10-19 | ETL.8310 | WATSONVILLE-SALINAS | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40858662 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.056231 | 5846.355 | 328.7458
121607755 | E | LC | ETL.7851.POLE.WOOD | 40824578 | EUREKA | HUMBOLDT | 2021-06-23 |  | ETL.7851 | RIO DELL TAP | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40824578 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Non Ceramic | [5 empty] | 0.85569 | 221.4831 | 189.5211
121631656 | B | LC | ETL.1420.TOWR | 40594932 | SACTO | SACRAMENTO | 2021-06-29 | 2021-07-02 | ETL.1420 | DRUM-RIO OSO #1 | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40594932 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 7.4542e-05 | 237.3808
121631656 | B | LC | ETL.1420.TOWR | 40594932 | SACTO | SACRAMENTO | 2021-06-29 | 2021-07-02 | ETL.1420 | DRUM-RIO OSO #1 | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40594932 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-08-05 | Glass | Suspension |  |  |  |  | 7.4542e-05 | 237.3808
121633322 | E | LC | ETL.7291.POLE.WDPS | 45099460 | TABLEMTN | NORTH VALLEY | 2021-06-29 |  | ETL.7291 | CLOVER CREEK TAP | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42712147 |  | 2-Pole Wood | FSS - Field Switch Structure | [7 empty] | 0.014825 | 158.265 | 2.3463
121634317 | F | LC | ETL.7212.POLE.STPS | 44286986 | METCALF | PENINSULA | 2021-06-23 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44286985 | 2015-06-25 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.14469 | 696.7528
121638598 | E | LC | ETL.7180.POLE.WDPS | 44360909 | LAKEVLLE | NORTH BAY | 2021-06-23 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44360907 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0045311 | 146.3688 | 0.66322
121641141 | F | LC | ETL.1650.POLE.NWOD | 43680372 | LAKEVLLE | SONOMA | 2021-06-26 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 43680372 |  | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees |  | Polymer | Other |  |  |  |  | 1.2944e-08 | 792.5971
121642405 | E | LC | ETL.1600.INSL | 40835243 | LAKEVLLE | SONOMA | 2021-06-11 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810366 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.6406e-07 | 6494.9727 | 0.0010656
121647725 | E | LC | ETL.8405.INSL.CERA | 40630451 | SACTO | SACRAMENTO | 2021-06-30 |  | ETL.8405 | MIDDLE FORK #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40589945 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.4367 | 4160.9766 | 1817.0859
121653115 | A | LC | ETL.1350.POLE.WDPS | 44549927 | TABLEMTN |  | 2021-07-01 | 2021-07-07 | ETL.1350 | CRAG VIEW-CASCADE | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
121659012 | B | LC | ETL.3530.POLE.WDPS | 44269066 | PISMOBCH | LOS PADRES | 2021-07-01 | 2021-07-29 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44269063 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00035636 | 2690.7754
121719513 | E | LC | ETL.1820.INSL.CERA | 45089726 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 45089712 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.075959 | 5288.2002 | 401.6887
121726274 | E | LC | ETL.5420.POLE.WDPS | 44562634 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562323 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.025087 | 2550.5932 | 63.9862
121732113 | F | LC | ETL.4440.POLE.NWOD | 44191915 | TABLEMTN | NORTH VALLEY | 2021-07-12 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44191915 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 1.8498e-07 | 490.3705
121747272 | F | LC | ETL.1820.POLE.NWOD | 45106279 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45106279 | 2020-03-09 | Light Duty Steel Pole | 3P DDE-A - 3 Pole Double Dead End Angle | 2020-03-09 | Glass | Dead End | [5 empty] | 0.065152
121749987 | E | LC | ETL.1810.POLE.WDPS | 44322522 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44322521 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0050197
121750167 | E | LC | ETL.7390.POLE.WOOD | 40826238 | LAKEVLLE | HUMBOLDT | 2021-07-17 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40826238 |  | Single Wood Pole | T2N | 2021-01-28 | Polymer | Post |  |  |  |  | 0.20524 | 411.397 | 84.4351
121781808 | E | LC | ETL.2390.POLE.WDPS | 44391256 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391254 |  | 2-Pole Wood | FSS - Field Switch Structure | [7 empty] | 5.8388e-05 | 4273.2705 | 0.24951
121791350 | B | LC | ETL.1810.POLE.STPS | 44395985 | EUREKA | HUMBOLDT | 2021-07-24 | 2021-08-10 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44395984 | 2017-08-23 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.0592e-06
121797497 | E | LC | ETL.9240.TOWR | 43249667 | PISMOBCH | LOS PADRES | 2021-07-26 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 43249667 |  | LATTICE STEEL TOWER | [9 empty] | 2470.1736
121800253 | B | LC | ETL.9240.TOWR | 43249621 | PISMOBCH | LOS PADRES | 2021-07-26 | 2021-09-23 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249621 |  | LATTICE STEEL TOWER | [9 empty] | 1871.2655
121812659 | F | LC | ETL.7060.POLE.WOOD | 40668120 | METCALF | PENINSULA | 2021-07-28 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40668120 |  | Single Wood Pole | 3P DV - 3 Pole Double Vertical |  | Non Ceramic | Other |  |  |  |  | 0.008435 | 1060.2281
121819225 | E | LC | ETL.6760.POLE.WOOD | 40598594 | SACTO | SIERRA | 2021-07-29 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40598594 |  | Single Wood Pole | TCDE - Tap Construction Dead End |  | Polymer | [5 empty] | 0.040227 | 237.3428 | 9.5475
121824800 | E | LC | ETL.6760.POLE.WOOD | 40693460 | SACTO | SIERRA | 2021-07-31 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40693460 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 0.013601 | 1138.9978 | 15.4913
121883914 | B | LC | ETL.8170.POLE.WOOD | 44948561 | EUREKA | HUMBOLDT | 2021-08-10 |  | ETL.8170 | TRINITY-MAPLE CREEK | Emergency | Fire | [Replace] | Tier2 |  |  | PEND | [12 empty] | 5065.561
121979240 | F | LC | ETL.6500.POLE.NWOD | 45144259 | SACTO | NORTH VALLEY | 2021-08-31 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45144259 | 2021-08-20 | Light Duty Steel Pole | T-1 - Tri Post | 2021-08-20 | Polymer | Post
122065513 | E | LC | ETL.4780.INSL | 40848020 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40819577 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.14354 | 205.8835 | 29.5527
122065668 | E | LC | ETL.4780.INSL | 40886715 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40864245 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.012287 | 732.0612 | 8.9947
122065668 | E | LC | ETL.4780.INSL | 40886715 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40864245 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.012287 | 732.0612 | 8.9947
122245197 | E | LC | ETL.6760.POLE.WOOD | 40816319 | SACTO | SIERRA | 2021-10-07 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40816319 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.036167 | 1313.09 | 47.491
122250717 | E | LC | ETL.7160.POLE.WOOD | 44871196 | LAKEVLLE | SONOMA | 2021-10-24 | 2021-10-25 | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44871196 | 2019-09-19 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2019-09-19 | Polymer | Dead End |  |  |  |  | 0.21707 | 205.9363
118576244 | E | LC | ETL.4340.INSL | 40713875 | CONCORD |  | 2020-02-25 | 2021-07-12 | ETL.4340 | BAHIA-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
118779828 | E | LC | ETL.6750.INSL.NCER | 44932577 | TABLEMTN | NORTH VALLEY | 2020-04-06 |  | ETL.6750 | DELTA-MTN GATE JCT | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44932562 | 2020-02-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-02-06 | Glass | Suspension |  |  |  |  | 1.3682e-06
118779828 | E | LC | ETL.6750.INSL.NCER | 44932577 | TABLEMTN | NORTH VALLEY | 2020-04-06 |  | ETL.6750 | DELTA-MTN GATE JCT | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44932562 | 2020-02-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-02-06 | Glass | Suspension |  |  |  |  | 1.3682e-06
118936774 | E | LC | ETL.6330.POLE.WOOD | 40815779 | TABLEMTN | NORTH VALLEY | 2020-04-21 | 2021-09-14 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40815779 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00051121 | 1046.0669
118975864 | E | LC | ETL.1330.TOWR | 40870083 | LAKEVLLE | HUMBOLDT | 2020-04-23 | 2021-04-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870083 | 1951-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 0.00028991 | 6189.9644
118975864 | E | LC | ETL.1330.TOWR | 40870083 | LAKEVLLE | HUMBOLDT | 2020-04-23 | 2021-04-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870083 | 1951-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-05-05 | Glass | Suspension |  |  |  |  | 0.00028991 | 6189.9644
118976123 | B | LC | ETL.6440.POLE.WOOD | 44191513 | TABLEMTN | NORTH VALLEY | 2020-05-01 | 2020-05-19 | ETL.6440 | COLEMAN-RED BLUFF | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
118980632 | F | LC | ETL.6880.POLE.NWOD | 40601478 | LAKEVLLE | SONOMA | 2020-04-22 | 2020-11-10 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 |  |  | DLFL
119016690 | E | LC | ETL.4392.INSL.CERA | 41129239 | LAKEVLLE | SONOMA | 2020-05-11 | 2021-06-23 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119043531 | B | LC | ETL.1420.TOWR | 40654185 | SACTO | SIERRA | 2020-05-19 | 2020-06-15 | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40654185 | 1966-01-01 | LATTICE STEEL TOWER | FDDE - Flat Dead End Construction |  | Glass | Dead End |  |  |  |  | 4.4422e-06 | 269.0173
119043531 | B | LC | ETL.1420.TOWR | 40654185 | SACTO | SIERRA | 2020-05-19 | 2020-06-15 | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40654185 | 1966-01-01 | LATTICE STEEL TOWER | FDDE - Flat Dead End Construction | 2020-06-10 | Glass | Dead End |  |  |  |  | 4.4422e-06 | 269.0173
119049728 | E | LC | ETL.4040.POLE.WDPS | 44553563 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2020-07-10 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119083307 | B | LC | ETL.6690.POLE.WOOD | 40597182 | SACTO | SIERRA | 2020-05-29 | 2020-08-12 | ETL.6690 | DEER CREEK-DRUM | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40597182 |  | Single Wood Pole | T2N | 2020-08-05 | Polymer | Post |  |  |  |  | 0.08668 | 142.4769
119083472 | E | LC | ETL.7290.POLE.NWOD | 44175308 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-02-26 | ETL.7290 | KILARC-CEDAR CREEK | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44175308 | 2014-10-15 | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.00016732 | 1744.4635
119084614 | E | LC | ETL.1650.POLE.WOOD | 40594505 | LAKEVLLE | SONOMA | 2020-05-27 | 2021-03-15 | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594505 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Dead End |  |  |  |  | 2.7077e-05 | 4151.2271
119091228 | E | LC | ETL.8410.POLE.WOOD | 40701049 | LAKEVLLE | HUMBOLDT | 2020-05-15 |  | ETL.8410 | ELK-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40701049 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Polymer | Suspension |  |  |  |  | 0.88952 | 15.8807 | 14.1261
119097570 | F | LC | ETL.6720.POLE.WDPS | 44949092 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2021-03-03 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42578815 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0022315 | 174.0849
119118675 | E | LC | ETL.6950.POLE.WOOD | 40908785 | SACTO | SIERRA | 2020-05-22 | 2021-10-13 | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40908785 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End - Suspension |  |  |  |  | 0.001303 | 1676.4927 | 2.1844
119119119 | E | LC | ETL.1420.TOWR | 40814348 | SACTO | SIERRA | 2020-06-04 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40814348 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 7.2234e-05 | 3797.0496 | 0.27428
119119298 | F | LC | ETL.6330.INSL.NCER | 44418268 | TABLEMTN | NORTH VALLEY | 2020-06-02 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40675499 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0010437 | 3165.6362
119120367 | F | LC | ETL.6330.POLE.WOOD | 40664493 | TABLEMTN | NORTH VALLEY | 2020-06-02 | 2020-08-10 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40664493 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0031139 | 3343.2844
119127092 | B | LC | ETL.7270.POLE.WOOD | 40810422 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2020-12-31 | ETL.7270 | KESWICK-TRINITY | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119130408 | F | LC | ETL.7300.POLE.WOOD | 40816218 | TABLEMTN |  | 2020-06-04 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40816218 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00083772 | 608.2984
119163465 | E | LC | ETL.6760.INSL.CERA | 40639222 | SACTO | SACRAMENTO | 2020-06-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40611360 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0059288 | 17.4655 | 0.10355
119164293 | E | LC | ETL.1071.INSL.NCER | 44923018 | VICTOR | STOCKTON | 2020-06-14 |  | ETL.1071 | TULLOCH TAP | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44922959 | 2020-05-01 | Light Duty Steel Pole | T1-1A | 2020-05-01 | Polymer | Post |  |  |  |  | 1.4223e-07 | 1977.8663 | 0.00028131
119164997 | F | LC | ETL.6470.POLE.WOOD | 40598561 | SACTO | SIERRA | 2020-06-10 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40598561 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.16255 | 474.9903
119166063 | E | LC | ETL.8300.POLE.WOOD | 40700030 | TABLEMTN | NORTH VALLEY | 2020-06-11 | 2021-07-22 | ETL.8300 | VOLTA-SOUTH | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40700030 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0079086 | 5642.0104
119166872 | B | LC | ETL.8170.POLE.WDPS | 44420649 | EUREKA | HUMBOLDT | 2020-06-15 | 2020-08-05 | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 44420646 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0097533 | 189.9226
119175174 | F | LC | ETL.6280.POLE.WOOD | 40751799 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2021-02-10 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40751799 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Other |  |  |  |  | 1.1844e-05 | 126.5956
119179610 | F | LC | ETL.1073.POLE.STPS | 44880498 | VICTOR | YOSEMITE | 2020-06-17 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44880485 | 2019-12-03 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.1103e-06 | 63.3245
119180804 | E | LC | ETL.6310.POLE.WOOD | 41177757 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-09-28 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41177757 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0051153 | 3041.8088
119181033 | F | LC | ETL.6280.POLE.WOOD | 40769477 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40769477 |  | Single Wood Pole | T2N | 2018-11-24 | Polymer | Post |  |  |  |  | 5.5609e-06 | 6110.2441
119182145 | E | LC | ETL.7300.POLE.WOOD | 40825991 | TABLEMTN |  | 2020-06-16 | 2021-08-25 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825991 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.00013407 | 3455.4893
119184641 | F | LC | ETL.6280.POLE.WOOD | 40876563 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40876563 |  | Single Wood Pole | T2N | 2020-02-18 | Polymer | Post |  |  |  |  | 3.0314e-05 | 1739.9091
119189162 | E | LC | ETL.6220.POLE.WOOD | 40661882 | EUREKA | HUMBOLDT | 2020-06-19 | 2020-07-14 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40661882 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.15009 | 2421.884
119194018 | E | LC | ETL.5790.TOWR | 40811845 | VICTOR | STOCKTON | 2020-06-19 | 2021-03-25 | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40811845 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 5.1261e-05 | 1202.2845
119198818 | F | LC | ETL.6470.POLE.WOOD | 40767326 | SACTO | SIERRA | 2020-06-23 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767326 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.061003 | 205.7345
119200191 | F | LC | ETL.6470.POLE.WOOD | 40822736 | SACTO | SIERRA | 2020-06-23 | 2021-07-06 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40822736 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.25085 | 110.8102
119200350 | B | LC | ETL.4220.POLE.WOOD | 40751673 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-10-26 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue, Completed] | Tier2 |  |  | COMP
119229259 | E | LC | ETL.6030.TOWR | 40586557 | MIDWAY | KERN | 2020-06-24 | 2020-07-28 | ETL.6030 | MIDWAY-WHIRLWIND | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40586557 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-01-28 | Glass | Suspension |  |  |  |  | 7.2611e-06 | 6859.2124
119232108 | F | LC | ETL.6020.TOWR | 40753364 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2020-07-27 | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40753364 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00029009 | 2487.2815
119232382 | E | LC | ETL.8170.INSL | 40641476 | EUREKA | HUMBOLDT | 2020-06-29 | 2021-06-14 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119236227 | F | LC | ETL.8170.POLE.WOOD | 40585390 | EUREKA | HUMBOLDT | 2020-06-30 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40585390 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.1614 | 79.1467
119293609 | B | LC | ETL.5280.INSL.CERA | 44358895 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-06-08 | ETL.5280 | MORRO BAY-CALIFORNIA FLATS SW STA | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40810829 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2016-08-27 | Ceramic | Dead End |  |  |  |  | 3.543e-08 | 2881.3301
119295309 | E | LC | ETL.1820.POLE.WDPS | 44560592 | EUREKA | HUMBOLDT | 2020-07-01 | 2020-12-14 | ETL.1820 | HUMBOLDT-TRINITY | Vegetation | Overgrown | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44560104 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.043289 | 23.8531
119310784 | E | LC | ETL.6980.POLE.WOOD | 40584647 | LAKEVLLE | SONOMA | 2020-07-03 | 2021-06-22 | ETL.6980 | FORT ROSS-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40584647 | 1953-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1953-01-01 | Polymer | Suspension |  |  |  |  | 0.46419 | 79.1393
119312659 | F | LC | ETL.8170.POLE.WDPS | 44565593 | EUREKA | HUMBOLDT | 2020-06-30 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
119314491 | E | LC | ETL.7270.POLE.WOOD | 40906084 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-08-07 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906084 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0043398 | 933.5561
119315201 | E | LC | ETL.1110.POLE.WDPS | 44424497 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-04-12 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424495 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00084562 | 4066.2923
119317252 | F | LC | ETL.4393.POLE.STPS | 44258713 | SACTO | SACRAMENTO | 2020-07-02 | 2021-07-06 | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44258711 | 2016-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.0565e-05 | 680.3559
119325029 | E | LC | ETL.6300.POLE.WDPS | 44976246 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-08-26 | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL | [12 empty] | 2595.2925
119330665 | E | LC | ETL.4680.TOWR | 40597134 | LAKEVLLE | SONOMA | 2020-07-08 | 2020-11-20 | ETL.4680 | FULTON-IGNACIO #1 | Vegetation-Tower | Overgrown | [Cage Clearing, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40597134 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.3131e-05 | 965.4728
119335049 | E | LC | ETL.8170.POLE.WOOD | 44190923 | EUREKA | HUMBOLDT | 2020-07-08 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44190923 |  | Single Wood Pole | T2N | 2020-05-04 | Polymer | Post |  |  |  |  | 0.021091 | 31.7081 | 0.66876
119340827 | F | LC | ETL.5934.TOWR | 40647367 | PISMOBCH | LOS PADRES | 2020-07-09 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40647367 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00025376 | 4115.4043 | 1.0443
119350220 | F | LC | ETL.1110.POLE.WDPS | 44561150 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44515871 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0068861 | 4623.019
119353579 | E | LC | ETL.7030.POLE.WOOD | 40601622 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-07 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119355372 | F | LC | ETL.4220.POLE.NWOD | 44272856 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2020-08-03 | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44272856 | 2014-10-27 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2014-10-27 | Ceramic | Suspension |  |  |  |  | 0.00013445 | 5756.8081
119361815 | E | LC | ETL.5440.POLE.WDPS | 44558307 | TABLEMTN |  | 2020-07-01 | 2020-09-01 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119364070 | E | LC | ETL.7270.POLE.NWOD | 44649285 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-08-24 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44649285 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 0.0031383 | 510.5901
119378261 | E | LC | ETL.6880.POLE.WOOD | 40751140 | LAKEVLLE | SONOMA | 2020-07-15 | 2021-09-20 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Rotten | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.0010628 | 33.2887
119480590 | E | LC | ETL.6760.POLE.WOOD | 42549844 | SACTO | SIERRA | 2020-07-21 | 2021-03-11 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42549844 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.091408 | 47.5273
119483869 | E | LC | ETL.6890.POLE.WOOD | 40667805 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-08-12 | ETL.6890 | FULTON-HOPLAND | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40667805 | 1990-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.0004542 | 1615.6473
119489731 | F | LC | ETL.6950.POLE.NWOD | 44437355 | SACTO | SACRAMENTO | 2020-07-22 |  | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44437355 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.0012056 | 1997.2292
119491340 | E | LC | ETL.1650.INSL.CERA | 40609295 | LAKEVLLE |  | 2020-07-21 | 2021-03-10 | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed, Completed] | Tier3 |  |  | COMP
119495716 | F | LC | ETL.1450.POLE.WDPS | 44212219 | SACTO | SACRAMENTO | 2020-07-22 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44212218 | 2013-09-30 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0013869 | 31.7066
119558773 | E | LC | ETL.6490.POLE.WOOD | 40825238 | SACTO | SACRAMENTO | 2020-08-04 | 2021-03-03 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825238 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.0071732 | 664.4426
119566474 | E | LC | ETL.7780.POLE.WOOD | 40684445 | LAKEVLLE | HUMBOLDT | 2020-08-05 | 2021-01-11 | ETL.7780 | PHILO JCT-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40684445 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00016483 | 6063.5518
119601273 | E | LC | ETL.6490.POLE.WOOD | 40612747 | SACTO | SACRAMENTO | 2020-08-11 | 2021-03-02 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119617845 | E | LC | ETL.3500.TOWR | 40643405 | VICTOR | STOCKTON | 2020-08-14 | 2021-04-06 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40643405 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 5.4541e-06 | 253.2219
119632815 | F | LC | ETL.8182.POLE.STPS | 44820898 | SACTO | SACRAMENTO | 2020-08-18 |  | ETL.8182 | CORDELIA #1 TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44813257 | 2019-05-22 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.6692e-07 | 2396.849
119637857 | E | LC | ETL.1470.INSL.CERA | 40847660 | LAKEVLLE | HUMBOLDT | 2020-08-19 | 2021-03-17 | ETL.1470 | EAGLE ROCK-CORTINA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119638374 | E | LC | ETL.7490.POLE.WOOD | 40586855 | EUREKA | HUMBOLDT | 2020-08-19 | 2021-08-11 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40586855 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-07-30 | Polymer | Dead End |  |  |  |  | 0.46676 | 126.5956
119654219 | E | LC | ETL.1600.TOWR | 40656848 | LAKEVLLE | SONOMA | 2020-08-21 | 2021-02-24 | ETL.1600 | FULTON-PUEBLO | Vegetation | Overgrown | [Trim, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40656848 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 1.7125e-05 | 95.0507
119654219 | E | LC | ETL.1600.TOWR | 40656848 | LAKEVLLE | SONOMA | 2020-08-21 | 2021-02-24 | ETL.1600 | FULTON-PUEBLO | Vegetation | Overgrown | [Trim, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40656848 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-10-27 | Glass | Suspension |  |  |  |  | 1.7125e-05 | 95.0507
119656363 | A | LC | ETL.7590.POLE.WDPS | 44949095 | MOSSLNDG | CENTRAL COAST | 2020-08-21 | 2020-08-26 | ETL.7590 | MONTA VISTA-BURNS | Emergency-Wood | Other | [Replace] | Tier3 |  |  | DLFL
119676315 | E | LC | ETL.7980.POLE.WOOD | 40760141 | SACTO | SIERRA | 2020-04-27 |  | ETL.7980 | SMARTVILLE-MARYSVILLE | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40760141 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.020452 | 1080.2767 | 22.0938
119677071 | E | LC | ETL.2420.POLE.WOOD | 40810777 | LAKEVLLE | SONOMA | 2020-08-26 | 2020-09-14 | ETL.2420 | MENDOCINO-UKIAH | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810777 | 1970-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1970-01-01 | Porcelain | Post |  |  |  |  | 5.6407e-05 | 3685.8157
119719268 | E | LC | ETL.1110.POLE.WDPS | 44561141 | TABLEMTN | HUMBOLDT | 2020-09-03 | 2021-05-10 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Rotten | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 44515861 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0023204 | 4702.3208
119720862 | E | LC | ETL.8253.POLE.WOOD | 40644745 | VICTOR | STOCKTON | 2020-07-28 |  | ETL.8253 | IONE TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40644745 | 1987-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Other |  |  |  |  | 6.0914e-05 | 2266.8525 | 0.13808
119721879 | A | LC | ETL.7590.POLE.WDPS | 44949088 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-10-21 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119722720 | F | LC | ETL.6440.POLE.WOOD | 41144211 | TABLEMTN | NORTH VALLEY | 2020-08-04 |  | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41144211 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.00039951 | 6617.2612
119723737 | F | LC | ETL.6490.POLE.WOOD | 40679376 | SACTO | SIERRA | 2020-08-05 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40679376 |  | Single Wood Pole | T-1 - Tri Post | 2019-07-16 | Polymer | Post |  |  |  |  | 0.0047879 | 3211.3491
119727748 | B | LC | ETL.1110.POLE.WDPS | 44423405 | TABLEMTN | NORTH VALLEY | 2020-09-04 | 2020-10-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423405 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.0011382
119727748 | B | LC | ETL.1110.POLE.WDPS | 44423405 | TABLEMTN | NORTH VALLEY | 2020-09-04 | 2020-10-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423405 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.0011382
119754752 | F | LC | ETL.4050.POLE.NWOD | 44660753 | LAKEVLLE | SONOMA | 2020-07-21 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44660753 | 2018-09-30 | Light Duty Steel Pole | T-1 - Tri Post | 2018-09-30 | Polymer | Post |  |  |  |  | 1.8301e-08 | 1554.2012
119754781 | F | LC | ETL.8170.POLE.WOOD | 40906303 | EUREKA | HUMBOLDT | 2020-08-17 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906303 |  | Single Wood Pole | T-1 - Tri Post | 2019-06-25 | Polymer | Post |  |  |  |  | 0.033126 | 5491.4502
119763823 | F | LC | ETL.2395.POLE.WDPS | 44551452 | TABLEMTN | NORTH VALLEY | 2020-09-08 |  | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | PEND
119769192 | F | LC | ETL.8290.POLE.WOOD | 40601137 | TABLEMTN | NORTH VALLEY | 2020-09-09 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40601137 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 4.1916e-05 | 3010.644
119776284 | E | LC | ETL.8210.POLE.WOOD | 40907069 | VICTOR | STOCKTON | 2020-09-15 | 2021-08-30 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.30735 | 4132.7466
119780342 | E | LC | ETL.7930.POLE.WOOD | 40600141 | MOSSLNDG | CENTRAL COAST | 2020-09-12 | 2021-08-17 | ETL.7930 | SALINAS-LAURELES | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600141 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0047464 | 0.066432
119787071 | E | LC | ETL.6470.INSL.NCER | 40921903 | SACTO | SACRAMENTO | 2020-09-18 | 2021-07-27 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40912097 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0029541 | 680.261
119787328 | F | LC | ETL.6470.POLE.WOOD | 40664650 | SACTO | SIERRA | 2020-09-16 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40664650 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.091084 | 221.5931
119792002 | E | LC | ETL.6440.POLE.WOOD | 44191471 | TABLEMTN | NORTH VALLEY | 2020-09-17 | 2021-09-01 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191471 |  | Single Wood Pole | T-1 - Tri Post | [7 empty] | 0.0010732 | 3756.4604
119809862 | F | LC | ETL.7260.POLE.WOOD | 40816354 | TABLEMTN | NORTH VALLEY | 2020-08-13 |  | ETL.7260 | KESWICK-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40816354 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 4.1743e-05 | 2021.9017
119810347 | F | LC | ETL.7490.POLE.STPS | 44145843 | EUREKA | HUMBOLDT | 2020-08-13 |  | ETL.7490 | MAPLE CREEK-HOOPA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44145842 | 2011-12-30 | 2-Pole Non Wood | DDE - Double Dead End | [7 empty] | 0.33546 | 79.1467
119825202 | A | LC | ETL.4221.INSL.CERA | 44356194 | TABLEMTN | NORTH VALLEY | 2020-09-28 | 2020-10-08 | ETL.4221 | SLY CREEK TAP | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119835232 | F | LC | ETL.6470.POLE.WOOD | 40822612 | SACTO | SIERRA | 2020-09-08 | 2021-07-06 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 3 | Within Both | DLFL | 40822612 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.18576 | 427.3383
119844529 | A | LC | ETL.1110.POLE.WDPS | 44424652 | TABLEMTN | HUMBOLDT | 2020-09-28 | 2020-10-13 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP
119870296 | F | LC | ETL.7030.POLE.WOOD | 40668059 | TABLEMTN | NORTH VALLEY | 2020-10-05 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40668059 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.014181 | 3135.1345
119898513 | F | LC | ETL.6880.POLE.WOOD | 40912453 | LAKEVLLE | NORTH BAY | 2020-10-06 | 2021-10-04 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40912453 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.21054 | 4748.4502
119923199 | E | LC | ETL.1400.POLE.STPS | 44806630 | VICTOR | STOCKTON | 2020-10-19 | 2021-05-17 | ETL.1400 | DONNELLS-MI-WUK | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 3 | Within Both | COMP | 44779589 | 2019-06-25 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.3911e-05 | 1242.0833
119954407 | E | LC | ETL.8650.TOWR | 40582621 | FRESNO | YOSEMITE | 2020-10-23 | 2020-10-29 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40582621 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-11-18 | Glass | Dead End |  |  |  |  | 0.052158 | 4725.8886
119995840 | F | LC | ETL.6480.POLE.NWOD | 44695515 | SACTO | NORTH VALLEY | 2020-10-06 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44695515 | 2018-12-10 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-12-10 | Polymer | Dead End |  |  |  |  | 0.011494 | 284.7983
120160549 | E | LC | ETL.8650.POLE.NWOD | 44420190 | FRESNO | FRESNO | 2020-12-09 | 2021-08-12 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420190 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0056349 | 15.88
120161426 | F | LC | ETL.1050.TOWR | 40748612 | FRESNO | FRESNO | 2020-12-08 |  | ETL.1050 | BALCH-SANGER | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40748612 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.029624 | 6426.646
120190879 | E | LC | ETL.1110.POLE.WDPS | 44423921 | TABLEMTN | HUMBOLDT | 2020-12-11 | 2021-04-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423920 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012769 | 4848.5083
120235812 | E | LC | ETL.6280.POLE.WOOD | 40863721 | TABLEMTN | NORTH VALLEY | 2020-12-24 | 2021-08-23 | ETL.6280 | CARIBOU #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863721 | 2012-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Other |  |  |  |  | 3.3774e-05 | 1550.0629
120418557 | E | LC | ETL.6880.POLE.NWOD | 44928866 | LAKEVLLE | SONOMA | 2021-01-08 | 2021-07-06 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44928866 | 2020-06-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-06-11 | Glass | Dead End |  |  |  |  | 5.0707e-06 | 3852.5246
120646807 | F | LC | ETL.5290.TOWR | 40594693 | PISMOBCH | LOS PADRES | 2021-03-12 |  | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40594693 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-09-13 | Ceramic | Suspension |  |  |  |  | 2.1705e-09 | 1418.7379 | 3.0793e-06
120646807 | F | LC | ETL.5290.TOWR | 40594693 | PISMOBCH | LOS PADRES | 2021-03-12 |  | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40594693 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.1705e-09 | 1418.7379 | 3.0793e-06
120651585 | E | LC | ETL.4620.INSL.NCER | 45041286 | PISMOBCH | LOS PADRES | 2021-03-12 | 2021-08-12 | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40862858 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-09 | Glass | Suspension |  |  |  |  | 4.7724e-10 | 2438.1428
120651585 | E | LC | ETL.4620.INSL.NCER | 45041286 | PISMOBCH | LOS PADRES | 2021-03-12 | 2021-08-12 | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40862858 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 4.7724e-10 | 2438.1428
120666917 | E | LC | ETL.6880.POLE.WOOD | 40808985 | LAKEVLLE | SONOMA | 2021-03-20 | 2021-08-11 | ETL.6880 | FULTON-CALISTOGA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808985 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.078075 | 248.5123
120683984 | E | LC | ETL.3700.POLE.WOOD | 40751469 | PISMOBCH | LOS PADRES | 2021-03-22 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40751469 | 1989-01-01 | Single Wood Pole | SV-PJ-90 - Single Vertical Post Jumper 90 | 1989-01-01 | Porcelain | Dead End |  |  |  |  | 5.8243e-05 | 1792.0754 | 0.10438
120686235 | E | LC | ETL.6770.INSL.NCER | 40698932 | SACTO | SIERRA | 2021-03-24 |  | ETL.6770 | DRUM-SPAULDING | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40667549 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.0068047 | 443.0452 | 3.0148
120690056 | E | LC | ETL.8290.POLE.WOOD | 40826986 | TABLEMTN | NORTH VALLEY | 2021-03-25 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40826986 |  | Single Wood Pole | T-1 - Tri Post | 2019-06-07 | Polymer | Post |  |  |  |  | 0.010107 | 398.6012 | 4.0288
120701037 | E | LC | ETL.7390.POLE.WOOD | 40808769 | LAKEVLLE | SONOMA | 2021-03-27 | 2021-06-29 | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120713495 | F | LC | ETL.1890.TOWR | 40592622 | FRESNO | FRESNO | 2021-03-29 | 2021-09-27 | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40592622 | 1940-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1986-01-01 | Porcelain | Dead End |  |  |  |  | 8.2375e-07 | 5232.3709
120713495 | F | LC | ETL.1890.TOWR | 40592622 | FRESNO | FRESNO | 2021-03-29 | 2021-09-27 | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40592622 | 1940-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2015-12-01 | Ceramic | Dead End |  |  |  |  | 8.2375e-07 | 5232.3709
120715992 | E | LC | ETL.5330.TOWR | 40811397 | MOSSLNDG | CENTRAL COAST | 2021-03-30 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40811397 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 4.3115e-05 | 111.4269 | 0.0048042
120733717 | F | LC | ETL.7390.POLE.WDPS | 44411995 | LAKEVLLE | SONOMA | 2021-04-01 | 2021-05-31 | ETL.7390 | LAYTONVILLE-COVELO | Road | Brush Fuel | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44411993 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.064411 | 1344.7017
120750276 | E | LC | ETL.1350.POLE.NWOD | 44993117 | TABLEMTN | NORTH VALLEY | 2021-04-06 | 2021-07-28 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993117 | 2020-06-11 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-11 | Glass | Dead End |  |  |  |  | 6.2682e-05 | 79.1724
120794962 | E | LC | ETL.8250.POLE.WOOD | 40904162 | VICTOR | STOCKTON | 2021-04-12 | 2021-08-24 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40904162 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 8.6246e-05 | 1080.3165
120801780 | B | LC | ETL.3830.TOWR | 40803325 | VICTOR | STOCKTON | 2021-04-12 | 2021-04-27 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Tower | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803325 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.8861e-08 | 95.2198
120803493 | B | LC | ETL.4460.INSL | 40611979 | MOSSLNDG | CENTRAL COAST | 2021-04-12 | 2021-05-04 | ETL.4460 | COBURN-LAS AGUILAS SW STA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
120809096 | E | LC | ETL.3500.TOWR | 40822188 | VICTOR | STOCKTON | 2021-04-13 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40822188 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 1.8415e-05 | 2816.2285 | 0.051862
120833016 | B | LC | ETL.3830.INSL | 40669649 | VICTOR | STOCKTON | 2021-04-16 | 2021-05-27 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40642778 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 7.3198e-06 | 130.1517
120833586 | F | LC | ETL.6760.POLE.WOOD | 43249384 | SACTO | SACRAMENTO | 2021-04-16 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
120849392 | B | LC | ETL.3830.TOWR | 40744435 | VICTOR | STOCKTON | 2021-04-16 | 2021-05-27 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40744435 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 0.00050217 | 253.1151
120851064 | E | LC | ETL.4316.TOWR | 40591512 | TABLEMTN | NORTH VALLEY | 2021-04-13 | 2021-06-17 | ETL.4316 | PARADISE-TABLE MTN | Foundation/Concrete-Tower | Earth Covered Tower | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591512 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-18 | Glass | Suspension |  |  |  |  | 0.0087661 | 2883.9575
120869370 | F | LC | ETL.5463.TOWR | 40857950 | CONCORD | DIABLO | 2021-04-22 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40857950 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 5.7545e-08 | 3798.8403 | 0.0002186
120879128 | B | LC | ETL.3830.INSL | 40669649 | VICTOR | STOCKTON | 2021-04-24 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40642778 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 7.3198e-06 | 130.1517
120879264 | E | LC | ETL.8060.POLE.WOOD | 44145239 | SACTO | SACRAMENTO | 2021-04-24 | 2021-08-11 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44145239 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0088798 | 110.8102
120904189 | E | LC | ETL.6890.POLE.NWOD | 44873434 | LAKEVLLE | SONOMA | 2021-04-29 |  | ETL.6890 | FULTON-HOPLAND | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44873434 | 2020-01-08 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-01-08 | Polymer | Dead End |  |  |  |  | 6.7683e-07 | 2471.7993 | 0.001673
120911572 | E | LC | ETL.5930.TOWR | 40811225 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40811225 | 1963-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1963-01-01 | Ceramic | Suspension |  |  |  |  | 1.4029e-08 | 540.818 | 7.5873e-06
120911572 | E | LC | ETL.5930.TOWR | 40811225 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40811225 | 1963-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-24 | Glass | Suspension |  |  |  |  | 1.4029e-08 | 540.818 | 7.5873e-06
120932697 | F | LC | ETL.5463.TOWR | 40646987 | CONCORD | DIABLO | 2021-05-04 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40646987 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.2735e-08 | 4104.2041 | 5.2267e-05
120935412 | F | LC | ETL.3830.POLE.NWOD | 45080511 | VICTOR | STOCKTON | 2021-05-05 | 2021-08-10 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 45080511 |  | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2015-11-02 | Ceramic | Suspension |  |  |  |  | 3.3609e-07 | 5001.7144
120949792 | E | LC | ETL.7490.POLE.WOOD | 44429888 | EUREKA | HUMBOLDT | 2021-05-07 | 2021-05-26 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44429888 | 2018-08-10 | Single Wood Pole | T-1 - Tri Post | 2018-08-10 | Polymer | Post |  |  |  |  | 0.0020998 | 96.5446
120953591 | E | LC | ETL.1820.POLE.WDPS | 44565355 | EUREKA | HUMBOLDT | 2021-05-08 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564254 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.21096 | 5273.0366 | 1112.4065
120995327 | E | LC | ETL.7610.POLE.WOOD | 40767250 | METCALF | SAN JOSE | 2021-05-08 |  | ETL.7610 | MONTA VISTA-LOS GATOS | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | HFRA Removal | PEND | 40767250 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Non Ceramic | Pin |  |  |  |  | 0.00025163 | 0.065147 | 1.6393e-05
121109613 | E | LC | ETL.7290.POLE.WOOD | 44837841 | TABLEMTN | NORTH VALLEY | 2021-04-19 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44837841 | 2019-06-14 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-06-14 | Glass | Dead End |  |  |  |  | 0.049495 | 3289.9408 | 162.8361
121322655 | F | LC | ETL.2740.TOWR | 40857640 | CONCORD | DIABLO | 2021-04-21 | 2021-09-30 | ETL.2740 | MORAGA-OAKLAND #3 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40857640 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1960-01-01 | Polymer | Suspension |  |  |  |  | 8.3697e-06 | 0.065147
121329383 | F | LC | ETL.9250.POLE.WOOD | 40807856 | MIDWAY | KERN | 2021-04-22 |  | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40807856 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Pin |  |  |  |  | 0.020641 | 9424.9238
121334166 | E | LC | ETL.7490.POLE.STPS | 44957569 | EUREKA | HUMBOLDT | 2021-05-14 |  | ETL.7490 | MAPLE CREEK-HOOPA | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44957546 | 2020-07-20 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0011696 | 0.065148 | 7.6194e-05
121334249 | E | LC | ETL.6861.POLE.WOOD | 40750938 | LAKEVLLE | HUMBOLDT | 2021-04-23 |  | ETL.6861 | KONOCTI-EAGLE ROCK | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40750938 |  | Single Wood Pole | DV - Double Vertical | 2018-11-06 | Ceramic | Dead End |  |  |  |  | 0.043559 | 1740.3998 | 75.8102
121335818 | E | LC | ETL.6110.TOWR | 40863444 | METCALF | SAN JOSE | 2021-05-14 |  | ETL.6110 | TESLA-METCALF | Raptor Guard-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40863444 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.17e-06 | 2711.6123 | 0.0031726
121337842 | F | LC | ETL.7560.POLE.NWOD | 44923840 | SACTO | SIERRA | 2021-04-26 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44923840 | 2019-06-25 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-06-25 | Glass | Dead End |  |  |  |  | 0.015651 | 537.9071
121347677 | E | LC | ETL.4440.POLE.NWOD | 40674604 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40674604 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.00093225 | 6711.4282 | 6.2567
121360953 | F | LC | ETL.5290.TOWR | 40604854 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40604854 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-01-08 | Glass | Suspension |  |  |  |  | 1.6768e-07 | 634.7587 | 0.00010643
121360953 | F | LC | ETL.5290.TOWR | 40604854 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40604854 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-01-26 | Ceramic | Suspension |  |  |  |  | 1.6768e-07 | 634.7587 | 0.00010643
121363636 | B | LC | ETL.3750.TOWR | 44188773 | CONCORD | DIABLO | 2021-05-19 | 2021-06-21 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Hardware-Tower | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44188773 | 2008-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | [7 empty] | 1.7285e-06 | 398.0443
121364041 | E | LC | ETL.3700.POLE.WOOD | 40809770 | PISMOBCH | LOS PADRES | 2021-04-27 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40809770 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Porcelain | Post |  |  |  |  | 1.1039e-05 | 2941.5684 | 0.032471
121378530 | F | LC | ETL.6760.POLE.WOOD | 40822636 | SACTO | SIERRA | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40822636 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0046495 | 610.6596
121379758 | B | LC | ETL.4440.POLE.NWOD | 44190869 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-29 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44190869 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Ceramic | [5 empty] | 0.00060401 | 4683.9302
121379791 | B | LC | ETL.4440.POLE.NWOD | 44190870 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-30 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44190870 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 0.00075924 | 4683.9302
121380509 | F | LC | ETL.6760.POLE.NWOD | 40598597 | SACTO | SIERRA | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40598597 | 2010-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00055942 | 0.066432
121381289 | F | LC | ETL.6320.POLE.NWOD | 44294681 | TABLEMTN | NORTH VALLEY | 2021-05-07 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44294681 | 2015-10-24 | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 3.0649e-06 | 2491.2594
121382010 | E | LC | ETL.8250.POLE.WOOD | 40873057 | VICTOR | STOCKTON | 2021-05-08 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40873057 | 1993-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | [5 empty] | 0.00027623 | 3343.1924 | 0.9235
121382057 | E | LC | ETL.8250.POLE.WOOD | 40908836 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40908836 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00053222 | 1664.5133 | 0.88589
121383274 | F | LC | ETL.8000.POLE.NWOD | 44177824 | SACTO | SIERRA | 2021-05-11 |  | ETL.8000 | SMARTVILLE-NICOLAUS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44177824 | 2013-08-20 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2013-08-20 | Polymer | Post |  |  |  |  | 0.0027165 | 2646.7427
121383850 | E | LC | ETL.6320.POLE.NWOD | 44417892 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44417892 | 2019-03-12 | Light Duty Steel Pole | T-1 - Tri Post | 2019-03-12 | Polymer | Post |  |  |  |  | 0.00013833 | 4083.1003 | 0.5648
121388603 | E | LC | ETL.1430.TOWR | 40746589 | SACTO | SIERRA | 2021-05-15 |  | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40746589 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical |  | Ceramic | Post |  |  |  |  | 0.035415 | 158.3103 | 5.6066
121389203 | F | LC | ETL.1651.POLE.NWOD | 44144184 | LAKEVLLE | SONOMA | 2021-05-12 |  | ETL.1651 | MISSION POWER TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44144184 |  | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper |  | Polymer | Dead End |  |  |  |  | 9.3271e-07 | 1362.0701
121396871 | E | LC | ETL.6470.POLE.WOOD | 40767200 | SACTO | SACRAMENTO | 2021-05-25 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40767200 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.016058 | 142.5583 | 2.2892
121422168 | F | LC | ETL.6470.POLE.WOOD | 40602531 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40602531 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.048678 | 269.0426
121445849 | F | LC | ETL.6220.POLE.NWOD | 45019168 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45019168 | 2020-08-24 | Light Duty Steel Pole | TPA - Tri Pin Arm | 2020-08-24 | Polymer | Post |  |  |  |  | 0.024231 | 1645.0619
121493055 | E | LC | ETL.1820.POLE.WDPS | 44557755 | EUREKA | HUMBOLDT | 2021-06-01 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44553999 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.19228 | 284.8513 | 54.7716
121493286 | E | LC | ETL.4440.TOWR | 40757709 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.4440 | CARIBOU-TABLE MTN | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40757709 | 1968-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1968-01-01 | Porcelain | Dead End |  |  |  |  | 3.3244e-07 | 5260.656 | 0.0017489
121512525 | F | LC | ETL.1600.TOWR | 40761989 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40761989 | 1955-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1946-01-01 | Polymer | Suspension |  |  |  |  | 1.7861e-05 | 313.8482 | 0.0056057
121512576 | E | LC | ETL.1820.INSL.NCER | 40838001 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553879 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.54781
121512576 | E | LC | ETL.1820.INSL.NCER | 40838001 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553879 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.54781
121516137 | F | LC | ETL.5630.TOWR | 40813986 | TABLEMTN | NORTH VALLEY | 2021-06-01 |  | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40813986 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 4.0593e-05 | 601.2112 | 0.024405
121519141 | B | LC | ETL.1810.POLE.WDPS | 44322597 | EUREKA | HUMBOLDT | 2021-06-09 | 2021-07-15 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322596 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.056277 | 142.4559
121519935 | F | LC | ETL.4040.POLE.STPS | 44646878 | TABLEMTN | NORTH VALLEY | 2021-06-09 | 2021-07-12 | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44646878 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2018-08-17 | Ceramic | Double Dead End |  |  |  |  | 0.00011588
121519935 | F | LC | ETL.4040.POLE.STPS | 44646878 | TABLEMTN | NORTH VALLEY | 2021-06-09 | 2021-07-12 | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44646878 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2018-08-17 | Ceramic | Double Dead End |  |  |  |  | 0.00011588
121521460 | E | LC | ETL.1810.INSL.NCER | 40633952 | EUREKA | HUMBOLDT | 2021-06-08 | 2021-06-22 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44322625 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 0.033155
121521460 | E | LC | ETL.1810.INSL.NCER | 40633952 | EUREKA | HUMBOLDT | 2021-06-08 | 2021-06-22 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44322625 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 0.033155
121522381 | E | LC | ETL.6870.POLE.WOOD | 40751850 | SACTO | SIERRA | 2021-06-07 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40751850 | 1966-01-01 | Single Wood Pole | 3P DDE-A - 3 Pole Double Dead End Angle | 1966-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.12008 | 63.386 | 7.6115
121523357 | E | LC | ETL.7000.POLE.WOOD | 40769921 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40769921 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.010979 | 31.6978 | 0.34802
121523578 | F | LC | ETL.5640.POLE.STPS | 44327043 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44327042 | 2016-09-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.5818e-10 | 2836.814
121523814 | E | LC | ETL.1440.POLE.WDPS | 44162102 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44162100 | 2013-09-22 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00054256 | 632.957 | 0.34342
121531384 | B | LC | ETL.1820.INSL.NCER | 44395704 | EUREKA | HUMBOLDT | 2021-06-12 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44395516 | 2020-03-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-03-09 | Glass | Suspension |  |  |  |  | 0.048141
121531384 | B | LC | ETL.1820.INSL.NCER | 44395704 | EUREKA | HUMBOLDT | 2021-06-12 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44395516 | 2020-03-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-03-09 | Glass | Suspension |  |  |  |  | 0.048141
121535933 | E | LC | ETL.5390.TOWR | 40600999 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40600999 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 3.2945e-08 | 4230.8027 | 0.00013938
121543882 | E | LC | ETL.5650.TOWR | 40599929 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40599929 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-09-12 | Ceramic | Suspension |  |  |  |  | 1.6733e-05 | 4041.2002 | 0.067622
121555578 | F | LC | ETL.6750.POLE.WDPS | 44562115 | TABLEMTN | NORTH VALLEY | 2021-06-17 | 2021-07-12 | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44561587 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0020263 | 316.5068
121568674 | F | LC | ETL.1450.POLE.WDPS | 44947122 | SACTO | SIERRA | 2021-06-15 | 2021-07-02 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 42572869 | 1948-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0007842 | 1344.8513
121572345 | E | LC | ETL.6760.POLE.WOOD | 40671693 | SACTO | SIERRA | 2021-06-16 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40671693 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.012306 | 15.8837 | 0.19546
121572717 | E | LC | ETL.7550.POLE.WOOD | 40809286 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40809286 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | [5 empty] | 6.1574e-05 | 110.7947 | 0.0068221
121578021 | E | LC | ETL.4750.INSL.CERA | 40620223 | LAKEVLLE | SONOMA | 2021-06-17 |  | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40594204 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 3.3443e-07 | 3054.8015 | 0.0010216
121587045 | E | LC | ETL.1820.POLE.WDPS | 44560553 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560101 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.15385 | 1377.4816 | 211.928
121601101 | E | LC | ETL.6060.TOWR | 40601316 | TABLEMTN | NORTH VALLEY | 2021-06-24 |  | ETL.6060 | ROUND MTN-TABLE MTN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40601316 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.3091e-06 | 158.7331 | 0.00036653
121604349 | E | LC | ETL.6020.TOWR | 40868287 | TABLEMTN | NORTH VALLEY | 2021-06-24 |  | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40868287 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.0006077 | 791.1378 | 0.48077
121621270 | E | LC | ETL.7130.POLE.WDPS | 44315161 | EUREKA | HUMBOLDT | 2021-06-27 |  | ETL.7130 | HUMBOLDT-MAPLE CREEK | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44315160 | 2013-10-26 | 3-Pole Wood | SVDE - Single Vertical Dead End | [7 empty] | 0.0095661 | 0.065148 | 0.00062321
121632974 | E | LC | ETL.8250.POLE.WOOD | 40908843 | VICTOR | STOCKTON | 2021-06-23 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40908843 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0057599 | 1727.0282 | 9.9475
121634246 | F | LC | ETL.5390.TOWR | 40815949 | TABLEMTN | NORTH VALLEY | 2021-06-23 |  | ETL.5390 | PIT #1-COTTONWOOD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40815949 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.7238e-07 | 5133.3115
121641652 | B | LC | ETL.1380.INSL.CERA | 40843541 | PISMOBCH | LOS PADRES | 2021-06-30 | 2021-09-16 | ETL.1380 | DIVIDE-CABRILLO #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121648464 | F | LC | ETL.2720.TOWR | 40804631 | CONCORD | DIABLO | 2021-06-26 |  | ETL.2720 | MORAGA-OAKLAND #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40804631 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-04 | Glass | Suspension |  |  |  |  | 2.3525e-05 | 1362.2408 | 0.032047
121648464 | F | LC | ETL.2720.TOWR | 40804631 | CONCORD | DIABLO | 2021-06-26 |  | ETL.2720 | MORAGA-OAKLAND #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40804631 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | [5 empty] | 2.3525e-05 | 1362.2408 | 0.032047
121649292 | E | LC | ETL.7390.POLE.WOOD | 40808771 | LAKEVLLE | HUMBOLDT | 2021-06-28 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40808771 |  | Single Wood Pole | T2N | 2015-09-01 | Polymer | Post |  |  |  |  | 0.2867 | 1566.2241 | 449.0422
121653365 | E | LC | ETL.5520.INSL.CERA | 44313266 | CONCORD | EAST BAY | 2021-07-02 |  | ETL.5520 | PITTSBURG-TESLA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40765277 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 3.9539e-07 | 5644.9208 | 0.002232
121661533 | B | LC | ETL.2395.INSL.CERA | 40856324 | TABLEMTN | NORTH VALLEY | 2021-07-02 | 2021-07-13 | ETL.2395 | GRIZZLY TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44550855 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.11585 | 300.6002
121662526 | E | LC | ETL.3700.POLE.WDPS | 44296826 | PISMOBCH | LOS PADRES | 2021-06-30 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44296825 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00016233 | 4022.5613 | 0.65299
121676076 | E | LC | ETL.9240.TOWR | 43249675 | PISMOBCH | LOS PADRES | 2021-07-07 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier3 | Tier 3 | Within Both | PEND | 43249675 |  | LATTICE STEEL TOWER | [9 empty] | 756.4429
121678894 | F | LC | ETL.7550.POLE.WOOD | 40768566 | LAKEVLLE | HUMBOLDT | 2021-07-05 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40768566 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00011071 | 2787.9438 | 0.30865
121683999 | E | LC | ETL.9240.TOWR | 43249671 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249671 |  | LATTICE STEEL TOWER | [9 empty] | 1143.0077
121720573 | B | LC | ETL.1820.POLE.WDPS | 44557508 | EUREKA | HUMBOLDT | 2021-07-13 | 2021-08-04 | ETL.1820 | HUMBOLDT-TRINITY | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553926 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.99436 | 253.1639
121731455 | F | LC | ETL.4220.POLE.NWOD | 44935266 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.4220 | WOODLEAF-PALERMO | Guy Wire Mark /Indic-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44935266 | 2020-06-29 | Light Duty Steel Pole | 3P TRP D - 3 Pole Tramp Double Dead End | 2020-06-29 | Glass | Dead End |  |  |  |  | 0.0046868 | 395.6659
121737562 | B | LC | ETL.6040.TOWR | 40817987 | MOSSLNDG | YOSEMITE | 2021-07-15 | 2021-07-21 | ETL.6040 | MOSS LANDING-LOS BANOS | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40817987 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2011-11-16 | Ceramic | Suspension |  |  |  |  | 1.7398e-07
121738310 | F | LC | ETL.5430.POLE.STPS | 44659677 | TABLEMTN |  | 2021-07-09 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44148948 | 2016-12-08 | 2-Pole Non Wood | SS1 - Susp. Steel Single. CIR | [7 empty] | 1.3576e-06 | 759.4948
121738440 | F | LC | ETL.1820.POLE.STPS | 44395128 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395127 | 2020-03-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0066227 | 94.9939
121757063 | E | LC | ETL.5420.POLE.WDPS | 44559004 | TABLEMTN | NORTH VALLEY | 2021-07-14 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44558497 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.026582 | 189.9226 | 5.0485
121768063 | E | LC | ETL.5650.TOWR | 40764770 | TABLEMTN | NORTH VALLEY | 2021-07-21 | 2021-07-29 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Splice-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40764770 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-06 | Glass | Suspension |  |  |  |  | 5.8417e-07 | 3835.4036
121785747 | F | LC | ETL.7380.POLE.WOOD | 44562376 | MOSSLNDG | CENTRAL COAST | 2021-07-21 |  | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44562376 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.40477 | 15.8815
121787373 | E | LC | ETL.1810.POLE.WDPS | 44322523 | EUREKA | HUMBOLDT | 2021-07-23 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44322521 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0050197
121787857 | F | LC | ETL.1820.POLE.NWOD | 45111726 | EUREKA | HUMBOLDT | 2021-07-21 | 2021-08-09 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 45111726 | 2019-05-03 | Light Duty Steel Pole | DDE - Double Dead End | 2019-05-03 | Glass | Dead End | [5 empty] | 94.9585
121802731 | F | LC | ETL.7212.POLE.STPS | 44913913 | METCALF | PENINSULA | 2021-07-26 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44913910 | 2019-11-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.12437 | 602.2181
121810803 | E | LC | ETL.4040.POLE.STPS | 45151924 | TABLEMTN | NORTH VALLEY | 2021-07-27 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45151850 | 2020-01-23 | 2-Pole Non Wood | 2PS - 2 Pole SUSP
121812213 | E | LC | ETL.6760.POLE.WOOD | 40756228 | SACTO | SIERRA | 2021-07-27 | 2021-08-03 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL | [11 empty] | 0.11325 | 933.5001
121838502 | B | LC | ETL.7800.POLE.WOOD | 40820912 | SACTO | SACRAMENTO | 2021-08-03 | 2021-08-03 | ETL.7800 | PLACER-DEL MAR | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.3176e-05 | 2677.1912
121864608 | E | LC | ETL.6320.POLE.NWOD | 44673294 | TABLEMTN | NORTH VALLEY | 2021-08-09 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Conductor-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44673294 | 2018-11-13 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2018-11-13 | Polymer | Suspension |  |  |  |  | 0.00078911 | 1997.9036 | 1.5766
121900975 | B | LC | ETL.6380.POLE.NWOD | 40661647 | LAKEVLLE | SONOMA | 2021-08-13 | 2021-09-27 | ETL.6380 | KONOCTI-MIDDLETOWN | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40661647 |  | Light Duty Steel Pole | TPSR - Tri Post & Susp Light |  | Polymer | [5 empty] | 2.2127e-09 | 5480.7725
121947435 | E | LC | ETL.7290.POLE.WOOD | 40668411 | TABLEMTN | NORTH VALLEY | 2021-08-21 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Rotten | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40668411 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.044097 | 110.843 | 4.8879
122063841 | E | LC | ETL.4780.INSL | 40635381 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40602102 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 4.5306e-05 | 411.6203 | 0.018649
118576246 | E | LC | ETL.5930.INSL | 40713873 | CONCORD |  | 2020-02-25 | 2020-07-15 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662572 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-03-03 | Glass | Suspension |  |  |  |  | 4.3933e-07 | 1395.4297
118576246 | E | LC | ETL.5930.INSL | 40713873 | CONCORD |  | 2020-02-25 | 2020-07-15 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662572 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 4.3933e-07 | 1395.4297
118679487 | E | LC | ETL.4392.INSL.CERA | 44387076 | LAKEVLLE |  | 2020-02-04 | 2020-04-23 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40814648 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-03-09 | Porcelain | Dead End |  |  |  |  | 1.7661e-07 | 5180.0576
118679487 | E | LC | ETL.4392.INSL.CERA | 44387076 | LAKEVLLE |  | 2020-02-04 | 2020-04-23 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40814648 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-05-12 | Porcelain | Dead End |  |  |  |  | 1.7661e-07 | 5180.0576
118730455 | E | LC | ETL.2460.TOWR | 41153655 | PISMOBCH | LOS PADRES | 2020-03-21 | 2021-05-11 | ETL.2460 | MESA-SISQUOC | Foundation/Concrete-Tower | Earth Covered Tower | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41153655 | 1987-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | [5 empty] | 7.6865e-08 | 969.1475
118926655 | F | LC | ETL.5780.TOWR | 40586965 | VICTOR | STOCKTON | 2020-04-15 |  | ETL.5780 | TIGER CREEK-ELECTRA | Structure-Steel | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40586965 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1931-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00012548 | 175.6506
118956961 | F | LC | ETL.6220.POLE.WOOD | 40769376 | EUREKA | HUMBOLDT | 2020-04-28 | 2021-07-20 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40769376 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.043231 | 633.9066
118964048 | E | LC | ETL.7510.POLE.WOOD | 40769749 | LAKEVLLE | SONOMA | 2020-04-30 | 2020-06-08 | ETL.7510 | MENDOCINO-HARTLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40769749 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 3.4509e-06 | 4317.0959
118977426 | F | LC | ETL.6220.POLE.WOOD | 40769394 | EUREKA | HUMBOLDT | 2020-05-03 | 2021-11-01 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40769394 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.081344 | 587.9506
119030244 | E | LC | ETL.3150.TOWR | 40857750 | CONCORD | EAST BAY | 2020-05-12 | 2021-06-01 | ETL.3150 | OLEUM-G #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | HFRA Removal | COMP | 40857750 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-15 | Glass | Dead End |  |  |  |  | 2.4254e-06 | 0.065147
119030244 | E | LC | ETL.3150.TOWR | 40857750 | CONCORD | EAST BAY | 2020-05-12 | 2021-06-01 | ETL.3150 | OLEUM-G #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | HFRA Removal | COMP | 40857750 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2005-01-01 | Non Ceramic | Suspension |  |  |  |  | 2.4254e-06 | 0.065147
119049420 | E | LC | ETL.1240.POLE.WDPS | 44386139 | TABLEMTN | NORTH VALLEY | 2020-05-13 | 2020-06-11 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44386137 |  | 2-Pole Wood | 2PS TRP - 2 Pole SUSP. Transposition | [7 empty] | 1.6686e-05 | 2218.8638
119074898 | E | LC | ETL.1240.INSL.CERA | 40638343 | TABLEMTN | NORTH VALLEY | 2020-05-13 | 2020-06-30 | ETL.1240 | CASCADE-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119094932 | E | LC | ETL.8290.POLE.WOOD | 40601159 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-05-19 | ETL.8290 | VOLTA-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40601159 |  | Single Wood Pole | T2N | 2021-04-21 | Polymer | Post |  |  |  |  | 0.00013774 | 5431.645
119097279 | E | LC | ETL.5140.INSL.CERA | 40636078 | SACTO | SIERRA | 2020-05-19 | 2021-11-08 | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44553222 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0026278
119097279 | E | LC | ETL.5140.INSL.CERA | 40636078 | SACTO | SIERRA | 2020-05-19 | 2021-11-08 | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44553222 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0026278
119102783 | F | LC | ETL.1600.TOWR | 40587750 | LAKEVLLE | SONOMA | 2020-05-27 | 2021-03-08 | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587750 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 1.9486e-07 | 1140.1291
119106427 | B | LC | ETL.6280.POLE.WOOD | 40758790 | TABLEMTN | NORTH VALLEY | 2020-06-03 | 2020-08-24 | ETL.6280 | CARIBOU #2 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758790 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-08-12 | Glass | Dead End |  |  |  |  | 7.6108e-06 | 0.065148
119115384 | F | LC | ETL.7290.POLE.WOOD | 40874681 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-08-19 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40874681 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.017805 | 967.9307
119119003 | F | LC | ETL.7300.POLE.WOOD | 40816220 | TABLEMTN |  | 2020-06-04 | 2021-03-08 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119125792 | E | LC | ETL.7300.POLE.WOOD | 40600387 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-03-15 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119126898 | E | LC | ETL.4590.TOWR | 40910126 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-07-20 | ETL.4590 | CRESTA-RIO OSO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40910126 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-05 | Glass | Suspension |  |  |  |  | 2.4388e-05 | 269.3844
119128579 | F | LC | ETL.7300.POLE.NWOD | 44836602 | TABLEMTN | NORTH VALLEY | 2020-06-04 |  | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44836602 | 2019-03-14 | Light Duty Steel Pole | T-1 - Tri Post | 2019-03-14 | Polymer | Post |  |  |  |  | 3.2844e-08 | 3169.3833
119131186 | E | LC | ETL.4220.POLE.NWOD | 44921290 | TABLEMTN | NORTH VALLEY | 2020-06-09 | 2020-07-09 | ETL.4220 | WOODLEAF-PALERMO | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44921290 | 2020-05-08 | Light Duty Steel Pole | TPS1D - Tri Post & Susp DDE 115 KV | 2020-05-08 | Glass | Suspension |  |  |  |  | 0.0087209 | 2854.0244
119131388 | E | LC | ETL.6870.POLE.WOOD | 40664826 | SACTO | SACRAMENTO | 2020-06-09 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40664826 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.067014 | 94.9894 | 6.3656
119165566 | F | LC | ETL.5980.TOWR | 40819447 | PISMOBCH | LOS PADRES | 2020-06-15 | 2020-12-14 | ETL.5980 | DIABLO-MIDWAY #3 | Road | Grade Change | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40819447 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-18 | Glass Silicone Coated | Suspension |  |  |  |  | 5.0275e-10 | 5681.6509
119166573 | F | LC | ETL.5980.TOWR | 40871223 | PISMOBCH | LOS PADRES | 2020-06-15 | 2020-12-14 | ETL.5980 | DIABLO-MIDWAY #3 | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40871223 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-17 | Glass Silicone Coated | Suspension |  |  |  |  | 7.3716e-09 | 1629.5242
119168024 | E | LC | ETL.4760.TOWR | 40819421 | LAKEVLLE | HUMBOLDT | 2020-06-10 |  | ETL.4760 | GEYSERS #16 TAP | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40819421 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 6.3293e-05 | 5543.9175 | 0.35089
119169488 | E | LC | ETL.5463.TOWR | 40764882 | CONCORD | MISSION | 2020-06-15 | 2021-02-11 | ETL.5463 | PITTSBURG-SAN MATEO | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40764882 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.2707e-09 | 866.4883
119169488 | E | LC | ETL.5463.TOWR | 40764882 | CONCORD | MISSION | 2020-06-15 | 2021-02-11 | ETL.5463 | PITTSBURG-SAN MATEO | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40764882 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Non Ceramic | Dead End |  |  |  |  | 1.2707e-09 | 866.4883
119174832 | F | LC | ETL.1073.POLE.WDPS | 44963368 | VICTOR | YOSEMITE | 2020-06-16 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40744523 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00027239 | 1298.4628
119178742 | E | LC | ETL.6280.POLE.WOOD | 40868139 | TABLEMTN | NORTH VALLEY | 2020-06-16 | 2021-08-05 | ETL.6280 | CARIBOU #2 | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40868139 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 5.0586e-06 | 4.81
119179399 | E | LC | ETL.6770.INSL.NCER | 44874817 | SACTO | SIERRA | 2020-06-17 | 2021-05-17 | ETL.6770 | DRUM-SPAULDING | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119191490 | E | LC | ETL.6490.POLE.WOOD | 40768368 | SACTO | SACRAMENTO | 2020-06-18 | 2021-02-22 | ETL.6490 | COLGATE-GRASS VALLEY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768368 |  | Single Wood Pole | T2N | 2021-02-14 | Polymer | Post |  |  |  |  | 0.0047253 | 419.3189
119194909 | E | LC | ETL.6470.POLE.WOOD | 40611347 | SACTO | SIERRA | 2020-06-22 | 2021-07-27 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611347 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.32939 | 221.5931
119196363 | E | LC | ETL.6470.POLE.WOOD | 40873773 | SACTO | SIERRA | 2020-06-22 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40873773 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.19695 | 110.8608
119197785 | E | LC | ETL.6470.POLE.WOOD | 40693259 | SACTO | SIERRA | 2020-06-22 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693259 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.046845 | 79.2067
119197811 | F | LC | ETL.6470.POLE.WOOD | 40693259 | SACTO | SIERRA | 2020-06-22 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693259 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.046845 | 79.2067
119197981 | E | LC | ETL.6470.POLE.WOOD | 40693267 | SACTO | SIERRA | 2020-06-22 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693267 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.24726 | 110.8355
119198887 | F | LC | ETL.6480.POLE.WOOD | 40873603 | SACTO | SIERRA | 2020-06-22 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40873603 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.06112 | 284.7983
119206361 | E | LC | ETL.1820.POLE.STPS | 44395220 | EUREKA | HUMBOLDT | 2020-06-24 | 2021-05-20 | ETL.1820 | HUMBOLDT-TRINITY | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44395220 | 2017-09-21 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-09-21 | Ceramic | Suspension |  |  |  |  | 0.025236
119206361 | E | LC | ETL.1820.POLE.STPS | 44395220 | EUREKA | HUMBOLDT | 2020-06-24 | 2021-05-20 | ETL.1820 | HUMBOLDT-TRINITY | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44395220 | 2017-09-21 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-09-21 | Ceramic | Suspension |  |  |  |  | 0.025236
119206721 | E | LC | ETL.1450.POLE.WDPS | 44552392 | SACTO | SACRAMENTO | 2020-06-24 | 2020-08-18 | ETL.1450 | DRUM-SUMMIT #2 | Damper-Wood | Missing | [Install, Completed] | Tier3 |  |  | COMP
119226765 | A | LC | ETL.1381.POLE.WOOD | 40654909 | PISMOBCH | LOS PADRES | 2020-06-28 | 2020-07-31 | ETL.1381 | SURF TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119230749 | B | LC | ETL.8060.POLE.WOOD | 40586083 | SACTO | SIERRA | 2020-06-29 | 2020-06-30 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL | [11 empty] | 0.020761 | 47.5273
119238501 | E | LC | ETL.4050.POLE.STPS | 44838830 | LAKEVLLE | SONOMA | 2020-06-30 | 2021-04-15 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44339697 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 5.6616e-07 | 2375.632
119292304 | E | LC | ETL.1110.POLE.WDPS | 44423849 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-04-20 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119294761 | E | LC | ETL.3530.INSL.CERA | 40610003 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-02-02 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119301798 | F | LC | ETL.1450.POLE.WDPS | 44550030 | SACTO | SACRAMENTO | 2020-06-30 | 2021-04-21 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549475 | 2012-03-08 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00018978 | 1329.6379
119305364 | F | LC | ETL.9100.POLE.WOOD | 44191390 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-02-24 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.00011558 | 1173.0348
119315086 | F | LC | ETL.8170.POLE.WOOD | 40906233 | EUREKA | HUMBOLDT | 2020-07-06 |  | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40906233 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.042086 | 253.2084
119317378 | E | LC | ETL.7030.POLE.WOOD | 40591882 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-06-14 | ETL.7030 | HAT CREEK #1-WESTWOOD | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591882 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.00623 | 15.8837
119330592 | E | LC | ETL.7930.POLE.WOOD | 40588377 | MOSSLNDG | CENTRAL COAST | 2020-07-08 |  | ETL.7930 | SALINAS-LAURELES | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40588377 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Post |  |  |  |  | 0.0014739 | 111.5028 | 0.16435
119331497 | E | LC | ETL.6290.POLE.WOOD | 40675224 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-09-27 | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40675224 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.048402 | 5504.3154
119334433 | E | LC | ETL.7030.POLE.WOOD | 40877509 | TABLEMTN | NORTH VALLEY | 2020-07-08 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Animal Guard-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40877509 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.015985 | 0.066432 | 0.0010619
119357559 | E | LC | ETL.8351.POLE.WOOD | 40587995 | VICTOR | STOCKTON | 2020-07-10 | 2021-06-28 | ETL.8351 | PINE GROVE TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587995 | 1977-01-01 | Single Wood Pole | FDDE - Flat Dead End Construction |  | Glass | [5 empty] | 0.00057178 | 33.284
119358821 | E | LC | ETL.4750.TOWR | 41129172 | LAKEVLLE | SONOMA | 2020-07-11 | 2021-06-10 | ETL.4750 | GEYSERS #12-FULTON | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129172 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | Dead End |  |  |  |  | 0.00039529 | 1172.524
119360158 | F | LC | ETL.7270.POLE.NWOD | 44649362 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44649362 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 5.2134e-05 | 538.1084
119362816 | E | LC | ETL.7590.POLE.WOOD | 40612294 | MOSSLNDG | CENTRAL COAST | 2020-07-13 | 2020-12-16 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119363717 | E | LC | ETL.6290.POLE.WOOD | 40768906 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-09-01 | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768906 | 1962-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2011-01-01 | Polymer | Dead End |  |  |  |  | 0.0096861 | 775.064
119364319 | E | LC | ETL.1430.TOWR | 40757182 | SACTO | SACRAMENTO | 2020-07-13 | 2021-06-28 | ETL.1430 | DRUM-RIO OSO #2 | Anchor-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40757182 | 1913-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-07-10 | Glass | Dead End |  |  |  |  | 0.0032913 | 1993.4753
119371180 | F | LC | ETL.2395.POLE.WDPS | 44550797 | TABLEMTN | NORTH VALLEY | 2020-07-14 |  | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 3 | Within Both | PEND | 44550099 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0057356 | 47.5394
119371333 | E | LC | ETL.6290.POLE.WOOD | 40698825 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-08-23 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40698825 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2011-01-01 | Polymer | Post |  |  |  |  | 0.0097571 | 63.3304
119481370 | F | LC | ETL.6290.POLE.WOOD | 40809564 | TABLEMTN | NORTH VALLEY | 2020-07-21 | 2021-10-04 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40809564 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.25245 | 1043.9412
119489896 | F | LC | ETL.8170.POLE.WOOD | 40906289 | EUREKA | HUMBOLDT | 2020-07-22 | 2020-08-10 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40906289 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0309 | 633.6064
119500589 | F | LC | ETL.7780.POLE.WOOD | 40666580 | LAKEVLLE | SONOMA | 2020-07-24 | 2021-02-16 | ETL.7780 | PHILO JCT-ELK | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40666580 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-07-27 | Glass | Double Dead End |  |  |  |  | 0.00016483 | 6063.5518
119517326 | E | LC | ETL.6480.POLE.WOOD | 40655138 | SACTO | SACRAMENTO | 2020-07-28 | 2021-06-22 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40655138 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.22184 | 664.4426
119554492 | E | LC | ETL.6220.POLE.WOOD | 40752600 | EUREKA | HUMBOLDT | 2020-07-30 | 2021-03-08 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752600 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.049547 | 499.5109
119557094 | E | LC | ETL.1073.POLE.WDPS | 44779570 | VICTOR | STOCKTON | 2020-08-04 | 2021-11-17 | ETL.1073 | MI-WUK-CURTIS | Hardware-Wood | Missing | [Install, Completed] |  | Tier 3 | Within Both | COMP | 40803725 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00070015 | 31.7081 | 0.0222
119566945 | F | LC | ETL.7780.POLE.WOOD | 40600310 | LAKEVLLE | HUMBOLDT | 2020-08-05 | 2021-01-20 | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40600310 |  | Single Wood Pole | T2N | 2020-01-05 | Polymer | Post |  |  |  |  | 8.0882e-05 | 474.6204
119596421 | F | LC | ETL.1380.POLE.WOOD | 40826472 | PISMOBCH | LOS PADRES | 2020-08-02 |  | ETL.1380 | DIVIDE-CABRILLO #1 | Road | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40826472 | 1960-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 2017-10-10 | Ceramic | Suspension |  |  |  |  | 0.0068468 | 696.2467
119608756 | E | LC | ETL.6220.POLE.WOOD | 40862820 | EUREKA | HUMBOLDT | 2020-08-12 | 2021-02-22 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40862820 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.019165 | 499.5363
119615458 | E | LC | ETL.1810.POLE.STPS | 44322671 | EUREKA | HUMBOLDT | 2020-08-14 | 2021-07-15 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Crossarm-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | DLFL | 44322671 | 2016-10-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2021-05-17 | Glass Silicone Coated | Suspension |  |  |  |  | 8.1857e-08
119615458 | E | LC | ETL.1810.POLE.STPS | 44322671 | EUREKA | HUMBOLDT | 2020-08-14 | 2021-07-15 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Crossarm-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | DLFL | 44322671 | 2016-10-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2021-05-17 | Glass Silicone Coated | Suspension |  |  |  |  | 8.1857e-08
119644991 | B | LC | ETL.8650.POLE.NWOD | 44420186 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420186 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0039383 | 6847.8872
119670065 | E | LC | ETL.4100.TOWR | 40755555 | SACTO | SACRAMENTO | 2020-08-25 | 2021-02-11 | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40755555 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 6.8488e-06 | 5905.3706
119670065 | E | LC | ETL.4100.TOWR | 40755555 | SACTO | SACRAMENTO | 2020-08-25 | 2021-02-11 | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40755555 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Polymer | Suspension |  |  |  |  | 6.8488e-06 | 5905.3706
119709836 | E | LC | ETL.7290.POLE.WOOD | 40664566 | TABLEMTN | NORTH VALLEY | 2020-08-29 | 2021-03-01 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664566 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0030092 | 968.9049
119719680 | B | LC | ETL.3960.INSL.CERA | 40833950 | PISMOBCH | LOS PADRES | 2020-08-18 | 2020-10-05 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809283 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 8.8025e-09 | 4322.5879
119722788 | E | LC | ETL.8410.POLE.WOOD | 40667884 | LAKEVLLE | HUMBOLDT | 2020-08-03 | 2021-05-24 | ETL.8410 | ELK-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40667884 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Porcelain | Suspension |  |  |  |  | 0.22459 | 15.8807
119754789 | F | LC | ETL.6890.POLE.WOOD | 40861110 | LAKEVLLE | SONOMA | 2020-07-21 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40861110 | 1991-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.00013572 | 1884.5717
119760683 | F | LC | ETL.4590.TOWR | 40910128 | TABLEMTN | NORTH VALLEY | 2020-09-04 |  | ETL.4590 | CRESTA-RIO OSO | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40910128 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-03-15 | Ceramic | Suspension |  |  |  |  | 0.00025627 | 3414.2131 | 0.87495
119764674 | B | LC | ETL.1800.INSL.NCER | 44325759 | EUREKA | HUMBOLDT | 2020-09-14 | 2020-10-01 | ETL.1800 | HUMBOLDT BAY-HUMBOLDT #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750600 | 1955-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1955-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.131e-06 | 0.066432
119766474 | E | LC | ETL.1110.POLE.WDPS | 44424526 | TABLEMTN | HUMBOLDT | 2020-09-08 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44424525 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012548 | 9423.3379
119769303 | E | LC | ETL.1110.POLE.WDPS | 44232668 | TABLEMTN | HUMBOLDT | 2020-07-13 | 2021-04-22 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44232667 | 2014-10-28 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017518 | 3692.7366
119781175 | F | LC | ETL.8350.POLE.WOOD | 40744880 | VICTOR | STOCKTON | 2020-09-11 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40744880 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.016454 | 2547.073
119794680 | F | LC | ETL.7510.POLE.WOOD | 40752849 | LAKEVLLE | HUMBOLDT | 2020-09-17 |  | ETL.7510 | MENDOCINO-HARTLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40752849 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 9.6599e-05 | 5382.7134
119794684 | F | LC | ETL.7510.POLE.WOOD | 40615488 | LAKEVLLE | HUMBOLDT | 2020-09-17 |  | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40615488 |  | Single Wood Pole | T-1 - Tri Post | 2019-11-17 | Polymer | Post |  |  |  |  | 3.4009e-06 | 5319.5312
119803256 | F | LC | ETL.8405.POLE.NWOD | 44312964 | SACTO | SIERRA | 2020-08-07 |  | ETL.8405 | MIDDLE FORK #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44312964 | 2016-08-15 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2016-08-15 | Porcelain | Suspension |  |  |  |  | 0.00010556 | 6759.7114
119815998 | F | LC | ETL.8650.POLE.NWOD | 44420197 | FRESNO | YOSEMITE | 2020-09-10 | 2021-09-01 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420197 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0062058 | 1281.0665
119825200 | A | LC | ETL.4221.INSL.CERA | 44356186 | TABLEMTN | NORTH VALLEY | 2020-09-28 | 2020-10-08 | ETL.4221 | SLY CREEK TAP | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119862681 | E | LC | ETL.1110.POLE.WDPS | 44423205 | TABLEMTN | HUMBOLDT | 2020-09-08 | 2021-05-04 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119867772 | E | LC | ETL.6110.TOWR | 40592647 | METCALF | SAN JOSE | 2020-10-07 | 2021-06-01 | ETL.6110 | TESLA-METCALF | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592647 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2012-01-31 | Ceramic | Suspension |  |  |  |  | 8.0064e-09 | 301.0515
119898486 | F | LC | ETL.7212.POLE.NWOD | 44649361 | METCALF | PENINSULA | 2020-10-07 | 2021-04-29 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44649361 | 2018-08-30 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-30 | Polymer | Suspension |  |  |  |  | 0.14466 | 94.9668
119898924 | B | LC | ETL.6610.INSL.NCER | 44214189 | SACTO | SACRAMENTO | 2020-10-13 | 2021-01-07 | ETL.6610 | CORTINA #4 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119953588 | E | LC | ETL.7380.POLE.WOOD | 40809417 | MOSSLNDG | CENTRAL COAST | 2020-10-22 | 2021-08-12 | ETL.7380 | LAURELES-OTTER | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809417 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0055092 | 0.065147
119992540 | E | LC | ETL.8405.POLE.WOOD | 40619304 | SACTO | SIERRA | 2020-11-03 | 2021-10-20 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40619304 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-10-18 | Glass | Dead End |  |  |  |  | 0.0095632 | 6723.8696 | 64.302
119994945 | F | LC | ETL.6280.POLE.NWOD | 40862047 | TABLEMTN | NORTH VALLEY | 2020-11-04 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40862047 |  | Light Duty Steel Pole | FDDE - Flat Dead End Construction |  | Non Ceramic | Dead End |  |  |  |  | 0.00018936 | 5538.7192
119995910 | F | LC | ETL.6880.POLE.WOOD | 40751174 | LAKEVLLE | NORTH BAY | 2020-10-06 | 2021-07-19 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
120069582 | E | LC | ETL.6070.TOWR | 40765614 | TABLEMTN | NORTH VALLEY | 2020-11-18 | 2021-09-07 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Anchor-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40765614 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-10-03 | Glass | Suspension |  |  |  |  | 0.0021674 | 2358.1025
120096891 | E | LC | ETL.8060.POLE.WOOD | 40770670 | SACTO | SIERRA | 2020-11-23 | 2021-07-06 | ETL.8060 | SPAULDING-SUMMIT | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40770670 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | [5 empty] | 0.072811 | 0.065152
120130517 | F | LC | ETL.6280.POLE.NWOD | 44908682 | TABLEMTN | NORTH VALLEY | 2020-10-21 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44908682 | 2020-02-21 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-02-21 | Polymer | Dead End |  |  |  |  | 9.3284e-08 | 1298.3811
120133710 | F | LC | ETL.6280.POLE.WOOD | 40675347 | TABLEMTN | NORTH VALLEY | 2020-12-04 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40675347 |  | Single Wood Pole | TP - Tri Pin |  | Unknown | Dead End |  |  |  |  | 0.08148 | 5538.7192
120133945 | F | LC | ETL.6280.POLE.WOOD | 40614985 | TABLEMTN | NORTH VALLEY | 2020-10-21 | 2021-08-05 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | DLFL | [11 empty] | 2.9953e-05 | 844.7215
120139503 | F | LC | ETL.8365.POLE.WOOD | 40912657 | EUREKA | HUMBOLDT | 2020-11-02 | 2021-06-30 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40912657 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.17783
120531117 | B | LC | ETL.4680.TOWR | 40765346 | LAKEVLLE | SONOMA | 2021-02-12 | 2021-02-22 | ETL.4680 | FULTON-IGNACIO #1 | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40765346 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Other |  |  |  |  | 9.6681e-05 | 5176.4469
120531117 | B | LC | ETL.4680.TOWR | 40765346 | LAKEVLLE | SONOMA | 2021-02-12 | 2021-02-22 | ETL.4680 | FULTON-IGNACIO #1 | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40765346 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 9.6681e-05 | 5176.4469
120601470 | E | LC | ETL.6020.TOWR | 40821490 | TABLEMTN | NORTH VALLEY | 2021-03-04 | 2021-07-19 | ETL.6020 | MALIN-ROUND MTN #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40821490 | 1993-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.9175e-07 | 1112.6673
120675012 | E | LC | ETL.7970.POLE.WOOD | 40866734 | SACTO | SACRAMENTO | 2021-03-22 |  | ETL.7970 | SMARTVILLE-CAMP FAR WEST | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40866734 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.00013418 | 2646.7427 | 0.35514
120677846 | E | LC | ETL.7270.POLE.WOOD | 40909434 | TABLEMTN | NORTH VALLEY | 2021-03-23 | 2021-10-26 | ETL.7270 | KESWICK-TRINITY | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40909434 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.003139 | 142.6986 | 0.44793
120698537 | E | LC | ETL.4393.INSL.NCER | 45074181 | SACTO | SIERRA | 2021-03-26 |  | ETL.4393 | DRUM-HIGGINS | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40650082 |  | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-03-20 | Glass | Double Dead End |  |  |  |  | 0.00012704 | 166.2143 | 0.021116
120717554 | B | LC | ETL.5090.INSL | 40851682 | MOSSLNDG | CENTRAL COAST | 2021-03-30 | 2021-06-10 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822617 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0019654 | 1488.3317
120719189 | E | LC | ETL.1890.TOWR | 40859600 | FRESNO | FRESNO | 2021-03-30 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40859600 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1986-01-01 | Porcelain | Suspension |  |  |  |  | 8.9142e-10
120726683 | E | LC | ETL.6760.POLE.WOOD | 44964260 | SACTO | SACRAMENTO | 2021-04-01 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44964260 | 2019-08-14 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-08-14 | Glass | Dead End |  |  |  |  | 0.0061744 | 901.7202 | 5.5676
120727388 | E | LC | ETL.7390.POLE.WDPS | 44412006 | LAKEVLLE | SONOMA | 2021-04-01 | 2021-07-29 | ETL.7390 | LAYTONVILLE-COVELO | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44412005 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.10287 | 1265.6471
120737370 | E | LC | ETL.3840.INSL.CERA | 40603119 | VICTOR | STOCKTON | 2021-04-01 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40579601 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 2.6396e-05 | 47.6362 | 0.0012574
120744811 | F | LC | ETL.4750.TOWR | 40865681 | LAKEVLLE | SONOMA | 2021-04-05 |  | ETL.4750 | GEYSERS #12-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40865681 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 5.0561e-06 | 3246.7576 | 0.016416
120746282 | F | LC | ETL.4316.POLE.NWOD | 44674852 | TABLEMTN | NORTH VALLEY | 2021-03-25 |  | ETL.4316 | PARADISE-TABLE MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44674852 | 2018-11-18 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-18 | Polymer | Post |  |  |  |  | 0.0001643 | 2867.8025
120759238 | E | LC | ETL.7590.POLE.NWOD | 45035841 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.7590 | MONTA VISTA-BURNS | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45035841 | 2020-09-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-09-18 | Glass | Dead End |  |  |  |  | 0.040138 | 47.5295 | 1.9077
120761803 | E | LC | ETL.7140.POLE.WDPS | 44942597 | LAKEVLLE | SONOMA | 2021-04-07 | 2021-08-04 | ETL.7140 | IGNACIO-BOLINAS #1 | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41118222 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.054361 | 4560.6943
120762651 | B | LC | ETL.8960.POLE.WOOD | 44231453 | FRESNO | YOSEMITE | 2021-04-07 | 2021-06-26 | ETL.8960 | LOS BANOS-PACHECO | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44231453 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | [5 empty] | 0.00017474
120806507 | E | LC | ETL.1450.POLE.WDPS | 44549946 | SACTO | SACRAMENTO | 2021-04-13 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44549462 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014358 | 47.5526 | 0.068274
120806599 | F | LC | ETL.4771.TOWR | 40752305 | LAKEVLLE | SONOMA | 2021-04-13 |  | ETL.4771 | BOTTLE ROCK TAP D.W.R. | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40752305 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 3.0064e-05 | 3276.6768 | 0.098511
120808941 | E | LC | ETL.8365.POLE.NWOD | 40912574 | EUREKA | HUMBOLDT | 2021-04-13 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Splice-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40912574 | 2010-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0050618
120812188 | E | LC | ETL.1252.INSL.NCER | 40708310 | FRESNO | FRESNO | 2021-04-08 |  | ETL.1252 | OAKHURST TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40652335 | 2005-01-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2005-01-01 | Polymer | Dead End |  |  |  |  | 1.2763e-07 | 94.9541 | 1.2119e-05
120813894 | E | LC | ETL.3820.TOWR | 40596302 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40596302 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 3.7609e-07 | 0.077799 | 2.926e-08
120821505 | E | LC | ETL.5850.TOWR | 40818160 | LAKEVLLE | SACRAMENTO | 2021-04-15 | 2021-10-20 | ETL.5850 | VACA-PARKWAY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818160 | 1946-01-01 | LATTICE STEEL TOWER | Unknown | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.9042e-07 | 4687.7139 | 0.0027677
120821505 | E | LC | ETL.5850.TOWR | 40818160 | LAKEVLLE | SACRAMENTO | 2021-04-15 | 2021-10-20 | ETL.5850 | VACA-PARKWAY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818160 | 1946-01-01 | LATTICE STEEL TOWER | Unknown | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.9042e-07 | 4687.7139 | 0.0027677
120833891 | F | LC | ETL.1420.TOWR | 40765378 | SACTO | SACRAMENTO | 2021-04-17 | 2021-11-15 | ETL.1420 | DRUM-RIO OSO #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40765378 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-12 | Glass | Suspension |  |  |  |  | 5.3062e-06 | 205.7345
120860539 | F | LC | ETL.1421.TOWR | 40581248 | SACTO | SACRAMENTO | 2021-04-21 |  | ETL.1421 | DUTCH FLAT #2 TAP | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40581248 | 1966-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | [7 empty] | 0.001368 | 664.5352 | 0.90908
120860714 | F | LC | ETL.1820.POLE.WDPS | 44562672 | EUREKA | HUMBOLDT | 2021-04-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Right of Way | Encroachment | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44562337 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.072731 | 0.065148
120868772 | E | LC | ETL.2790.INSL | 40851167 | CONCORD | EAST BAY | 2021-04-22 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40822221 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.71e-06 | 0.065159 | 3.069e-07
120873432 | E | LC | ETL.5330.INSL | 40885093 | MOSSLNDG | CENTRAL COAST | 2021-04-23 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40862917 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 5.1728e-07 | 47.5223 | 2.4582e-05
120873432 | E | LC | ETL.5330.INSL | 40885093 | MOSSLNDG | CENTRAL COAST | 2021-04-23 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40862917 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 5.1728e-07 | 47.5223 | 2.4582e-05
120879332 | B | LC | ETL.1810.POLE.WDPS | 44322219 | EUREKA | HUMBOLDT | 2021-04-23 | 2021-06-21 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322218 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.2137e-06 | 1118.868
120888744 | E | LC | ETL.6100.INSL | 40620972 | VICTOR | STOCKTON | 2021-04-27 |  | ETL.6100 | TESLA-LOS BANOS #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40594769 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.6561e-09 | 2046.0553 | 3.3885e-06
120891946 | E | LC | ETL.6890.POLE.WOOD | 40825324 | LAKEVLLE | SONOMA | 2021-04-27 | 2021-08-12 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40825324 | 1967-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Other |  |  |  |  | 0.0023391 | 982.4404
120910807 | E | LC | ETL.6470.POLE.WOOD | 40593288 | SACTO | SACRAMENTO | 2021-04-30 | 2021-05-27 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40593288 |  | Single Wood Pole | T2N | 2021-07-19 | Polymer | Post |  |  |  |  | 0.0041831 | 189.8873
120912640 | E | LC | ETL.6470.POLE.WOOD | 40598546 | SACTO | SACRAMENTO | 2021-05-01 | 2021-08-02 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40598546 |  | Single Wood Pole | T2N | 2021-07-19 | Polymer | Post |  |  |  |  | 0.0057501 | 221.5243
120922193 | E | LC | ETL.7000.POLE.WOOD | 40868223 | TABLEMTN | NORTH VALLEY | 2021-05-03 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40868223 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.0017074 | 47.5141 | 0.081124
120922269 | E | LC | ETL.4316.INSL.NCER | 44712222 | TABLEMTN | NORTH VALLEY | 2021-05-03 | 2021-09-15 | ETL.4316 | PARADISE-TABLE MTN | Damper-Wood | Missing | [Install, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44712214 | 2019-02-13 | 3-Pole Non Wood | T-1 - Tri Post | 2019-02-13 | Polymer | Post |  |  |  |  | 0.00031566
120922269 | E | LC | ETL.4316.INSL.NCER | 44712222 | TABLEMTN | NORTH VALLEY | 2021-05-03 | 2021-09-15 | ETL.4316 | PARADISE-TABLE MTN | Damper-Wood | Missing | [Install, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44712214 | 2019-02-13 | 3-Pole Non Wood | T-1 - Tri Post | 2019-02-13 | Polymer | Post |  |  |  |  | 0.00031566
120922269 | E | LC | ETL.4316.INSL.NCER | 44712222 | TABLEMTN | NORTH VALLEY | 2021-05-03 | 2021-09-15 | ETL.4316 | PARADISE-TABLE MTN | Damper-Wood | Missing | [Install, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44712214 | 2019-02-13 | 3-Pole Non Wood | T-1 - Tri Post | 2019-02-13 | Polymer | Post |  |  |  |  | 0.00031566
120924249 | F | LC | ETL.6890.POLE.NWOD | 44203654 | LAKEVLLE | SONOMA | 2021-05-03 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44203654 | 2014-02-26 | Light Duty Steel Pole | T-1 - Tri Post | 2014-02-26 | Polymer | Post |  |  |  |  | 1.1283e-06 | 2646.5767
120926996 | B | LC | ETL.6950.INSL.NCER | 40730999 | SACTO | SACRAMENTO | 2021-05-01 | 2021-07-28 | ETL.6950 | GOLD HILL #1 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
120938821 | B | LC | ETL.7490.INSL.NCER | 44651154 | EUREKA | HUMBOLDT | 2021-05-05 | 2021-08-02 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44145872 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-07 | Polymer | Suspension |  |  |  |  | 0.0001571 | 221.4934
121321142 | F | LC | ETL.1600.TOWR | 40752060 | LAKEVLLE | SONOMA | 2021-05-12 |  | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40752060 | 1946-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2019-08-17 | Ceramic | Dead End |  |  |  |  | 3.7935e-07 | 1680.2917 | 0.00063742
121322653 | F | LC | ETL.2740.TOWR | 40857640 | CONCORD | DIABLO | 2021-04-21 |  | ETL.2740 | MORAGA-OAKLAND #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40857640 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1960-01-01 | Polymer | Suspension |  |  |  |  | 8.3697e-06 | 0.065147 | 5.4526e-07
121325390 | B | LC | ETL.4393.INSL.CERA | 40834416 | SACTO | SACRAMENTO | 2021-05-12 | 2021-08-04 | ETL.4393 | DRUM-HIGGINS | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809704 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [6 empty] | 1914.2439
121329093 | F | LC | ETL.4393.TOWR | 40913041 | SACTO | SIERRA | 2021-04-24 |  | ETL.4393 | DRUM-HIGGINS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40913041 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 3.9449e-08 | 1471.1865 | 5.8037e-05
121340519 | E | LC | ETL.6470.POLE.WOOD | 40665267 | SACTO | SACRAMENTO | 2021-05-15 | 2021-08-05 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40665267 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.083269 | 142.5149
121363607 | F | LC | ETL.1420.TOWR | 40813551 | SACTO | SIERRA | 2021-04-28 | 2021-09-29 | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40813551 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-05-02 | Glass | Suspension |  |  |  |  | 0.0019671 | 3291.7322
121363607 | F | LC | ETL.1420.TOWR | 40813551 | SACTO | SIERRA | 2021-04-28 | 2021-09-29 | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40813551 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.0019671 | 3291.7322
121364879 | E | LC | ETL.6870.POLE.WOOD | 40586044 | SACTO | SIERRA | 2021-05-19 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40586044 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post | 1966-01-01 | Ceramic | Post |  |  |  |  | 0.14453 | 126.6562 | 18.3059
121370518 | E | LC | ETL.6950.INSL.NCER | 40901948 | SACTO | SACRAMENTO | 2021-05-01 |  | ETL.6950 | GOLD HILL #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40876107 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.001461 | 118.8961 | 0.17371
121381953 | E | LC | ETL.8250.POLE.WOOD | 40904115 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40904115 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00021053 | 4054.8416 | 0.85367
121384911 | F | LC | ETL.1430.TOWR | 40866979 | SACTO | SIERRA | 2021-05-12 |  | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40866979 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical | 2016-11-14 | Non Ceramic | Post |  |  |  |  | 0.00071044 | 775.2733 | 0.55078
121384963 | B | LC | ETL.4880.TOWR | 40740447 | FRESNO | FRESNO | 2021-05-22 | 2021-07-15 | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Zone 1 | HFRA Removal | COMP | 40740447 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 1.2866e-05 | 15.8815
121398027 | F | LC | ETL.6470.POLE.WOOD | 40868962 | SACTO | SIERRA | 2021-05-19 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40868962 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.21419 | 142.5149
121417480 | B | LC | ETL.4316.POLE.STPS | 44712240 | TABLEMTN | NORTH VALLEY | 2021-05-26 | 2021-06-04 | ETL.4316 | PARADISE-TABLE MTN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44712220 | 2019-02-13 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0042191 | 506.6335
121418572 | E | LC | ETL.1073.POLE.WDPS | 44948174 | VICTOR | YOSEMITE | 2021-05-25 | 2021-10-21 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40803417 |  | 3-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0036361 | 31.7081 | 0.11529
121418577 | F | LC | ETL.1073.POLE.STPS | 44384831 | VICTOR | YOSEMITE | 2021-05-25 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44384830 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.4669e-05 | 23.7973
121436770 | F | LC | ETL.6470.POLE.WOOD | 40658312 | SACTO | SIERRA | 2021-05-27 | 2021-06-11 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40658312 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.092793 | 110.8608
121445230 | F | LC | ETL.1400.POLE.STPS | 44806631 | VICTOR | YOSEMITE | 2021-06-01 | 2021-10-04 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44779589 | 2019-06-25 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.3911e-05 | 1242.0833
121446067 | B | LC | ETL.6110.INSL | 40887779 | METCALF | SAN JOSE | 2021-06-02 | 2021-06-28 | ETL.6110 | TESLA-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863783 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.8393e-08 | 1776.9337
121485297 | F | LC | ETL.5140.POLE.STPS | 45146371 | SACTO | SIERRA | 2021-05-29 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45146244 | 2020-10-11 | 2-Pole Non Wood | 2PS - 2 Pole SUSP
121485673 | E | LC | ETL.7550.POLE.WOOD | 40826155 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40826155 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00045837 | 4067.2947 | 1.8643
121491913 | B | LC | ETL.8060.INSL.NCER | 40901193 | SACTO | SIERRA | 2021-06-08 | 2021-08-31 | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876713 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Polymer | [5 empty] | 0.0067894 | 63.348
121496578 | E | LC | ETL.1600.TOWR | 40752686 | LAKEVLLE | NORTH BAY | 2021-06-01 |  | ETL.1600 | FULTON-PUEBLO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40752686 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Polymer | Suspension |  |  |  |  | 2.0113e-06 | 0.06643 | 1.3361e-07
121518333 | E | LC | ETL.5650.TOWR | 40765176 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40765176 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.3299e-06 | 2394.3987 | 0.0031843
121525691 | E | LC | ETL.6511.POLE.WDPS | 44192872 | SACTO | SACRAMENTO | 2021-06-12 |  | ETL.6511 | NARROWS #1 TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44192870 | 2014-10-22 | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 1.83e-05 | 348.6017 | 0.0063793
121526454 | F | LC | ETL.1350.POLE.WDPS | 44551488 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40759412 | 1993-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.059566 | 3817.3882 | 227.3864
121527094 | E | LC | ETL.3745.TOWR | 40863612 | LAKEVLLE | NORTH BAY | 2021-06-08 |  | ETL.3745 | LAKEVILLE-IGNACIO #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40863612 | 1956-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 1.1146e-06 | 94.985 | 0.00010587
121528843 | E | LC | ETL.2390.POLE.WDPS | 44195235 | VICTOR | STOCKTON | 2021-06-13 | 2021-10-12 | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44195233 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00012869 | 2485.8403 | 0.3199
121538015 | E | LC | ETL.3150.TOWR | 40805703 | CONCORD | EAST BAY | 2021-06-14 |  | ETL.3150 | OLEUM-G #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40805703 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-09-17 | Glass Silicone Coated | Suspension |  |  |  |  | 3.1653e-05 | 632.9703 | 0.020036
121538015 | E | LC | ETL.3150.TOWR | 40805703 | CONCORD | EAST BAY | 2021-06-14 |  | ETL.3150 | OLEUM-G #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40805703 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 3.1653e-05 | 632.9703 | 0.020036
121543699 | F | LC | ETL.1440.POLE.WOOD | 42572725 | SACTO | SIERRA | 2021-06-12 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42572725 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.016228 | 1260.556 | 20.4568
121544716 | B | LC | ETL.5980.INSL | 40782697 | PISMOBCH | LOS PADRES | 2021-06-15 | 2021-06-28 | ETL.5980 | DIABLO-MIDWAY #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40753841 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 2.1406e-10 | 1091.4023
121550045 | B | LC | ETL.6070.INSL | 40838918 | TABLEMTN | NORTH VALLEY | 2021-06-16 | 2021-07-29 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121550925 | F | LC | ETL.5650.TOWR | 40653348 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40653348 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.9576e-07 | 1158.6814 | 0.00022682
121552581 | E | LC | ETL.7640.POLE.WDPS | 44565550 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564209 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 0.0002165 | 253.4679 | 0.054877
121567628 | F | LC | ETL.6770.POLE.NWOD | 45037308 | SACTO | SIERRA | 2021-06-15 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45037308 | 2020-06-11 | Light Duty Steel Pole | T-1 - Tri Post | 2020-06-11 | Polymer | Post |  |  |  |  | 0.00021886 | 1329.6379
121569283 | E | LC | ETL.7560.POLE.WOOD | 40913148 | SACTO | SIERRA | 2021-06-16 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40913148 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.36072 | 189.9505 | 68.5194
121594903 | F | LC | ETL.1400.POLE.STPS | 44973647 | VICTOR | YOSEMITE | 2021-06-17 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44384155 | 2016-10-29 | 3-Pole Non Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 1.6646e-05 | 31.7334
121605419 | E | LC | ETL.7610.INSL | 40696597 | METCALF | DE ANZA | 2021-06-22 |  | ETL.7610 | MONTA VISTA-LOS GATOS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | HFRA Removal | PEND | 40665275 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00029525 | 0.066432 | 1.9614e-05
121609153 | E | LC | ETL.3780.INSL | 40604797 | CONCORD | DIABLO | 2021-06-22 |  | ETL.3780 | SOBRANTE-R #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40581011 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1923-01-01 | Ceramic | Suspension |  |  |  |  | 2.7233e-05 | 221.5946 | 0.0060347
121638371 | E | LC | ETL.1440.POLE.WOOD | 42572705 | SACTO | SIERRA | 2021-06-12 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 42572705 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 4.0753e-05 | 14.3038 | 0.00058293
121653650 | F | LC | ETL.4040.POLE.NWOD | 40760118 | TABLEMTN | NORTH VALLEY | 2021-06-27 |  | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40760118 |  | Light Duty Steel Pole | 3P SV - 3 Pole Single Vertical | 1949-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0039446 | 1645.5847
121655647 | F | LC | ETL.7820.POLE.WOOD | 40860907 | LAKEVLLE | SONOMA | 2021-07-02 |  | ETL.7820 | POTTER VALLEY-WILLITS | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40860907 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.0011534 | 3785.6865 | 4.3663
121662148 | E | LC | ETL.1730.POLE.WDPS | 44413314 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Crossarm-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44413313 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0016022 | 15.88 | 0.025443
121667096 | B | LC | ETL.6770.INSL.CERA | 44396928 | SACTO | SIERRA | 2021-07-06 | 2021-09-15 | ETL.6770 | DRUM-SPAULDING | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40770265 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 0.067484 | 1329.6379
121667096 | B | LC | ETL.6770.INSL.CERA | 44396928 | SACTO | SIERRA | 2021-07-06 | 2021-09-15 | ETL.6770 | DRUM-SPAULDING | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40770265 |  | Single Wood Pole | DDE - Double Dead End | 2017-08-02 | Polymer | Dead End |  |  |  |  | 0.067484 | 1329.6379
121667096 | B | LC | ETL.6770.INSL.CERA | 44396928 | SACTO | SIERRA | 2021-07-06 | 2021-09-15 | ETL.6770 | DRUM-SPAULDING | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44396917 | 2018-09-06 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-09-06 | Ceramic | Dead End |  |  |  |  | 0.0070422 | 1329.6379
121679373 | E | LC | ETL.4040.INSL.NCER | 40792956 | TABLEMTN |  | 2021-07-01 | 2021-07-12 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40762660 | 1949-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 1949-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.019896 | 3987.1216
121687927 | E | LC | ETL.3700.POLE.WDPS | 44296816 | PISMOBCH | LOS PADRES | 2021-07-09 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44296813 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.9923e-05 | 3642.803 | 0.109
121720658 | B | LC | ETL.9240.TOWR | 43249575 | PISMOBCH | LOS PADRES | 2021-07-13 | 2021-07-27 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Other | Vegetation Overgrown | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249575 |  | LATTICE STEEL TOWER | [9 empty] | 269.1183
121722176 | E | LC | ETL.5970.TOWR | 40753889 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.5970 | DIABLO-MIDWAY #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753889 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 0.0006113 | 3310.9736 | 2.024
121744076 | B | LC | ETL.2390.INSL.CERA | 40631612 | VICTOR | STOCKTON | 2021-07-13 | 2021-10-19 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121746423 | E | LC | ETL.2390.POLE.WDPS | 44195236 | VICTOR | YOSEMITE | 2021-07-14 | 2021-07-29 | ETL.2390 | MELONES-CURTIS | Structure-Steel | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44195236 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | 2013-09-19 | Porcelain | Suspension |  |  |  |  | 1.276e-05
121746423 | E | LC | ETL.2390.POLE.WDPS | 44195236 | VICTOR | YOSEMITE | 2021-07-14 | 2021-07-29 | ETL.2390 | MELONES-CURTIS | Structure-Steel | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44195236 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | 2013-09-19 | Porcelain | Suspension |  |  |  |  | 1.276e-05
121746557 | F | LC | ETL.1820.TOWR | 40770492 | EUREKA | HUMBOLDT | 2021-07-15 | 2021-09-28 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40770492 |  | LATTICE STEEL TOWER | FSS - Field Switch Structure | [7 empty] | 0.010806 | 0.065148
121748175 | E | LC | ETL.7850.POLE.WDPS | 40750372 | EUREKA | HUMBOLDT | 2021-07-13 | 2021-08-05 | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40750372 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2020-10-01 | Glass | Dead End |  |  |  |  | 0.0031334
121748175 | E | LC | ETL.7850.POLE.WDPS | 40750372 | EUREKA | HUMBOLDT | 2021-07-13 | 2021-08-05 | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40750372 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2020-10-01 | Glass | Dead End |  |  |  |  | 0.0031334
121748175 | E | LC | ETL.7850.POLE.WDPS | 40750372 | EUREKA | HUMBOLDT | 2021-07-13 | 2021-08-05 | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40750372 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2020-10-01 | Glass | Dead End |  |  |  |  | 0.0031334
121748846 | F | LC | ETL.1440.POLE.NWOD | 45109892 | SACTO | SIERRA | 2021-07-15 |  | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45109892 | 2020-08-10 | Light Duty Steel Pole | DDE - Double Dead End | 2020-08-10 | Glass | Dead End | [5 empty] | 0.065152
121752993 | E | LC | ETL.6470.INSL.CERA | 40843330 | SACTO | SACRAMENTO | 2021-07-19 |  | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40817342 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.12541 | 474.7904 | 59.5452
121767365 | F | LC | ETL.9240.TOWR | 43249765 | PISMOBCH | LOS PADRES | 2021-07-19 | 2021-09-27 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 43249765 |  | LATTICE STEEL TOWER | [9 empty] | 1316.5836
121770125 | F | LC | ETL.1810.POLE.STPS | 45128056 | EUREKA | HUMBOLDT | 2021-07-20 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 45128012 | 2020-10-21 | 2-Pole Non Wood | 2PS - 2 Pole SUSP
121810332 | E | LC | ETL.7390.POLE.WOOD | 40577254 | LAKEVLLE | HUMBOLDT | 2021-07-27 |  | ETL.7390 | LAYTONVILLE-COVELO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40577254 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.0092385
121814543 | B | LC | ETL.7140.INSL | 40629578 | LAKEVLLE | NORTH BAY | 2021-07-28 | 2021-08-19 | ETL.7140 | IGNACIO-BOLINAS #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40588047 |  | Single Wood Pole | TPS1D - Tri Post & Susp DDE 115 KV |  | Ceramic | Double Dead End |  |  |  |  | 0.012567 | 984.3435
121818327 | E | LC | ETL.5650.TOWR | 40820518 | TABLEMTN | NORTH VALLEY | 2021-07-28 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40820518 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-09-13 | Ceramic | Suspension |  |  |  |  | 1.8299e-06 | 6070.0615 | 0.011107
121906843 | F | LC | ETL.6890.POLE.NWOD | 44712972 | LAKEVLLE | SONOMA | 2021-06-28 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44712972 | 2019-02-16 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-02-16 | Ceramic | Suspension |  |  |  |  | 5.8116e-09 | 3356.5659
122019663 | B | LC | ETL.5140.TOWR | 40870401 | SACTO | SIERRA | 2021-09-09 | 2021-12-02 | ETL.5140 | MIDDLE FORK-GOLD HILL | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40870401 | 1965-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1965-01-01 | Ceramic | Dead End |  |  |  |  | 1.097e-06 | 6874.0736 | 0.0075411
122216426 | B | LC | ETL.1430.INSL.CERA | 44305009 | SACTO | SACRAMENTO | 2021-10-13 |  | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44304991 | 2016-11-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2016-11-14 | Ceramic | Suspension |  |  |  |  | 0.010296
122216426 | B | LC | ETL.1430.INSL.CERA | 44305009 | SACTO | SACRAMENTO | 2021-10-13 |  | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44304991 | 2016-11-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2016-11-14 | Ceramic | Suspension |  |  |  |  | 0.010296
122370134 | B | LC | ETL.6510.SWIT | 40743588 | SACTO | SACRAMENTO | 2021-11-12 | 2021-11-15 | ETL.6510 | COLGATE-SMARTVILLE #1 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 |  |  | COMP | [8 empty] | Unknown | HIGH VELOCITY INTERRUPTER | SCADA Only
118423700 | E | LC | ETL.1240.POLE.WDPS | 44386326 | TABLEMTN | NORTH VALLEY | 2020-01-11 | 2020-04-22 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118423701 | E | LC | ETL.1240.POLE.WDPS | 44386203 | TABLEMTN | NORTH VALLEY | 2020-01-11 | 2020-04-14 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118748010 | E | LC | ETL.4770.INSL.NCER | 44859240 | LAKEVLLE | SONOMA | 2020-03-26 | 2021-06-15 | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
118752446 | E | LC | ETL.4316.INSL.NCER | 40700450 | TABLEMTN |  | 2020-03-27 | 2021-08-12 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118926045 | F | LC | ETL.5780.TOWR | 40651009 | VICTOR | STOCKTON | 2020-04-15 | 2020-09-21 | ETL.5780 | TIGER CREEK-ELECTRA | Structure-Steel | Paint/Coating | [Other, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40651009 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 1.4187e-05 | 1313.0647
118954825 | B | LC | ETL.6760.POLE.NWOD | 40664661 | SACTO | SACRAMENTO | 2020-04-28 | 2020-07-13 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Switch | Out of Adjustment | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664661 | 2012-01-01 | Light Duty Steel Pole | FSS - Field Switch Structure | [7 empty] | 0.0078203 | 174.093
118955149 | E | LC | ETL.4440.TOWR | 40809972 | TABLEMTN | NORTH VALLEY | 2020-04-28 | 2020-10-09 | ETL.4440 | CARIBOU-TABLE MTN | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809972 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 7.3115e-07 | 189.9049
118957394 | E | LC | ETL.6890.POLE.WOOD | 40601400 | LAKEVLLE | SONOMA | 2020-04-27 | 2021-08-12 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601400 | 1990-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.00076221 | 2282.1562
118977364 | E | LC | ETL.6220.POLE.WOOD | 40614633 | EUREKA | HUMBOLDT | 2020-05-03 | 2020-08-10 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
118996319 | E | LC | ETL.3740.TOWR | 40857621 | CONCORD | DIABLO | 2020-05-04 | 2021-04-20 | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857621 | 2007-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2007-01-01 | Porcelain | Suspension |  |  |  |  | 0.0016997 | 839.5602
119005372 | E | LC | ETL.6770.POLE.WOOD | 40751829 | SACTO | SACRAMENTO | 2020-05-09 | 2021-04-20 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119016620 | F | LC | ETL.1330.TOWR | 40822489 | LAKEVLLE | HUMBOLDT | 2020-04-23 | 2021-04-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40822489 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 4.6355e-05 | 5303.9663
119057421 | F | LC | ETL.6440.POLE.WOOD | 44191472 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-08-20 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191472 |  | Single Wood Pole | TH - TriAngle Post 70 | [7 empty] | 0.0017843 | 3898.8367
119083029 | E | LC | ETL.6690.POLE.WOOD | 40590222 | SACTO | SIERRA | 2020-05-29 | 2020-11-12 | ETL.6690 | DEER CREEK-DRUM | Damper-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119083545 | E | LC | ETL.6470.POLE.WOOD | 40760753 | SACTO | SIERRA | 2020-05-29 | 2020-07-02 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760753 |  | Single Wood Pole | DDE - Double Dead End | 2018-11-30 | Ceramic | Suspension |  |  |  |  | 0.31231 | 237.4138
119083605 | E | LC | ETL.6760.POLE.NWOD | 40822664 | SACTO | SIERRA | 2020-05-28 | 2020-11-12 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40822664 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.082311 | 110.8706
119088468 | F | LC | ETL.3720.TOWR | 40581007 | CONCORD | EAST BAY | 2020-05-15 | 2021-04-13 | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581007 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1968-01-01 | Porcelain | Suspension |  |  |  |  | 3.7064e-05 | 221.5946
119097068 | B | LC | ETL.7780.INSL.NCER | 40640233 | LAKEVLLE | HUMBOLDT | 2020-06-02 | 2020-06-15 | ETL.7780 | PHILO JCT-ELK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40614173 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.00016781 | 1666.6323
119097074 | F | LC | ETL.1420.POLE.STPS | 44337068 | SACTO | SACRAMENTO | 2020-05-19 | 2021-07-08 | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44337067 | 2016-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.5637e-07 | 1328.8579
119100837 | B | LC | ETL.1050.TOWR | 40806881 | FRESNO | FRESNO | 2020-06-03 | 2020-12-08 | ETL.1050 | BALCH-SANGER | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40806881 | 1923-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1923-01-01 | Porcelain | Dead End |  |  |  |  | 0.0018259 | 8796.1572
119112978 | E | LC | ETL.1420.TOWR | 40866001 | SACTO | SIERRA | 2020-06-04 | 2021-02-22 | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40866001 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm |  | Polymer | [5 empty] | 7.4196e-05 | 3797.0496
119114394 | F | LC | ETL.2540.POLE.WDPS | 44908731 | MOSSLNDG | SAN JOSE | 2020-05-21 | 2020-11-12 | ETL.2540 | METCALF-GREEN VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44908678 | 2020-05-05 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0037174 | 2866.7197
119116866 | E | LC | ETL.8290.POLE.WOOD | 40592118 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-05-14 | ETL.8290 | VOLTA-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40592118 |  | Single Wood Pole | T2N | 2021-04-22 | Polymer | Post |  |  |  |  | 0.0014458 | 795.2646
119117811 | F | LC | ETL.7290.POLE.WOOD | 40825980 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40825980 |  | Single Wood Pole | T-1 - Tri Post | 2019-05-19 | Polymer | Post |  |  |  |  | 0.0091581 | 411.9666
119118335 | F | LC | ETL.4680.TOWR | 40811759 | LAKEVLLE | SONOMA | 2020-05-29 | 2021-03-08 | ETL.4680 | FULTON-IGNACIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40811759 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.7576e-07 | 221.7097
119144827 | E | LC | ETL.4220.POLE.STPS | 44339342 | TABLEMTN | NORTH VALLEY | 2020-05-12 | 2020-07-01 | ETL.4220 | WOODLEAF-PALERMO | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44339339 | 2017-09-20 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 8.0907e-05 | 1012.6957
119166116 | F | LC | ETL.6480.POLE.WOOD | 40664548 | SACTO | SIERRA | 2020-06-15 | 2021-06-23 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664548 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.12203 | 3859.7815
119168385 | F | LC | ETL.8170.POLE.NWOD | 44859212 | EUREKA | HUMBOLDT | 2020-06-15 | 2021-03-18 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44859212 | 2019-06-25 | Light Duty Steel Pole | DV - Double Vertical | 2019-06-25 | Glass | Dead End |  |  |  |  | 0.00030537 | 5730.9478
119175061 | F | LC | ETL.6890.POLE.NWOD | 44713011 | LAKEVLLE | SONOMA | 2020-06-15 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44713011 | 2019-02-16 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-02-16 | Ceramic | Suspension |  |  |  |  | 2.0237e-07 | 1631.0891
119175071 | E | LC | ETL.7300.POLE.WOOD | 40770409 | TABLEMTN |  | 2020-06-16 | 2021-03-05 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770409 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00028261 | 3613.8186
119179072 | E | LC | ETL.7300.POLE.WOOD | 40771246 | TABLEMTN |  | 2020-06-16 | 2021-03-09 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771246 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00045991 | 3912.7244
119199276 | F | LC | ETL.6470.POLE.WOOD | 40611201 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40611201 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.096492 | 221.6184
119229845 | F | LC | ETL.8060.POLE.WOOD | 40771562 | SACTO | SIERRA | 2020-06-29 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771562 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.080975 | 0.24228
119290291 | E | LC | ETL.6950.POLE.WOOD | 40821299 | SACTO | SACRAMENTO | 2020-07-01 | 2020-12-16 | ETL.6950 | GOLD HILL #1 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40821299 | 2014-08-18 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Post |  |  |  |  | 0.0034695 | 1504.152
119292344 | E | LC | ETL.8170.POLE.WDPS | 44565546 | EUREKA | HUMBOLDT | 2020-07-01 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | PEND | 44564241 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.05248 | 31.6978 | 1.6635
119304768 | E | LC | ETL.1180.POLE.WOOD | 44879461 | TABLEMTN | NORTH VALLEY | 2020-07-02 |  | ETL.1180 | BUTTE VALLEY-CARIBOU | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44879461 |  | Single Wood Pole | SV-DE-90 - Single Vertical Dead End 90 |  | Unknown | Unknown |  |  |  |  | 0.050008 | 5538.7192 | 276.981
119309902 | F | LC | ETL.8060.POLE.WOOD | 40878046 | SACTO | SIERRA | 2020-07-02 | 2021-05-03 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40878046 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.008989 | 31.7066
119311223 | E | LC | ETL.8170.POLE.WDPS | 44565487 | EUREKA | HUMBOLDT | 2020-07-03 | 2021-08-16 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564173 | 2011-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.008738 | 2589.7983
119315293 | E | LC | ETL.7560.POLE.WOOD | 40598724 | SACTO | SACRAMENTO | 2020-07-06 | 2021-04-19 | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119326656 | F | LC | ETL.6300.POLE.WOOD | 40600740 | TABLEMTN |  | 2020-07-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600740 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 4.7616e-06 | 2404.1431
119327825 | F | LC | ETL.8170.POLE.WOOD | 40906467 | EUREKA | HUMBOLDT | 2020-07-07 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40906467 |  | Single Wood Pole | 3P DDE - 3 Pole Double Dead End |  | Ceramic | [5 empty] | 0.044429 | 31.7081
119331303 | F | LC | ETL.6890.POLE.NWOD | 44873432 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-07-19 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44873432 | 2019-11-06 | Light Duty Steel Pole | T-1 - Tri Post | 2019-11-06 | Polymer | Post |  |  |  |  | 2.7185e-05 | 2248.4673
119333689 | E | LC | ETL.2060.POLE.WOOD | 40824333 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-08-09 | ETL.2060 | FORT BRAGG-ELK | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824333 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.096795 | 0.066303
119339773 | E | LC | ETL.1710.POLE.WDPS | 44696026 | MOSSLNDG | CENTRAL COAST | 2020-07-09 | 2021-05-03 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Vegetation | Overgrown | [Remove, Completed] |  | Tier 3 | Within Both | COMP | 42567475 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.00013371 | 47.5096
119340937 | F | LC | ETL.6300.POLE.WOOD | 40816738 | TABLEMTN |  | 2020-07-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40816738 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 3.6221e-06 | 15.8815
119355944 | E | LC | ETL.8240.POLE.WOOD | 40813064 | VICTOR | STOCKTON | 2020-07-10 | 2021-09-29 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0030231 | 4053.4192
119358408 | E | LC | ETL.6280.POLE.WOOD | 40815742 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2020-12-04 | ETL.6280 | CARIBOU #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119361763 | E | LC | ETL.7780.POLE.WOOD | 40819515 | LAKEVLLE | SONOMA | 2020-07-13 | 2021-04-28 | ETL.7780 | PHILO JCT-ELK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119368610 | F | LC | ETL.1450.POLE.WDPS | 44557643 | SACTO | SACRAMENTO | 2020-07-13 | 2020-11-12 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44554009 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00046809 | 2826.3738
119368777 | F | LC | ETL.1110.TOWR | 40604118 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-07-06 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40604118 | 1952-01-01 | LATTICE STEEL TOWER | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00019357 | 2008.0186
119372506 | F | LC | ETL.7170.POLE.WOOD | 44871197 | LAKEVLLE | NORTH BAY | 2020-07-15 |  | ETL.7170 | IGNACIO-ALTO-SAUSALITO #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871197 | 2019-09-19 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2019-09-19 | Polymer | Dead End |  |  |  |  | 0.29603 | 205.9363
119374845 | F | LC | ETL.1240.POLE.STPS | 44924640 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2020-07-28 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44924569 | 2020-03-31 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.9567e-09 | 2441.9417
119377417 | F | LC | ETL.7030.POLE.WOOD | 40601618 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40601618 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0064706 | 5114.0112
119381132 | F | LC | ETL.6280.POLE.WOOD | 40591845 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40591845 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Other |  |  |  |  | 8.693e-05 | 5282.8242
119464141 | F | LC | ETL.7390.POLE.WOOD | 40875254 | LAKEVLLE | HUMBOLDT | 2020-07-16 | 2021-02-16 | ETL.7390 | LAYTONVILLE-COVELO | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40875254 |  | Single Wood Pole | T2N | 2021-03-22 | Polymer | Post |  |  |  |  | 0.025177 | 3282.1799
119467663 | E | LC | ETL.8060.POLE.WOOD | 40577367 | SACTO | SACRAMENTO | 2020-07-17 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40577367 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.073438 | 31.7066
119469727 | E | LC | ETL.6290.POLE.WOOD | 40824673 | TABLEMTN | NORTH VALLEY | 2020-07-17 | 2021-11-29 | ETL.6290 | CARIBOU-PLUMAS JCT | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40824673 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.059404 | 3621.9985
119477666 | F | LC | ETL.5431.TOWR | 40586415 | TABLEMTN |  | 2020-07-20 | 2021-02-10 | ETL.5431 | BLACK TAP | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40586415 | 1964-01-01 | LATTICE STEEL TOWER | Unknown | [7 empty] | 2.7807e-08 | 269.0425
119478590 | E | LC | ETL.6950.POLE.WOOD | 40908727 | SACTO | SACRAMENTO | 2020-07-20 | 2021-03-16 | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40908727 | 2013-10-17 | Single Wood Pole | T-1 - Tri Post | 2013-10-17 | Non Ceramic | Post |  |  |  |  | 0.00174 | 2583.2712
119485127 | F | LC | ETL.8170.POLE.WOOD | 40906315 | EUREKA | HUMBOLDT | 2020-07-21 | 2021-01-25 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119485544 | E | LC | ETL.1650.POLE.NWOD | 40659187 | LAKEVLLE | SONOMA | 2020-07-21 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40659187 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 1966-01-01 | Polymer | Dead End |  |  |  |  | 1.1416e-08 | 951.7994 | 1.0865e-05
119489824 | F | LC | ETL.1400.POLE.STPS | 44382143 | VICTOR | YOSEMITE | 2020-07-22 | 2021-04-20 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44382141 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.8024e-05 | 79.1977
119520437 | F | LC | ETL.1670.POLE.WOOD | 40818236 | LAKEVLLE | SONOMA | 2020-07-29 |  | ETL.1670 | GEYSERS #5-GEYSERS #3 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40818236 | 1991-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.00072867 | 5607.6411
119527738 | F | LC | ETL.4450.TOWR | 40599996 | CONCORD | DIABLO | 2020-07-30 | 2021-01-20 | ETL.4450 | CASTRO VALLEY-NEWARK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40599996 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-08-13 | Glass | Dead End |  |  |  |  | 1.6801e-06 | 4431.938
119527738 | F | LC | ETL.4450.TOWR | 40599996 | CONCORD | DIABLO | 2020-07-30 | 2021-01-20 | ETL.4450 | CASTRO VALLEY-NEWARK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40599996 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.6801e-06 | 4431.938
119552062 | F | LC | ETL.7300.POLE.WOOD | 44872428 | TABLEMTN | NORTH VALLEY | 2020-08-03 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44872428 | 2019-05-30 | Single Wood Pole | T-1 - Tri Post | 2019-05-30 | Polymer | Post |  |  |  |  | 0.00017071 | 6149.0375
119567331 | F | LC | ETL.7060.POLE.WOOD | 40767967 | METCALF | PENINSULA | 2020-08-06 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40767967 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00011147 | 458.7206
119570938 | F | LC | ETL.7575.POLE.WOOD | 40653193 | METCALF | PENINSULA | 2020-08-06 |  | ETL.7575 | SNEATH LANE-PACIFICA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40653193 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.16875 | 760.1513
119575404 | F | LC | ETL.5650.TOWR | 40821600 | TABLEMTN | NORTH VALLEY | 2020-08-07 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40821600 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 2.8867e-06 | 2329.9167 | 0.0067259
119576093 | F | LC | ETL.7590.POLE.WOOD | 40645470 | MOSSLNDG | DE ANZA | 2020-08-06 | 2020-09-09 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40645470 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Pin |  |  |  |  | 0.16608 | 237.3869
119605606 | E | LC | ETL.6220.POLE.WOOD | 40752635 | EUREKA | HUMBOLDT | 2020-08-12 | 2021-01-25 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40752635 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.20367
119626280 | E | LC | ETL.7490.POLE.WOOD | 40752758 | EUREKA | HUMBOLDT | 2020-08-17 | 2021-08-18 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752758 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.35098 | 94.963
119634098 | E | LC | ETL.9200.POLE.WOOD | 40586290 | MIDWAY | KERN | 2020-08-18 | 2021-05-18 | ETL.9200 | TAFT-CUYAMA #1 | Anchor-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40586290 | 1962-01-01 | Single Wood Pole | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.01374
119635793 | E | LC | ETL.6710.POLE.WOOD | 40649689 | MOSSLNDG | CENTRAL COAST | 2020-08-18 | 2021-03-11 | ETL.6710 | DEL MONTE-VIEJO | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40649689 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.1186 | 0.065148
119642317 | A | LC | ETL.4090.INSL.CERA | 40717424 | SACTO | SACRAMENTO | 2020-08-20 | 2020-08-31 | ETL.4090 | VACA-VACAVILLE-CORDELIA | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP
119686231 | B | LC | ETL.1110.TOWR | 40760519 | EUREKA | HUMBOLDT | 2020-08-27 | 2020-10-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760519 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Suspension |  |  |  |  | 2.5375e-05 | 0.065152
119688334 | E | LC | ETL.1110.INSL.NCER | 40721721 | TABLEMTN | HUMBOLDT | 2020-08-25 | 2021-04-20 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119716111 | E | LC | ETL.8170.POLE.WOOD | 40751121 | EUREKA | HUMBOLDT | 2020-09-02 |  | ETL.8170 | TRINITY-MAPLE CREEK | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40751121 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.34157 | 253.2652 | 86.5079
119716969 | E | LC | ETL.1450.POLE.WDPS | 44553753 | SACTO | SACRAMENTO | 2020-08-31 | 2021-04-27 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44553112 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0020267 | 47.5273
119719379 | E | LC | ETL.1110.INSL.CERA | 40712930 | TABLEMTN | HUMBOLDT | 2020-08-13 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119721049 | A | LC | ETL.6230.POLE.WOOD | 42565851 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-09-24 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP
119724446 | F | LC | ETL.8170.POLE.WOOD | 43250112 | EUREKA | HUMBOLDT | 2020-08-05 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 43250112 | 2011-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Ceramic | [5 empty] | 0.00379 | 1174.8506
119763860 | F | LC | ETL.1440.POLE.WDPS | 44768889 | SACTO | SACRAMENTO | 2020-09-08 | 2021-05-05 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40654771 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.011393 | 31.7066
119769197 | F | LC | ETL.8060.POLE.WOOD | 40590047 | SACTO | SIERRA | 2020-09-09 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40590047 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.059897 | 31.7066
119775278 | F | LC | ETL.6760.POLE.NWOD | 44924545 | SACTO | SIERRA | 2020-09-08 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44924545 | 2020-03-12 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-12 | Polymer | Post |  |  |  |  | 0.00032447 | 31.7022
119791595 | F | LC | ETL.1730.TOWR | 40655902 | MOSSLNDG | CENTRAL COAST | 2020-07-28 | 2020-10-21 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40655902 | 1954-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1972-01-01 | Porcelain | Suspension |  |  |  |  | 3.5146e-08 | 0.065147
119794770 | E | LC | ETL.1600.INSL.NCER | 40884252 | LAKEVLLE | SONOMA | 2020-09-18 | 2021-04-20 | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119794901 | F | LC | ETL.4220.POLE.STPS | 44388397 | TABLEMTN |  | 2020-07-29 |  | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44388396 | 2016-12-05 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00017614 | 0.065151
119800452 | F | LC | ETL.6880.POLE.NWOD | 40912478 | LAKEVLLE | HUMBOLDT | 2020-08-06 | 2021-09-23 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40912478 | 2009-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Porcelain | [5 empty] | 0.00053269 | 696.472
119808719 | F | LC | ETL.7490.POLE.NWOD | 44145846 | EUREKA | HUMBOLDT | 2020-08-13 |  | ETL.7490 | MAPLE CREEK-HOOPA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44145846 |  | Light Duty Steel Pole | TPS - Tri Post & Susp (1-3) |  | Polymer | Suspension |  |  |  |  | 0.20962 | 0.065148
119835049 | E | LC | ETL.1073.POLE.WDPS | 44774784 | VICTOR | YOSEMITE | 2020-09-29 | 2021-11-17 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [12 empty] | 0.065147
119844679 | A | LC | ETL.1110.INSL.CERA | 40621365 | EUREKA | HUMBOLDT | 2020-10-02 | 2020-10-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119848391 | F | LC | ETL.6290.POLE.WOOD | 40768876 | TABLEMTN | NORTH VALLEY | 2020-09-09 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40768876 | 2010-01-01 | Single Wood Pole | DDE-A - Double Dead End Angle | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.00041003 | 1202.1041
119967858 | F | LC | ETL.1110.POLE.WDPS | 44515799 | TABLEMTN | HUMBOLDT | 2020-08-26 | 2021-01-29 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44515181 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0036983 | 5350.7036
119982983 | E | LC | ETL.8580.TOWR | 40873866 | FRESNO | FRESNO | 2020-10-29 | 2021-11-29 | ETL.8580 | COALINGA #1-SAN MIGUEL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40873866 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Porcelain | Dead End |  |  |  |  | 5.6015e-06
119994658 | F | LC | ETL.8960.POLE.WOOD | 44231461 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44231461 |  | Single Wood Pole | SUSP - Suspension (TWR) |  | Glass | [5 empty] | 0.00016248
119995105 | F | LC | ETL.1450.POLE.WDPS | 44565791 | SACTO | SIERRA | 2020-10-05 | 2021-08-30 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553897 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00015334 | 95.0021
120008394 | E | LC | ETL.1650.INSL.CERA | 40792130 | LAKEVLLE |  | 2020-11-10 | 2021-03-25 | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
120010042 | E | LC | ETL.6020.INSL | 40790047 | TABLEMTN | NORTH VALLEY | 2020-11-10 | 2021-06-15 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40759950 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.7218e-05 | 1202.6853
120011413 | E | LC | ETL.6020.TOWR | 40819382 | TABLEMTN | NORTH VALLEY | 2020-11-05 | 2021-04-28 | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40819382 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.0015356 | 269.0298
120139237 | F | LC | ETL.6380.POLE.NWOD | 44732841 | LAKEVLLE | HUMBOLDT | 2020-08-31 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44732841 | 2013-04-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2013-04-17 | Polymer | Dead End - Pin |  |  |  |  | 3.7438e-09 | 6774.2739
120612703 | F | LC | ETL.9341.POLE.WOOD | 40764694 | FRESNO | YOSEMITE | 2021-03-02 | 2021-05-24 | ETL.9341 | YANKE (NORTH FORK) TAP | Structure-Wood | Idle | [Remove, Completed] | Tier3 |  |  | COMP
120647984 | E | LC | ETL.6760.POLE.WOOD | 40756959 | SACTO | SACRAMENTO | 2021-03-16 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Vegetation | Overgrown | [Trim] | Tier2 | Tier 2 | Within Both | PEND | 40756959 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.16288 | 0.066432 | 0.010821
120678087 | E | LC | ETL.1710.TOWR | 40815170 | MOSSLNDG | CENTRAL COAST | 2021-03-23 | 2021-08-25 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40815170 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-06 | Glass | Double Dead End |  |  |  |  | 2.2668e-06 | 0.065147
120678087 | E | LC | ETL.1710.TOWR | 40815170 | MOSSLNDG | CENTRAL COAST | 2021-03-23 | 2021-08-25 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40815170 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-05 | Glass | Dead End |  |  |  |  | 2.2668e-06 | 0.065147
120707625 | E | LC | ETL.3840.INSL.CERA | 40836246 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40809563 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 4.0266e-07 | 268.9173 | 0.00010828
120711067 | E | LC | ETL.6890.POLE.WOOD | 40769764 | LAKEVLLE | SONOMA | 2021-03-30 | 2021-08-11 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
120717028 | E | LC | ETL.1110.POLE.WDPS | 44423272 | TABLEMTN | NORTH VALLEY | 2020-07-23 | 2021-04-20 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
120724852 | E | LC | ETL.7390.POLE.NWOD | 44965314 | LAKEVLLE | SONOMA | 2021-04-01 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44965314 | 2020-08-28 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-08-28 | Glass | Suspension |  |  |  |  | 0.0044222
120736801 | F | LC | ETL.3830.TOWR | 40865916 | VICTOR | STOCKTON | 2021-04-01 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40865916 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.1324e-05 | 2282.6465
120738953 | F | LC | ETL.6040.TOWR | 40581574 | MOSSLNDG | CENTRAL COAST | 2021-04-02 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40581574 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 6.7935e-08
120740234 | F | LC | ETL.8365.POLE.WOOD | 40698324 | EUREKA | HUMBOLDT | 2021-04-03 | 2021-07-16 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40698324 | 2010-01-01 | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.069923 | 237.4061
120742728 | E | LC | ETL.1720.POLE.WDPS | 44400954 | MOSSLNDG | CENTRAL COAST | 2021-04-05 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44400953 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.0014197 | 1004.7273 | 1.4264
120750914 | E | LC | ETL.1180.INSL.CERA | 40793415 | TABLEMTN | NORTH VALLEY | 2021-04-06 | 2021-10-19 | ETL.1180 | BUTTE VALLEY-CARIBOU | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44399902 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper |  | Porcelain | [5 empty] | 0.0023649 | 5538.7192
120754760 | F | LC | ETL.5780.TOWR | 40681643 | VICTOR | STOCKTON | 2021-03-24 |  | ETL.5780 | TIGER CREEK-ELECTRA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40681643 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 1.6585e-07 | 1075.7365 | 0.00017841
120755978 | E | LC | ETL.3830.TOWR | 40607299 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40607299 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.0536e-07 | 47.9272 | 9.8423e-06
120759796 | F | LC | ETL.8350.POLE.NWOD | 44761253 | VICTOR | STOCKTON | 2021-04-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44761253 | 2019-05-10 | Light Duty Steel Pole | T2N | 2019-05-10 | Polymer | Post |  |  |  |  | 2.2466e-08 | 571.9987
120761604 | E | LC | ETL.6720.INSL | 40712274 | TABLEMTN | NORTH VALLEY | 2021-04-07 |  | ETL.6720 | DESABLA-CENTERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40659712 | 1998-01-01 | Tubular Steel Pole | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 7.0006e-05 | 23.7951 | 0.0016658
120788066 | E | LC | ETL.6870.POLE.WOOD | 40767435 | SACTO | SACRAMENTO | 2021-04-10 | 2021-06-15 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120794428 | B | LC | ETL.6880.POLE.NWOD | 44668642 | LAKEVLLE | SONOMA | 2021-04-12 | 2021-05-06 | ETL.6880 | FULTON-CALISTOGA | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44668642 | 2018-11-05 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-11-05 | Polymer | Dead End - Suspension |  |  |  |  | 3.684e-06 | 458.8659
120801314 | E | LC | ETL.5980.TOWR | 40812095 | PISMOBCH | LOS PADRES | 2021-04-12 | 2021-04-28 | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40812095 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-07-30 | Ceramic | Suspension |  |  |  |  | 8.5727e-12 | 2660.0097
120805477 | E | LC | ETL.7270.POLE.NWOD | 44164727 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.7270 | KESWICK-TRINITY | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44164727 | 2014-08-15 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2014-08-15 | Polymer | Dead End |  |  |  |  | 9.0167e-07 | 2708.5825 | 0.0024422
120805632 | E | LC | ETL.8365.POLE.WOOD | 40912569 | EUREKA | HUMBOLDT | 2021-04-13 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40912569 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0075276
120810843 | E | LC | ETL.6040.TOWR | 40762402 | MOSSLNDG | CENTRAL COAST | 2021-04-14 | 2021-04-27 | ETL.6040 | MOSS LANDING-LOS BANOS | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40762402 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 2.2865e-05 | 192.7658
120811409 | F | LC | ETL.9100.POLE.WOOD | 44191307 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191307 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 9.0122e-06 | 1584.2686
120811411 | E | LC | ETL.1730.INSL.NCER | 40736007 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40702152 | 1972-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1972-01-01 | Polymer | Dead End |  |  |  |  | 0.00034031 | 0.065147 | 2.217e-05
120812400 | F | LC | ETL.9100.POLE.WOOD | 44191872 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191872 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 1.7939e-06 | 1898.3486
120812521 | F | LC | ETL.9100.POLE.WOOD | 44191889 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191889 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Polymer | [5 empty] | 2.0162e-06 | 2470.3545
120815460 | F | LC | ETL.5660.TOWR | 40811847 | CONCORD | DIABLO | 2021-04-14 |  | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40811847 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 2.2805e-06 | 2709.8901 | 0.0061798
120815460 | F | LC | ETL.5660.TOWR | 40811847 | CONCORD | DIABLO | 2021-04-14 |  | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40811847 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Double Dead End |  |  |  |  | 2.2805e-06 | 2709.8901 | 0.0061798
120820369 | E | LC | ETL.2740.TOWR | 40644201 | CONCORD | DIABLO | 2021-04-14 |  | ETL.2740 | MORAGA-OAKLAND #3 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40644201 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 0.028775 | 0.065152 | 0.0018747
120838094 | E | LC | ETL.6020.TOWR | 40761922 | TABLEMTN | NORTH VALLEY | 2021-04-16 | 2021-05-28 | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40761922 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 3.2987e-10 | 3198.3669
120844627 | E | LC | ETL.7290.POLE.WOOD | 42615555 | TABLEMTN | NORTH VALLEY | 2021-04-19 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42615555 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.015134 | 31.7051 | 0.47982
120858665 | F | LC | ETL.5400.POLE.NWOD | 44445546 | TABLEMTN | NORTH VALLEY | 2021-04-21 |  | ETL.5400 | PIT #3-PIT #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44445546 | 2017-10-03 | Tubular Steel Pole | DV-DE - Double Vertical Dead End | 2017-10-03 | Non Ceramic | Dead End |  |  |  |  | 0.00026079 | 4706.947
120866929 | F | LC | ETL.5390.TOWR | 40762590 | TABLEMTN | NORTH VALLEY | 2021-04-22 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762590 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 0.016938 | 379.707 | 6.4314
120873331 | F | LC | ETL.3720.TOWR | 40761878 | CONCORD | DIABLO | 2021-04-23 |  | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40761878 | 1968-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2016-11-06 | Porcelain | Dead End |  |  |  |  | 0.00050948 | 443.3865 | 0.2259
120874051 | E | LC | ETL.2720.INSL | 40773206 | CONCORD | DIABLO | 2021-04-21 |  | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40745886 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0014271 | 0.065147 | 9.2972e-05
120880388 | E | LC | ETL.1810.POLE.WDPS | 44322254 | EUREKA | HUMBOLDT | 2021-04-24 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Anchor-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44322252 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0012259
120880494 | E | LC | ETL.1810.POLE.STPS | 44996083 | EUREKA | HUMBOLDT | 2021-04-24 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44996003 | 2020-04-27 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00010282
120889948 | E | LC | ETL.6890.POLE.NWOD | 44973662 | LAKEVLLE | SONOMA | 2021-04-27 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44973662 | 2018-11-26 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-26 | Polymer | Post |  |  |  |  | 0.00019245 | 965.7661 | 0.18586
120912165 | E | LC | ETL.3830.TOWR | 40642910 | VICTOR | STOCKTON | 2021-05-01 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40642910 | 1927-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post | 1999-01-01 | Polymer | Suspension |  |  |  |  | 7.0696e-09 | 3491.7839 | 2.4686e-05
120921883 | E | LC | ETL.3960.INSL.CERA | 40833955 | PISMOBCH | LOS PADRES | 2021-04-30 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40809288 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 7.245e-07 | 4844.4717 | 0.0035098
120923263 | E | LC | ETL.3960.INSL.CERA | 40885201 | PISMOBCH | LOS PADRES | 2021-05-03 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40861841 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Dead End |  |  |  |  | 6.8004e-07 | 3451.7769 | 0.0023474
120929783 | E | LC | ETL.4550.TOWR | 40657699 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40657699 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.0181e-05 | 5070.043 | 0.25442
120934494 | E | LC | ETL.6890.POLE.NWOD | 44628928 | LAKEVLLE | SONOMA | 2021-05-05 |  | ETL.6890 | FULTON-HOPLAND | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44628928 | 2018-06-13 | Light Duty Steel Pole | 3HP - 3 Horizontal Post | 2018-06-13 | Polymer | Post |  |  |  |  | 0.00018039 | 2236.0244 | 0.40336
120948921 | E | LC | ETL.9331.INSL.NCER | 40625988 | FRESNO | FRESNO | 2021-05-05 |  | ETL.9331 | AUBERRY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40584844 |  | Light Duty Steel Pole | TH - TriAngle Post 70 | 1964-01-01 | Polymer | Pin |  |  |  |  | 0.00011343 | 6505.4014 | 0.73791
121322942 | E | LC | ETL.1422.TOWR | 40875721 | SACTO | SIERRA | 2021-04-22 |  | ETL.1422 | BRUNSWICK #1 TAP | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40875721 | 1975-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 3.9285e-06 | 1297.1829 | 0.0050959
121326135 | E | LC | ETL.4316.INSL.NCER | 41176865 | TABLEMTN | SIERRA | 2021-05-05 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41127241 | 2002-01-01 | Tubular Steel Pole | DCPOST - Double Circuit Post | 2002-01-01 | Polymer | Post |  |  |  |  | 0.0017937 | 2534.72 | 4.5466
121326135 | E | LC | ETL.4316.INSL.NCER | 41176865 | TABLEMTN | SIERRA | 2021-05-05 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41127241 | 2002-01-01 | Tubular Steel Pole | DCPOST - Double Circuit Post | 2021-04-16 | Polymer | Post |  |  |  |  | 0.0017937 | 2534.72 | 4.5466
121329622 | F | LC | ETL.1820.POLE.WDPS | 44565583 | EUREKA | HUMBOLDT | 2021-05-13 | 2021-07-12 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44564230 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.90741 | 79.1467
121330721 | E | LC | ETL.5630.TOWR | 40663015 | TABLEMTN | NORTH VALLEY | 2021-04-24 |  | ETL.5630 | ROCK CREEK-POE | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40663015 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 2.0295e-06 | 427.2046 | 0.00086699
121331000 | E | LC | ETL.8423.POLE.NWOD | 40652674 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.8423 | SALINAS-FORT ORD #2 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40652674 |  | Lattice Steel Pole | DCPOST - Double Circuit Post |  | Porcelain | [5 empty] | 4.9839e-06 | 0.065148 | 3.2469e-07
121341240 | F | LC | ETL.3700.POLE.WOOD | 40818030 | PISMOBCH | LOS PADRES | 2021-04-27 | 2021-11-09 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818030 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Porcelain | Post |  |  |  |  | 2.0768e-05 | 5477.0957
121343352 | E | LC | ETL.1420.INSL.NCER | 40614858 | SACTO | SACRAMENTO | 2021-05-15 |  | ETL.1420 | DRUM-RIO OSO #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40589593 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm |  | Polymer | [5 empty] | 0.00059755 | 158.285 | 0.094583
121345661 | F | LC | ETL.1600.POLE.WOOD | 40821134 | LAKEVLLE | SONOMA | 2021-05-17 |  | ETL.1600 | FULTON-PUEBLO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40821134 | 1977-01-01 | Single Wood Pole | T-1 - Tri Post | 1977-01-01 | Polymer | Post |  |  |  |  | 1.205e-05 | 820.0981
121360592 | E | LC | ETL.6380.POLE.NWOD | 45080912 | LAKEVLLE | HUMBOLDT | 2021-04-24 | 2021-05-21 | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 45080912 | 2021-04-21 | Light Duty Steel Pole | T2N | 2021-04-21 | Polymer | Post |  |  |  |  | 9.7976e-11 | 5983.9028
121361259 | E | LC | ETL.5290.INSL.CERA | 44377882 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40863196 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2011-08-19 | Ceramic | Suspension |  |  |  |  | 2.4925e-07 | 537.8833 | 0.00013407
121364753 | B | LC | ETL.6870.INSL | 40630445 | SACTO | SACRAMENTO | 2021-05-19 | 2021-06-01 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40589928 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.28022 | 79.2067
121376672 | E | LC | ETL.4550.TOWR | 40869181 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40869181 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.6922e-05 | 4215.3687 | 0.11349
121382254 | F | LC | ETL.6500.POLE.WOOD | 40664502 | SACTO | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40664502 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.001994 | 1505.8166
121382286 | E | LC | ETL.6500.POLE.WOOD | 40664458 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40664458 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0083404 | 5662.0693 | 47.224
121384103 | E | LC | ETL.6500.POLE.WOOD | 40597471 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40597471 |  | Single Wood Pole | T2N | 2018-06-29 | Polymer | Post |  |  |  |  | 0.0089008 | 2010.2684 | 17.893
121438595 | E | LC | ETL.1400.INSL.CERA | 44382681 | VICTOR | YOSEMITE | 2021-05-25 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44382663 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 0.00046883
121438595 | E | LC | ETL.1400.INSL.CERA | 44382681 | VICTOR | YOSEMITE | 2021-05-25 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44382663 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 0.00046883
121447233 | F | LC | ETL.1820.POLE.NWOD | 44947382 | EUREKA | HUMBOLDT | 2021-05-27 | 2021-06-25 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44947382 | 2018-09-14 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2018-09-14 | Glass | Suspension |  |  |  |  | 0.00024792 | 110.7793
121475340 | F | LC | ETL.8365.POLE.WOOD | 40768631 | EUREKA | HUMBOLDT | 2021-05-28 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40768631 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0080539 | 174.2838
121493356 | E | LC | ETL.1420.TOWR | 40689729 | SACTO | SIERRA | 2021-05-29 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40689729 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.00049076 | 94.9762 | 0.046611
121493356 | E | LC | ETL.1420.TOWR | 40689729 | SACTO | SIERRA | 2021-05-29 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40689729 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-05-02 | Porcelain | Suspension |  |  |  |  | 0.00049076 | 94.9762 | 0.046611
121499843 | E | LC | ETL.5630.TOWR | 40605765 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5630 | ROCK CREEK-POE | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40605765 | 1968-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1968-01-01 | Ceramic | Suspension |  |  |  |  | 1.2094e-05 | 6600.5874 | 0.07983
121517063 | F | LC | ETL.4392.TOWR | 41129390 | LAKEVLLE | SONOMA | 2021-06-07 | 2021-06-25 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41129390 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.0011045 | 996.9683
121521486 | B | LC | ETL.1610.INSL.CERA | 40636603 | LAKEVLLE | SONOMA | 2021-06-10 | 2021-08-30 | ETL.1610 | SILVERADO-FULTON JCT | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121524508 | F | LC | ETL.1440.POLE.WDPS | 44149434 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44149433 | 2013-11-06 | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.0010462 | 11.1397 | 0.011654
121536476 | E | LC | ETL.5390.INSL.NCER | 45115857 | TABLEMTN | NORTH VALLEY | 2021-06-10 | 2021-09-23 | ETL.5390 | PIT #1-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 41107604 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 8.9433e-08 | 4610.73
121538279 | B | LC | ETL.4760.TOWR | 40808584 | LAKEVLLE | HUMBOLDT | 2021-06-14 | 2021-08-31 | ETL.4760 | GEYSERS #16 TAP | Switch | Out of Adjustment | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808584 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 9.0072e-05 | 5828.5811
121544053 | F | LC | ETL.6300.POLE.WOOD | 40816746 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.6300 | CARIBOU-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40816746 |  | Single Wood Pole | 3P DDE-A - 3 Pole Double Dead End Angle | 2014-11-06 | Non Ceramic | Post |  |  |  |  | 0.0070415 | 47.5141 | 0.33457
121550814 | E | LC | ETL.5630.TOWR | 41084289 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5630 | ROCK CREEK-POE | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 41084289 |  | LATTICE STEEL TOWER | DDE - Double Dead End | [7 empty] | 4.3902e-05 | 2296.8577 | 0.10084
121551772 | F | LC | ETL.1820.POLE.NWOD | 44395430 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395430 | 2020-03-11 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-03-11 | Glass | Suspension |  |  |  |  | 0.0028195 | 3688.5637
121555923 | E | LC | ETL.5970.TOWR | 40680291 | PISMOBCH | LOS PADRES | 2021-06-17 |  | ETL.5970 | DIABLO-MIDWAY #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40680291 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-09-25 | Glass Silicone Coated | Suspension |  |  |  |  | 5.536e-09 | 3057.3379 | 1.6926e-05
121556827 | B | LC | ETL.5420.POLE.WOOD | 44562858 | TABLEMTN | NORTH VALLEY | 2021-06-12 | 2021-09-29 | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 696.9175
121573880 | F | LC | ETL.1350.POLE.STPS | 44994611 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44993925 | 2020-10-08 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.005443 | 316.5321
121574566 | F | LC | ETL.7490.POLE.STPS | 44145842 | EUREKA | HUMBOLDT | 2021-06-17 | 2021-07-12 | ETL.7490 | MAPLE CREEK-HOOPA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44145842 | 2011-12-30 | 2-Pole Non Wood | DDE - Double Dead End | 2011-12-30 | Ceramic | Suspension |  |  |  |  | 0.33546
121574566 | F | LC | ETL.7490.POLE.STPS | 44145842 | EUREKA | HUMBOLDT | 2021-06-17 | 2021-07-12 | ETL.7490 | MAPLE CREEK-HOOPA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44145842 | 2011-12-30 | 2-Pole Non Wood | DDE - Double Dead End | 2011-12-30 | Ceramic | Suspension |  |  |  |  | 0.33546
121575259 | F | LC | ETL.4771.TOWR | 40819518 | LAKEVLLE | HUMBOLDT | 2021-06-14 |  | ETL.4771 | BOTTLE ROCK TAP D.W.R. | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40819518 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 3.7522e-05 | 1472.3439
121589449 | E | LC | ETL.4620.INSL | 40611915 | PISMOBCH | LOS PADRES | 2021-06-23 |  | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587106 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.279e-08 | 2629.9578 | 3.3638e-05
121603841 | F | LC | ETL.4040.POLE.STPS | 45006546 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-07-19 | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 45006453 | 2020-09-17 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.6921e-05 | 2294.1755
121618021 | E | LC | ETL.6060.INSL | 40891395 | TABLEMTN | NORTH VALLEY | 2021-06-27 |  | ETL.6060 | ROUND MTN-TABLE MTN #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40868402 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.3091e-06 | 189.9176 | 0.00043854
121629117 | E | LC | ETL.5960.TOWR | 40664683 | PISMOBCH | LOS PADRES | 2021-06-24 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40664683 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 5.1284e-07 | 363.8316 | 0.00018659
121659248 | B | LC | ETL.8231.INSL.CERA | 40897572 | VICTOR | STOCKTON | 2021-07-02 | 2021-08-27 | ETL.8231 | PARDEE #1 TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
121661450 | F | LC | ETL.6020.TOWR | 40760708 | TABLEMTN | NORTH VALLEY | 2021-06-30 |  | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40760708 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.8494e-10 | 63.3636
121676361 | F | LC | ETL.9240.TOWR | 43249701 | PISMOBCH | LOS PADRES | 2021-07-07 | 2021-09-29 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 43249701 |  | LATTICE STEEL TOWER | [9 empty] | 158.4262
121682756 | F | LC | ETL.9240.TOWR | 43249623 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 43249623 |  | LATTICE STEEL TOWER | [9 empty] | 335.0007
121688881 | F | LC | ETL.3180.TOWR | 40857755 | CONCORD | DIABLO | 2021-07-09 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40857755 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-12 | Glass Silicone Coated | Suspension |  |  |  |  | 6.7786e-07 | 79.7793 | 5.4079e-05
121688881 | F | LC | ETL.3180.TOWR | 40857755 | CONCORD | DIABLO | 2021-07-09 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40857755 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | Suspension |  |  |  |  | 6.7786e-07 | 79.7793 | 5.4079e-05
121706526 | E | LC | ETL.4040.POLE.WDPS | 44557564 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553913 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.074947 | 1791.3177 | 134.2539
121737272 | E | LC | ETL.5520.INSL.CERA | 44313404 | CONCORD | EAST BAY | 2021-07-12 |  | ETL.5520 | PITTSBURG-TESLA #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40872738 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 1.1144e-08 | 4750.3203 | 5.2937e-05
121748472 | B | LC | ETL.6020.INSL | 40837366 | TABLEMTN | NORTH VALLEY | 2021-07-16 | 2021-08-11 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810536 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 5.0049e-07 | 791.1504
121748473 | B | LC | ETL.6020.TOWR | 40810536 | TABLEMTN | NORTH VALLEY | 2021-07-16 | 2021-08-11 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810536 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 5.0049e-07 | 791.1504
121749864 | F | LC | ETL.6110.TOWR | 40760883 | METCALF | STOCKTON | 2021-07-17 | 2021-07-28 | ETL.6110 | TESLA-METCALF | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40760883 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-09-15 | Glass Silicone Coated | Suspension |  |  |  |  | 1.4326e-07
121749942 | F | LC | ETL.1820.POLE.WDPS | 44557624 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44553945 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.1765 | 189.9226
121760186 | E | LC | ETL.5950.TOWR | 40819287 | PISMOBCH | LOS PADRES | 2021-07-19 |  | ETL.5950 | DIABLO UNIT #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40819287 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.010867 | 1061 | 11.5304
121769655 | E | LC | ETL.6810.POLE.WOOD | 40658082 | EUREKA | HUMBOLDT | 2021-07-19 |  | ETL.6810 | ESSEX JCT-ORICK | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] |  | Zone 1 | HFRA Removal | PEND | 40658082 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.016099
121781443 | F | LC | ETL.4050.POLE.WOOD | 44310999 | LAKEVLLE | SONOMA | 2021-07-21 | 2021-07-29 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44310999 | 2014-12-18 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2014-12-18 | Polymer | Suspension |  |  |  |  | 2.231e-05 | 2248.4673
121795135 | F | LC | ETL.9240.TOWR | 45104765 | PISMOBCH | LOS PADRES | 2021-07-26 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45104765 |  | LATTICE STEEL TOWER | [9 empty] | 761.3521
121810319 | E | LC | ETL.8365.POLE.WOOD | 40808444 | EUREKA | HUMBOLDT | 2021-07-28 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40808444 | 2010-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.024766 | 284.811 | 7.0536
121810521 | F | LC | ETL.8350.POLE.WDPS | 44405870 | VICTOR | STOCKTON | 2021-07-27 | 2021-08-02 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44405867 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0013535 | 398.6916
121810727 | F | LC | ETL.2420.POLE.STPS | 44408054 | LAKEVLLE |  | 2021-07-27 |  | ETL.2420 | MENDOCINO-UKIAH | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44408053 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.2442e-06 | 2169.5542
121816521 | E | LC | ETL.2540.POLE.WDPS | 44551376 | MOSSLNDG | CENTRAL COAST | 2021-07-29 |  | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44550894 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.34725 | 3120.0405 | 1083.4268
121942065 | E | LC | ETL.3540.INSL.CERA | 40636618 | PISMOBCH | LOS PADRES | 2021-08-23 |  | ETL.3540 | SAN LUIS OBISPO-SANTA MARIA | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40604818 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1958-01-01 | Polymer | Suspension |  |  |  |  | 0.0010544 | 3152.6191 | 3.324
121942065 | E | LC | ETL.3540.INSL.CERA | 40636618 | PISMOBCH | LOS PADRES | 2021-08-23 |  | ETL.3540 | SAN LUIS OBISPO-SANTA MARIA | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40604818 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 0.0010544 | 3152.6191 | 3.324
121974069 | E | LC | ETL.6750.POLE.WDPS | 44232854 | TABLEMTN | NORTH VALLEY | 2021-08-30 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44232853 | 2012-09-17 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00036396 | 31.7081 | 0.01154
122400132 | F | LC | ETL.2030.POLE.WOOD | 40748069 | FRESNO | FRESNO | 2021-11-19 |  | ETL.2030 | KINGS RIVER-SANGER-REEDLEY | Right of Way | Encroachment | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40748069 | 1963-01-01 | Single Wood Pole | WB - Wishbone | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 2.2868e-05 | 5574.5678
118388885 | E | LC | ETL.1431.INSL | 40678233 | SACTO | SACRAMENTO | 2020-01-02 | 2021-03-23 | ETL.1431 | BRUNSWICK #2 TAP | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
118753058 | F | LC | ETL.4590.TOWR | 40910153 | TABLEMTN | NORTH VALLEY | 2020-03-27 | 2021-02-10 | ETL.4590 | CRESTA-RIO OSO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40910153 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.642e-07 | 15.8851
118761449 | F | LC | ETL.5780.TOWR | 40604806 | VICTOR | STOCKTON | 2020-03-31 | 2021-06-01 | ETL.5780 | TIGER CREEK-ELECTRA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40604806 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 1.2961e-05 | 63.3898
118793697 | E | LC | ETL.8210.POLE.WOOD | 40908269 | VICTOR | STOCKTON | 2020-04-07 | 2020-05-12 | ETL.8210 | VALLEY SPRINGS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40908269 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0018677 | 1221.7842
118913773 | E | LC | ETL.6979.POLE.WOOD | 40648464 | LAKEVLLE | SONOMA | 2020-04-13 |  | ETL.6979 | MONTE RIO-FORT ROSS | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40648464 | 1969-01-01 | Single Wood Pole | TPSR - Tri Post & Susp Light | 2010-01-01 | Polymer | Other |  |  |  |  | 0.030088 | 876.5875 | 26.3749
118922208 | E | LC | ETL.5220.INSL | 40892241 | METCALF | SAN JOSE | 2020-04-13 | 2021-03-09 | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118927805 | E | LC | ETL.6852.POLE.WOOD | 40747630 | LAKEVLLE | SONOMA | 2020-04-16 | 2021-05-17 | ETL.6852 | CLEAR LAKE-KONOCTI | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40747630 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2011-04-19 | Polymer | Dead End |  |  |  |  | 0.039646 | 6204.4409
118943948 | F | LC | ETL.4440.POLE.NWOD | 41162691 | TABLEMTN | NORTH VALLEY | 2020-04-23 | 2021-07-19 | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41162691 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | Dead End |  |  |  |  | 4.1027e-12 | 713.1375
118945014 | F | LC | ETL.4750.TOWR | 41081388 | LAKEVLLE | SONOMA | 2020-04-23 | 2020-05-05 | ETL.4750 | GEYSERS #12-FULTON | Structure-Tower | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41081388 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1979-01-01 | Porcelain | Dead End |  |  |  |  | 0.0022144 | 1646.4998
118945014 | F | LC | ETL.4750.TOWR | 41081388 | LAKEVLLE | SONOMA | 2020-04-23 | 2020-05-05 | ETL.4750 | GEYSERS #12-FULTON | Structure-Tower | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41081388 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.0022144 | 1646.4998
118948416 | F | LC | ETL.6220.POLE.WOOD | 40698417 | EUREKA | HUMBOLDT | 2020-04-24 | 2021-03-30 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40698417 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.2171 | 633.4258
118950508 | F | LC | ETL.6880.POLE.NWOD | 40593315 | LAKEVLLE | SONOMA | 2020-04-23 | 2020-11-10 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
118953083 | F | LC | ETL.1330.TOWR | 40751501 | LAKEVLLE | HUMBOLDT | 2020-04-23 | 2021-01-12 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751501 | 1951-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 0.00040771 | 6696.3608
118964083 | E | LC | ETL.6650.INSL.NCER | 44906715 | TABLEMTN | NORTH VALLEY | 2020-04-30 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44906704 | 2020-04-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-04-08 | Glass | Suspension |  |  |  |  | 0.00064921
118964083 | E | LC | ETL.6650.INSL.NCER | 44906715 | TABLEMTN | NORTH VALLEY | 2020-04-30 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44906704 | 2020-04-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-04-08 | Glass | Suspension |  |  |  |  | 0.00064921
118964673 | B | LC | ETL.1330.TOWR | 40750581 | LAKEVLLE | HUMBOLDT | 2020-04-24 | 2020-06-15 | ETL.1330 | CORTINA-MENDOCINO #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750581 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Dead End |  |  |  |  | 0.00081752 | 1518.6221
118964673 | B | LC | ETL.1330.TOWR | 40750581 | LAKEVLLE | HUMBOLDT | 2020-04-24 | 2020-06-15 | ETL.1330 | CORTINA-MENDOCINO #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750581 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00081752 | 1518.6221
118981691 | E | LC | ETL.8650.TOWR | 40684990 | FRESNO | YOSEMITE | 2020-05-01 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40684990 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-12-17 | Glass | Suspension |  |  |  |  | 0.00058291 | 2944.5339
118993864 | F | LC | ETL.5930.TOWR | 40868391 | CONCORD | DIABLO | 2020-05-04 | 2021-01-28 | ETL.5930 | PARKWAY-MORAGA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40868391 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2017-10-27 | Glass | Dead End |  |  |  |  | 2.4053e-07 | 712.379
118993864 | F | LC | ETL.5930.TOWR | 40868391 | CONCORD | DIABLO | 2020-05-04 | 2021-01-28 | ETL.5930 | PARKWAY-MORAGA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40868391 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.4053e-07 | 712.379
119004730 | E | LC | ETL.2740.INSL.NCER | 40704844 | CONCORD | EAST BAY | 2020-05-04 | 2021-06-14 | ETL.2740 | MORAGA-OAKLAND #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119017209 | E | LC | ETL.8650.POLE.NWOD | 44420144 | FRESNO | YOSEMITE | 2020-05-04 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44420144 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0047429 | 6552.5298
119036736 | E | LC | ETL.2060.POLE.WOOD | 40860776 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-06-04 | ETL.2060 | FORT BRAGG-ELK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40860776 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.16458 | 593.3324
119056551 | E | LC | ETL.6440.POLE.WOOD | 41144179 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-07-08 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41144179 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0021531 | 3993.7583
119059635 | F | LC | ETL.1240.POLE.STPS | 44200949 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2020-06-05 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Tier 2 | Within Both | COMP | 44200948 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.3951e-08 | 3186.3738
119081471 | E | LC | ETL.6950.INSL.NCER | 40707573 | SACTO | SACRAMENTO | 2020-05-28 |  | ETL.6950 | GOLD HILL #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40650785 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0014234 | 2422.7009 | 3.4484
119084734 | E | LC | ETL.6760.POLE.WOOD | 40814230 | SACTO | SIERRA | 2020-05-29 | 2021-09-02 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40814230 |  | Single Wood Pole | LB - Line and Buck |  | Ceramic | [5 empty] | 0.089755 | 1138.9978
119096406 | E | LC | ETL.7290.POLE.WOOD | 44159606 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2020-11-09 | ETL.7290 | KILARC-CEDAR CREEK | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44159606 | 2014-06-02 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | Post |  |  |  |  | 0.017962 | 364.8483
119096714 | E | LC | ETL.7140.POLE.WOOD | 40617116 | LAKEVLLE | SONOMA | 2020-06-02 | 2021-05-11 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119097154 | F | LC | ETL.6760.POLE.WOOD | 40611224 | SACTO | SIERRA | 2020-05-28 | 2021-03-18 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Rotten | [Stub, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611224 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.076665 | 332.3255
119103080 | E | LC | ETL.3190.INSL | 40801850 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.3190 | CARIBOU-PALERMO | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | PEND
119106181 | F | LC | ETL.7300.POLE.WOOD | 40877870 | TABLEMTN |  | 2020-06-04 | 2021-02-10 | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40877870 |  | Single Wood Pole | T-1 - Tri Post | 2018-06-03 | Polymer | Post |  |  |  |  | 0.00011919 | 5053.5459
119118835 | E | LC | ETL.5290.TOWR | 40764931 | PISMOBCH | LOS PADRES | 2020-05-21 | 2021-01-25 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40764931 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 4.8503e-08 | 1014.3526
119118855 | F | LC | ETL.7930.POLE.WOOD | 42564785 | MOSSLNDG | CENTRAL COAST | 2020-06-03 | 2021-01-25 | ETL.7930 | SALINAS-LAURELES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 42564785 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.019282 | 0.065789
119124241 | F | LC | ETL.7300.POLE.WOOD | 40770437 | TABLEMTN |  | 2020-06-03 | 2021-07-07 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770437 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0012689 | 3200.7368
119129381 | F | LC | ETL.2790.TOWR | 40646083 | CONCORD | EAST BAY | 2020-06-04 | 2021-03-16 | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40646083 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-22 | Glass | Suspension |  |  |  |  | 0.00020684 | 0.065147
119129381 | F | LC | ETL.2790.TOWR | 40646083 | CONCORD | EAST BAY | 2020-06-04 | 2021-03-16 | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40646083 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 0.00020684 | 0.065147
119142145 | F | LC | ETL.8290.POLE.NWOD | 44774787 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44774787 | 2019-06-12 | Light Duty Steel Pole | T-1 - Tri Post | 2019-06-12 | Polymer | Post |  |  |  |  | 8.8229e-07 | 2911.8145
119170296 | E | LC | ETL.6280.POLE.WOOD | 40599687 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2020-12-08 | ETL.6280 | CARIBOU #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40599687 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0037146 | 6616.2266
119174320 | E | LC | ETL.7380.POLE.WDPS | 44562931 | MOSSLNDG | CENTRAL COAST | 2020-06-12 | 2021-08-12 | ETL.7380 | LAURELES-OTTER | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44562444 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.17392 | 0.065148
119180644 | E | LC | ETL.6470.POLE.WOOD | 40611344 | SACTO | SACRAMENTO | 2020-06-17 | 2021-07-27 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611344 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.30511 | 189.9644
119180985 | E | LC | ETL.8350.POLE.WOOD | 40603877 | VICTOR | STOCKTON | 2020-06-16 | 2021-06-03 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119183246 | F | LC | ETL.6470.POLE.WOOD | 40664633 | SACTO | SACRAMENTO | 2020-06-18 | 2021-02-11 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL | [11 empty] | 0.042253 | 300.6841
119185832 | F | LC | ETL.5463.TOWR | 40746340 | CONCORD | MISSION | 2020-04-20 | 2021-01-14 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746340 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Ceramic | Dead End |  |  |  |  | 1.1895e-07 | 2727.2507
119185832 | F | LC | ETL.5463.TOWR | 40746340 | CONCORD | MISSION | 2020-04-20 | 2021-01-14 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746340 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.1895e-07 | 2727.2507
119196215 | F | LC | ETL.6470.POLE.WOOD | 40874720 | SACTO | SIERRA | 2020-06-22 | 2021-07-08 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40874720 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.078782 | 110.8608
119200327 | E | LC | ETL.6470.POLE.WOOD | 40767226 | SACTO | SIERRA | 2020-06-23 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767226 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.10433 | 110.8102
119201083 | E | LC | ETL.9340.POLE.NWOD | 43680878 | FRESNO | FRESNO | 2020-06-23 | 2020-08-06 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 43680878 | 2016-02-11 | Light Duty Steel Pole | TPS1D - Tri Post & Susp DDE 115 KV | 2016-02-11 | Polymer | Suspension |  |  |  |  | 0.00061973 | 5192.4033
119203501 | F | LC | ETL.6480.POLE.WOOD | 40815337 | SACTO | SIERRA | 2020-06-22 | 2021-05-23 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119237898 | F | LC | ETL.6020.TOWR | 40810014 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2021-02-22 | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40810014 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.9028e-06 | 641.2011
119301261 | F | LC | ETL.8060.POLE.WOOD | 40603063 | SACTO | SIERRA | 2020-06-29 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40603063 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.05494 | 31.7066
119301559 | F | LC | ETL.7140.POLE.WOOD | 41118236 | LAKEVLLE | SONOMA | 2020-07-02 | 2021-07-02 | ETL.7140 | IGNACIO-BOLINAS #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41118236 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.011717 | 94.9668
119302136 | E | LC | ETL.1110.POLE.WDPS | 44424401 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-04-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424399 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00083679 | 3706.9577
119309750 | F | LC | ETL.1440.TOWR | 44768871 | SACTO | SIERRA | 2020-07-01 | 2021-09-01 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44768871 |  | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-08-26 | Glass | Dead End |  |  |  |  | 4.832e-05 | 1123.6396
119310375 | F | LC | ETL.1440.POLE.WDPS | 44767648 | SACTO | SACRAMENTO | 2020-07-01 | 2021-02-18 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | DLFL
119315269 | F | LC | ETL.7560.POLE.WOOD | 40761785 | SACTO | SACRAMENTO | 2020-07-06 |  | ETL.7560 | WEIMAR #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40761785 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.038567 | 300.8699
119326788 | E | LC | ETL.7270.INSL.NCER | 40919283 | TABLEMTN |  | 2020-07-06 | 2021-10-04 | ETL.7270 | KESWICK-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40909544 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0016009 | 933.5561
119327162 | F | LC | ETL.1110.POLE.WDPS | 44423918 | TABLEMTN | HUMBOLDT | 2020-07-07 | 2021-01-22 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119333440 | E | LC | ETL.1110.POLE.WDPS | 44561161 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-04-30 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44515859 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0020157 | 5129.4224
119341813 | E | LC | ETL.3190.TOWR | 40863363 | TABLEMTN | NORTH VALLEY | 2020-07-08 |  | ETL.3190 | CARIBOU-PALERMO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40863363 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.0086864 | 857.7261 | 7.4505
119341894 | F | LC | ETL.7620.POLE.NWOD | 40593652 | METCALF | DE ANZA | 2020-07-08 |  | ETL.7620 | MONTA VISTA-PERMANENTE | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40593652 |  | Light Duty Steel Pole | DDE-A - Double Dead End Angle |  | Non Ceramic | Dead End | [5 empty] | 349.1872
119358148 | E | LC | ETL.8170.POLE.WOOD | 40579641 | EUREKA | HUMBOLDT | 2020-07-10 |  | ETL.8170 | TRINITY-MAPLE CREEK | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40579641 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.023322 | 300.6727 | 7.0123
119364713 | F | LC | ETL.7270.POLE.NWOD | 44649343 | TABLEMTN | NORTH VALLEY | 2020-07-13 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44649343 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 2.7375e-05 | 2.8233
119377665 | E | LC | ETL.2060.POLE.WOOD | 40600336 | LAKEVLLE | SONOMA | 2020-07-15 | 2021-08-12 | ETL.2060 | FORT BRAGG-ELK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600336 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.16999 | 31.6963
119466731 | F | LC | ETL.7030.POLE.WOOD | 40769970 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40769970 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0065348 | 159.1485
119469740 | F | LC | ETL.7030.POLE.NWOD | 44686500 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44686500 | 2018-11-24 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2018-11-24 | Polymer | Post |  |  |  |  | 0.0029509 | 15.8837
119471034 | F | LC | ETL.7030.POLE.NWOD | 44686398 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44686398 | 2018-11-24 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-24 | Polymer | Post |  |  |  |  | 0.0014859
119478985 | F | LC | ETL.7270.POLE.WOOD | 42621513 | TABLEMTN | NORTH VALLEY | 2020-07-20 | 2021-08-19 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42621513 |  | Single Wood Pole | SVDE - Single Vertical Dead End |  | Polymer | [5 empty] | 0.0057655 | 899.2657
119489219 | F | LC | ETL.1820.POLE.STPS | 44395128 | EUREKA | HUMBOLDT | 2020-07-15 | 2021-09-01 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44395127 | 2020-03-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0066227 | 94.9939
119528502 | F | LC | ETL.8060.POLE.WDPS | 44420797 | SACTO | SACRAMENTO | 2020-07-30 | 2021-07-23 | ETL.8060 | SPAULDING-SUMMIT | Vegetation | Overgrown | [Trim, No Action Taken] |  | Tier 2 | Within Both | CNCL | 44420794 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0081448 | 31.7192
119539109 | E | LC | ETL.6380.POLE.WOOD | 40699027 | LAKEVLLE | HUMBOLDT | 2020-07-31 | 2021-03-08 | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40699027 |  | Single Wood Pole | T2N | 2018-09-29 | Polymer | Post |  |  |  |  | 5.1266e-05 | 6300.8276
119549347 | E | LC | ETL.7490.POLE.WOOD | 44362121 | EUREKA | HUMBOLDT | 2020-07-31 | 2021-01-15 | ETL.7490 | MAPLE CREEK-HOOPA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44362121 | 2019-11-20 | Single Wood Pole | T-1 - Tri Post | 2019-11-20 | Polymer | Post |  |  |  |  | 0.0069597 | 1898.0215
119575410 | E | LC | ETL.6220.POLE.WOOD | 40875294 | EUREKA | HUMBOLDT | 2020-08-06 | 2021-01-25 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40875294 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Porcelain | [5 empty] | 0.11216
119591427 | B | LC | ETL.7180.POLE.WOOD | 40808629 | LAKEVLLE | NORTH BAY | 2020-08-10 | 2020-08-26 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119597076 | E | LC | ETL.7950.POLE.WOOD | 40825031 | METCALF | PENINSULA | 2020-08-10 |  | ETL.7950 | SAN MATEO-HILLSDALE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | PEND | 40825031 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Post |  |  |  |  | 0.0096938 | 156.8703 | 1.5207
119599113 | E | LC | ETL.8365.POLE.WOOD | 40906594 | EUREKA | HUMBOLDT | 2020-08-11 | 2021-05-10 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906594 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-04-28 | Glass | Dead End |  |  |  |  | 0.011207
119599572 | E | LC | ETL.1110.TOWR | 40594234 | TABLEMTN | HUMBOLDT | 2020-08-11 | 2021-04-05 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40594234 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.1064e-05 | 2658.1575
119600380 | F | LC | ETL.7930.POLE.WOOD | 40875031 | MOSSLNDG | CENTRAL COAST | 2020-08-11 |  | ETL.7930 | SALINAS-LAURELES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40875031 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.0051838 | 174.585
119604799 | E | LC | ETL.6220.POLE.WOOD | 40824466 | EUREKA | HUMBOLDT | 2020-08-10 | 2021-02-03 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40824466 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.53266
119608951 | E | LC | ETL.1450.POLE.WDPS | 44557781 | SACTO | SACRAMENTO | 2020-08-12 | 2021-10-11 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44554054 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.05406 | 1123.6396
119615503 | E | LC | ETL.1810.POLE.STPS | 44322700 | EUREKA | HUMBOLDT | 2020-08-14 | 2021-06-17 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Crossarm-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322700 | 2016-10-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2021-05-15 | Glass | Suspension |  |  |  |  | 2.4007e-08
119615503 | E | LC | ETL.1810.POLE.STPS | 44322700 | EUREKA | HUMBOLDT | 2020-08-14 | 2021-06-17 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Crossarm-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322700 | 2016-10-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2021-05-15 | Glass | Suspension |  |  |  |  | 2.4007e-08
119616764 | E | LC | ETL.5710.POLE.NWOD | 44191446 | METCALF | SAN JOSE | 2020-08-14 |  | ETL.5710 | JEFFERSON-MARTIN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44191446 |  | Tubular Steel Pole | Unknown |  | Non Ceramic | [5 empty] | 0.00013997 | 15.88 | 0.0022227
119635513 | F | LC | ETL.3800.TOWR | 40644455 | CONCORD | EAST BAY | 2020-08-18 | 2021-04-15 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40644455 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 1.3194e-07 | 0.090453
119635513 | F | LC | ETL.3800.TOWR | 40644455 | CONCORD | EAST BAY | 2020-08-18 | 2021-04-15 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40644455 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.3194e-07 | 0.090453
119636240 | B | LC | ETL.6979.POLE.WOOD | 40587333 | LAKEVLLE | SONOMA | 2020-08-19 | 2020-08-27 | ETL.6979 | MONTE RIO-FORT ROSS | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP
119637099 | E | LC | ETL.5490.TOWR | 40857920 | CONCORD | DIABLO | 2020-08-19 | 2021-04-13 | ETL.5490 | PITTSBURG-SAN RAMON | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857920 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 4.0377e-05 | 2266.6296
119639941 | B | LC | ETL.8650.POLE.NWOD | 44420205 | FRESNO | FRESNO | 2020-08-19 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420205 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.013497 | 5840.8999
119658803 | A | LC | ETL.6240.POLE.WOOD | 40659322 | MOSSLNDG | CENTRAL COAST | 2020-08-22 | 2020-09-19 | ETL.6240 | BURNS-LONE STAR #2 | Emergency-Wood | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40659322 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Polymer | [5 empty] | 0.12369 | 110.8153
119666444 | A | LC | ETL.7590.POLE.WOOD | 40592833 | MOSSLNDG | CENTRAL COAST | 2020-08-25 | 2020-10-01 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119692429 | A | LC | ETL.7590.POLE.NWOD | 40824961 | MOSSLNDG | CENTRAL COAST | 2020-08-30 | 2020-10-01 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119694043 | E | LC | ETL.1650.POLE.WOOD | 40594505 | LAKEVLLE | SONOMA | 2020-08-31 | 2021-03-09 | ETL.1650 | GEYSERS #3-CLOVERDALE | Vegetation | Overgrown | [Trim, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594505 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Dead End |  |  |  |  | 2.7077e-05 | 4151.2271
119715923 | E | LC | ETL.7820.INSL | 40884221 | LAKEVLLE | HUMBOLDT | 2020-09-02 | 2021-02-22 | ETL.7820 | POTTER VALLEY-WILLITS | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40861073 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Non Ceramic | [5 empty] | 0.00081362 | 237.3428
119718684 | E | LC | ETL.8210.POLE.WOOD | 40907096 | VICTOR | STOCKTON | 2020-07-27 | 2021-09-07 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0034473 | 2455.4761
119722996 | B | LC | ETL.1810.POLE.WDPS | 44322241 | EUREKA | HUMBOLDT | 2020-08-07 | 2020-09-17 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322240 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012246
119723028 | F | LC | ETL.1440.POLE.STPS | 44338099 | SACTO | SIERRA | 2020-08-11 | 2021-05-03 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Tier 3 | Within Both | COMP | 44338098 | 2018-09-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.6436e-07 | 433.5528
119727933 | F | LC | ETL.6760.POLE.NWOD | 44260130 | SACTO | SIERRA | 2020-09-08 | 2021-04-29 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44260130 | 2016-05-19 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2016-05-19 | Polymer | Post |  |  |  |  | 0.037271 | 63.3392
119760405 | B | LC | ETL.7490.POLE.WOOD | 40771313 | EUREKA | HUMBOLDT | 2020-09-14 | 2020-10-20 | ETL.7490 | MAPLE CREEK-HOOPA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40771313 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.0096405 | 215.1669
119769393 | F | LC | ETL.1400.POLE.WDPS | 44789686 | VICTOR | STOCKTON | 2020-07-29 | 2021-01-19 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40803723 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00033217 | 31.7081
119770141 | F | LC | ETL.6440.POLE.WOOD | 40826842 | TABLEMTN | NORTH VALLEY | 2020-08-25 | 2021-03-31 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826842 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | [5 empty] | 0.00021558 | 3629.7212
119776894 | E | LC | ETL.2790.INSL | 40676711 | CONCORD | DIABLO | 2020-09-17 | 2020-09-22 | ETL.2790 | MORAGA-SAN LEANDRO #3 | Insulator | Contaminated | [Ground Wash, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648782 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1994-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.3053e-08 | 0.066432
119789498 | F | LC | ETL.1650.POLE.WOOD | 40648815 | LAKEVLLE | SONOMA | 2020-07-29 | 2021-11-29 | ETL.1650 | GEYSERS #3-CLOVERDALE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40648815 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 0.0013226 | 3263.3687
119816138 | F | LC | ETL.1421.POLE.NWOD | 44814409 | SACTO | SIERRA | 2020-08-29 |  | ETL.1421 | DUTCH FLAT #2 TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44814409 | 2019-06-04 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-06-04 | Glass | Suspension |  |  |  |  | 1.077e-05 | 664.5352
119831643 | A | LC | ETL.1110.POLE.WDPS | 44424110 | TABLEMTN | HUMBOLDT | 2020-09-28 | 2020-10-21 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP
119838817 | F | LC | ETL.6280.POLE.WOOD | 40698842 | TABLEMTN | NORTH VALLEY | 2020-10-01 | 2021-01-20 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40698842 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 5.7796e-05 | 5225.9537
119897376 | F | LC | ETL.6810.POLE.WOOD | 40585287 | EUREKA | HUMBOLDT | 2020-10-08 | 2021-08-27 | ETL.6810 | ESSEX JCT-ORICK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Zone 1 | HFRA Removal | DLFL | 40585287 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.015714
119906219 | E | LC | ETL.7590.INSL.CERA | 44631863 | MOSSLNDG | CENTRAL COAST | 2020-10-14 | 2021-03-24 | ETL.7590 | MONTA VISTA-BURNS | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed, Completed, Completed, Completed] | Tier3 |  |  | COMP
119961983 | F | LC | ETL.8960.POLE.WOOD | 40594486 | FRESNO | YOSEMITE | 2020-10-27 |  | ETL.8960 | LOS BANOS-PACHECO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40594486 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.2832e-05
120070550 | E | LC | ETL.6070.TOWR | 40678023 | TABLEMTN | NORTH VALLEY | 2020-11-18 | 2021-06-14 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40678023 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 0.00090169 | 398.6012
120079557 | E | LC | ETL.1450.POLE.WDPS | 44552276 | SACTO | SACRAMENTO | 2020-09-09 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44551525 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0002956 | 0.065152 | 1.9259e-05
120097149 | F | LC | ETL.3180.POLE.WOOD | 41196302 | CONCORD | EAST BAY | 2020-11-16 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41196302 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Non Ceramic | Suspension |  |  |  |  | 0.002057 | 16.3369
120120941 | E | LC | ETL.8170.POLE.WOOD | 40668488 | EUREKA | HUMBOLDT | 2020-11-30 | 2021-06-03 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120125427 | F | LC | ETL.6375.POLE.WOOD | 43196977 | SACTO | SIERRA | 2020-11-30 | 2021-02-09 | ETL.6375 | DRUM PH #2 TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 43196977 |  | Single Wood Pole | DE - Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.0014337 | 2082.0714
120144086 | E | LC | ETL.1600.INSL.NCER | 40879846 | LAKEVLLE | SONOMA | 2020-12-05 | 2021-04-08 | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40858398 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 1.3983e-05 | 142.516
120144086 | E | LC | ETL.1600.INSL.NCER | 40879846 | LAKEVLLE | SONOMA | 2020-12-05 | 2021-04-08 | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40858398 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-03-21 | Glass | Suspension |  |  |  |  | 1.3983e-05 | 142.516
120150762 | F | LC | ETL.8960.POLE.WOOD | 40754874 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40754874 | 1979-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1979-01-01 | Porcelain | Post |  |  |  |  | 0.00038506
120191441 | E | LC | ETL.1450.POLE.WDPS | 44549846 | SACTO | SACRAMENTO | 2020-12-11 | 2021-08-19 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549456 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 8.6548e-05 | 2056.7583
120634951 | E | LC | ETL.4620.INSL | 40885022 | PISMOBCH | LOS PADRES | 2021-03-11 |  | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40862866 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.6467e-08 | 3405.4033 | 5.6075e-05
120653976 | B | LC | ETL.5630.TOWR | 40757660 | TABLEMTN | NORTH VALLEY | 2021-03-17 | 2021-03-29 | ETL.5630 | ROCK CREEK-POE | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40757660 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 3.6586e-06 | 254.0199
120680385 | E | LC | ETL.2540.POLE.WOOD | 40585532 | MOSSLNDG | SAN JOSE | 2021-03-22 | 2021-09-23 | ETL.2540 | METCALF-GREEN VALLEY | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40585532 | 1952-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1952-01-01 | Polymer | Double Dead End - Suspension |  |  |  |  | 0.29604 | 2452.0347
120687151 | B | LC | ETL.5630.TOWR | 40867172 | TABLEMTN | NORTH VALLEY | 2021-03-24 | 2021-04-30 | ETL.5630 | ROCK CREEK-POE | Other | Land/Enviro Issue | [Access Issue] | Tier2 | Tier 2 | Within Both | COMP | 40867172 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-26 | Ceramic | Suspension |  |  |  |  | 9.2659e-05 | 2497.7503
120694985 | B | LC | ETL.3830.INSL | 40836472 | VICTOR | STOCKTON | 2021-03-25 | 2021-06-03 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809713 | 1989-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.1595e-07 | 3532.8677
120696006 | E | LC | ETL.4040.POLE.WOOD | 42622323 | TABLEMTN | NORTH VALLEY | 2021-03-26 | 2021-09-27 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.029938 | 2010.385
120714411 | E | LC | ETL.5630.POLE.NWOD | 43249819 | TABLEMTN | NORTH VALLEY | 2021-03-30 |  | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 43249819 |  | Lattice Steel Pole | Unknown |  | Ceramic | Suspension |  |  |  |  | 0.0012522 | 6046.7764 | 7.5715
120715964 | E | LC | ETL.5330.TOWR | 40810761 | MOSSLNDG | CENTRAL COAST | 2021-03-30 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810761 | 1949-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1949-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.197e-06 | 47.5223 | 0.00010441
120721181 | E | LC | ETL.1650.POLE.WOOD | 40750645 | LAKEVLLE | SONOMA | 2021-03-31 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40750645 | 1994-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1966-01-01 | Porcelain | Dead End |  |  |  |  | 0.00012258 | 4151.2271 | 0.50886
120725694 | E | LC | ETL.7380.POLE.WDPS | 44562780 | MOSSLNDG | CENTRAL COAST | 2021-04-01 |  | ETL.7380 | LAURELES-OTTER | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44562375 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.10504 | 47.5141 | 4.9908
120726400 | E | LC | ETL.4040.POLE.STPS | 44647524 | TABLEMTN | NORTH VALLEY | 2021-04-01 | 2021-09-14 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44646912 | 2018-08-17 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00021353 | 205.7554
120726805 | E | LC | ETL.7390.POLE.NWOD | 40602928 | LAKEVLLE | SONOMA | 2021-04-01 | 2021-06-28 | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602928 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00027535 | 2683.8744
120742994 | E | LC | ETL.1350.POLE.WDPS | 44549859 | TABLEMTN | NORTH VALLEY | 2021-04-05 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
120749872 | B | LC | ETL.3830.INSL.CERA | 40696872 | VICTOR | STOCKTON | 2021-04-06 | 2021-05-26 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40642774 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.6926e-07 | 229.4194
120764308 | E | LC | ETL.6370.POLE.WDPS | 44560460 | CONCORD | DIABLO | 2021-04-08 |  | ETL.6370 | CHRISTIE-WILLOW PASS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560098 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.85628 | 71.2575 | 61.0163
120764510 | E | LC | ETL.5650.TOWR | 40591939 | TABLEMTN | NORTH VALLEY | 2021-04-08 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40591939 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-15 | Glass | Suspension |  |  |  |  | 9.2087e-07 | 4041.2002 | 0.0037214
120792754 | E | LC | ETL.1420.TOWR | 40814360 | SACTO | SACRAMENTO | 2021-04-10 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40814360 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-05-02 | Porcelain | Suspension |  |  |  |  | 0.0043375 | 63.3392 | 0.27474
120792754 | E | LC | ETL.1420.TOWR | 40814360 | SACTO | SACRAMENTO | 2021-04-10 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40814360 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.0043375 | 63.3392 | 0.27474
120793811 | E | LC | ETL.5353.TOWR | 40680369 | METCALF | SAN JOSE | 2021-04-08 |  | ETL.5353 | LOS ESTEROS-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40680369 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Ceramic | Suspension |  |  |  |  | 5.8636e-06 | 2822.5605 | 0.01655
120795690 | B | LC | ETL.3840.INSL.NCER | 40710336 | VICTOR | STOCKTON | 2021-04-06 | 2021-05-24 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656228 | 1910-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post | 1989-01-01 | Polymer | Post |  |  |  |  | 3.8322e-07 | 229.4194
120803366 | E | LC | ETL.3840.INSL.CERA | 40630090 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40589038 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 5.4919e-05 | 4843.4395 | 0.266
120803456 | E | LC | ETL.7140.POLE.WOOD | 40648883 | LAKEVLLE | SONOMA | 2021-04-12 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40648883 |  | Single Wood Pole | FIG4W - Wood X Arm |  | Ceramic | Other |  |  |  |  | 0.19878 | 31.7369 | 6.3088
120805043 | E | LC | ETL.1450.POLE.WDPS | 44549919 | SACTO | SACRAMENTO | 2021-04-13 | 2021-06-09 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44549459 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00053387 | 79.1687
120805080 | E | LC | ETL.5390.INSL.NCER | 45114498 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.5390 | PIT #1-COTTONWOOD | Splice-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40820876 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 7.8343e-09 | 4626.835 | 3.6248e-05
120815694 | F | LC | ETL.1400.POLE.STPS | 44384825 | VICTOR | STOCKTON | 2021-04-14 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44384824 | 2019-06-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.023e-06 | 31.7081
120827843 | F | LC | ETL.7290.POLE.WOOD | 40586358 | TABLEMTN | NORTH VALLEY | 2021-04-16 |  | ETL.7290 | KILARC-CEDAR CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40586358 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.016348 | 183.2412
120829499 | B | LC | ETL.8405.POLE.WOOD | 40611426 | SACTO | SACRAMENTO | 2021-04-16 | 2021-06-29 | ETL.8405 | MIDDLE FORK #1 | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611426 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0017884 | 6807.7681
120831313 | B | LC | ETL.8405.POLE.WDPS | 44650652 | SACTO | SACRAMENTO | 2021-04-16 | 2021-06-29 | ETL.8405 | MIDDLE FORK #1 | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44414875 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0010974 | 6864.6014
120831314 | B | LC | ETL.8405.POLE.WDPS | 44650653 | SACTO | SACRAMENTO | 2021-04-16 | 2021-06-29 | ETL.8405 | MIDDLE FORK #1 | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44414875 | 2018-08-30 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0010974 | 6864.6014
120831374 | F | LC | ETL.8365.POLE.NWOD | 40906615 | EUREKA | HUMBOLDT | 2021-04-16 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40906615 | 2010-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0025139
120839582 | E | LC | ETL.6500.POLE.WOOD | 40757189 | SACTO | SACRAMENTO | 2021-04-17 | 2021-08-18 | ETL.6500 | COLGATE-PALERMO | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40757189 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0020218 | 4702.3125
120840120 | E | LC | ETL.5540.INSL.CERA | 40636869 | TABLEMTN | NORTH VALLEY | 2021-04-09 |  | ETL.5540 | POE-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40605300 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 5.2122e-06 | 3674.2734 | 0.019151
120841387 | E | LC | ETL.1600.INSL.NCER | 40879863 | LAKEVLLE | SONOMA | 2021-04-12 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40858410 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Polymer | Suspension |  |  |  |  | 1.3332e-06 | 269.18 | 0.00035886
120843099 | E | LC | ETL.7140.POLE.WOOD | 40648885 | LAKEVLLE | SONOMA | 2021-04-13 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40648885 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.011717 | 94.9668 | 1.1127
120859402 | E | LC | ETL.7380.POLE.WOOD | 44645835 | MOSSLNDG | CENTRAL COAST | 2021-04-21 | 2021-11-01 | ETL.7380 | LAURELES-OTTER | Vegetation | Overgrown | [Trim, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44645835 | 2018-08-24 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-24 | Polymer | Dead End - Post |  |  |  |  | 0.051626 | 59.4629 | 3.0698
120891944 | E | LC | ETL.6890.POLE.WOOD | 40825324 | LAKEVLLE | SONOMA | 2021-04-27 |  | ETL.6890 | FULTON-HOPLAND | Vegetation | Overgrown | [Trim] | Tier3 | Tier 3 | Within Both | PEND | 40825324 | 1967-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Other |  |  |  |  | 0.0023391 | 982.4404 | 2.298
120897586 | E | LC | ETL.8060.POLE.WOOD | 40818276 | SACTO | SACRAMENTO | 2021-04-28 |  | ETL.8060 | SPAULDING-SUMMIT | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40818276 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0049935 | 0.065152 | 0.00032533
120903289 | E | LC | ETL.1250.INSL.NCER | 40791671 | FRESNO | FRESNO | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761741 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 1.5099e-05 | 5920.3032 | 0.089393
120913450 | F | LC | ETL.6890.POLE.WOOD | 40769675 | LAKEVLLE | SONOMA | 2021-05-01 | 2021-10-14 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40769675 | 1993-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Other |  |  |  |  | 0.00025806 | 2674.8999
120938151 | E | LC | ETL.4316.INSL.CERA | 40788736 | TABLEMTN | NORTH VALLEY | 2021-05-05 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40758646 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0020407
120938151 | E | LC | ETL.4316.INSL.CERA | 40788736 | TABLEMTN | NORTH VALLEY | 2021-05-05 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40758646 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0020407
120938151 | E | LC | ETL.4316.INSL.CERA | 40788736 | TABLEMTN | NORTH VALLEY | 2021-05-05 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40758646 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0020407
120948702 | E | LC | ETL.2900.INSL.CERA | 40635957 | MOSSLNDG | CENTRAL COAST | 2021-04-19 | 2021-11-08 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40603459 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1963-01-01 | Porcelain | Dead End |  |  |  |  | 0.020505 | 5490.064 | 112.5755
121317514 | F | LC | ETL.7590.POLE.WOOD | 45028790 | METCALF | DE ANZA | 2021-04-19 |  | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45028790 | 2020-09-13 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-09-13 | Polymer | Dead End |  |  |  |  | 0.45002 | 110.8153
121320742 | E | LC | ETL.8365.POLE.NWOD | 45087778 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Damper-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 45087778 | 2021-04-22 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.023065
121332297 | F | LC | ETL.2790.TOWR | 40861007 | CONCORD | MISSION | 2021-04-23 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40861007 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 4.2554e-07 | 15.8932 | 6.7632e-06
121336277 | F | LC | ETL.7260.POLE.WOOD | 44651522 | TABLEMTN | NORTH VALLEY | 2021-04-23 | 2021-10-07 | ETL.7260 | KESWICK-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44651522 | 2018-08-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2018-08-01 | Ceramic | Dead End |  |  |  |  | 0.00033324 | 2074.0583
121338441 | F | LC | ETL.3500.TOWR | 40596311 | VICTOR | STOCKTON | 2021-04-26 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40596311 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.00086079 | 284.8886 | 0.24523
121347412 | E | LC | ETL.4340.INSL | 40726172 | LAKEVLLE | NORTH BAY | 2021-04-20 | 2021-11-16 | ETL.4340 | BAHIA-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40683919 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.1821e-08 | 158.2408 | 3.453e-06
121347412 | E | LC | ETL.4340.INSL | 40726172 | LAKEVLLE | NORTH BAY | 2021-04-20 | 2021-11-16 | ETL.4340 | BAHIA-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40683919 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.1821e-08 | 158.2408 | 3.453e-06
121356422 | F | LC | ETL.7560.POLE.WOOD | 40767413 | SACTO | SIERRA | 2021-04-23 | 2021-10-11 | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40767413 |  | Single Wood Pole | TCDE - Tap Construction Dead End |  | Porcelain | [5 empty] | 0.25393 | 79.1577
121358864 | E | LC | ETL.8060.POLE.WOOD | 40602257 | SACTO | SIERRA | 2021-05-18 | 2021-05-24 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40602257 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0070958 | 0.065152
121359225 | F | LC | ETL.8490.POLE.NWOD | 42700019 | PISMOBCH | LOS PADRES | 2021-04-23 |  | ETL.8490 | ATASCADERO-SAN LUIS OBISPO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 42700019 | 2013-03-11 | Light Duty Steel Pole | T-1 - Tri Post | 2013-03-11 | Non Ceramic | Post |  |  |  |  | 1.943e-06 | 967.313
121365308 | E | LC | ETL.3500.INSL | 40604070 | VICTOR | STOCKTON | 2021-04-29 | 2021-06-11 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
121372762 | B | LC | ETL.1070.INSL.NCER | 40772639 | VICTOR | STOCKTON | 2021-05-20 | 2021-07-01 | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40745396 | 1957-01-01 | Single Wood Pole | WB - Wishbone | 1998-01-01 | Polymer | Post |  |  |  |  | 0.0011047 | 2978.6118
121372899 | F | LC | ETL.4550.TOWR | 40753190 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753190 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 3.9014e-07 | 4563.5537 | 0.0017804
121372899 | F | LC | ETL.4550.TOWR | 40753190 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753190 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 3.9014e-07 | 4563.5537 | 0.0017804
121379024 | F | LC | ETL.8640.POLE.NWOD | 40662917 | FRESNO | YOSEMITE | 2021-05-05 |  | ETL.8640 | EXCHEQUER-MARIPOSA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40662917 | 2005-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2005-01-01 | Polymer | Post |  |  |  |  | 3.1778e-11 | 6758.4639
121380984 | F | LC | ETL.2900.TOWR | 40858551 | MOSSLNDG | CENTRAL COAST | 2021-05-07 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40858551 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.013459 | 1836.6479 | 24.7187
121381959 | F | LC | ETL.8250.POLE.WOOD | 40908868 | VICTOR | STOCKTON | 2021-05-11 | 2021-06-24 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40908868 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.791e-05 | 2899.7386
121383548 | E | LC | ETL.6760.INSL.CERA | 40922872 | SACTO | SACRAMENTO | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40913028 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0083192 | 31.7022 | 0.26374
121384867 | E | LC | ETL.7000.INSL.NCER | 40699318 | TABLEMTN |  | 2021-05-22 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40667916 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00079827 | 47.5141 | 0.037929
121385812 | E | LC | ETL.8250.POLE.WOOD | 40908830 | VICTOR | STOCKTON | 2021-05-10 | 2021-08-25 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908830 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 8.6465e-05 | 1759.9811
121391728 | F | LC | ETL.6760.POLE.WOOD | 40654091 | SACTO | SIERRA | 2021-05-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40654091 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.01275 | 79.1687
121401085 | F | LC | ETL.1420.POLE.STPS | 44415571 | SACTO | SACRAMENTO | 2021-05-25 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44415570 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.8603e-05 | 775.2101
121420569 | E | LC | ETL.7000.POLE.WOOD | 40868220 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40868220 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0020298 | 664.3499 | 1.3485
121430960 | F | LC | ETL.7212.POLE.WOOD | 40599265 | METCALF | PENINSULA | 2021-05-27 | 2021-07-14 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
121431266 | E | LC | ETL.7550.POLE.WOOD | 40809282 | LAKEVLLE | HUMBOLDT | 2021-05-28 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40809282 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0015334 | 1534.8907 | 2.3535
121436776 | E | LC | ETL.6470.POLE.WOOD | 40658312 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40658312 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.092793 | 110.8608 | 10.2871
121466833 | B | LC | ETL.6020.TOWR | 40576654 | TABLEMTN | NORTH VALLEY | 2021-06-03 | 2021-06-14 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40576654 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.5611e-08 | 253.2084
121470697 | F | LC | ETL.5390.TOWR | 40858181 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40858181 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.6954e-05 | 1856.0791
121474582 | E | LC | ETL.1350.INSL.CERA | 40634901 | TABLEMTN |  | 2021-06-04 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44551623 |  | 2-Pole Wood | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.0047746
121474582 | E | LC | ETL.1350.INSL.CERA | 40634901 | TABLEMTN |  | 2021-06-04 |  | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44551623 |  | 2-Pole Wood | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.0047746
121475129 | F | LC | ETL.7550.POLE.WOOD | 40697995 | LAKEVLLE | HUMBOLDT | 2021-05-29 | 2021-09-30 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40697995 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0036638 | 221.5243
121475467 | E | LC | ETL.6750.POLE.WDPS | 44562139 | TABLEMTN | NORTH VALLEY | 2021-06-05 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44561583 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017792 | 490.5302 | 0.87277
121493666 | F | LC | ETL.5640.TOWR | 40867729 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40867729 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 4.0587e-08 | 674.4989 | 2.7376e-05
121500453 | E | LC | ETL.5640.TOWR | 40761256 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40761256 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 6.1942e-09 | 2401.9163 | 1.4878e-05
121512086 | E | LC | ETL.4221.POLE.STPS | 44356168 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4221 | SLY CREEK TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44356167 | 2016-11-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.8192e-05 | 348.1806 | 0.0063342
121521735 | E | LC | ETL.5980.TOWR | 40863582 | PISMOBCH | LOS PADRES | 2021-06-05 |  | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40863582 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-07-30 | Ceramic | Suspension |  |  |  |  | 2.4633e-07 | 300.5469 | 7.4034e-05
121522325 | E | LC | ETL.1350.POLE.WDPS | 44512136 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40871613 | 1943-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.013068 | 205.744 | 2.6887
121522655 | E | LC | ETL.1350.POLE.WDPS | 44552453 | TABLEMTN |  | 2021-06-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44551585 |  | 2-Pole Wood | TRP SUSP - Tramp Susp | [7 empty] | 0.011324 | 0.065152 | 0.00073781
121523985 | E | LC | ETL.1450.POLE.WDPS | 44553569 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553152 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0026947 | 31.7066 | 0.085441
121526049 | E | LC | ETL.8650.POLE.NWOD | 44420171 | FRESNO | FRESNO | 2021-06-12 |  | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44420171 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0020571 | 3210.4758 | 6.6042
121526923 | E | LC | ETL.1350.POLE.WOOD | 44552363 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44551533 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.055453 | 79.1851 | 4.391
121527107 | E | LC | ETL.6880.POLE.NWOD | 45121221 | LAKEVLLE | NORTH BAY | 2021-06-09 |  | ETL.6880 | FULTON-CALISTOGA | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45121221 | 2020-10-04 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-10-04 | Glass | Dead End | [5 empty] | 1770.0726
121527142 | E | LC | ETL.6660.POLE.NWOD | 45087059 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45087059 | 2021-03-04 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2021-03-04 | Glass | Dead End |  |  |  |  | 1.7016e-08 | 1591.9734 | 2.7089e-05
121532612 | E | LC | ETL.4550.TOWR | 40678174 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40678174 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 6.5976e-05 | 2901.2927 | 0.19142
121535916 | F | LC | ETL.6890.POLE.WOOD | 40750512 | LAKEVLLE | SONOMA | 2021-06-09 |  | ETL.6890 | FULTON-HOPLAND | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40750512 | 1948-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Ceramic | Other |  |  |  |  | 0.00017554 | 126.6897 | 0.02224
121536594 | F | LC | ETL.4680.TOWR | 40651565 | LAKEVLLE | SONOMA | 2021-06-09 |  | ETL.4680 | FULTON-IGNACIO #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40651565 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 3.2458e-05 | 665.4853
121536594 | F | LC | ETL.4680.TOWR | 40651565 | LAKEVLLE | SONOMA | 2021-06-09 |  | ETL.4680 | FULTON-IGNACIO #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40651565 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.2458e-05 | 665.4853
121536785 | F | LC | ETL.7990.POLE.WOOD | 40908960 | SACTO | SIERRA | 2021-06-09 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908960 |  | Single Wood Pole | T-1 - Tri Post | 2020-03-09 | Polymer | Post |  |  |  |  | 0.00013421 | 5662.8193
121536793 | F | LC | ETL.6640.POLE.NWOD | 44919755 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44919755 | 2020-03-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-03-11 | Glass | Dead End |  |  |  |  | 0.00040916 | 2107.8877
121538248 | E | LC | ETL.6861.POLE.WOOD | 40615077 | LAKEVLLE | HUMBOLDT | 2021-06-14 |  | ETL.6861 | KONOCTI-EAGLE ROCK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40615077 |  | Single Wood Pole | T1DE - Tri Post Dead End 115 | 2018-11-06 | Polymer | Dead End |  |  |  |  | 6.3947e-05 | 1518.7485 | 0.09712
121538819 | F | LC | ETL.6510.POLE.STPS | 44399415 | SACTO | SACRAMENTO | 2021-06-15 |  | ETL.6510 | COLGATE-SMARTVILLE #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44399412 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 2.6861e-08 | 237.8615
121552378 | E | LC | ETL.5970.TOWR | 40818888 | PISMOBCH | LOS PADRES | 2021-06-16 |  | ETL.5970 | DIABLO-MIDWAY #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40818888 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 1.067e-08 | 1091.4023 | 1.1645e-05
121561533 | E | LC | ETL.7780.POLE.WOOD | 44947092 | LAKEVLLE | SONOMA | 2021-06-18 |  | ETL.7780 | PHILO JCT-ELK | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44947092 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Non Ceramic | Suspension |  |  |  |  | 0.00018829 | 0.065148 | 1.2266e-05
121567907 | E | LC | ETL.2395.POLE.WOOD | 44551463 | TABLEMTN |  | 2021-06-15 |  | ETL.2395 | GRIZZLY TAP | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550851 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.032409 | 189.8861 | 6.1539
121591939 | E | LC | ETL.8350.POLE.NWOD | 44918805 | VICTOR | STOCKTON | 2021-06-22 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44918805 | 2020-03-03 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-03 | Polymer | Post |  |  |  |  | 6.2739e-07 | 1015.8607 | 0.00063734
121596419 | E | LC | ETL.1440.POLE.WDPS | 44180217 | SACTO | SIERRA | 2021-06-17 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44180214 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.010399 | 713.184 | 7.4162
121600991 | B | LC | ETL.1184.TOWR | 45098593 | LAKEVLLE | SONOMA | 2021-06-25 | 2021-07-29 | ETL.1184 | SMUD TAP | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45098593 |  | LATTICE STEEL TOWER | Unknown |  | Unknown | Unknown | [5 empty] | 1662.4275
121609456 | B | LC | ETL.6020.INSL | 40723669 | TABLEMTN | NORTH VALLEY | 2021-06-26 | 2021-08-31 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40680171 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension | [5 empty] | 666.2431
121609730 | E | LC | ETL.6520.POLE.WOOD | 40828234 | SACTO | SIERRA | 2021-06-16 |  | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40828234 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 0.083521 | 744.7016 | 62.1985
121624076 | E | LC | ETL.8250.INSL.CERA | 40913751 | VICTOR | STOCKTON | 2021-06-28 |  | ETL.8250 | CLAY-MARTEL | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40904145 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.021549 | 808.7196 | 17.4274
121630247 | E | LC | ETL.4440.INSL | 40788526 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758427 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 0.0014912 | 6600.5874 | 9.8427
121631340 | B | LC | ETL.5420.POLE.WDPS | 44559047 | TABLEMTN | NORTH VALLEY | 2021-06-26 | 2021-09-22 | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 952.427
121657024 | E | LC | ETL.6760.POLE.WOOD | 40598946 | SACTO | SIERRA | 2021-06-28 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40598946 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Dead End |  |  |  |  | 0.094471 | 901.7202 | 85.186
121657499 | F | LC | ETL.6750.POLE.STPS | 45142321 | TABLEMTN | NORTH VALLEY | 2021-07-02 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45142258 | 2020-02-10 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End
121678973 | F | LC | ETL.5140.POLE.STPS | 45146382 | SACTO | SIERRA | 2021-07-05 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45146249 | 2020-10-16 | 2-Pole Non Wood | 2PS - 2 Pole SUSP
121679120 | E | LC | ETL.9240.TOWR | 43249769 | PISMOBCH | LOS PADRES | 2021-07-07 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier3 | Tier 3 | Within Both | PEND | 43249769 |  | LATTICE STEEL TOWER | [9 empty] | 1475.0885
121679170 | E | LC | ETL.1440.POLE.WDPS | 40683598 | SACTO | SIERRA | 2021-07-02 | 2021-07-19 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL | [11 empty] | 0.006264
121684825 | B | LC | ETL.9240.TOWR | 43249494 | PISMOBCH | LOS PADRES | 2021-07-08 | 2021-07-27 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249494 |  | LATTICE STEEL TOWER | [9 empty] | 269.1183
121731924 | F | LC | ETL.6760.POLE.WOOD | 40693374 | SACTO | SACRAMENTO | 2021-07-12 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40693374 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | [5 empty] | 0.011109 | 253.1613
121732260 | F | LC | ETL.4393.POLE.NWOD | 44254473 | SACTO | SIERRA | 2021-06-12 |  | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44254473 | 2016-01-12 | Light Duty Steel Pole | Unknown | 2021-03-28 | Glass | Dead End |  |  |  |  | 4.6111e-05 | 721.4898
121744276 | E | LC | ETL.2390.POLE.WDPS | 44391106 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391105 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 6.19e-05 | 5127.0312 | 0.31737
121748671 | F | LC | ETL.1810.POLE.STPS | 45095889 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45095827 | 2020-12-04 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.1122e-09 | 0.065148 | 4.6334e-10
121758573 | B | LC | ETL.6280.POLE.WOOD | 40599679 | TABLEMTN | NORTH VALLEY | 2021-07-19 | 2021-10-11 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40599679 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 4.3922e-05 | 1739.9091
121767808 | E | LC | ETL.2390.POLE.WDPS | 44391021 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391020 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00014121 | 2751.947 | 0.38861
121781125 | E | LC | ETL.5140.POLE.STPS | 45146351 | SACTO | SIERRA | 2021-07-21 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45146224 | 2020-10-05 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End
121781661 | E | LC | ETL.1400.INSL.NCER | 40620397 | VICTOR | YOSEMITE | 2021-07-21 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40580177 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.008921
121781661 | E | LC | ETL.1400.INSL.NCER | 40620397 | VICTOR | YOSEMITE | 2021-07-21 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40580177 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.008921
121806947 | F | LC | ETL.8350.POLE.NWOD | 44918764 | VICTOR | STOCKTON | 2021-07-26 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44918764 | 2020-03-03 | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 8.0261e-08 | 964.8596
121809926 | F | LC | ETL.7550.POLE.WOOD | 40875186 | LAKEVLLE | HUMBOLDT | 2021-07-28 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40875186 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 6.1574e-05 | 110.7947 | 0.0068221
121822897 | F | LC | ETL.4040.POLE.STPS | 44551433 | TABLEMTN | NORTH VALLEY | 2021-07-30 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44550892 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.2627e-06 | 3987.1216
121830561 | B | LC | ETL.6280.POLE.WOOD | 40656543 | TABLEMTN | NORTH VALLEY | 2021-08-01 | 2021-10-06 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40656543 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 5.6472e-06 | 2630.0249
122059639 | E | LC | ETL.4780.INSL.CERA | 40844718 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129389 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.012248 | 886.3674 | 10.8559
118442078 | A | LC | ETL.7490.POLE.WDPS | 44743796 | EUREKA | HUMBOLDT | 2020-01-17 | 2020-04-14 | ETL.7490 | MAPLE CREEK-HOOPA | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL | [12 empty] | 0.065148
118572252 | E | LC | ETL.7640.POLE.WDPS | 44565533 | TABLEMTN | NORTH VALLEY | 2020-02-24 | 2021-02-11 | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 44564207 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.5603e-06 | 224.9154
118603403 | F | LC | ETL.2720.TOWR | 40581554 | CONCORD | DIABLO | 2020-03-04 |  | ETL.2720 | MORAGA-OAKLAND #1 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40581554 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.00036468 | 0.065158 | 2.3762e-05
118603403 | F | LC | ETL.2720.TOWR | 40581554 | CONCORD | DIABLO | 2020-03-04 |  | ETL.2720 | MORAGA-OAKLAND #1 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40581554 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | [5 empty] | 0.00036468 | 0.065158 | 2.3762e-05
118763172 | F | LC | ETL.1710.TOWR | 40605354 | MOSSLNDG | CENTRAL COAST | 2020-03-31 | 2020-04-09 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40605354 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-06 | Glass | Dead End |  |  |  |  | 6.9828e-08 | 0.065147
118763172 | F | LC | ETL.1710.TOWR | 40605354 | MOSSLNDG | CENTRAL COAST | 2020-03-31 | 2020-04-09 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40605354 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147
118764471 | E | LC | ETL.2740.TOWR | 40872973 | CONCORD | EAST BAY | 2020-04-01 | 2020-04-20 | ETL.2740 | MORAGA-OAKLAND #3 | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40872973 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1960-01-01 | Polymer | Suspension |  |  |  |  | 0.00011193 | 0.065147
118774533 | B | LC | ETL.6861.POLE.WOOD | 40809245 | LAKEVLLE | HUMBOLDT | 2020-04-03 | 2020-05-13 | ETL.6861 | KONOCTI-EAGLE ROCK | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809245 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2018-11-06 | Ceramic | Suspension |  |  |  |  | 0.00040641 | 6411.6025
118776217 | F | LC | ETL.5100.TOWR | 40870255 | MOSSLNDG | SAN JOSE | 2020-04-03 | 2020-04-20 | ETL.5100 | METCALF-MOSS LANDING #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40870255 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2005-01-01 | Non Ceramic | Suspension |  |  |  |  | 9.1477e-05 | 0.12841
118944195 | E | LC | ETL.6880.POLE.NWOD | 40825316 | LAKEVLLE | SONOMA | 2020-04-22 | 2021-05-18 | ETL.6880 | FULTON-CALISTOGA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
118947645 | E | LC | ETL.1680.TOWR | 40861322 | LAKEVLLE | SONOMA | 2020-04-24 | 2020-06-22 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40861322 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1978-01-01 | Porcelain | Dead End |  |  |  |  | 2.4207e-06 | 4639.9287
118947645 | E | LC | ETL.1680.TOWR | 40861322 | LAKEVLLE | SONOMA | 2020-04-24 | 2020-06-22 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40861322 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1978-01-01 | Porcelain | Other |  |  |  |  | 2.4207e-06 | 4639.9287
118951405 | E | LC | ETL.4770.INSL.CERA | 40842350 | LAKEVLLE | SONOMA | 2020-04-27 | 2021-05-19 | ETL.4770 | GEYSERS #17-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40814640 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 4.5919e-05 | 2758.967
118959203 | E | LC | ETL.1330.TOWR | 40860995 | LAKEVLLE | HUMBOLDT | 2020-04-27 | 2021-06-07 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860995 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2021-06-03 | Glass | Double Dead End |  |  |  |  | 5.4153e-05 | 1028.2683
118959203 | E | LC | ETL.1330.TOWR | 40860995 | LAKEVLLE | HUMBOLDT | 2020-04-27 | 2021-06-07 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860995 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2021-02-17 | Glass | Dead End |  |  |  |  | 5.4153e-05 | 1028.2683
119034728 | B | LC | ETL.1240.INSL.CERA | 44184983 | TABLEMTN | NORTH VALLEY | 2020-05-13 | 2020-06-08 | ETL.1240 | CASCADE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44184953 | 2014-07-24 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2014-07-24 | Porcelain | Suspension |  |  |  |  | 1.5895e-07
119034728 | B | LC | ETL.1240.INSL.CERA | 44184983 | TABLEMTN | NORTH VALLEY | 2020-05-13 | 2020-06-08 | ETL.1240 | CASCADE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44184953 | 2014-07-24 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2014-07-24 | Porcelain | Suspension |  |  |  |  | 1.5895e-07
119036551 | E | LC | ETL.6390.POLE.WOOD | 40667033 | LAKEVLLE | HUMBOLDT | 2020-05-14 | 2021-03-29 | ETL.6390 | CLEAR LAKE-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119036737 | F | LC | ETL.2060.POLE.WOOD | 40860776 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-04-07 | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40860776 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.16458 | 593.3324
119049797 | E | LC | ETL.4220.POLE.NWOD | 44388411 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-06-19 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44388411 | 2017-09-06 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2017-09-06 | Polymer | Post |  |  |  |  | 0.0003438 | 1819.3629
119054469 | F | LC | ETL.1730.POLE.WDPS | 44413369 | MOSSLNDG | CENTRAL COAST | 2020-05-11 | 2020-06-03 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Tier 3 | Within Both | COMP | 44413367 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.4632e-05 | 31.6948
119078250 | E | LC | ETL.7510.POLE.WOOD | 40769951 | LAKEVLLE | HUMBOLDT | 2020-05-26 | 2020-07-02 | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40769951 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 8.7956e-06 | 7063.4648
119082250 | E | LC | ETL.6760.POLE.WOOD | 40822654 | SACTO | SIERRA | 2020-05-28 | 2021-03-22 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822654 |  | Single Wood Pole | T-1 - Tri Post | 2020-05-26 | Polymer | Post |  |  |  |  | 0.022195 | 110.8102
119082457 | F | LC | ETL.6760.POLE.WOOD | 40873705 | SACTO | SIERRA | 2020-05-27 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40873705 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | [5 empty] | 0.10119 | 275.3937
119096610 | F | LC | ETL.1430.TOWR | 40576825 | SACTO | SIERRA | 2020-05-19 | 2021-04-07 | ETL.1430 | DRUM-RIO OSO #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119099930 | F | LC | ETL.5390.TOWR | 40870192 | TABLEMTN | NORTH VALLEY | 2020-05-19 |  | ETL.5390 | PIT #1-COTTONWOOD | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40870192 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.586e-06 | 1285.8232
119101537 | E | LC | ETL.6950.POLE.WOOD | 40908725 | SACTO | SIERRA | 2020-05-18 | 2021-10-12 | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908725 | 2013-10-17 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2013-10-17 | Non Ceramic | Dead End |  |  |  |  | 0.0022661 | 2361.6328 | 5.3518
119102393 | F | LC | ETL.5452.TOWR | 40761593 | CONCORD | DIABLO | 2020-05-12 |  | ETL.5452 | CONTRA COSTA-MORAGA #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40761593 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-01-01 | Ceramic | Suspension |  |  |  |  | 7.2734e-09 | 2103.6333 | 1.5301e-05
119103037 | F | LC | ETL.7380.POLE.WDPS | 44563003 | MOSSLNDG | CENTRAL COAST | 2020-05-29 |  | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44562377 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.83856 | 0.065148
119103181 | F | LC | ETL.3770.TOWR | 40581011 | CONCORD | EAST BAY | 2020-05-15 | 2021-04-19 | ETL.3770 | SOBRANTE-R #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581011 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1923-01-01 | Ceramic | Suspension |  |  |  |  | 2.7233e-05 | 221.5946
119116157 | E | LC | ETL.1112.POLE.NWOD | 44420230 | FRESNO | YOSEMITE | 2020-06-04 |  | ETL.1112 | INDIAN FLAT-YOSEMITE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44420230 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.00059495 | 4306.9175 | 2.5624
119117611 | F | LC | ETL.6470.POLE.WOOD | 40873660 | SACTO | SIERRA | 2020-06-01 | 2021-07-06 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40873660 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.19944 | 569.5315
119118694 | F | LC | ETL.1050.TOWR | 40816899 | FRESNO | FRESNO | 2020-05-26 | 2021-07-20 | ETL.1050 | BALCH-SANGER | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816899 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1923-01-01 | Porcelain | Suspension |  |  |  |  | 0.0012174 | 6854.0659
119143343 | F | LC | ETL.6490.POLE.WOOD | 40817317 | SACTO | SIERRA | 2020-06-02 |  | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40817317 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.034951 | 1336.7596
119146173 | E | LC | ETL.9090.POLE.WOOD | 40597837 | PISMOBCH | LOS PADRES | 2020-06-05 | 2021-03-10 | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Non-HFTD | Non-HFRA | COMP | 40597837 |  | Single Wood Pole | FIG4W - Wood X Arm | 1964-01-01 | Ceramic | Other |  |  |  |  | 0.0054189
119163061 | E | LC | ETL.1810.POLE.WDPS | 44322279 | EUREKA | HUMBOLDT | 2020-06-12 | 2021-05-10 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322278 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0001338
119189093 | E | LC | ETL.6310.POLE.WOOD | 40676955 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-08-19 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676955 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 9.0755e-06 | 6462.6191
119212917 | E | LC | ETL.8411.POLE.WDPS | 45021927 | LAKEVLLE | HUMBOLDT | 2020-06-25 | 2021-06-01 | ETL.8411 | GARCIA TAP | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40740720 | 1961-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.29742 | 94.9585
119293981 | F | LC | ETL.3500.TOWR | 40750193 | VICTOR | STOCKTON | 2020-07-01 | 2020-07-31 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40750193 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 2.6318e-05 | 1866.9476
119295028 | F | LC | ETL.7270.POLE.WOOD | 40906497 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906497 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0031954 | 996.8419
119302423 | E | LC | ETL.6760.POLE.WOOD | 40766648 | SACTO | SACRAMENTO | 2020-07-02 | 2021-03-11 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119304193 | E | LC | ETL.8060.POLE.WOOD | 40876711 | SACTO | SIERRA | 2020-07-02 | 2021-07-06 | ETL.8060 | SPAULDING-SUMMIT | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40876711 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0068715 | 696.1766
119304567 | F | LC | ETL.7030.POLE.WOOD | 40601690 | TABLEMTN | NORTH VALLEY | 2020-07-02 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40601690 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0057875 | 31.7022
119315439 | E | LC | ETL.7270.INSL.NCER | 40915754 | TABLEMTN |  | 2020-07-06 | 2021-09-01 | ETL.7270 | KESWICK-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906085 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0031707 | 933.5561
119316893 | E | LC | ETL.1110.POLE.WDPS | 44424468 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-08-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424467 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00077317 | 2837.7712
119328157 | F | LC | ETL.6300.POLE.WOOD | 44191043 | TABLEMTN | NORTH VALLEY | 2020-07-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44191043 |  | Single Wood Pole | TH - TriAngle Post 70 | [7 empty] | 8.5095e-05 | 0.065148
119328552 | E | LC | ETL.7270.POLE.WOOD | 40906490 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-08-07 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906490 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0020572 | 996.9431
119330483 | E | LC | ETL.6980.POLE.WOOD | 40808669 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-06-17 | ETL.6980 | FORT ROSS-GUALALA | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
119336596 | E | LC | ETL.1480.TOWR | 40653032 | LAKEVLLE | SACRAMENTO | 2020-07-09 |  | ETL.1480 | EAGLE ROCK-REDBUD | Vegetation | Overgrown | [Trim] | Tier3 | Tier 3 | Within Both | PEND | 40653032 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 0.0032821 | 1852.3262 | 6.0796
119337250 | E | LC | ETL.6710.POLE.WOOD | 40600106 | MOSSLNDG | CENTRAL COAST | 2020-07-09 |  | ETL.6710 | DEL MONTE-VIEJO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40600106 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.11756 | 0.065148 | 0.0076589
119350446 | F | LC | ETL.6280.POLE.NWOD | 44259059 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44259059 | 2020-07-16 | Light Duty Steel Pole | T2N | 2020-07-16 | Polymer | Post |  |  |  |  | 1.7956e-10 | 300.5749
119353563 | E | LC | ETL.7030.POLE.NWOD | 44686475 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44686475 | 2018-11-30 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-30 | Polymer | Post |  |  |  |  | 0.0029831 | 0.06515
119354522 | F | LC | ETL.6710.POLE.WOOD | 44379220 | MOSSLNDG | CENTRAL COAST | 2020-07-10 |  | ETL.6710 | DEL MONTE-VIEJO | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44379220 | 2016-08-24 | Single Wood Pole | T-1 - Tri Post | 2016-08-24 | Polymer | Post |  |  |  |  | 0.10652 | 0.065148 | 0.0069395
119354541 | E | LC | ETL.8480.POLE.WOOD | 40597525 | PISMOBCH | LOS PADRES | 2020-07-10 | 2021-04-05 | ETL.8480 | ATASCADERO-CAYUCOS | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40597525 | 1954-01-01 | Single Wood Pole | T-1 - Tri Post | 2019-07-14 | Polymer | Post |  |  |  |  | 7.8558e-05 | 3039.8909
119361934 | E | LC | ETL.5440.POLE.WDPS | 44558422 | TABLEMTN |  | 2020-07-01 | 2020-08-20 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119363380 | E | LC | ETL.6290.POLE.WOOD | 40769034 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-09-13 | ETL.6290 | CARIBOU-PLUMAS JCT | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40769034 | 1958-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2011-01-01 | Polymer | Post |  |  |  |  | 0.031033 | 0.066432
119363764 | F | LC | ETL.7030.POLE.WOOD | 40877474 | TABLEMTN | NORTH VALLEY | 2020-07-13 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40877474 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.024256 | 444.4778
119375088 | E | LC | ETL.8250.POLE.WOOD | 40821937 | VICTOR | STOCKTON | 2020-07-14 | 2021-08-12 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40821937 | 2007-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | Dead End |  |  |  |  | 2.9566e-06 | 5352.8145
119469564 | F | LC | ETL.7030.POLE.WOOD | 40599860 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40599860 |  | Single Wood Pole | T-1 - Tri Post | 2017-08-17 | Polymer | Post |  |  |  |  | 0.010785
119470063 | F | LC | ETL.7030.POLE.WOOD | 40827515 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40827515 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0066447
119488931 | F | LC | ETL.6950.POLE.WOOD | 40666247 | SACTO | SACRAMENTO | 2020-07-22 |  | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40666247 |  | Single Wood Pole | DCPOST - Double Circuit Post |  | Porcelain | [5 empty] | 0.00058057 | 5756.2148
119489823 | F | LC | ETL.1400.POLE.STPS | 44382142 | VICTOR | YOSEMITE | 2020-07-22 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44382141 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.8024e-05 | 79.1977
119492615 | E | LC | ETL.1370.INSL.CERA | 42574075 | PISMOBCH | LOS PADRES | 2020-07-23 | 2021-08-23 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119493061 | E | LC | ETL.1450.POLE.WDPS | 44557532 | SACTO | SACRAMENTO | 2020-07-22 | 2021-04-27 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44554010 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00068086 | 427.2245
119494733 | F | LC | ETL.1110.POLE.WDPS | 44424070 | TABLEMTN | HUMBOLDT | 2020-07-22 | 2021-04-13 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424069 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0036414 | 332.3156
119498783 | E | LC | ETL.6520.POLE.WOOD | 40817201 | SACTO | SIERRA | 2020-07-23 | 2021-06-23 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817201 |  | Single Wood Pole | TRP SUSP - Tramp Susp |  | Ceramic | [5 empty] | 0.019475 | 1919.2795
119534247 | E | LC | ETL.7490.POLE.WOOD | 40586865 | EUREKA | HUMBOLDT | 2020-07-30 | 2021-08-17 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40586865 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.4335 | 189.8608
119576432 | F | LC | ETL.6880.POLE.WOOD | 40861386 | LAKEVLLE | SONOMA | 2020-08-07 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40861386 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0030996 | 1403.447
119592598 | F | LC | ETL.8350.POLE.WOOD | 40803742 | VICTOR | STOCKTON | 2020-08-07 | 2021-09-23 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40803742 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2020-05-11 | Glass | Suspension |  |  |  |  | 0.015866 | 537.8945
119599415 | E | LC | ETL.4780.INSL.CERA | 40676810 | LAKEVLLE | SONOMA | 2020-08-11 | 2021-05-28 | ETL.4780 | GEYSERS #9-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 41129185 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2020-04-16 | Glass | Dead End |  |  |  |  | 0.015336 | 3637.895
119599415 | E | LC | ETL.4780.INSL.CERA | 40676810 | LAKEVLLE | SONOMA | 2020-08-11 | 2021-05-28 | ETL.4780 | GEYSERS #9-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 41129185 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1973-01-01 | Porcelain | Dead End |  |  |  |  | 0.015336 | 3637.895
119600610 | E | LC | ETL.7930.POLE.WOOD | 40594191 | MOSSLNDG | CENTRAL COAST | 2020-08-11 |  | ETL.7930 | SALINAS-LAURELES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40594191 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.002186 | 0.066432 | 0.00014522
119604140 | F | LC | ETL.8650.TOWR | 40806458 | FRESNO | YOSEMITE | 2020-08-11 |  | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40806458 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-11-18 | Glass | Dead End |  |  |  |  | 0.013228 | 15.88
119638278 | F | LC | ETL.8365.POLE.NWOD | 40906663 | EUREKA | HUMBOLDT | 2020-08-19 | 2021-02-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40906663 | 2011-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0028175
119649552 | A | LC | ETL.7590.POLE.WDPS | 44401929 | MOSSLNDG | CENTRAL COAST | 2020-08-21 | 2020-08-26 | ETL.7590 | MONTA VISTA-BURNS | Emergency-Wood | Other | [Replace] | Tier3 |  |  | DLFL
119669761 | F | LC | ETL.8365.POLE.WOOD | 40600475 | EUREKA | HUMBOLDT | 2020-08-25 | 2021-05-03 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40600475 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-04-28 | Glass | Dead End |  |  |  |  | 0.0030446 | 4895.8984
119721014 | F | LC | ETL.9100.POLE.WOOD | 44191413 | PISMOBCH | LOS PADRES | 2020-08-04 | 2021-01-20 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL | [11 empty] | 0.0028246 | 1613.8738
119721510 | F | LC | ETL.1330.TOWR | 40584915 | LAKEVLLE | HUMBOLDT | 2020-07-29 | 2021-04-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40584915 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 4.1625e-06 | 5715.6968
119721510 | F | LC | ETL.1330.TOWR | 40584915 | LAKEVLLE | HUMBOLDT | 2020-07-29 | 2021-04-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40584915 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 4.1625e-06 | 5715.6968
119722800 | B | LC | ETL.7270.POLE.WOOD | 40576143 | TABLEMTN | NORTH VALLEY | 2020-08-06 | 2020-09-22 | ETL.7270 | KESWICK-TRINITY | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40576143 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.045322 | 1918.4999
119722993 | F | LC | ETL.1400.POLE.STPS | 44382670 | VICTOR | YOSEMITE | 2020-08-07 | 2021-04-14 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44382669 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.3844e-05 | 47.5295
119772558 | F | LC | ETL.7270.POLE.WOOD | 42621502 | TABLEMTN | NORTH VALLEY | 2020-08-22 | 2021-01-29 | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42621502 |  | Single Wood Pole | SVDE - Single Vertical Dead End |  | Polymer | [5 empty] | 0.003292 | 2409.1135
119782601 | F | LC | ETL.6310.POLE.WOOD | 40600705 | TABLEMTN | NORTH VALLEY | 2020-09-14 | 2021-02-01 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40600705 |  | Single Wood Pole | T2N | 2020-11-05 | Polymer | Post |  |  |  |  | 3.1302e-05 | 7306.2056
119783606 | E | LC | ETL.6220.INSL.CERA | 44232145 | EUREKA | HUMBOLDT | 2020-09-14 | 2021-11-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119789428 | F | LC | ETL.5090.TOWR | 40587121 | MOSSLNDG | SAN JOSE | 2020-07-28 | 2021-01-06 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587121 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 3.8791e-05 | 1824.7068
119790355 | F | LC | ETL.8410.POLE.WOOD | 40876116 | LAKEVLLE | HUMBOLDT | 2020-07-30 | 2021-06-03 | ETL.8410 | ELK-GUALALA | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876116 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Porcelain | Dead End |  |  |  |  | 0.17098 | 71.2352
119808192 | E | LC | ETL.6240.POLE.WOOD | 40768008 | MOSSLNDG | CENTRAL COAST | 2020-09-24 | 2020-09-25 | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119810008 | F | LC | ETL.8365.POLE.NWOD | 44639156 | EUREKA | HUMBOLDT | 2020-08-14 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44639156 | 2018-07-01 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2018-07-11 | Polymer | Suspension |  |  |  |  | 0.00020771
119818874 | F | LC | ETL.6980.POLE.WOOD | 40587355 | LAKEVLLE | SONOMA | 2020-09-01 |  | ETL.6980 | FORT ROSS-GUALALA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40587355 | 1985-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1953-01-01 | Polymer | Dead End |  |  |  |  | 0.24994 | 63.3539
119835236 | F | LC | ETL.6480.POLE.NWOD | 44695512 | SACTO | NORTH VALLEY | 2020-09-08 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44695512 | 2018-12-10 | Light Duty Steel Pole | T2N | 2018-12-10 | Polymer | Post |  |  |  |  | 0.0093446 | 284.7983
119837668 | B | LC | ETL.6880.POLE.WOOD | 40585444 | LAKEVLLE | NORTH BAY | 2020-09-30 | 2020-10-09 | ETL.6880 | FULTON-CALISTOGA | Emergency | Fire | [Replace] | Tier3 |  |  | DLFL
119845768 | F | LC | ETL.6330.POLE.NWOD | 44673326 | TABLEMTN | NORTH VALLEY | 2020-09-16 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44673326 | 2018-11-14 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-14 | Polymer | Post |  |  |  |  | 0.00011049 | 2534.72
119897664 | F | LC | ETL.6720.POLE.WOOD | 40616045 | TABLEMTN | NORTH VALLEY | 2020-10-08 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40616045 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00076239 | 0.065151
119968119 | A | LC | ETL.7140.POLE.WOOD | 40576063 | LAKEVLLE | SONOMA | 2020-10-31 | 2020-11-05 | ETL.7140 | IGNACIO-BOLINAS #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40576063 |  | Single Wood Pole | DV-DE - Double Vertical Dead End | 2020-11-04 | Glass | Suspension |  |  |  |  | 0.014689 | 31.7138
119973710 | F | LC | ETL.8580.POLE.WOOD | 40748091 | FRESNO | FRESNO | 2020-10-29 | 2021-02-09 | ETL.8580 | COALINGA #1-SAN MIGUEL | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40748091 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Unknown |  |  |  |  | 0.00037732
119996618 | A | LC | ETL.2270.INSL | 40623969 | CONCORD | DIABLO | 2020-11-07 | 2020-11-14 | ETL.2270 | MARTINEZ-SOBRANTE | Emergency | Storm Related | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40597404 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1941-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.2316e-07 | 31.9508
120130612 | E | LC | ETL.1110.INSL | 40799052 | EUREKA | HUMBOLDT | 2020-12-04 | 2021-08-02 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768277 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.5487e-05 | 0.065152
120160563 | F | LC | ETL.8650.TOWR | 40606165 | FRESNO | FRESNO | 2020-12-09 | 2021-09-01 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40606165 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0051682 | 4649.6255
120575791 | E | LC | ETL.4770.INSL.CERA | 40636814 | LAKEVLLE |  | 2021-02-25 |  | ETL.4770 | GEYSERS #17-FULTON | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40605188 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | [5 empty] | 5.8043e-07 | 2581.509 | 0.0014984
120592074 | E | LC | ETL.8350.POLE.WOOD | 40824062 | VICTOR | STOCKTON | 2020-04-01 | 2021-07-06 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120647810 | F | LC | ETL.2540.POLE.WOOD | 40818691 | MOSSLNDG | SAN JOSE | 2021-03-16 |  | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40818691 | 1952-01-01 | Single Wood Pole | T-1 - Tri Post | 1952-01-01 | Polymer | Suspension |  |  |  |  | 0.003923 | 4000.2325
120660376 | F | LC | ETL.2395.POLE.WOOD | 44550845 | TABLEMTN | NORTH VALLEY | 2021-03-18 | 2021-07-19 | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44550845 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00083335 | 300.6129
120672266 | E | LC | ETL.4316.INSL.CERA | 40682621 | TABLEMTN | NORTH VALLEY | 2021-03-22 | 2021-08-09 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
120683702 | F | LC | ETL.5100.TOWR | 40811017 | MOSSLNDG | SAN JOSE | 2021-03-23 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40811017 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2005-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.6079e-05 | 996.8166 | 0.016028
120686462 | E | LC | ETL.4570.INSL | 40893730 | TABLEMTN | NORTH VALLEY | 2021-03-24 |  | ETL.4570 | COTTONWOOD-LOGAN CREEK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40869181 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.6922e-05 | 4215.3687 | 0.11349
120695160 | B | LC | ETL.5790.INSL.CERA | 40885785 | VICTOR | STOCKTON | 2021-03-24 | 2021-05-17 | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40863343 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 5.6459e-06 | 822.6555
120695342 | B | LC | ETL.3830.INSL | 40786291 | VICTOR | STOCKTON | 2021-03-25 | 2021-05-26 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756403 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.588e-07 | 158.4159
120695834 | F | LC | ETL.3820.TOWR | 40870967 | VICTOR | STOCKTON | 2021-03-25 | 2021-10-05 | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870967 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 8.8154e-07 | 4005.7028
120696895 | E | LC | ETL.6320.POLE.WOOD | 40874516 | TABLEMTN | NORTH VALLEY | 2021-03-26 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40874516 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0092027 | 2301.5235 | 21.1802
120700741 | A | LC | ETL.3820.TOWR | 40856503 | VICTOR | STOCKTON | 2021-03-27 | 2021-03-27 | ETL.3820 | STANISLAUS-MANTECA #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40856503 | 1910-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1989-01-01 | Glass | Dead End |  |  |  |  | 0.000102 | 2454.5776
120704841 | E | LC | ETL.1810.INSL.CERA | 40720041 | EUREKA | HUMBOLDT | 2021-03-27 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Damper-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44322518 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0012862
120704841 | E | LC | ETL.1810.INSL.CERA | 40720041 | EUREKA | HUMBOLDT | 2021-03-27 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Damper-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44322518 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0012862
120708819 | F | LC | ETL.3830.TOWR | 40642779 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40642779 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 6.5152e-07 | 5033.749 | 0.0032796
120711978 | B | LC | ETL.6760.POLE.WOOD | 40598937 | SACTO | SACRAMENTO | 2021-03-30 | 2021-07-01 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40598937 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0039099 | 63.3392
120719020 | E | LC | ETL.5960.TOWR | 40658790 | PISMOBCH | LOS PADRES | 2021-03-31 |  | ETL.5960 | DIABLO-GATES #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40658790 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 1.4497e-05 | 1550.6904 | 0.022481
120719620 | F | LC | ETL.2900.TOWR | 40811070 | MOSSLNDG | CENTRAL COAST | 2021-03-31 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40811070 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Polymer | Suspension |  |  |  |  | 0.0040595 | 1013.5428 | 4.1145
120719620 | F | LC | ETL.2900.TOWR | 40811070 | MOSSLNDG | CENTRAL COAST | 2021-03-31 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40811070 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0040595 | 1013.5428 | 4.1145
120737322 | E | LC | ETL.7390.POLE.WOOD | 40860899 | LAKEVLLE | SONOMA | 2021-04-02 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40860899 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.59678
120743040 | E | LC | ETL.4000.POLE.WOOD | 40912754 | VICTOR | YOSEMITE | 2021-04-01 | 2021-10-12 | ETL.4000 | TESLA-SALADO-MANTECA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40912754 | 1925-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1925-01-01 | Porcelain | Suspension |  |  |  |  | 0.0079644 | 1824.6388 | 14.5321
120758523 | E | LC | ETL.1350.POLE.STPS | 44273548 | TABLEMTN | NORTH VALLEY | 2021-04-07 | 2021-06-30 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44273547 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 6.234e-05 | 15.8866
120770966 | E | LC | ETL.8250.POLE.WOOD | 40609833 | VICTOR | STOCKTON | 2021-04-09 | 2021-08-19 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 1665.905
120771578 | E | LC | ETL.8250.POLE.WOOD | 43250585 | VICTOR | STOCKTON | 2021-04-09 | 2021-08-18 | ETL.8250 | CLAY-MARTEL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 43250585 | 2007-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 4.9386e-06 | 5352.8145
120774035 | F | LC | ETL.8250.POLE.WOOD | 40908831 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40908831 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0057346 | 1759.9811
120799530 | B | LC | ETL.3840.INSL.NCER | 44951994 | VICTOR | STOCKTON | 2021-04-12 | 2021-05-24 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120807442 | E | LC | ETL.5970.INSL.NCER | 45009333 | PISMOBCH | LOS PADRES | 2021-04-13 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40818967 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-09-24 | Glass Silicone Coated | Suspension |  |  |  |  | 8.1449e-10 | 2296.8596 | 1.8708e-06
120810833 | B | LC | ETL.8365.POLE.WOOD | 40750533 | EUREKA | HUMBOLDT | 2021-04-12 | 2021-04-30 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750533 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.0058435 | 553.966
120812313 | E | LC | ETL.5300.INSL | 40793121 | PISMOBCH | LOS PADRES | 2021-04-14 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40762340 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 7.3545e-07 | 652.484 | 0.00047987
120815778 | F | LC | ETL.1400.POLE.STPS | 44418045 | VICTOR | YOSEMITE | 2021-04-14 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44418043 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.8193e-06 | 31.7081
120819438 | B | LC | ETL.4680.TOWR | 40811136 | LAKEVLLE | SONOMA | 2021-04-15 | 2021-05-04 | ETL.4680 | FULTON-IGNACIO #1 | Other | Customer Issue | [Access Issue] | Tier3 | Tier 3 | Within Both | COMP | 40811136 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.034e-05 | 110.894
120820366 | B | LC | ETL.2750.INSL.NCER | 40671324 | CONCORD | DIABLO | 2021-04-14 | 2021-04-27 | ETL.2750 | MORAGA-OAKLAND #4 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40644201 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 0.028775 | 0.065152
120822773 | F | LC | ETL.1073.POLE.STPS | 44384831 | VICTOR | STOCKTON | 2021-04-15 | 2021-06-10 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44384830 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.4669e-05 | 23.7973
120827201 | B | LC | ETL.4316.INSL.CERA | 40841316 | TABLEMTN | NORTH VALLEY | 2021-04-15 | 2021-04-27 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40815553 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Suspension |  |  |  |  | 0.044083 | 4386.7925
120829886 | E | LC | ETL.8060.INSL.CERA | 40855938 | SACTO | SACRAMENTO | 2021-04-16 | 2021-06-08 | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
120857091 | F | LC | ETL.5780.TOWR | 40659002 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.5780 | TIGER CREEK-ELECTRA | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40659002 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.0194e-06 | 237.591
120862476 | E | LC | ETL.1820.POLE.WDPS | 44560514 | EUREKA | HUMBOLDT | 2021-04-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Vegetation | Overgrown | [Remove] | Tier2 |  |  | PEND
120875668 | F | LC | ETL.1820.POLE.STPS | 44395175 | EUREKA | HUMBOLDT | 2021-04-23 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395173 | 2017-10-04 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.051848 | 94.9585
120875896 | E | LC | ETL.6470.POLE.WOOD | 40693201 | SACTO | SIERRA | 2021-04-23 | 2021-08-12 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693201 |  | Single Wood Pole | T2N | 2021-07-19 | Polymer | Post |  |  |  |  | 0.0031705 | 680.261
120880565 | F | LC | ETL.5790.TOWR | 40811207 | VICTOR | STOCKTON | 2021-04-24 |  | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40811207 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 7.8084e-06 | 63.3392
120886588 | E | LC | ETL.1810.POLE.WDPS | 44322579 | EUREKA | HUMBOLDT | 2021-04-26 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44322578 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0043695 | 0.066432 | 0.00029027
120914444 | E | LC | ETL.6890.POLE.WOOD | 40808481 | LAKEVLLE | SONOMA | 2021-04-30 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40808481 | 1988-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.00064953 | 4165.6978 | 2.7057
120932504 | F | LC | ETL.4920.TOWR | 40817207 | LAKEVLLE | EAST BAY | 2021-04-13 |  | ETL.4920 | IGNACIO-SOBRANTE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40817207 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.0011183 | 0.066432
120995313 | F | LC | ETL.1810.POLE.WDPS | 44322632 | EUREKA | HUMBOLDT | 2021-05-08 | 2021-06-02 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44322631 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0020141 | 63.3274
121190962 | E | LC | ETL.8250.POLE.WOOD | 40908845 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40908845 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0061726 | 1727.0282 | 10.6603
121191945 | E | LC | ETL.5140.INSL | 40796134 | SACTO | SIERRA | 2021-04-01 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40765402 | 1965-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.0516e-05 | 2949.7161 | 0.060517
121340568 | E | LC | ETL.1820.POLE.WDPS | 44562919 | EUREKA | HUMBOLDT | 2021-05-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562477 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.088665 | 142.4119 | 12.627
121341467 | F | LC | ETL.5330.TOWR | 40863246 | MOSSLNDG | CENTRAL COAST | 2021-04-22 | 2021-06-07 | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40863246 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 4.9323e-07 | 48.0031
121341467 | F | LC | ETL.5330.TOWR | 40863246 | MOSSLNDG | CENTRAL COAST | 2021-04-22 | 2021-06-07 | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40863246 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 4.9323e-07 | 48.0031
121359261 | F | LC | ETL.3210.TOWR | 40870592 | SACTO | NORTH VALLEY | 2021-04-21 |  | ETL.3210 | PALERMO-NICOLAUS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40870592 | 1962-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | Suspension |  |  |  |  | 8.078e-08 | 4520.0254
121359261 | F | LC | ETL.3210.TOWR | 40870592 | SACTO | NORTH VALLEY | 2021-04-21 |  | ETL.3210 | PALERMO-NICOLAUS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40870592 | 1962-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-05-23 | Ceramic | Suspension |  |  |  |  | 8.078e-08 | 4520.0254
121367361 | F | LC | ETL.1250.POLE.WOOD | 40748520 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40748520 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 8.2454e-05 | 6552.9849
121370946 | E | LC | ETL.5070.TOWR | 40651192 | FRESNO | YOSEMITE | 2021-05-04 |  | ETL.5070 | QUINTO SW STA-WESTLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40651192 | 1947-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1947-01-01 | Ceramic | Suspension |  |  |  |  | 1.9213e-06 | 1834.1865 | 0.0035241
121371265 | E | LC | ETL.1820.POLE.NWOD | 45009257 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45009257 | 2020-11-13 | Light Duty Steel Pole | DDE - Double Dead End | 2020-11-13 | Glass | Dead End |  |  |  |  | 0.001685 | 205.7277 | 0.34666
121379629 | F | LC | ETL.7990.POLE.WOOD | 44150264 | SACTO | SACRAMENTO | 2021-05-20 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44150264 | 2014-06-05 | Single Wood Pole | TH - TriAngle Post 70 | 2014-06-05 | Polymer | Post |  |  |  |  | 8.2118e-06 | 2552.4258
121379790 | B | LC | ETL.4440.POLE.NWOD | 44191954 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-30 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191954 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 0.00075924 | 4683.9302
121379905 | F | LC | ETL.8350.POLE.NWOD | 44885860 | VICTOR | STOCKTON | 2021-05-08 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44885860 | 2019-10-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-10-16 | Polymer | Dead End |  |  |  |  | 2.962e-06 | 2503.6165
121380364 | B | LC | ETL.4440.TOWR | 40757709 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-24 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40757709 | 1968-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1968-01-01 | Porcelain | Dead End |  |  |  |  | 3.3244e-07 | 5260.656
121387843 | E | LC | ETL.8250.POLE.WOOD | 40908885 | VICTOR | STOCKTON | 2021-05-21 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40908885 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2019-07-23 | Polymer | Post |  |  |  |  | 0.00041104 | 2108.3171 | 0.86661
121391807 | E | LC | ETL.1470.INSL.CERA | 40676855 | LAKEVLLE | HUMBOLDT | 2021-05-13 |  | ETL.1470 | EAGLE ROCK-CORTINA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40648890 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1978-01-01 | Glass | Dead End |  |  |  |  | 0.0081755 | 4728.469 | 38.6577
121391927 | F | LC | ETL.8060.POLE.WOOD | 40828179 | SACTO | SIERRA | 2021-05-17 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40828179 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.085124 | 221.6944
121392242 | F | LC | ETL.1480.TOWR | 40819850 | LAKEVLLE | HUMBOLDT | 2021-05-15 |  | ETL.1480 | EAGLE ROCK-REDBUD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40819850 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Porcelain | Suspension |  |  |  |  | 0.0032017 | 2358.4949 | 7.5513
121392242 | F | LC | ETL.1480.TOWR | 40819850 | LAKEVLLE | HUMBOLDT | 2021-05-15 |  | ETL.1480 | EAGLE ROCK-REDBUD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40819850 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 0.0032017 | 2358.4949 | 7.5513
121397615 | F | LC | ETL.8060.POLE.NWOD | 44349499 | SACTO | SIERRA | 2021-05-18 |  | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44349499 | 2018-09-06 | Light Duty Steel Pole | T2N | 2018-09-06 | Polymer | Post |  |  |  |  | 0.00056628 | 395.7096
121402987 | E | LC | ETL.7300.POLE.WOOD | 40759097 | TABLEMTN | NORTH VALLEY | 2021-05-19 |  | ETL.7300 | KILARC-DESCHUTES | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40759097 |  | Single Wood Pole | T-1 - Tri Post | 2018-06-03 | Polymer | Post |  |  |  |  | 0.0057101 | 1439.4246 | 8.2193
121405651 | E | LC | ETL.1650.INSL.NCER | 44398457 | LAKEVLLE | SONOMA | 2021-05-21 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44398435 | 2018-09-28 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-09-23 | Polymer | Dead End |  |  |  |  | 9.821e-09 | 4055.4705 | 3.9829e-05
121408569 | E | LC | ETL.7290.POLE.WOOD | 40657254 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40657254 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.022384 | 747.6403 | 16.7349
121420192 | F | LC | ETL.4392.TOWR | 41129328 | LAKEVLLE | SONOMA | 2021-05-26 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41129328 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 3.2516e-06 | 2220.2603 | 0.0072194
121420192 | F | LC | ETL.4392.TOWR | 41129328 | LAKEVLLE | SONOMA | 2021-05-26 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41129328 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 3.2516e-06 | 2220.2603 | 0.0072194
121422409 | E | LC | ETL.7000.POLE.WOOD | 40656649 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40656649 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00020964 | 0.065148 | 1.3657e-05
121427969 | E | LC | ETL.4220.POLE.WDPS | 44512165 | TABLEMTN |  | 2021-05-25 |  | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40809483 | 1962-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.15558 | 395.6659 | 61.5568
121428452 | E | LC | ETL.1400.POLE.STPS | 44379640 | VICTOR | YOSEMITE | 2021-05-25 |  | ETL.1400 | DONNELLS-MI-WUK | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44379638 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.9197e-05 | 2626.426 | 0.18174
121431223 | B | LC | ETL.1820.INSL.CERA | 40672596 | EUREKA | HUMBOLDT | 2021-05-28 | 2021-08-17 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121431261 | E | LC | ETL.5140.POLE.WDPS | 44557761 | SACTO | SACRAMENTO | 2021-05-29 | 2021-11-17 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44554048 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0026989 | 63.3518 | 0.17098
121435277 | F | LC | ETL.1350.TOWR | 40650383 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.1350 | CRAG VIEW-CASCADE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40650383 | 1944-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0094278 | 0.066431 | 0.0006263
121482819 | F | LC | ETL.6230.POLE.WOOD | 40755347 | MOSSLNDG | CENTRAL COAST | 2021-05-29 | 2021-09-23 | ETL.6230 | BURNS-LONE STAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40755347 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 0.1316 | 190.0709
121484125 | E | LC | ETL.6980.POLE.WOOD | 40750362 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.6980 | FORT ROSS-GUALALA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40750362 | 1986-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.42143 | 0.066303 | 0.027942
121484892 | E | LC | ETL.6980.POLE.WOOD | 40769863 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.6980 | FORT ROSS-GUALALA | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40769863 | 1953-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.88806 | 15.88 | 14.1024
121490855 | F | LC | ETL.8060.TOWR | 40618244 | SACTO | SACRAMENTO | 2021-06-08 | 2021-10-18 | ETL.8060 | SPAULDING-SUMMIT | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40618244 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Polymer | [5 empty] | 0.35936 | 1123.6396
121492953 | E | LC | ETL.7550.POLE.WOOD | 40750933 | LAKEVLLE | HUMBOLDT | 2021-06-08 | 2021-06-17 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40750933 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0002251 | 1631.1429
121500159 | F | LC | ETL.8350.POLE.WOOD | 40768199 | VICTOR | STOCKTON | 2021-06-03 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40768199 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-05-06 | Glass | Dead End |  |  |  |  | 0.0024211 | 95.0395 | 0.2301
121512527 | F | LC | ETL.1600.TOWR | 40761989 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Road | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40761989 | 1955-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1946-01-01 | Polymer | Suspension |  |  |  |  | 1.7861e-05 | 313.8482
121516113 | E | LC | ETL.4040.POLE.STPS | 44784268 | TABLEMTN | NORTH VALLEY | 2021-06-04 |  | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44784124 | 2019-07-14 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00021446 | 5212.1279 | 1.1178
121516625 | F | LC | ETL.4221.POLE.WDPS | 44561282 | TABLEMTN |  | 2021-06-04 |  | ETL.4221 | SLY CREEK TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44559139 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00044292 | 110.7793 | 0.049066
121519009 | F | LC | ETL.7140.POLE.WOOD | 40668081 | LAKEVLLE | NORTH BAY | 2021-06-07 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40668081 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0099688 | 1284.3926 | 12.8039
121524201 | E | LC | ETL.5630.INSL | 40780812 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5630 | ROCK CREEK-POE | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40751804 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 3.449e-06 | 4207.2017 | 0.014511
121525023 | E | LC | ETL.1440.POLE.WDPS | 44987046 | SACTO | SACRAMENTO | 2021-06-12 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42572739 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0083443 | 3765.6233 | 31.4214
121532012 | F | LC | ETL.1350.POLE.STPS | 44409332 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44409331 | 2017-10-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.1089e-05 | 411.4229
121536000 | E | LC | ETL.6360.POLE.WDPS | 44560613 | CONCORD | DIABLO | 2021-06-14 |  | ETL.6360 | CHRISTIE-FRANKLIN #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560144 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00019741 | 127.6204 | 0.025193
121536155 | F | LC | ETL.4440.TOWR | 40871546 | TABLEMTN | NORTH VALLEY | 2021-06-10 | 2021-10-11 | ETL.4440 | CARIBOU-TABLE MTN | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40871546 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 0.00019014 | 4401.4888
121536156 | E | LC | ETL.1600.INSL | 40713505 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40661937 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.7005e-07 | 2203.4587 | 0.0003747
121540156 | E | LC | ETL.4440.TOWR | 40595027 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4440 | CARIBOU-TABLE MTN | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40595027 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 0.0002025 | 5999.3906 | 1.2149
121543887 | E | LC | ETL.5390.TOWR | 40868148 | TABLEMTN | NORTH VALLEY | 2021-06-10 | 2021-08-05 | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40868148 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.9899e-08 | 4002.8656
121550729 | F | LC | ETL.5400.TOWR | 41184143 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5400 | PIT #3-PIT #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41184143 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Double Dead End |  |  |  |  | 0.015022 | 4131.7891
121554848 | F | LC | ETL.7640.POLE.STPS | 45158738 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45158715 | 2021-09-26 | 3-Pole Non Wood | DDE - Double Dead End
121557237 | E | LC | ETL.5630.INSL.CERA | 40899229 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5630 | ROCK CREEK-POE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40873466 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1950-01-01 | Ceramic | Dead End |  |  |  |  | 1.772e-05 | 857.7261 | 0.015199
121560446 | F | LC | ETL.7550.POLE.WOOD | 40600351 | LAKEVLLE | HUMBOLDT | 2021-06-17 | 2021-10-04 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40600351 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 1.3404e-05 | 15.8807
121564073 | F | LC | ETL.6500.POLE.WDPS | 44399061 | SACTO | SACRAMENTO | 2021-06-18 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44399060 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00025586 | 237.8615
121587381 | B | LC | ETL.4040.INSL.CERA | 44646957 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-08-11 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44646866 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2018-08-17 | Ceramic | Suspension |  |  |  |  | 0.00034786
121587381 | B | LC | ETL.4040.INSL.CERA | 44646957 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-08-11 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44646866 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2018-08-17 | Ceramic | Suspension |  |  |  |  | 0.00034786
121596348 | E | LC | ETL.5960.TOWR | 40765373 | PISMOBCH | LOS PADRES | 2021-06-24 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40765373 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-11-01 | Glass | Suspension |  |  |  |  | 1.817e-07 | 711.7325 | 0.00012933
121607609 | F | LC | ETL.4393.POLE.NWOD | 44767005 | SACTO | SIERRA | 2021-06-15 |  | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44767005 | 2019-04-22 | Light Duty Steel Pole | DE - Dead End | 2019-04-22 | Glass | Dead End |  |  |  |  | 1.0588e-05 | 822.7424
121609301 | E | LC | ETL.6500.POLE.WOOD | 40866224 | SACTO | NORTH VALLEY | 2021-06-22 |  | ETL.6500 | COLGATE-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40866224 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00076687 | 2473.1323 | 1.8966
121609551 | F | LC | ETL.1070.POLE.WOOD | 40681772 | VICTOR | STOCKTON | 2021-06-22 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40681772 | 1998-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1998-01-01 | Polymer | Post |  |  |  |  | 1.114e-05 | 2504.1895
121633552 | E | LC | ETL.7000.POLE.WOOD | 40667917 | TABLEMTN | NORTH VALLEY | 2021-06-24 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40667917 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0020132 | 47.5141 | 0.095654
121634166 | E | LC | ETL.6720.POLE.STPS | 44920567 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44920559 | 2020-05-31 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.9889e-08 | 443.0373 | 1.3242e-05
121644659 | E | LC | ETL.4396.POLE.STPS | 44382921 | TABLEMTN | NORTH VALLEY | 2021-06-28 |  | ETL.4396 | PARADISE-BUTTE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44382918 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.10965 | 1585.8691 | 173.8929
121653176 | E | LC | ETL.6020.TOWR | 40862529 | TABLEMTN | NORTH VALLEY | 2021-06-30 |  | ETL.6020 | MALIN-ROUND MTN #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40862529 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 3.8313e-06 | 275.4242 | 0.0010552
121658657 | F | LC | ETL.6890.POLE.WOOD | 40816675 | LAKEVLLE | SONOMA | 2021-06-01 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40816675 | 1967-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00041413 | 1836.4569
121664785 | F | LC | ETL.6852.POLE.WOOD | 40650066 | LAKEVLLE | HUMBOLDT | 2021-07-05 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40650066 | 2011-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | Pin |  |  |  |  | 0.1611 | 4734.4888 | 762.7194
121668175 | B | LC | ETL.1420.INSL.CERA | 40833397 | SACTO | SACRAMENTO | 2021-07-06 | 2021-08-10 | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121676078 | B | LC | ETL.9240.TOWR | 43249490 | PISMOBCH | LOS PADRES | 2021-07-07 | 2021-07-27 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249490 |  | LATTICE STEEL TOWER | [9 empty] | 4846.4956
121705029 | B | LC | ETL.1810.POLE.WOOD | 43250075 | EUREKA | HUMBOLDT | 2021-07-09 | 2021-08-12 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 43250075 | 2011-01-01 | Single Wood Pole | SVDE - Single Vertical Dead End |  | Porcelain | [5 empty] | 7.175e-07 | 221.5566
121705246 | F | LC | ETL.8060.POLE.WOOD | 40861956 | SACTO | SIERRA | 2021-07-07 |  | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40861956 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.024462 | 2826.3738
121717639 | F | LC | ETL.1450.POLE.NWOD | 45125374 | SACTO | SIERRA | 2021-07-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45125374 | 2020-08-28 | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper | 2020-08-28 | Glass | Double Dead End | [5 empty] | 158.2723
121737643 | E | LC | ETL.7390.POLE.NWOD | 45123750 | LAKEVLLE | HUMBOLDT | 2021-07-15 | 2021-10-26 | ETL.7390 | LAYTONVILLE-COVELO | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45123750 | 2021-06-22 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-06-22 | Glass | Dead End | [5 empty] | 617.0351
121744769 | E | LC | ETL.1820.POLE.WDPS | 44560558 | EUREKA | HUMBOLDT | 2021-07-13 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44560079 |  | 2-Pole Wood | 2PS TRP - 2 Pole SUSP. Transposition | [7 empty] | 0.071381
121746387 | F | LC | ETL.6480.POLE.NWOD | 44229521 | SACTO | SIERRA | 2021-07-15 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44229521 | 2013-10-02 | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.01904 | 348.1483
121747007 | E | LC | ETL.5420.POLE.WDPS | 44559059 | TABLEMTN | NORTH VALLEY | 2021-07-14 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44558511 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.008234 | 189.9226 | 1.5638
121781614 | F | LC | ETL.4040.POLE.STPS | 45151928 | TABLEMTN | NORTH VALLEY | 2021-07-21 |  | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45151848 | 2020-08-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP
121785127 | F | LC | ETL.8350.POLE.WOOD | 42833787 | VICTOR | STOCKTON | 2021-07-21 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42833787 |  | Single Wood Pole | DDE - Double Dead End |  | Glass | [5 empty] | 0.0001855 | 300.6168 | 0.055763
121786235 | F | LC | ETL.1810.POLE.WDPS | 44322258 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44322256 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0068813
121803000 | B | LC | ETL.5960.INSL.NCER | 44647546 | PISMOBCH | LOS PADRES | 2021-07-26 | 2021-09-14 | ETL.5960 | DIABLO-GATES #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664670 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-06-11 | Glass | Suspension |  |  |  |  | 3.0999e-07 | 79.1393
121810306 | B | LC | ETL.2420.POLE.WDPS | 44226603 | LAKEVLLE |  | 2021-07-27 | 2021-08-16 | ETL.2420 | MENDOCINO-UKIAH | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44226600 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 5.9346e-05 | 2309.5676
121810868 | E | LC | ETL.6500.INSL.CERA | 40633605 | SACTO | SACRAMENTO | 2021-07-27 | 2021-08-17 | ETL.6500 | COLGATE-PALERMO | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40597436 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.027368 | 1094.4017
121810882 | E | LC | ETL.1162.INSL.CERA | 45070089 | CONCORD | EAST BAY | 2021-07-27 | 2021-10-18 | ETL.1162 | BRIGHTON-OLEUM JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
121815689 | F | LC | ETL.7390.POLE.WDPS | 44412037 | LAKEVLLE |  | 2021-07-26 |  | ETL.7390 | LAYTONVILLE-COVELO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44412036 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.12177
121816524 | E | LC | ETL.6760.POLE.WOOD | 40674403 | SACTO | SIERRA | 2021-07-29 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40674403 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.097983 | 442.9834 | 43.4051
121821048 | E | LC | ETL.6300.POLE.WDPS | 45015255 | TABLEMTN | NORTH VALLEY | 2021-07-29 | 2021-08-03 | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44225925 | 2014-11-07 | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 1.4267e-06 | 1123.0226
121860344 | B | LC | ETL.6300.POLE.WOOD | 44191130 | TABLEMTN | NORTH VALLEY | 2021-08-07 | 2021-11-23 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | DLFL | [11 empty] | 3.6221e-06 | 15.8815
121951521 | F | LC | ETL.2395.POLE.WOOD | 45001467 | TABLEMTN | NORTH VALLEY | 2021-07-31 |  | ETL.2395 | GRIZZLY TAP | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45001467 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | Dead End |  |  |  |  | 0.00026142 | 3021.0042 | 0.78976
121982790 | E | LC | ETL.1070.POLE.WOOD | 40745431 | VICTOR | STOCKTON | 2021-09-01 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40745431 | 1957-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2021-07-06 | Glass | Suspension |  |  |  |  | 0.011257 | 2390.8503 | 26.9135
122007612 | E | LC | ETL.6310.POLE.NWOD | 45156670 | TABLEMTN | NORTH VALLEY | 2021-09-07 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Anchor-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 45156670 | 2021-08-12 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-08-12 | Glass | Dead End
122059234 | E | LC | ETL.4780.INSL.NCER | 45129033 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129379 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.00061078 | 221.6376 | 0.13537
122059234 | E | LC | ETL.4780.INSL.NCER | 45129033 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129379 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2020-03-11 | Porcelain | Dead End |  |  |  |  | 0.00061078 | 221.6376 | 0.13537
122111846 | E | LC | ETL.3980.TOWR | 40744569 | VICTOR | STOCKTON | 2021-09-28 |  | ETL.3980 | TESLA-SCHULTE SW STA #1 | Structure-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Non-HFTD | Non-HFRA | PEND | 40744569 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1998-01-01 | Porcelain | Suspension |  |  |  |  | 0.00015194
118498947 | E | LC | ETL.1710.POLE.WDPS | 44513729 | MOSSLNDG | CENTRAL COAST | 2020-02-05 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | PEND | 44512275 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0038027 | 16.6744 | 0.063407
118955020 | B | LC | ETL.4440.TOWR | 40751682 | TABLEMTN | NORTH VALLEY | 2020-04-28 | 2020-05-14 | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751682 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2015-12-22 | Ceramic | Dead End |  |  |  |  | 7.4599e-07 | 189.9049
119039817 | E | LC | ETL.2660.INSL.CERA | 40898939 | SACTO | SACRAMENTO | 2020-05-15 | 2021-04-22 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119060419 | F | LC | ETL.6440.POLE.WOOD | 40760269 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-06-11 | ETL.6440 | COLEMAN-RED BLUFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760269 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 8.4509e-05 | 4421.0889
119061033 | E | LC | ETL.7590.POLE.WOOD | 40665291 | MOSSLNDG | DE ANZA | 2020-05-12 | 2020-08-18 | ETL.7590 | MONTA VISTA-BURNS | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40665291 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.24576 | 822.7527
119061033 | E | LC | ETL.7590.POLE.WOOD | 40665291 | MOSSLNDG | DE ANZA | 2020-05-12 | 2020-08-18 | ETL.7590 | MONTA VISTA-BURNS | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40665291 |  | Single Wood Pole | DDE - Double Dead End | 2014-06-24 | Polymer | Dead End |  |  |  |  | 0.24576 | 822.7527
119063558 | E | LC | ETL.8650.TOWR | 40651187 | FRESNO | YOSEMITE | 2020-05-05 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40651187 | 1929-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.008378 | 6900.5825
119082378 | E | LC | ETL.6720.POLE.WOOD | 40616098 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2020-06-24 | ETL.6720 | DESABLA-CENTERVILLE | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119083252 | F | LC | ETL.6320.POLE.NWOD | 43702491 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 43702491 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 0.00079626 | 1871.3108
119084723 | E | LC | ETL.6720.POLE.WOOD | 42578829 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2020-11-06 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL | [11 empty] | 1.8716e-07
119094508 | F | LC | ETL.8290.POLE.WOOD | 40600271 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40600271 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00014455 | 5431.645
119101082 | E | LC | ETL.1112.INSL.CERA | 40707780 | FRESNO | YOSEMITE | 2020-06-02 |  | ETL.1112 | INDIAN FLAT-YOSEMITE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44420217 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0018613 | 6710.374 | 12.49
119102208 | E | LC | ETL.6520.POLE.WOOD | 40618357 | SACTO | SACRAMENTO | 2020-06-03 | 2021-06-14 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119103055 | F | LC | ETL.7380.POLE.WDPS | 44563003 | EUREKA | CENTRAL COAST | 2020-05-29 | 2020-06-24 | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 3 | Within Both | DLFL | 44562377 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.83856 | 0.065148
119103160 | E | LC | ETL.7140.POLE.WOOD | 41118222 | LAKEVLLE | NORTH BAY | 2020-05-29 | 2021-05-23 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41118222 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.054361
119103160 | E | LC | ETL.7140.POLE.WOOD | 41118222 | LAKEVLLE | NORTH BAY | 2020-05-29 | 2021-05-23 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41118222 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.054361
119103160 | E | LC | ETL.7140.POLE.WOOD | 41118222 | LAKEVLLE | NORTH BAY | 2020-05-29 | 2021-05-23 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41118222 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.054361
119106522 | E | LC | ETL.1820.POLE.WDPS | 44553876 | EUREKA | HUMBOLDT | 2020-06-04 | 2021-03-20 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553876 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2021-03-05 | Glass | Suspension |  |  |  |  | 0.017411 | 4621.6372
119107833 | F | LC | ETL.1720.POLE.WDPS | 44565746 | MOSSLNDG | CENTRAL COAST | 2020-05-20 | 2021-04-15 | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Tier 3 | Within Both | COMP | 44512241 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00023117 | 1234.1384
119118942 | F | LC | ETL.7300.POLE.WOOD | 40656957 | TABLEMTN |  | 2020-06-03 | 2021-07-07 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119126797 | E | LC | ETL.8290.POLE.WOOD | 40875808 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-22 | ETL.8290 | VOLTA-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40875808 |  | Single Wood Pole | T2N | 2021-04-19 | Polymer | Post |  |  |  |  | 0.00012346 | 3211.8755
119132075 | E | LC | ETL.6770.POLE.WOOD | 40667536 | SACTO | SIERRA | 2020-06-04 | 2021-04-19 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119132580 | F | LC | ETL.4221.POLE.NWOD | 44820160 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2020-08-06 | ETL.4221 | SLY CREEK TAP | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44820160 | 2019-05-24 | Light Duty Steel Pole | DDE - Double Dead End | 2020-10-01 | Glass | Double Dead End |  |  |  |  | 2.0305e-05 | 348.1806
119144825 | E | LC | ETL.7390.POLE.WOOD | 44412207 | LAKEVLLE | HUMBOLDT | 2020-06-09 | 2020-09-10 | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44412207 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.080209
119162038 | F | LC | ETL.6470.POLE.WOOD | 40869659 | SACTO | SIERRA | 2020-06-10 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40869659 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.06153 | 474.9903
119163180 | F | LC | ETL.1400.POLE.WDPS | 44776440 | VICTOR | STOCKTON | 2020-06-12 | 2021-05-17 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40580204 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.0043374 | 31.7334
119176482 | E | LC | ETL.1330.TOWR | 40860981 | LAKEVLLE | HUMBOLDT | 2020-04-24 | 2021-05-11 | ETL.1330 | CORTINA-MENDOCINO #1 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40860981 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.0019357 | 5714.4312
119176879 | E | LC | ETL.7300.POLE.WOOD | 40617694 | TABLEMTN |  | 2020-06-16 | 2021-03-05 | ETL.7300 | KILARC-DESCHUTES | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40617694 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00042519 | 3914.5493
119180731 | E | LC | ETL.6760.INSL.CERA | 40639222 | SACTO | SACRAMENTO | 2020-06-17 | 2020-07-29 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40611360 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0059288 | 17.4655
119181507 | E | LC | ETL.6720.POLE.WOOD | 40825217 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40825217 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0012324 | 269.1313 | 0.33169
119185961 | F | LC | ETL.8350.POLE.WOOD | 40613697 | VICTOR | STOCKTON | 2020-04-10 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40613697 |  | Single Wood Pole | TPSRD - Tri Post & Susp Dead End |  | Glass | [5 empty] | 0.0026129 | 1202.2845
119189046 | E | LC | ETL.2390.POLE.WDPS | 44391057 | VICTOR | STOCKTON | 2020-06-19 | 2021-03-09 | ETL.2390 | MELONES-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119190315 | F | LC | ETL.6310.POLE.WOOD | 41177755 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41177755 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.2431e-05 | 3041.8088
119194768 | F | LC | ETL.6470.POLE.WOOD | 40693271 | SACTO | SIERRA | 2020-06-22 | 2021-07-13 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693271 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.17399 | 269.0426
119196423 | F | LC | ETL.6470.POLE.WOOD | 40767222 | SACTO | SIERRA | 2020-06-22 | 2021-07-21 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40767222 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.16852 | 79.2067
119209053 | F | LC | ETL.7270.POLE.NWOD | 44649334 | TABLEMTN | NORTH VALLEY | 2020-06-25 | 2021-08-25 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44649334 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.0012999 | 753.1941
119228815 | F | LC | ETL.7270.POLE.NWOD | 44649286 | TABLEMTN | NORTH VALLEY | 2020-06-29 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44649286 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.0041139 | 510.5901
119293321 | F | LC | ETL.8060.POLE.WOOD | 40770690 | SACTO | SIERRA | 2020-06-29 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770690 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.059897 | 31.7066
119293623 | F | LC | ETL.3530.TOWR | 40751318 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-05-10 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40751318 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 1.5319e-06 | 2690.7754
119293623 | F | LC | ETL.3530.TOWR | 40751318 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-05-10 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40751318 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1952-01-01 | Porcelain | Suspension |  |  |  |  | 1.5319e-06 | 2690.7754
119300665 | E | LC | ETL.4441.POLE.NWOD | 43198032 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-04-22 | ETL.4441 | BELDEN TAP | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119304274 | E | LC | ETL.7180.POLE.WDPS | 44360860 | LAKEVLLE | SONOMA | 2020-07-02 | 2021-04-22 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44360859 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.9765e-05 | 31.7075
119311081 | E | LC | ETL.6290.INSL.NCER | 40614048 | TABLEMTN | NORTH VALLEY | 2020-07-03 | 2021-09-01 | ETL.6290 | CARIBOU-PLUMAS JCT | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40588932 | 1958-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1973-01-01 | Polymer | Post |  |  |  |  | 0.031062 | 0.066432
119311355 | F | LC | ETL.8060.POLE.WOOD | 40771544 | SACTO | SIERRA | 2020-07-02 | 2021-08-19 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771544 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.019525 | 3274.9534
119316106 | E | LC | ETL.6020.TOWR | 41162606 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-07-15 | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41162606 | 1965-01-01 | LATTICE STEEL TOWER | Unknown | [7 empty] | 1.3011e-07 | 332.4042
119317620 | E | LC | ETL.6290.POLE.WOOD | 40585991 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-09-27 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585991 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.068351 | 4811.106
119325907 | F | LC | ETL.6650.POLE.WDPS | 44386887 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44386886 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012691 | 491.2338
119326518 | E | LC | ETL.7030.POLE.WOOD | 40816896 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-06-14 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40816896 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0039036
119334958 | E | LC | ETL.7300.POLE.WOOD | 40617691 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-08-18 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40617691 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00017812 | 1379.2567
119341378 | E | LC | ETL.7030.POLE.WOOD | 40816130 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-05-13 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816130 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.027778 | 31.7022
119348378 | E | LC | ETL.6870.POLE.WOOD | 40766819 | SACTO | SIERRA | 2020-07-08 | 2021-06-07 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40766819 | 1966-01-01 | Single Wood Pole | 3P DDE-A - 3 Pole Double Dead End Angle | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 0.043642 | 0.065152
119358841 | E | LC | ETL.4750.TOWR | 41129173 | LAKEVLLE | SONOMA | 2020-07-11 | 2020-08-18 | ETL.4750 | GEYSERS #12-FULTON | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129173 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.0047741 | 2012.3107
119359801 | B | LC | ETL.7270.INSL.NCER | 44649400 | TABLEMTN |  | 2020-07-10 | 2020-08-05 | ETL.7270 | KESWICK-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44649366 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.0020244 | 840.0571
119360113 | E | LC | ETL.1440.POLE.WOOD | 40590113 | SACTO | SIERRA | 2020-07-13 | 2021-03-12 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL | [11 empty] | 0.0012487
119363585 | F | LC | ETL.6280.POLE.WOOD | 40666886 | TABLEMTN | NORTH VALLEY | 2020-07-13 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40666886 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Other |  |  |  |  | 0.00015132 | 1376.0835
119374681 | F | LC | ETL.7930.POLE.WOOD | 40809408 | MOSSLNDG | CENTRAL COAST | 2020-07-15 |  | ETL.7930 | SALINAS-LAURELES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40809408 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Other |  |  |  |  | 0.023853 | 15.8926
119468289 | F | LC | ETL.7030.POLE.WOOD | 40589880 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-02-11 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40589880 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0043412
119481929 | F | LC | ETL.7030.POLE.WOOD | 40827462 | TABLEMTN | NORTH VALLEY | 2020-07-21 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40827462 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0090576 | 6240.1276
119481956 | F | LC | ETL.8960.POLE.NWOD | 41196591 | FRESNO | FRESNO | 2020-07-21 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 41196591 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 3.8187e-07
119487565 | E | LC | ETL.8060.POLE.WOOD | 40869224 | SACTO | SACRAMENTO | 2020-07-22 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40869224 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.046183 | 1260.556
119489001 | E | LC | ETL.3860.INSL.NCER | 44942304 | CONCORD | MISSION | 2020-07-22 | 2021-03-16 | ETL.3860 | STANISLAUS-NEWARK #2 (12KV) | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40645805 | 1962-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2020-07-03 | Glass Silicone Coated | Dead End |  |  |  |  | 1.1074e-07 | 2763.1851
119489001 | E | LC | ETL.3860.INSL.NCER | 44942304 | CONCORD | MISSION | 2020-07-22 | 2021-03-16 | ETL.3860 | STANISLAUS-NEWARK #2 (12KV) | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40645805 | 1962-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1962-01-01 | Porcelain | Dead End |  |  |  |  | 1.1074e-07 | 2763.1851
119515799 | E | LC | ETL.1110.POLE.NWOD | 42603425 | TABLEMTN | HUMBOLDT | 2020-07-22 | 2021-07-20 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42603425 |  | Lattice Steel Pole | DDE - Double Dead End | 2021-05-28 | Ceramic | Dead End |  |  |  |  | 0.00044445 | 221.5655
119516169 | F | LC | ETL.6280.POLE.NWOD | 44259046 | TABLEMTN | NORTH VALLEY | 2020-07-23 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44259046 | 2020-07-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-07-16 | Polymer | Dead End |  |  |  |  | 3.4343e-05 | 57.0038
119523195 | B | LC | ETL.7490.POLE.WOOD | 40811041 | EUREKA | HUMBOLDT | 2020-07-29 | 2020-08-17 | ETL.7490 | MAPLE CREEK-HOOPA | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119535745 | F | LC | ETL.6861.POLE.WOOD | 40600734 | LAKEVLLE | HUMBOLDT | 2020-07-31 |  | ETL.6861 | KONOCTI-EAGLE ROCK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40600734 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.00040547 | 427.3348
119573663 | E | LC | ETL.7270.POLE.WDPS | 44421168 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-08-17 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44421166 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0024963 | 933.5561
119611218 | F | LC | ETL.1600.TOWR | 40808851 | LAKEVLLE | SONOMA | 2020-08-13 |  | ETL.1600 | FULTON-PUEBLO | Structure-Tower | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40808851 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 2.2018e-07 | 31.7331
119617009 | B | LC | ETL.8365.POLE.WOOD | 40912596 | EUREKA | HUMBOLDT | 2020-08-14 | 2020-11-05 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912596 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | Pin |  |  |  |  | 0.095404
119639924 | B | LC | ETL.8650.TOWR | 40871018 | FRESNO | FRESNO | 2020-08-19 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871018 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.014604 | 6283.7788
119639936 | B | LC | ETL.8650.POLE.NWOD | 44420200 | FRESNO | FRESNO | 2020-08-19 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420200 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0058416 | 2214.1416
119666328 | E | LC | ETL.7490.POLE.WOOD | 40752763 | EUREKA | HUMBOLDT | 2020-08-25 | 2021-08-17 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40752763 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.77239 | 63.3304
119677569 | E | LC | ETL.1330.TOWR | 40870095 | LAKEVLLE | SONOMA | 2020-08-26 | 2021-04-14 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870095 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.000103 | 4132.8335
119678814 | E | LC | ETL.1110.POLE.WDPS | 44423382 | TABLEMTN | HUMBOLDT | 2020-08-26 | 2021-04-13 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423381 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012744 | 5339.1709
119703457 | E | LC | ETL.8365.POLE.WOOD | 40906655 | EUREKA | HUMBOLDT | 2020-08-15 | 2021-04-29 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906655 |  | Single Wood Pole | T1DE - Tri Post Dead End 115 | 2021-04-25 | Glass | Dead End |  |  |  |  | 0.19321
119720548 | A | LC | ETL.6240.POLE.NWOD | 44624112 | MOSSLNDG | CENTRAL COAST | 2020-09-05 | 2020-10-13 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44624112 | 2018-06-29 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-06-29 | Polymer | Dead End |  |  |  |  | 0.098099 | 585.7959
119723029 | F | LC | ETL.1440.POLE.STPS | 44338100 | SACTO | SIERRA | 2020-08-11 | 2021-05-03 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] |  | Tier 3 | Within Both | COMP | 44338098 | 2018-09-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.6436e-07 | 433.5528
119758518 | E | LC | ETL.7300.POLE.WOOD | 41118630 | TABLEMTN |  | 2020-09-11 | 2021-03-23 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119766823 | E | LC | ETL.6760.POLE.WOOD | 40865387 | SACTO | SIERRA | 2020-09-08 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND | [12 empty] | 110.8102
119779993 | B | LC | ETL.7300.INSL.NCER | 40781200 | TABLEMTN |  | 2020-09-10 | 2020-11-16 | ETL.7300 | KILARC-DESCHUTES | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40752152 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.098072 | 221.5566
119799520 | F | LC | ETL.1400.POLE.NWOD | 44384154 | VICTOR | YOSEMITE | 2020-08-07 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | PEND
119805053 | F | LC | ETL.7300.POLE.WOOD | 41118608 | TABLEMTN |  | 2020-08-07 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41118608 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00019513 | 1586.913
119816312 | F | LC | ETL.6770.POLE.NWOD | 44928251 | SACTO | SIERRA | 2020-08-29 |  | ETL.6770 | DRUM-SPAULDING | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44928251 | 2020-05-21 | Light Duty Steel Pole | T2N | 2020-05-21 | Polymer | Post |  |  |  |  | 0.00026903 | 3069.2839
119894322 | B | LC | ETL.8170.INSL | 40728955 | EUREKA | HUMBOLDT | 2020-10-12 | 2020-11-16 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40689251 |  | Single Wood Pole | 3P DDE - 3 Pole Double Dead End |  | Ceramic | [5 empty] | 0.024404 | 6060.7563
119924817 | E | LC | ETL.5980.TOWR | 40662862 | PISMOBCH | LOS PADRES | 2020-10-19 | 2021-07-30 | ETL.5980 | DIABLO-MIDWAY #3 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40662862 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 5.9816e-10 | 2204.9475
119967639 | F | LC | ETL.6220.POLE.WOOD | 40752633 | EUREKA | HUMBOLDT | 2020-10-30 | 2021-01-25 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40752633 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2020-01-19 | Glass | Double Dead End |  |  |  |  | 0.11297
119971890 | E | LC | ETL.6240.POLE.WOOD | 40585755 | MOSSLNDG | CENTRAL COAST | 2020-10-28 | 2021-08-17 | ETL.6240 | BURNS-LONE STAR #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585755 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Porcelain | [5 empty] | 0.16266 | 1123.7659
119988057 | F | LC | ETL.8960.POLE.WOOD | 40596617 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40596617 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 1925-01-01 | Polymer | Suspension |  |  |  |  | 9.6826e-05
120007297 | E | LC | ETL.1650.POLE.WOOD | 40603859 | LAKEVLLE | SONOMA | 2020-11-09 | 2021-03-24 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120014601 | E | LC | ETL.1650.POLE.WOOD | 40681323 | LAKEVLLE | SONOMA | 2020-11-12 | 2021-02-03 | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40681323 | 1966-01-01 | Single Wood Pole | WB - Wishbone | 1966-01-01 | Porcelain | Suspension |  |  |  |  | 0.00027549 | 3263.3687
120079434 | E | LC | ETL.1440.POLE.WOOD | 42572716 | SACTO | SIERRA | 2020-09-11 | 2021-07-06 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.00098099 | 9.5576
120114764 | E | LC | ETL.7060.POLE.WDPS | 44732844 | METCALF | SAN JOSE | 2020-11-24 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42564698 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0077985 | 0.066432 | 0.00051807
120134237 | F | LC | ETL.5220.TOWR | 40811339 | METCALF | DE ANZA | 2020-10-21 | 2021-03-01 | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40811339 | 1963-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle |  | Non Ceramic | Double Dead End |  |  |  |  | 4.6801e-05
120134237 | F | LC | ETL.5220.TOWR | 40811339 | METCALF | DE ANZA | 2020-10-21 | 2021-03-01 | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40811339 | 1963-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle |  | Non Ceramic | [5 empty] | 4.6801e-05
120139177 | F | LC | ETL.1110.POLE.WDPS | 44423210 | TABLEMTN | HUMBOLDT | 2020-10-28 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44423209 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00094901 | 5196.7314
120143784 | E | LC | ETL.6380.INSL.NCER | 44371582 | LAKEVLLE |  | 2020-12-07 | 2021-03-04 | ETL.6380 | KONOCTI-MIDDLETOWN | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44371580 | 2015-09-15 | Single Wood Pole | T-1 - Tri Post | 2015-09-15 | Polymer | Post |  |  |  |  | 6.7107e-06 | 6045.3115
120144071 | F | LC | ETL.8650.TOWR | 40606162 | FRESNO | FRESNO | 2020-12-08 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40606162 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0044388 | 6995.4082
120243178 | E | LC | ETL.1440.POLE.WDPS | 44837642 | SACTO | SACRAMENTO | 2020-12-31 | 2021-07-06 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [12 empty] | 47.5273
120243329 | E | LC | ETL.4393.POLE.WDPS | 44172124 | SACTO | SACRAMENTO | 2020-12-31 | 2021-04-01 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120244247 | F | LC | ETL.7780.POLE.NWOD | 44773173 | LAKEVLLE | HUMBOLDT | 2020-12-11 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44773173 | 2019-04-03 | Light Duty Steel Pole | 3HP - 3 Horizontal Post | 2019-04-03 | Ceramic | Suspension - Post |  |  |  |  | 4.3164e-06 | 174.0688
120686490 | F | LC | ETL.5100.TOWR | 40662774 | MOSSLNDG | SAN JOSE | 2021-03-23 |  | ETL.5100 | METCALF-MOSS LANDING #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40662774 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2005-01-01 | Non Ceramic | Dead End |  |  |  |  | 7.8242e-06 | 1487.2816 | 0.011637
120687142 | E | LC | ETL.4392.TOWR | 41129373 | LAKEVLLE | SONOMA | 2021-03-24 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129373 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.00033265 | 740.6124 | 0.24637
120687142 | E | LC | ETL.4392.TOWR | 41129373 | LAKEVLLE | SONOMA | 2021-03-24 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129373 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.00033265 | 740.6124 | 0.24637
120692477 | E | LC | ETL.5140.POLE.WDPS | 44558298 | SACTO | SACRAMENTO | 2021-03-24 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | Rotten | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44557929 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0011225 | 6077.7764 | 6.822
120696202 | E | LC | ETL.5410.TOWR | 40822613 | TABLEMTN | NORTH VALLEY | 2021-03-26 |  | ETL.5410 | CARBERRY SW STA-ROUND MTN | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40822613 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 9.1232e-05 | 411.3143 | 0.037525
120715195 | E | LC | ETL.6720.INSL.CERA | 44324230 | TABLEMTN | NORTH VALLEY | 2021-03-26 |  | ETL.6720 | DESABLA-CENTERVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44324208 | 2015-11-03 | Fiberglass | TPD - Tri Post Dead End Construction | 2015-11-03 | Ceramic | Suspension |  |  |  |  | 0.00055987 | 63.3704 | 0.035479
120724002 | E | LC | ETL.4316.POLE.STPS | 44712232 | TABLEMTN | NORTH VALLEY | 2021-04-01 | 2021-08-17 | ETL.4316 | PARADISE-TABLE MTN | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44712214 | 2019-02-13 | 3-Pole Non Wood | T-1 - Tri Post | [7 empty] | 0.00031566 | 2045.7959
120725594 | E | LC | ETL.4440.TOWR | 40816421 | TABLEMTN | NORTH VALLEY | 2021-03-23 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40816421 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 1.2287e-06 | 206.0033 | 0.00025312
120739900 | E | LC | ETL.2900.TOWR | 40761041 | MOSSLNDG | CENTRAL COAST | 2021-04-03 | 2021-07-26 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761041 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1991-01-01 | Porcelain | Dead End |  |  |  |  | 0.0043859 | 4398.79
120739900 | E | LC | ETL.2900.TOWR | 40761041 | MOSSLNDG | CENTRAL COAST | 2021-04-03 | 2021-07-26 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761041 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-11-05 | Glass Silicone Coated | Dead End |  |  |  |  | 0.0043859 | 4398.79
120748782 | E | LC | ETL.1730.POLE.WDPS | 44413375 | MOSSLNDG | CENTRAL COAST | 2021-04-06 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44413374 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 6.5395e-05 | 126.5838 | 0.008278
120752002 | E | LC | ETL.1810.POLE.WDPS | 44322488 | EUREKA | HUMBOLDT | 2021-04-06 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44322486 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.01066
120766338 | E | LC | ETL.1890.TOWR | 40819773 | FRESNO | FRESNO | 2021-03-29 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40819773 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1986-01-01 | Porcelain | Suspension |  |  |  |  | 8.3707e-07 | 6030.9819 | 0.0050483
120773130 | E | LC | ETL.3820.TOWR | 40764246 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40764246 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 9.4113e-06 | 5398.1479 | 0.050804
120794319 | E | LC | ETL.3830.INSL | 40828577 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40804665 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.6507e-05 | 95.2198 | 0.002524
120796827 | E | LC | ETL.3820.TOWR | 40750279 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40750279 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 1.7634e-06 | 2326.9204 | 0.0041032
120802275 | E | LC | ETL.1880.TOWR | 40582954 | FRESNO | FRESNO | 2021-04-12 |  | ETL.1880 | KERCKHOFF #1-KERCKHOFF #2 | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40582954 | 1942-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2015-03-03 | Polymer | Dead End |  |  |  |  | 3.2151e-07 | 5129.5112 | 0.0016492
120802275 | E | LC | ETL.1880.TOWR | 40582954 | FRESNO | FRESNO | 2021-04-12 |  | ETL.1880 | KERCKHOFF #1-KERCKHOFF #2 | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40582954 | 1942-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2002-01-01 | Polymer | Dead End |  |  |  |  | 3.2151e-07 | 5129.5112 | 0.0016492
120816096 | F | LC | ETL.4316.POLE.NWOD | 44674847 | TABLEMTN | NORTH VALLEY | 2021-04-14 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44674847 | 2018-11-18 | Light Duty Steel Pole | DDE - Double Dead End | 2018-11-18 | Polymer | Dead End |  |  |  |  | 0.00012772 | 2314.6216
120828964 | F | LC | ETL.6490.POLE.WOOD | 40767588 | SACTO | SACRAMENTO | 2021-04-16 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40767588 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0030936 | 2815.7598
120829456 | E | LC | ETL.4580.TOWR | 40657664 | TABLEMTN | NORTH VALLEY | 2021-04-16 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40657664 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Porcelain | Suspension |  |  |  |  | 1.9381e-07 | 4705.9995 | 0.00091205
120829456 | E | LC | ETL.4580.TOWR | 40657664 | TABLEMTN | NORTH VALLEY | 2021-04-16 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40657664 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.9381e-07 | 4705.9995 | 0.00091205
120836044 | E | LC | ETL.8060.POLE.WOOD | 40876679 | SACTO | SACRAMENTO | 2021-04-17 | 2021-05-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876679 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.011388 | 95.1488
120846801 | E | LC | ETL.3500.TOWR | 40745438 | VICTOR | STOCKTON | 2021-04-19 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40745438 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 0.00076387 | 142.4769 | 0.10883
120860774 | E | LC | ETL.8240.POLE.WOOD | 40758344 | VICTOR | STOCKTON | 2021-04-21 | 2021-05-07 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Hardware-Wood | Missing | [Install] | Tier2 |  |  | DLFL
120866636 | F | LC | ETL.1710.POLE.WOOD | 40577372 | MOSSLNDG | CENTRAL COAST | 2021-04-14 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40577372 |  | Single Wood Pole | T-1 - Tri Post | 2019-04-11 | Polymer | Post |  |  |  |  | 0.015596 | 31.6948
120874353 | E | LC | ETL.6470.POLE.WOOD | 40602487 | SACTO | SACRAMENTO | 2021-04-23 | 2021-08-31 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602487 |  | Single Wood Pole | T2N | 2021-08-07 | Polymer | Post |  |  |  |  | 0.0090941 | 5857.8857
120880208 | E | LC | ETL.1810.INSL.CERA | 40835746 | EUREKA | HUMBOLDT | 2021-04-24 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44321394 |  | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 4.8867e-08
120897357 | E | LC | ETL.6890.POLE.WOOD | 40808478 | LAKEVLLE | SONOMA | 2021-04-28 | 2021-08-30 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP | [12 empty] | 2375.323
120904340 | E | LC | ETL.5933.TOWR | 40810829 | PISMOBCH | LOS PADRES | 2021-04-29 | 2021-04-30 | ETL.5933 | MORRO BAY-TEMPLETON | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40810829 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2016-08-27 | Ceramic | Dead End |  |  |  |  | 3.543e-08 | 2881.3301
120904569 | E | LC | ETL.7550.POLE.WOOD | 40809258 | LAKEVLLE | SONOMA | 2021-04-29 | 2021-06-11 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | DLFL | 40809258 |  | Single Wood Pole | SV-PJ-90 - Single Vertical Post Jumper 90 |  | Porcelain | [5 empty] | 3.198e-05 | 854.2646
120914616 | E | LC | ETL.5930.TOWR | 40868389 | LAKEVLLE | DIABLO | 2021-05-01 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40868389 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 4.3332e-08 | 31.6978 | 1.3735e-06
121319703 | F | LC | ETL.4440.TOWR | 40656173 | TABLEMTN | NORTH VALLEY | 2021-04-21 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40656173 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 4.9705e-06 | 1044.361 | 0.005191
121329434 | E | LC | ETL.2395.POLE.WOOD | 44948578 | TABLEMTN | NORTH VALLEY | 2021-05-13 |  | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44948578 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Unknown | Suspension |  |  |  |  | 0.0011295 | 189.8861 | 0.21448
121336998 | E | LC | ETL.2395.POLE.WOOD | 45013477 | TABLEMTN | NORTH VALLEY | 2021-05-14 | 2021-05-28 | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45013477 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00017633 | 3021.0042
121363306 | E | LC | ETL.1250.POLE.WOOD | 40682182 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40682182 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.00032563 | 6647.8232 | 2.1648
121367505 | F | LC | ETL.5980.TOWR | 40576266 | PISMOBCH | LOS PADRES | 2021-04-28 |  | ETL.5980 | DIABLO-MIDWAY #3 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40576266 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-10-06 | Glass Silicone Coated | Suspension |  |  |  |  | 2.2455e-11 | 2533.0825
121370913 | E | LC | ETL.5070.TOWR | 40869395 | FRESNO | YOSEMITE | 2021-05-04 |  | ETL.5070 | QUINTO SW STA-WESTLEY | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40869395 | 1947-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1947-01-01 | Ceramic | Suspension |  |  |  |  | 8.3005e-08 | 740.0169 | 6.1425e-05
121383437 | F | LC | ETL.1650.POLE.NWOD | 40576054 | LAKEVLLE | SONOMA | 2021-05-12 | 2021-06-14 | ETL.1650 | GEYSERS #3-CLOVERDALE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40576054 | 2011-01-01 | Light Duty Steel Pole | 3HP - 3 Horizontal Post | 1989-01-01 | Polymer | Post |  |  |  |  | 1.2912e-08 | 3278.8411
121383759 | F | LC | ETL.8250.POLE.WOOD | 40904105 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40904105 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 2014-04-29 | Polymer | Post |  |  |  |  | 8.7306e-06 | 3548.5354
121383817 | F | LC | ETL.1420.TOWR | 40805287 | SACTO | SIERRA | 2021-05-06 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40805287 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.00069243 | 15.8837
121384314 | E | LC | ETL.6470.POLE.WOOD | 40760435 | SACTO | SIERRA | 2021-05-07 | 2021-07-29 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760435 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.015604 | 411.5556
121385436 | F | LC | ETL.6760.POLE.WOOD | 40589525 | SACTO | SIERRA | 2021-05-13 | 2021-06-25 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40589525 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.059992 | 110.8706
121387268 | E | LC | ETL.1470.INSL.NCER | 40845128 | LAKEVLLE | HUMBOLDT | 2021-05-15 |  | ETL.1470 | EAGLE ROCK-CORTINA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40818664 | 2005-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2005-01-01 | Polymer | Suspension |  |  |  |  | 0.00094496 | 2358.8699 | 2.229
121387667 | E | LC | ETL.8250.POLE.WOOD | 40904147 | VICTOR | STOCKTON | 2021-05-10 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40904147 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.009211 | 1362.709 | 12.5519
121395157 | E | LC | ETL.6660.POLE.NWOD | 45086320 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45086320 | 2021-03-04 | Light Duty Steel Pole | T2N | 2021-03-04 | Polymer | Post |  |  |  |  | 2.2512e-08 | 1062.9271 | 2.3928e-05
121397701 | F | LC | ETL.3740.TOWR | 44188838 | CONCORD | DIABLO | 2021-05-19 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44188838 | 2008-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-07-19 | Glass | Dead End |  |  |  |  | 0.007633 | 603.2272 | 4.6044
121400177 | B | LC | ETL.1073.INSL.CERA | 44385297 | VICTOR | YOSEMITE | 2021-05-25 | 2021-07-27 | ETL.1073 | MI-WUK-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44385266 | 2017-08-17 | 2-Pole Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 0.00072916
121400177 | B | LC | ETL.1073.INSL.CERA | 44385297 | VICTOR | YOSEMITE | 2021-05-25 | 2021-07-27 | ETL.1073 | MI-WUK-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44385266 | 2017-08-17 | 2-Pole Wood | 2PS - 2 Pole SUSP | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 0.00072916
121404256 | F | LC | ETL.6760.POLE.WOOD | 40598686 | SACTO | SIERRA | 2021-05-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40598686 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.012888 | 79.1577
121404742 | E | LC | ETL.1070.POLE.WOOD | 40593489 | VICTOR | STOCKTON | 2021-05-20 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40593489 | 1998-01-01 | Single Wood Pole | TPSR - Tri Post & Susp Light | 1957-01-01 | Polymer | Dead End |  |  |  |  | 0.00016244 | 3105.197 | 0.50441
121406891 | E | LC | ETL.4220.POLE.STPS | 44558404 | TABLEMTN |  | 2021-05-25 | 2021-06-17 | ETL.4220 | WOODLEAF-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44557885 | 2019-07-27 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0011981 | 174.0849
121422882 | E | LC | ETL.2540.POLE.WDPS | 44401517 | METCALF | CENTRAL COAST | 2021-05-26 |  | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44401516 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.15372 | 253.2084 | 38.9233
121427286 | E | LC | ETL.7040.POLE.WOOD | 40758098 | TABLEMTN | NORTH VALLEY | 2021-05-24 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40758098 |  | Single Wood Pole | T-1 - Tri Post |  | Porcelain | [5 empty] | 0.040894 | 1870.6526 | 76.4976
121428614 | E | LC | ETL.4316.POLE.STPS | 44383192 | TABLEMTN | NORTH VALLEY | 2021-05-26 |  | ETL.4316 | PARADISE-TABLE MTN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44383189 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00034535 | 238.4023 | 0.082333
121431160 | E | LC | ETL.6110.TOWR | 40753705 | METCALF | SAN JOSE | 2021-05-27 |  | ETL.6110 | TESLA-METCALF | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753705 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.0693e-08 | 1792.4329 | 1.9166e-05
121452720 | F | LC | ETL.6470.POLE.WOOD | 40760449 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40760449 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.036689 | 269.0426
121469946 | E | LC | ETL.7180.INSL.NCER | 44836666 | LAKEVLLE | NORTH BAY | 2021-06-03 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40750715 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 2019-08-27 | Polymer | Post |  |  |  |  | 4.2762e-06 | 412.6046 | 0.0017644
121470950 | E | LC | ETL.6880.INSL.NCER | 45063792 | LAKEVLLE | SONOMA | 2021-05-26 |  | ETL.6880 | FULTON-CALISTOGA | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45063778 | 2019-08-21 | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-08-21 | Glass | Suspension | [5 empty] | 1790.5603
121485435 | F | LC | ETL.7780.POLE.WOOD | 40769172 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7780 | PHILO JCT-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40769172 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Ceramic | [5 empty] | 0.0012695 | 0.065148 | 8.2706e-05
121493738 | E | LC | ETL.5650.TOWR | 40862345 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40862345 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-17 | Glass | Suspension |  |  |  |  | 2.9138e-08 | 1856.0791 | 5.4083e-05
121500480 | E | LC | ETL.1450.POLE.WDPS | 44553704 | SACTO | SACRAMENTO | 2021-06-04 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553217 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.011396 | 1260.556 | 14.3658
121511347 | E | LC | ETL.1402.POLE.WDPS | 44550778 | VICTOR | STOCKTON | 2021-06-01 | 2021-09-27 | ETL.1402 | SPRING GAP TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [12 empty] | 1329.0924
121512350 | E | LC | ETL.1450.POLE.WDPS | 44553703 | SACTO | SACRAMENTO | 2021-06-10 | 2021-07-06 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44553217 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.011396 | 1260.556
121518391 | F | LC | ETL.5390.TOWR | 40816486 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40816486 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 8.9041e-09 | 4254.8906
121518519 | F | LC | ETL.7550.POLE.WOOD | 40588469 | LAKEVLLE | HUMBOLDT | 2021-06-10 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40588469 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0017681 | 110.7947 | 0.1959
121519231 | F | LC | ETL.1440.POLE.WDPS | 44765211 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40756901 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0077222 | 632.957 | 4.8878
121519754 | E | LC | ETL.5650.TOWR | 40871582 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40871582 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 4.324e-05 | 2884.6409 | 0.12473
121531184 | B | LC | ETL.1450.POLE.WOOD | 42572875 | SACTO | SIERRA | 2021-06-12 | 2021-08-31 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0014079 | 934.6734
121532145 | F | LC | ETL.6230.POLE.WOOD | 40669419 | MOSSLNDG | CENTRAL COAST | 2021-06-09 |  | ETL.6230 | BURNS-LONE STAR #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40669419 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.30576 | 1028.9148 | 314.5971
121535091 | F | LC | ETL.1440.POLE.STPS | 44338168 | SACTO | SIERRA | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44338167 | 2018-09-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.0369e-06 | 15.8859
121536852 | E | LC | ETL.6500.POLE.WOOD | 44223735 | SACTO | NORTH VALLEY | 2021-06-09 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44223735 | 2013-07-02 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2013-07-02 | Polymer | Suspension |  |  |  |  | 0.006093 | 5662.0693 | 34.4991
121539986 | F | LC | ETL.6510.POLE.STPS | 44399433 | SACTO | SACRAMENTO | 2021-06-15 |  | ETL.6510 | COLGATE-SMARTVILLE #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44399432 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 2.9344e-08 | 381.0252
121545998 | F | LC | ETL.1600.TOWR | 40750507 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40750507 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 4.2342e-07 | 919.9402
121550506 | F | LC | ETL.4680.TOWR | 40663844 | LAKEVLLE | SONOMA | 2021-06-05 |  | ETL.4680 | FULTON-IGNACIO #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40663844 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 0.00023563 | 142.5034
121553818 | E | LC | ETL.7640.POLE.WDPS | 44565506 | TABLEMTN | NORTH VALLEY | 2021-06-17 | 2021-08-10 | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44564292 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0035575 | 506.6299
121592905 | E | LC | ETL.8365.INSL.NCER | 45083856 | EUREKA | HUMBOLDT | 2021-06-23 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 45083838 | 2021-04-20 | Light Duty Steel Pole | T2N | 2021-04-20 | Polymer | Post |  |  |  |  | 0.054912
121599356 | B | LC | ETL.6020.INSL | 40895894 | TABLEMTN | NORTH VALLEY | 2021-06-24 | 2021-07-19 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870788 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.4464e-09 | 1286.051
121621031 | E | LC | ETL.6980.INSL.NCER | 40882480 | LAKEVLLE | HUMBOLDT | 2021-06-18 |  | ETL.6980 | FORT ROSS-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40860813 | 1985-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1985-01-01 | Polymer | Suspension |  |  |  |  | 0.39329 | 792.0737 | 311.5178
121642534 | E | LC | ETL.1450.INSL.CERA | 40717467 | SACTO | SIERRA | 2021-06-18 | 2021-07-06 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44553150 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0028326
121642534 | E | LC | ETL.1450.INSL.CERA | 40717467 | SACTO | SIERRA | 2021-06-18 | 2021-07-06 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44553150 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0028326
121658214 | F | LC | ETL.4040.POLE.WOOD | 40601510 | TABLEMTN | NORTH VALLEY | 2021-06-28 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40601510 | 2011-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 1949-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0096735 | 142.5046
121660851 | F | LC | ETL.6650.POLE.STPS | 44154510 | TABLEMTN | NORTH VALLEY | 2021-07-01 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44154508 | 2015-03-16 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.00061089 | 2632.3416
121662395 | F | LC | ETL.6650.POLE.WDPS | 44386878 | TABLEMTN | NORTH VALLEY | 2021-07-01 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44386877 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0045587 | 2520.012
121684015 | E | LC | ETL.9240.TOWR | 43249763 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249763 |  | LATTICE STEEL TOWER | [9 empty] | 1473.9071
121715193 | E | LC | ETL.1820.POLE.WDPS | 44562782 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562464 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.76981 | 36.4545 | 28.0629
121717967 | E | LC | ETL.1350.POLE.NWOD | 45093838 | TABLEMTN | NORTH VALLEY | 2021-07-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45093838 | 2020-12-16 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2020-12-16 | Glass | Dead End |  |  |  |  | 4.804e-05 | 142.4582 | 0.0068437
121731742 | E | LC | ETL.1400.INSL.NCER | 40772091 | VICTOR | YOSEMITE | 2021-07-07 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40744831 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | 1956-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0033999
121731742 | E | LC | ETL.1400.INSL.NCER | 40772091 | VICTOR | YOSEMITE | 2021-07-07 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40744831 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | 1956-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0033999
121736969 | F | LC | ETL.5510.TOWR | 40872738 | CONCORD | DIABLO | 2021-07-12 | 2021-10-11 | ETL.5510 | PITTSBURG-TESLA #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40872738 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 1.1144e-08 | 4750.3203
121741190 | E | LC | ETL.1820.POLE.WDPS | 44557589 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44554047 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.23704 | 31.7081 | 7.5161
121744497 | E | LC | ETL.2390.POLE.WDPS | 44390983 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44390981 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0001964 | 2751.947 | 0.54047
121745636 | B | LC | ETL.1820.POLE.NWOD | 45102851 | EUREKA | HUMBOLDT | 2021-07-15 | 2021-08-04 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45102851 | 2014-09-20 | Light Duty Steel Pole | 3P SV - 3 Pole Single Vertical | 2014-09-20 | Ceramic | Suspension |  |  |  |  | 0.41683 | 47.5118
121770401 | E | LC | ETL.6510.POLE.STPS | 44399418 | SACTO | SACRAMENTO | 2021-07-19 |  | ETL.6510 | COLGATE-SMARTVILLE #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44399416 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 4.5629e-07 | 1092.7948 | 0.00049864
121785192 | E | LC | ETL.2030.POLE.NWOD | 44191988 | FRESNO | FRESNO | 2021-07-23 |  | ETL.2030 | KINGS RIVER-SANGER-REEDLEY | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44191988 |  | Lattice Steel Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 1.744e-05 | 4149.042 | 0.072359
121794215 | B | LC | ETL.6280.POLE.WOOD | 40599705 | TABLEMTN | NORTH VALLEY | 2021-07-25 | 2021-10-14 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40599705 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 4.9817e-06 | 411.289
121797509 | E | LC | ETL.9240.TOWR | 43249601 | PISMOBCH | LOS PADRES | 2021-07-26 | 2021-10-14 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 43249601 |  | LATTICE STEEL TOWER | [9 empty] | 4576.4678
121804613 | E | LC | ETL.6050.INSL | 40783425 | MOSSLNDG | CENTRAL COAST | 2021-07-26 |  | ETL.6050 | MOSS LANDING-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40753798 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 8.0772e-06 | 1265.7812 | 0.010224
121810871 | E | LC | ETL.8365.INSL.CERA | 40916258 | EUREKA | HUMBOLDT | 2021-07-27 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40906586 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.019477
121815794 | E | LC | ETL.5960.TOWR | 40805565 | FRESNO | FRESNO | 2021-07-29 |  | ETL.5960 | DIABLO-GATES #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40805565 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 0.00015152
121816256 | E | LC | ETL.6690.INSL | 40842904 | SACTO | SIERRA | 2021-07-29 |  | ETL.6690 | DEER CREEK-DRUM | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40815088 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | [5 empty] | 0.22892 | 158.2976 | 36.2382
121823155 | E | LC | ETL.6760.INSL.NCER | 44969867 | SACTO | SIERRA | 2021-07-27 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44969820 | 2020-08-28 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-08-28 | Glass | Dead End |  |  |  |  | 0.00221 | 332.3255 | 0.73445
121825163 | F | LC | ETL.4393.POLE.WDPS | 44172318 | SACTO | SACRAMENTO | 2021-07-30 |  | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44172317 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 7.8124e-05 | 110.7947
121900682 | E | LC | ETL.8170.POLE.WOOD | 40822548 | EUREKA | HUMBOLDT | 2021-08-13 | 2021-10-18 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40822548 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.0093661 | 6319.5718 | 59.1897
122057153 | E | LC | ETL.4780.INSL.NCER | 45128991 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129324 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.00016787 | 3246.7576 | 0.54502
122057153 | E | LC | ETL.4780.INSL.NCER | 45128991 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129324 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.00016787 | 3246.7576 | 0.54502
122057566 | E | LC | ETL.4780.INSL.NCER | 45128971 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129334 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 1.0433e-06 | 2534.3203 | 0.0026442
122057566 | E | LC | ETL.4780.INSL.NCER | 45128971 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129334 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 1.0433e-06 | 2534.3203 | 0.0026442
118525824 | E | LC | ETL.4870.TOWR | 40869064 | FRESNO | FRESNO | 2020-02-11 | 2021-06-29 | ETL.4870 | HELMS-GREGG #1 | Structure-Steel | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | DLFL | 40869064 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 1.8822e-07
118562353 | B | LC | ETL.1810.POLE.WDPS | 44322214 | EUREKA | HUMBOLDT | 2020-02-16 | 2020-03-04 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322214 |  | Light Duty Steel Pole | DDE - Double Dead End | 2016-10-30 | Ceramic | Dead End |  |  |  |  | 3.2049e-10 | 224.7199
118759043 | E | LC | ETL.8350.POLE.WOOD | 40600017 | VICTOR | STOCKTON | 2020-03-31 | 2020-05-13 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40600017 |  | Single Wood Pole | DDE - Double Dead End | 2015-09-17 | Ceramic | Pin |  |  |  |  | 0.00017205 | 110.7947
118763152 | E | LC | ETL.1730.POLE.WOOD | 40602386 | MOSSLNDG | CENTRAL COAST | 2020-03-31 | 2020-06-22 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40602386 | 1972-01-01 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2020-06-03 | Porcelain | Dead End |  |  |  |  | 4.0834e-05 | 0.065147
118922288 | E | LC | ETL.6320.POLE.WOOD | 40874520 | TABLEMTN | NORTH VALLEY | 2020-04-15 | 2021-06-01 | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40874520 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0010787 | 2140.4165
118952421 | E | LC | ETL.2410.INSL | 40835492 | LAKEVLLE |  | 2020-04-23 | 2021-04-05 | ETL.2410 | MENDOCINO-REDBUD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40808923 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 1.9217e-05 | 3958.4939
118952421 | E | LC | ETL.2410.INSL | 40835492 | LAKEVLLE |  | 2020-04-23 | 2021-04-05 | ETL.2410 | MENDOCINO-REDBUD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40808923 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-09 | Glass | Suspension |  |  |  |  | 1.9217e-05 | 3958.4939
118971826 | F | LC | ETL.2060.POLE.NWOD | 44141375 | LAKEVLLE | HUMBOLDT | 2020-04-30 |  | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | PEND
118983984 | E | LC | ETL.7950.POLE.WOOD | 40612465 | METCALF | SAN JOSE | 2020-05-05 | 2021-02-10 | ETL.7950 | SAN MATEO-HILLSDALE JCT | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | HFRA Removal | COMP | 40612465 |  | Single Wood Pole | FIG4DDE - Figure 4 Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.028893 | 0.065147
119050120 | F | LC | ETL.6440.POLE.WOOD | 40825061 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-08-25 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825061 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.001343 | 4421.0889
119050120 | F | LC | ETL.6440.POLE.WOOD | 40825061 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-08-25 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825061 |  | Single Wood Pole | TP - Tri Pin |  | Non Ceramic | [5 empty] | 0.001343 | 4421.0889
119056334 | F | LC | ETL.6440.POLE.WOOD | 40752067 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-08-20 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752067 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0018684 | 4220.167
119084475 | E | LC | ETL.1050.TOWR | 40585033 | FRESNO | FRESNO | 2020-05-27 | 2021-06-29 | ETL.1050 | BALCH-SANGER | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585033 | 1923-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2019-04-02 | Ceramic | Dead End |  |  |  |  | 0.0027094 | 6295.1361
119084475 | E | LC | ETL.1050.TOWR | 40585033 | FRESNO | FRESNO | 2020-05-27 | 2021-06-29 | ETL.1050 | BALCH-SANGER | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585033 | 1923-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1923-01-01 | Porcelain | Dead End |  |  |  |  | 0.0027094 | 6295.1361
119085896 | E | LC | ETL.6470.POLE.WOOD | 40760414 | SACTO | SIERRA | 2020-05-29 | 2020-07-07 | ETL.6470 | COLGATE-ALLEGHANY | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760414 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.014415 | 1044.1248
119096618 | E | LC | ETL.5660.INSL | 40786486 | CONCORD | EAST BAY | 2020-05-22 | 2021-08-12 | ETL.5660 | SAN RAMON-MORAGA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119097178 | E | LC | ETL.8231.POLE.WOOD | 40679939 | VICTOR | STOCKTON | 2020-06-02 | 2021-01-20 | ETL.8231 | PARDEE #1 TAP | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40679939 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.0026504 | 5617.3223
119102049 | F | LC | ETL.6750.POLE.STPS | 44357227 | TABLEMTN |  | 2020-05-19 | 2021-07-20 | ETL.6750 | DELTA-MTN GATE JCT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44357225 | 2017-03-16 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00015588 | 316.4942
119115194 | E | LC | ETL.6760.POLE.WOOD | 40756216 | SACTO | SIERRA | 2020-05-28 | 2021-03-24 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756216 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.02819 | 142.4769
119116281 | E | LC | ETL.8650.TOWR | 40764105 | FRESNO | YOSEMITE | 2020-06-02 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40764105 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.006241 | 15.88
119116497 | F | LC | ETL.6950.POLE.WOOD | 44207061 | SACTO | SIERRA | 2020-05-28 | 2021-04-07 | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44207061 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.0060754 | 538.1728
119118658 | F | LC | ETL.1651.POLE.NWOD | 44865988 | LAKEVLLE | SONOMA | 2020-05-28 |  | ETL.1651 | MISSION POWER TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44865988 | 2019-11-10 | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper | 2019-11-10 | Glass | Suspension |  |  |  |  | 0.0056862 | 459.3529
119127500 | F | LC | ETL.7140.POLE.WOOD | 41111760 | LAKEVLLE | NORTH BAY | 2020-05-27 | 2020-11-10 | ETL.7140 | IGNACIO-BOLINAS #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119132043 | E | LC | ETL.6290.POLE.WOOD | 40675220 | TABLEMTN | NORTH VALLEY | 2020-06-09 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40675220 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.071877 | 4824.2021 | 346.75
119132425 | F | LC | ETL.8170.POLE.WOOD | 40906457 | EUREKA | HUMBOLDT | 2020-06-04 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906457 |  | Single Wood Pole | 3P DDE - 3 Pole Double Dead End | 2019-11-14 | Glass | Suspension |  |  |  |  | 0.046107 | 664.5661
119142430 | E | LC | ETL.1112.POLE.NWOD | 44420223 | FRESNO | YOSEMITE | 2020-06-04 |  | ETL.1112 | INDIAN FLAT-YOSEMITE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44420223 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Glass | Suspension |  |  |  |  | 0.0007353 | 6664.3394 | 4.9003
119158607 | F | LC | ETL.8170.POLE.WOOD | 40605815 | EUREKA | HUMBOLDT | 2020-06-02 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40605815 |  | Single Wood Pole | 3P DDE - 3 Pole Double Dead End |  | Ceramic | [5 empty] | 0.061156 | 4621.6372
119166002 | E | LC | ETL.8300.POLE.WOOD | 40657238 | TABLEMTN | NORTH VALLEY | 2020-06-11 | 2021-07-20 | ETL.8300 | VOLTA-SOUTH | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40657238 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.015945 | 6096.1982
119166149 | E | LC | ETL.8290.POLE.WOOD | 40669479 | TABLEMTN | NORTH VALLEY | 2020-06-11 | 2021-04-29 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119168096 | E | LC | ETL.1073.POLE.WOOD | 40643775 | VICTOR | YOSEMITE | 2020-06-15 | 2021-03-17 | ETL.1073 | MI-WUK-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40643775 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0001415
119168096 | E | LC | ETL.1073.POLE.WOOD | 40643775 | VICTOR | YOSEMITE | 2020-06-15 | 2021-03-17 | ETL.1073 | MI-WUK-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40643775 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0001415
119170290 | F | LC | ETL.6480.POLE.WOOD | 40757198 | SACTO | NORTH VALLEY | 2020-06-15 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40757198 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.39201 | 2072.3279
119179069 | F | LC | ETL.1073.POLE.WDPS | 44962141 | VICTOR | YOSEMITE | 2020-06-16 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40803739 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00014147 | 19.0429
119183687 | E | LC | ETL.2730.INSL | 40577583 | CONCORD | EAST BAY | 2020-06-16 | 2021-06-10 | ETL.2730 | MORAGA-OAKLAND #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119185999 | E | LC | ETL.7300.POLE.WOOD | 40668421 | TABLEMTN |  | 2020-06-16 | 2021-08-17 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40668421 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00031537 | 3905.6172
119195362 | F | LC | ETL.6470.POLE.WOOD | 40598667 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40598667 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.046945 | 269.0426
119196248 | F | LC | ETL.3530.TOWR | 40751316 | PISMOBCH | LOS PADRES | 2020-06-16 | 2021-03-06 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40751316 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1952-01-01 | Porcelain | Suspension |  |  |  |  | 4.9093e-06 | 1745.2675
119203173 | E | LC | ETL.5440.POLE.WDPS | 44558239 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-09-17 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44557935 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0027324 | 969.4996
119204894 | E | LC | ETL.6979.POLE.WDPS | 44762512 | LAKEVLLE |  | 2020-06-23 | 2021-06-15 | ETL.6979 | MONTE RIO-FORT ROSS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44312202 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0010338 | 174.1901
119204894 | E | LC | ETL.6979.POLE.WDPS | 44762512 | LAKEVLLE |  | 2020-06-23 | 2021-06-15 | ETL.6979 | MONTE RIO-FORT ROSS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44312202 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0010338 | 174.1901
119231724 | F | LC | ETL.8060.POLE.WOOD | 40818852 | SACTO | SIERRA | 2020-06-29 | 2021-01-26 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 0.059897 | 31.7066
119235495 | E | LC | ETL.7300.POLE.WOOD | 40656957 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2021-03-17 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119235802 | F | LC | ETL.8060.POLE.WOOD | 40586102 | SACTO | SIERRA | 2020-06-29 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586102 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.05494 | 31.7066
119294217 | F | LC | ETL.4221.POLE.WDPS | 44565812 | TABLEMTN |  | 2020-06-30 | 2020-08-24 | ETL.4221 | SLY CREEK TAP | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44558453 |  | 2-Pole Wood | 2P DDE-A - 2 Pole Double Dead End Angle | [7 empty] | 0.0013221 | 79.1467
119302178 | F | LC | ETL.8170.POLE.WDPS | 44752428 | EUREKA | HUMBOLDT | 2020-07-02 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40861547 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.2659 | 284.7712
119312975 | B | LC | ETL.7160.TOWR | 40701449 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-09-21 | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40701449 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | [5 empty] | 0.069878 | 15.8851
119312975 | B | LC | ETL.7160.TOWR | 40701449 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-09-21 | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40701449 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | [5 empty] | 0.069878 | 15.8851
119317801 | F | LC | ETL.7270.POLE.WOOD | 40908549 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908549 |  | Single Wood Pole | T2N | 2020-02-26 | Polymer | Post |  |  |  |  | 0.0049078 | 1794.3202
119326222 | E | LC | ETL.6880.POLE.NWOD | 40912452 | LAKEVLLE | SONOMA | 2020-07-07 | 2020-08-05 | ETL.6880 | FULTON-CALISTOGA | Vegetation | Overgrown | [Trim, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40912452 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.00013253 | 4748.4502
119329458 | E | LC | ETL.8170.POLE.WDPS | 44769573 | EUREKA | HUMBOLDT | 2020-07-07 | 2021-06-10 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906466 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.029769 | 0.065152
119333462 | B | LC | ETL.6280.POLE.WOOD | 40600606 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2020-10-27 | ETL.6280 | CARIBOU #2 | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600606 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 0.00027402 | 174.0445
119336118 | F | LC | ETL.7930.POLE.WOOD | 40666632 | MOSSLNDG | CENTRAL COAST | 2020-07-09 |  | ETL.7930 | SALINAS-LAURELES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40666632 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0014703 | 79.5225
119341842 | F | LC | ETL.2540.POLE.NWOD | 44149925 | MOSSLNDG | SAN JOSE | 2020-07-08 |  | ETL.2540 | METCALF-GREEN VALLEY | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44149925 |  | Tubular Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 3.1055e-06 | 15.9053
119357442 | F | LC | ETL.1450.POLE.WOOD | 44150221 | SACTO | SIERRA | 2020-07-10 | 2021-07-06 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44150221 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.00034241 | 0.065152
119368173 | E | LC | ETL.1440.POLE.WDPS | 44768910 | SACTO | SACRAMENTO | 2020-07-13 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40609285 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0114 | 31.7066
119373469 | E | LC | ETL.6880.POLE.WDPS | 44286449 | LAKEVLLE | SONOMA | 2020-07-15 | 2021-04-05 | ETL.6880 | FULTON-CALISTOGA | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 3 | Within Both | COMP | 44286446 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0022828 | 1219.0785
119373507 | F | LC | ETL.6280.POLE.WOOD | 40769621 | TABLEMTN | NORTH VALLEY | 2020-07-14 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40769621 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Other |  |  |  |  | 3.881e-05 | 5520.0938
119374829 | F | LC | ETL.7170.POLE.WOOD | 44871195 | LAKEVLLE | NORTH BAY | 2020-07-14 |  | ETL.7170 | IGNACIO-ALTO-SAUSALITO #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871195 | 2019-09-19 | Single Wood Pole | 3HP - 3 Horizontal Post | 2019-09-19 | Polymer | Post |  |  |  |  | 0.29138 | 205.9363
119374844 | F | LC | ETL.1240.POLE.STPS | 44924640 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2020-07-27 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44924569 | 2020-03-31 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.9567e-09 | 2441.9417
119467297 | E | LC | ETL.6222.POLE.WOOD | 40700552 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6222 | FORT SEWARD TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40700552 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0092799
119469337 | F | LC | ETL.7030.POLE.WOOD | 40601697 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-07-08 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601697 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.03145 | 6610.0464
119474949 | E | LC | ETL.1450.POLE.WDPS | 44559002 | SACTO | SACRAMENTO | 2020-07-16 | 2020-08-05 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119483361 | E | LC | ETL.4050.POLE.WOOD | 40750649 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-04-15 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119488216 | E | LC | ETL.8170.POLE.NWOD | 44630140 | EUREKA | HUMBOLDT | 2020-07-22 | 2021-06-08 | ETL.8170 | TRINITY-MAPLE CREEK | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44630140 | 2018-06-07 | Light Duty Steel Pole | T2N | 2018-06-07 | Polymer | Post |  |  |  |  | 0.00032437 | 727.8519
119492630 | E | LC | ETL.8405.POLE.WOOD | 40589957 | SACTO | SACRAMENTO | 2020-07-23 | 2021-04-27 | ETL.8405 | MIDDLE FORK #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40589957 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0023638 | 2246.6448
119513703 | E | LC | ETL.6030.TOWR | 40648042 | MIDWAY | KERN | 2020-07-27 | 2020-12-21 | ETL.6030 | MIDWAY-WHIRLWIND | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648042 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-12-09 | Glass Silicone Coated | Suspension |  |  |  |  | 3.4984e-06 | 7017.4551
119553812 | E | LC | ETL.5650.INSL | 40619622 | TABLEMTN | NORTH VALLEY | 2020-08-03 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40593780 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 5.5227e-08 | 1285.8232 | 7.1012e-05
119578403 | E | LC | ETL.7490.POLE | 40591312 | EUREKA | HUMBOLDT | 2020-08-07 | 2021-08-12 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 40591312 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 0.2275 | 3.2297
119582172 | A | LC | ETL.6230.POLE.WOOD | 40618224 | MOSSLNDG | CENTRAL COAST | 2020-08-09 | 2020-08-12 | ETL.6230 | BURNS-LONE STAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119600581 | E | LC | ETL.9210.POLE.WOOD | 42696712 | MIDWAY | KERN | 2020-08-11 |  | ETL.9210 | TAFT-CUYAMA #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 42696712 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Pin |  |  |  |  | 0.028774
119608882 | E | LC | ETL.7490.POLE.WOOD | 40662154 | EUREKA | HUMBOLDT | 2020-08-08 | 2021-07-26 | ETL.7490 | MAPLE CREEK-HOOPA | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40662154 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.73152
119608882 | E | LC | ETL.7490.POLE.WOOD | 40662154 | EUREKA | HUMBOLDT | 2020-08-08 | 2021-07-26 | ETL.7490 | MAPLE CREEK-HOOPA | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40662154 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.73152
119627013 | E | LC | ETL.7380.POLE.WOOD | 40701567 | MOSSLNDG | CENTRAL COAST | 2020-08-17 | 2021-08-19 | ETL.7380 | LAURELES-OTTER | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40701567 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.12411 | 1693.2699
119637860 | E | LC | ETL.1450.POLE.WDPS | 44553754 | SACTO | SACRAMENTO | 2020-08-18 | 2021-08-12 | ETL.1450 | DRUM-SUMMIT #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553189 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0023818 | 174.093
119642134 | E | LC | ETL.1440.POLE.WOOD | 40814118 | SACTO | SACRAMENTO | 2020-08-20 | 2021-03-12 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL | [11 empty] | 0.00025215
119648676 | E | LC | ETL.3800.TOWR | 40804893 | CONCORD | EAST BAY | 2020-08-20 | 2021-05-10 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40804893 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.8876e-07 | 63.3304
119669061 | E | LC | ETL.7490.POLE.WOOD | 40701781 | EUREKA | HUMBOLDT | 2020-08-25 |  | ETL.7490 | MAPLE CREEK-HOOPA | Vegetation | Overgrown | [Trim] | Tier3 | Tier 3 | Within Both | PEND | 40701781 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.40849 | 0.065148 | 0.026613
119675910 | F | LC | ETL.1420.TOWR | 40866014 | SACTO | SACRAMENTO | 2020-08-26 | 2021-02-16 | ETL.1420 | DRUM-RIO OSO #1 | Marker (i.e. signs)-Steel | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40866014 | 1965-01-01 | LATTICE STEEL TOWER | FDDE - Flat Dead End Construction | 1965-01-01 | Porcelain | Dead End |  |  |  |  | 7.6678e-07 | 553.7902
119681560 | F | LC | ETL.5090.TOWR | 40662892 | MOSSLNDG | DE ANZA | 2020-08-25 | 2021-01-12 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40662892 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.03839 | 474.7087
119719935 | E | LC | ETL.6470.POLE.WOOD | 40824242 | SACTO | SIERRA | 2020-08-05 | 2021-05-23 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40824242 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0072058 | 1850.8561
119720300 | E | LC | ETL.2060.INSL | 40902038 | LAKEVLLE | HUMBOLDT | 2020-06-22 | 2021-08-12 | ETL.2060 | FORT BRAGG-ELK | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119721230 | E | LC | ETL.6470.INSL.CERA | 40898089 | SACTO | SACRAMENTO | 2020-08-10 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119721863 | A | LC | ETL.7590.POLE.WOOD | 40583307 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-09-30 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119722589 | F | LC | ETL.6440.POLE.WOOD | 44191459 | TABLEMTN | NORTH VALLEY | 2020-08-04 | 2021-04-21 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191459 |  | Single Wood Pole | TH - TriAngle Post 70 | [7 empty] | 0.0017843 | 3756.4604
119723871 | F | LC | ETL.6950.POLE.WOOD | 40697213 | SACTO | SIERRA | 2020-08-07 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40697213 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.00038617 | 3591.1831
119726023 | E | LC | ETL.8170.POLE.WDPS | 44420637 | EUREKA | HUMBOLDT | 2020-08-12 |  | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | PEND | 44420634 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.010105 | 31.7207 | 0.32053
119743766 | E | LC | ETL.3960.INSL.CERA | 40829438 | PISMOBCH | LOS PADRES | 2020-09-10 | 2021-07-28 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119750271 | E | LC | ETL.4221.POLE.WDPS | 44356487 | TABLEMTN |  | 2020-08-18 | 2021-04-22 | ETL.4221 | SLY CREEK TAP | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 42564583 | 2016-11-26 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00044268 | 316.4165
119754035 | A | LC | ETL.1710.INSL | 40844052 | MOSSLNDG | CENTRAL COAST | 2020-09-03 | 2021-06-08 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Emergency-Steel | Other | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119780907 | F | LC | ETL.8240.POLE.WOOD | 40864370 | VICTOR | STOCKTON | 2020-09-12 |  | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40864370 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0095067 | 1550.8043
119786157 | E | LC | ETL.4392.INSL.NCER | 40676581 | LAKEVLLE | SONOMA | 2020-09-15 | 2021-04-17 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119790514 | F | LC | ETL.7560.POLE.WOOD | 40767411 | SACTO | SIERRA | 2020-08-03 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40767411 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.14911 | 205.8196
119798855 | E | LC | ETL.1430.INSL | 40774252 | SACTO | SACRAMENTO | 2020-09-21 | 2021-03-15 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119808520 | F | LC | ETL.1400.POLE.STPS | 44384133 | VICTOR | YOSEMITE | 2020-08-13 | 2020-10-13 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | DLFL | 44384132 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.7304e-05 | 31.7081
119822447 | F | LC | ETL.8580.TOWR | 40690774 | FRESNO | FRESNO | 2020-09-25 | 2020-12-18 | ETL.8580 | COALINGA #1-SAN MIGUEL | Marker (i.e. signs)-Steel | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40690774 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Porcelain | Dead End |  |  |  |  | 9.182e-07
119825191 | E | LC | ETL.8580.TOWR | 40748092 | FRESNO | FRESNO | 2020-09-28 | 2021-11-15 | ETL.8580 | COALINGA #1-SAN MIGUEL | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40748092 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.001059
119845281 | E | LC | ETL.6330.POLE.WOOD | 40656590 | TABLEMTN | NORTH VALLEY | 2020-09-15 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40656590 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.005395 | 3216.668 | 17.354
119848510 | F | LC | ETL.6880.POLE.NWOD | 44877346 | LAKEVLLE | SONOMA | 2020-09-09 | 2021-01-20 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44877346 | 2019-08-14 | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-08-14 | Glass | Suspension |  |  |  |  | 1.1913e-05 | 142.5961
119856580 | B | LC | ETL.7030.INSL | 40718831 | TABLEMTN | NORTH VALLEY | 2020-10-05 | 2020-11-04 | ETL.7030 | HAT CREEK #1-WESTWOOD | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119899360 | F | LC | ETL.6380.POLE.NWOD | 44667812 | LAKEVLLE | HUMBOLDT | 2020-10-07 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44667812 | 2018-10-31 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-10-31 | Polymer | Dead End |  |  |  |  | 2.2505e-07 | 4893.2662
119928854 | E | LC | ETL.6240.POLE.WOOD | 44991777 | MOSSLNDG | CENTRAL COAST | 2020-10-20 | 2021-06-23 | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44991777 | 2020-09-19 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2020-09-19 | Glass | Suspension |  |  |  |  | 0.1762 | 15.8866
120071386 | B | LC | ETL.8580.INSL.CERA | 40613560 | PISMOBCH | LOS PADRES | 2020-11-17 | 2020-12-22 | ETL.8580 | COALINGA #1-SAN MIGUEL | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120084881 | F | LC | ETL.6280.POLE.NWOD | 40769523 | TABLEMTN | NORTH VALLEY | 2020-11-20 | 2021-02-10 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40769523 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-12-11 | Polymer | Dead End |  |  |  |  | 6.7215e-06 | 0.065148
120114689 | F | LC | ETL.5630.POLE.STPS | 44727539 | TABLEMTN | NORTH VALLEY | 2020-11-24 |  | ETL.5630 | ROCK CREEK-POE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40591374 |  | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 1.112e-09 | 63.3704
120143892 | F | LC | ETL.8960.POLE.WDPS | 45020876 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40764171 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00052547
120160683 | E | LC | ETL.1110.TOWR | 40657081 | EUREKA | HUMBOLDT | 2020-12-09 | 2021-06-23 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40657081 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-08-29 | Ceramic | Suspension |  |  |  |  | 6.7914e-05 | 0.066432
120160683 | E | LC | ETL.1110.TOWR | 40657081 | EUREKA | HUMBOLDT | 2020-12-09 | 2021-06-23 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40657081 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-07-20 | Ceramic | Suspension |  |  |  |  | 6.7914e-05 | 0.066432
120160876 | F | LC | ETL.6621.TOWR | 44812745 | TABLEMTN | NORTH VALLEY | 2020-12-10 |  | ETL.6621 | OROVILLE-THERMALITO-TABLE MTN #1 (CDWR) | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44812745 |  | LATTICE STEEL TOWER |  |  | Glass | Suspension |  |  |  |  | 9.5538e-07 | 1324.893
120211009 | F | LC | ETL.1810.TOWR | 40757794 | EUREKA | HUMBOLDT | 2020-11-10 | 2021-01-27 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40757794 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Porcelain | Suspension |  |  |  |  | 2.6268e-05
120232354 | F | LC | ETL.6220.POLE.WOOD | 40698350 | EUREKA | HUMBOLDT | 2020-11-20 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40698350 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Pin |  |  |  |  | 0.15632
120238245 | F | LC | ETL.7140.POLE.WOOD | 41111801 | LAKEVLLE | NORTH BAY | 2020-12-02 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
120241183 | F | LC | ETL.5463.TOWR | 40862985 | CONCORD | DIABLO | 2020-12-04 | 2021-04-05 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862985 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 2.9673e-08 | 5228.478
120243186 | F | LC | ETL.5630.POLE.NWOD | 40589907 | TABLEMTN | NORTH VALLEY | 2020-12-10 | 2021-04-02 | ETL.5630 | ROCK CREEK-POE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40589907 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle | 1958-01-01 | Non Ceramic | Dead End |  |  |  |  | 2.5606e-05 | 6034.1842
120243308 | E | LC | ETL.1450.POLE.WDPS | 44553636 | SACTO | SACRAMENTO | 2020-12-31 | 2021-09-22 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553188 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.132 | 3274.9534
120648106 | B | LC | ETL.4680.TOWR | 40658940 | LAKEVLLE | SONOMA | 2021-03-16 | 2021-04-30 | ETL.4680 | FULTON-IGNACIO #1 | Other | Customer Issue | [Access Issue] | Tier3 | Tier 3 | Within Both | COMP | 40658940 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 5.1026e-05 | 221.6343
120680761 | E | LC | ETL.3700.POLE.WOOD | 40771456 | PISMOBCH | LOS PADRES | 2021-03-22 | 2021-11-29 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771456 | 1989-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 1989-01-01 | Porcelain | Suspension |  |  |  |  | 4.586e-05 | 4891.9976 | 0.22435
120689194 | E | LC | ETL.5660.INSL | 40786486 | CONCORD | EAST BAY | 2021-03-25 | 2021-08-11 | ETL.5660 | SAN RAMON-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
120712121 | E | LC | ETL.4620.INSL | 40578132 | PISMOBCH | LOS PADRES | 2021-03-26 |  | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40576200 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 6.3987e-07 | 650.8898 | 0.00041648
120714914 | B | LC | ETL.5090.INSL | 40886929 | MOSSLNDG | CENTRAL COAST | 2021-03-30 | 2021-06-10 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40863204 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.053345 | 189.9226
120714959 | E | LC | ETL.5980.TOWR | 40587696 | PISMOBCH | LOS PADRES | 2021-03-29 | 2021-04-15 | ETL.5980 | DIABLO-MIDWAY #3 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40587696 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.0434e-09 | 1550.9055
120715817 | F | LC | ETL.7380.POLE.WOOD | 40668287 | MOSSLNDG | CENTRAL COAST | 2021-03-30 |  | ETL.7380 | LAURELES-OTTER | Road | Brush Fuel | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40668287 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.12985 | 1693.2699
120717282 | E | LC | ETL.5780.TOWR | 40811159 | VICTOR | STOCKTON | 2021-03-30 | 2021-04-13 | ETL.5780 | TIGER CREEK-ELECTRA | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40811159 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 0.00068133 | 1202.2845
120725607 | E | LC | ETL.7140.POLE.WOOD | 40668079 | LAKEVLLE | SONOMA | 2021-04-01 | 2021-09-08 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.014769 | 4211.6216
120743017 | E | LC | ETL.8365.POLE.WOOD | 40584840 | EUREKA | HUMBOLDT | 2021-04-05 | 2021-04-20 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40584840 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | Pin |  |  |  |  | 0.0040727 | 297.504
120744981 | F | LC | ETL.5790.TOWR | 40756172 | VICTOR | STOCKTON | 2021-03-24 |  | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40756172 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 1.186e-05 | 2009.0664 | 0.023827
120745359 | E | LC | ETL.2540.POLE.WDPS | 44401496 | MOSSLNDG | CENTRAL COAST | 2021-04-05 | 2021-07-19 | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120750163 | E | LC | ETL.6721.POLE.WOOD | 40751729 | TABLEMTN | NORTH VALLEY | 2021-03-30 |  | ETL.6721 | ORO FINO TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40751729 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.0028068 | 79.1651 | 0.2222
120750828 | E | LC | ETL.7590.POLE.NWOD | 45037612 | MOSSLNDG | CENTRAL COAST | 2021-04-06 |  | ETL.7590 | MONTA VISTA-BURNS | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45037612 | 2020-09-19 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-09-19 | Glass | Dead End |  |  |  |  | 0.57902 | 63.351 | 36.6815
120756733 | B | LC | ETL.7140.POLE.WOOD | 40588056 | LAKEVLLE | SONOMA | 2021-04-07 | 2021-07-06 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40588056 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.14837 | 4560.6943
120757713 | E | LC | ETL.5970.INSL | 40839495 | PISMOBCH | LOS PADRES | 2021-04-07 | 2021-04-15 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
120769752 | E | LC | ETL.3960.INSL.CERA | 40603454 | PISMOBCH | LOS PADRES | 2021-04-09 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40579868 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 2.645e-07 | 5474.0403 | 0.0014479
120769752 | E | LC | ETL.3960.INSL.CERA | 40603454 | PISMOBCH | LOS PADRES | 2021-04-09 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40579868 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 2.645e-07 | 5474.0403 | 0.0014479
120786420 | E | LC | ETL.2900.TOWR | 40591366 | MOSSLNDG | CENTRAL COAST | 2021-04-10 | 2021-07-26 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591366 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2007-01-01 | Porcelain | Suspension |  |  |  |  | 0.0046082 | 428.4953
120793900 | E | LC | ETL.6030.TOWR | 40860572 | MIDWAY | KERN | 2021-04-12 |  | ETL.6030 | MIDWAY-WHIRLWIND | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40860572 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 5.1355e-06 | 6764.2437 | 0.034738
120795923 | F | LC | ETL.4100.TOWR | 40812934 | LAKEVLLE | SONOMA | 2021-04-12 | 2021-04-29 | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | DLFL | 40812934 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2018-05-29 | Glass Silicone Coated | Suspension |  |  |  |  | 6.8826e-09 | 5430.7744
120800243 | E | LC | ETL.3820.TOWR | 40607305 | VICTOR | STOCKTON | 2021-04-12 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40607305 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | [5 empty] | 3.4517e-06 | 4353.7114 | 0.015028
120806287 | E | LC | ETL.7140.POLE.WOOD | 41118234 | LAKEVLLE | SONOMA | 2021-04-13 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41118234 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.011717 | 94.9668 | 1.1127
120820746 | E | LC | ETL.4316.INSL.CERA | 40720804 | TABLEMTN |  | 2021-04-09 | 2021-07-27 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120823659 | E | LC | ETL.1073.POLE.WDPS | 44774771 | VICTOR | STOCKTON | 2021-04-15 |  | ETL.1073 | MI-WUK-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40660477 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00051048 | 31.7081 | 0.016186
120824145 | B | LC | ETL.7180.SWIT | 44963456 | LAKEVLLE | SONOMA | 2021-04-15 | 2021-05-11 | ETL.7180 | IGNACIO-BOLINAS #2 | Switch | Out of Adjustment | [Repair, Completed] | Tier2 |  |  | COMP | [7 empty] | 2020-05-04 | SEECO | VACUUM INTERRUPTER (3 GAP) | SCADA Only
120834410 | E | LC | ETL.9340.POLE.WOOD | 40748455 | FRESNO | FRESNO | 2021-04-17 | 2021-10-21 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.016049 | 5176.5 | 83.0791
120834565 | E | LC | ETL.2740.POLE.NWOD | 44367706 | CONCORD | DIABLO | 2021-04-17 |  | ETL.2740 | MORAGA-OAKLAND #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44367706 |  | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 7.2356e-05 | 0.065158 | 4.7146e-06
120836014 | E | LC | ETL.3500.TOWR | 40803569 | VICTOR | STOCKTON | 2021-04-17 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40803569 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 5.4541e-06 | 1740.3693 | 0.0094922
120844779 | B | LC | ETL.4880.INSL | 40881230 | FRESNO | FRESNO | 2021-04-19 | 2021-06-07 | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40858331 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.8357e-08 | 5240.2021
120858016 | E | LC | ETL.4590.TOWR | 40910154 | TABLEMTN | NORTH VALLEY | 2021-04-20 |  | ETL.4590 | CRESTA-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40910154 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.9556e-05 | 0.065151 | 3.2287e-06
120859466 | E | LC | ETL.1110.POLE.WDPS | 44424411 | TABLEMTN | NORTH VALLEY | 2021-04-21 | 2021-07-06 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
120875677 | E | LC | ETL.5390.TOWR | 40677461 | TABLEMTN | NORTH VALLEY | 2021-04-23 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40677461 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Dead End |  |  |  |  | 7.8272e-07 | 206.0313 | 0.00016127
120876488 | E | LC | ETL.4040.POLE.NWOD | 45006473 | TABLEMTN | NORTH VALLEY | 2021-04-23 |  | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45006473 | 2020-09-18 | Light Duty Steel Pole | 3P DV - 3 Pole Double Vertical | 2020-09-18 | Ceramic | Dead End - Suspension |  |  |  |  | 0.0011693 | 79.1724 | 0.092573
120882270 | B | LC | ETL.5090.INSL | 40714120 | MOSSLNDG | CENTRAL COAST | 2021-04-23 | 2021-05-26 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40662900 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.010758 | 465.2803
120891039 | E | LC | ETL.3960.TOWR | 40809249 | PISMOBCH | LOS PADRES | 2021-04-27 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40809249 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension | [5 empty] | 2123.9971
120906885 | F | LC | ETL.6020.TOWR | 40753301 | TABLEMTN | NORTH VALLEY | 2021-04-29 |  | ETL.6020 | MALIN-ROUND MTN #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40753301 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 9.9361e-05 | 569.8778 | 0.056624
120907884 | E | LC | ETL.6020.TOWR | 40753364 | TABLEMTN | NORTH VALLEY | 2021-04-30 |  | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753364 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00029009 | 2487.2815 | 0.72153
120910698 | F | LC | ETL.7550.POLE.WOOD | 40861423 | LAKEVLLE | SONOMA | 2021-04-30 | 2021-06-30 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40861423 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0012095 | 2025.4416
120922304 | E | LC | ETL.1250.POLE.NWOD | 40748529 | FRESNO | FRESNO | 2021-05-03 | 2021-11-02 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Vegetation | Overgrown | [Trim, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40748529 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.3974e-06 | 4148.9409 | 0.0057976
120940115 | E | LC | ETL.2740.INSL.NCER | 40828532 | CONCORD | DIABLO | 2021-05-05 |  | ETL.2740 | MORAGA-OAKLAND #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40804641 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1960-01-01 | Polymer | Suspension |  |  |  |  | 0.00011193 | 0.065147 | 7.292e-06
121129534 | E | LC | ETL.7550.POLE.WOOD | 40826143 | LAKEVLLE | SONOMA | 2021-05-08 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40826143 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 1.1597e-05 | 854.1058 | 0.0099054
121317005 | E | LC | ETL.7550.POLE.WDPS | 44837684 | LAKEVLLE | SONOMA | 2021-05-03 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40809291 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00097131 | 110.7947 | 0.10762
121322206 | E | LC | ETL.6020.TOWR | 40576654 | TABLEMTN | NORTH VALLEY | 2021-05-12 |  | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576654 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.5611e-08 | 253.2084 | 3.9527e-06
121323644 | E | LC | ETL.7060.INSL | 40682275 | METCALF | SAN JOSE | 2021-05-12 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40653284 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Non Ceramic | Other |  |  |  |  | 9.5063e-05 | 752.0984 | 0.071497
121332879 | F | LC | ETL.4440.TOWR | 40660506 | TABLEMTN | NORTH VALLEY | 2021-05-14 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40660506 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.00016132 | 3638.1943 | 0.58691
121336331 | F | LC | ETL.4316.TOWR | 40871568 | TABLEMTN | NORTH VALLEY | 2021-04-15 |  | ETL.4316 | PARADISE-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40871568 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-11-18 | Glass | Suspension |  |  |  |  | 0.0029119 | 4386.7925 | 12.7738
121339057 | F | LC | ETL.4410.TOWR | 40870203 | CONCORD | DIABLO | 2021-04-26 | 2021-09-14 | ETL.4410 | BRENTWOOD-KELSO | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870203 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-03 | Glass | Suspension |  |  |  |  | 4.6487e-07 | 4101.8267
121339057 | F | LC | ETL.4410.TOWR | 40870203 | CONCORD | DIABLO | 2021-04-26 | 2021-09-14 | ETL.4410 | BRENTWOOD-KELSO | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870203 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 4.6487e-07 | 4101.8267
121346211 | E | LC | ETL.1430.INSL | 40922926 | SACTO | SACRAMENTO | 2021-05-12 |  | ETL.1430 | DRUM-RIO OSO #2 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40913082 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical | 1989-01-01 | Ceramic | Post |  |  |  |  | 0.001041 | 553.7902 | 0.57649
121346930 | E | LC | ETL.5920.INSL | 40686430 | CONCORD | EAST BAY | 2021-04-29 |  | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40656762 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Dead End |  |  |  |  | 2.352e-05 | 4660.7414 | 0.10962
121346930 | E | LC | ETL.5920.INSL | 40686430 | CONCORD | EAST BAY | 2021-04-29 |  | ETL.5920 | TASSAJARA-NEWARK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40656762 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.352e-05 | 4660.7414 | 0.10962
121347808 | F | LC | ETL.3742.POLE.NWOD | 40575707 | CONCORD | DIABLO | 2021-04-24 |  | ETL.3742 | SOBRANTE-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40575707 | 1947-01-01 | Lattice Steel Pole | DDE - Double Dead End | 1947-01-01 | Ceramic | Other |  |  |  |  | 2.0218e-05 | 458.8659 | 0.0092775
121348344 | E | LC | ETL.4870.TOWR | 40576902 | FRESNO | FRESNO | 2021-05-17 |  | ETL.4870 | HELMS-GREGG #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40576902 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 6.317e-09 | 414.4015 | 2.6178e-06
121350194 | B | LC | ETL.7930.INSL.NCER | 40791380 | MOSSLNDG | CENTRAL COAST | 2021-05-17 | 2021-07-01 | ETL.7930 | SALINAS-LAURELES | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761087 |  | Tubular Steel Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Post |  |  |  |  | 0.0001241 | 238.1463
121356969 | F | LC | ETL.4870.TOWR | 40576624 | FRESNO | FRESNO | 2021-05-18 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576624 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.8363e-08 | 5867.9263 | 0.00028379
121379795 | B | LC | ETL.4440.TOWR | 40593731 | TABLEMTN | NORTH VALLEY | 2021-05-22 | 2021-06-29 | ETL.4440 | CARIBOU-TABLE MTN | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40593731 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2015-12-22 | Ceramic | Dead End |  |  |  |  | 8.1647e-05 | 3795.9778
121384668 | F | LC | ETL.8250.POLE.WOOD | 44673345 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44673345 | 2018-11-08 | Single Wood Pole | T-1 - Tri Post | 2018-11-08 | Polymer | Post |  |  |  |  | 3.6838e-05 | 2852.8489
121385125 | F | LC | ETL.1430.TOWR | 40913091 | SACTO | SIERRA | 2021-05-12 |  | ETL.1430 | DRUM-RIO OSO #2 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40913091 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-11-15 | Glass | Suspension |  |  |  |  | 0.0049224 | 553.7902 | 2.726
121385657 | E | LC | ETL.6760.POLE.WOOD | 40865387 | SACTO | SIERRA | 2021-05-13 | 2021-06-24 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL | [12 empty] | 110.8102
121395448 | F | LC | ETL.8060.POLE.WOOD | 44349544 | SACTO | SIERRA | 2021-05-17 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44349544 | 2018-09-06 | Single Wood Pole | T2N | 2018-09-06 | Polymer | Post |  |  |  |  | 0.003606 | 427.2245
121417758 | F | LC | ETL.8250.POLE.WOOD | 40908852 | VICTOR | STOCKTON | 2021-05-21 | 2021-09-22 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908852 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2009-01-01 | Polymer | Post |  |  |  |  | 0.0004856 | 444.527
121417902 | E | LC | ETL.6979.POLE.WOOD | 40648462 | LAKEVLLE | SONOMA | 2021-05-27 | 2021-08-02 | ETL.6979 | MONTE RIO-FORT ROSS | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40648462 | 1998-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1998-01-01 | Polymer | Post |  |  |  |  | 0.039975 | 2117.6331
121420610 | E | LC | ETL.1710.POLE.STPS | 44879499 | MOSSLNDG | CENTRAL COAST | 2021-05-25 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44879475 | 2019-07-27 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 6.1109e-07 | 63.3245 | 3.8697e-05
121453849 | E | LC | ETL.1350.POLE.WDPS | 44513815 | TABLEMTN |  | 2021-05-29 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44512283 | 2012-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0019596 | 3880.9729 | 7.6052
121466480 | E | LC | ETL.5140.POLE.WDPS | 44337488 | SACTO | SACRAMENTO | 2021-05-29 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44337486 | 2017-03-15 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0028046 | 316.5174 | 0.88772
121466546 | E | LC | ETL.1810.POLE.WDPS | 44322704 | EUREKA | HUMBOLDT | 2021-06-03 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44322703 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 4.5956e-05 | 63.3274 | 0.0029103
121482024 | B | LC | ETL.1350.INSL.NCER | 44641675 | TABLEMTN |  | 2021-06-04 | 2021-07-22 | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549446 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 2018-08-22 | Glass | Suspension |  |  |  |  | 0.23654
121482024 | B | LC | ETL.1350.INSL.NCER | 44641675 | TABLEMTN |  | 2021-06-04 | 2021-07-22 | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549446 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 2018-08-22 | Glass | Suspension |  |  |  |  | 0.23654
121482564 | F | LC | ETL.1820.POLE.STPS | 44194938 | EUREKA | HUMBOLDT | 2021-05-28 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44194937 | 2014-09-20 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0016427 | 5206.4815
121485626 | F | LC | ETL.3740.TOWR | 44188754 | CONCORD | DIABLO | 2021-06-01 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44188754 | 2008-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | Dead End |  |  |  |  | 0.068226 | 445.731 | 30.4103
121485670 | F | LC | ETL.7550.POLE.WOOD | 40826155 | LAKEVLLE | HUMBOLDT | 2021-05-29 | 2021-07-01 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40826155 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00045837 | 4067.2947
121492754 | F | LC | ETL.5630.TOWR | 40810116 | TABLEMTN | NORTH VALLEY | 2021-06-02 | 2021-09-27 | ETL.5630 | ROCK CREEK-POE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40810116 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-09-18 | Ceramic | Double Dead End |  |  |  |  | 0.00023002 | 6493.0113
121499930 | F | LC | ETL.6890.POLE.WOOD | 40825399 | LAKEVLLE | SONOMA | 2021-06-02 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40825399 | 1977-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Other |  |  |  |  | 0.0018102 | 1836.4062
121513247 | F | LC | ETL.4040.POLE.WDPS | 44551407 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44550875 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.11649 | 174.3412
121522578 | F | LC | ETL.8350.POLE.NWOD | 44920057 | VICTOR | STOCKTON | 2021-06-08 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44920057 | 2020-01-15 | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper | 2020-01-15 | Polymer | Post |  |  |  |  | 8.9283e-07 | 101.2805
121523141 | F | LC | ETL.5640.TOWR | 40591311 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40591311 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 5.64e-06 | 3835.2644 | 0.021631
121523469 | E | LC | ETL.4040.POLE.WDPS | 44552482 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44551571 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.045394 | 1426.2432 | 64.7425
121524303 | E | LC | ETL.1350.POLE.WDPS | 44552490 | TABLEMTN |  | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44551620 |  | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.055284 | 79.1851 | 4.3776
121525280 | F | LC | ETL.1820.POLE.WDPS | 44557667 | EUREKA | HUMBOLDT | 2021-06-08 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44553880 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.81235 | 31.6978
121526572 | F | LC | ETL.1820.POLE.WDPS | 44560479 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44560069 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.5233 | 79.1467
121530681 | E | LC | ETL.1440.INSL.CERA | 42572964 | SACTO | SIERRA | 2021-06-12 | 2021-06-16 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
121536558 | F | LC | ETL.1070.POLE.NWOD | 45016529 | VICTOR | YOSEMITE | 2021-06-09 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45016529 | 2020-04-22 | Light Duty Steel Pole | T-1 - Tri Post | 2020-04-22 | Polymer | Post |  |  |  |  | 1.1354e-09 | 2376.3638
121536598 | F | LC | ETL.1600.POLE.NWOD | 45121243 | LAKEVLLE | NORTH BAY | 2021-06-09 |  | ETL.1600 | FULTON-PUEBLO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45121243 | 2020-10-04 | Light Duty Steel Pole | T-1 - Tri Post | 2020-10-04 | Polymer | Post | [5 empty] | 736.9064
121536774 | E | LC | ETL.5390.TOWR | 40820527 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40820527 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 8.2315e-06 | 1760.7263 | 0.014493
121537976 | F | LC | ETL.5390.TOWR | 41107615 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41107615 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 4.2716e-08 | 2283.4246
121542316 | F | LC | ETL.1820.POLE.STPS | 44395533 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395532 | 2020-03-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0082312 | 936.7255
121544296 | F | LC | ETL.1820.POLE.STPS | 44395381 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395380 | 2020-03-04 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.002921 | 363.9585
121544945 | E | LC | ETL.5420.POLE.WDPS | 44562770 | TABLEMTN | NORTH VALLEY | 2021-06-14 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562393 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.026582 | 411.4355 | 10.9368
121548383 | E | LC | ETL.4580.TOWR | 40684139 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40684139 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1956-01-01 | Porcelain | Suspension |  |  |  |  | 1.127e-05 | 4056.6345 | 0.04572
121548383 | E | LC | ETL.4580.TOWR | 40684139 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40684139 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 1.127e-05 | 4056.6345 | 0.04572
121548559 | E | LC | ETL.7640.INSL.NCER | 40735727 | TABLEMTN | NORTH VALLEY | 2021-06-16 | 2021-07-19 | ETL.7640 | MTN GATE JCT-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44564269 |  | 2-Pole Wood | TH - TriAngle Post 70 |  | Non Ceramic | Post |  |  |  |  | 9.7619e-05
121548559 | E | LC | ETL.7640.INSL.NCER | 40735727 | TABLEMTN | NORTH VALLEY | 2021-06-16 | 2021-07-19 | ETL.7640 | MTN GATE JCT-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44564269 |  | 2-Pole Wood | TH - TriAngle Post 70 |  | Non Ceramic | Post |  |  |  |  | 9.7619e-05
121556119 | E | LC | ETL.7390.POLE.WDPS | 44412032 | LAKEVLLE |  | 2021-06-09 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44412029 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.036649 | 2214.7324 | 81.1687
121560055 | E | LC | ETL.1810.INSL.NCER | 40854178 | EUREKA | HUMBOLDT | 2021-06-17 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44322619 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.0019289
121560055 | E | LC | ETL.1810.INSL.NCER | 40854178 | EUREKA | HUMBOLDT | 2021-06-17 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44322619 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.0019289
121574743 | E | LC | ETL.1350.POLE.WDPS | 44550037 | TABLEMTN |  | 2021-06-17 | 2021-07-12 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
121586226 | B | LC | ETL.8170.POLE.NWOD | 44846598 | EUREKA | HUMBOLDT | 2021-06-22 | 2021-08-30 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44846598 | 2019-05-10 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-05-10 | Glass | Dead End |  |  |  |  | 0.00024379 | 0.065152
121607273 | F | LC | ETL.7212.POLE.STPS | 44264957 | METCALF | PENINSULA | 2021-06-23 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44264956 | 2009-11-20 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.14481 | 704.4957
121628015 | E | LC | ETL.5640.POLE.WDPS | 44741490 | TABLEMTN |  | 2021-06-18 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44741475 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.01129 | 2947.0984 | 33.2735
121628934 | E | LC | ETL.5650.INSL.CERA | 44765637 | TABLEMTN |  | 2021-06-18 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44765635 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00047428
121628934 | E | LC | ETL.5650.INSL.CERA | 44765637 | TABLEMTN |  | 2021-06-18 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44765635 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00047428
121630570 | E | LC | ETL.1450.POLE.WDPS | 44159082 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44159080 | 2013-09-30 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00024162 | 387.6727 | 0.093668
121632977 | F | LC | ETL.8250.POLE.WOOD | 44681906 | VICTOR | STOCKTON | 2021-06-23 |  | ETL.8250 | CLAY-MARTEL | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44681906 | 2018-12-11 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2018-12-11 | Polymer | Dead End |  |  |  |  | 1.1371e-05 | 2614.054
121642241 | F | LC | ETL.6880.POLE.NWOD | 45072146 | LAKEVLLE | SONOMA | 2021-06-25 |  | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45072146 | 2020-03-05 | Lattice Steel Pole | TPSRD - Tramp Double Dead End | 2020-03-05 | Glass | Dead End |  |  |  |  | 0.0031836 | 110.9048
121659190 | E | LC | ETL.6050.TOWR | 40818954 | MOSSLNDG | CENTRAL COAST | 2021-06-30 | 2021-11-02 | ETL.6050 | MOSS LANDING-METCALF | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818954 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 2019-08-29 | Glass | Suspension |  |  |  |  | 1.6629e-05 | 490.5807 | 0.0081579
121662254 | E | LC | ETL.7550.POLE.WOOD | 40576084 | LAKEVLLE | HUMBOLDT | 2021-07-01 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40576084 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 5.3576e-05 | 142.4053 | 0.0076295
121715160 | B | LC | ETL.4410.INSL | 40781547 | CONCORD | DIABLO | 2021-07-12 | 2021-09-23 | ETL.4410 | BRENTWOOD-KELSO | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121717758 | E | LC | ETL.4430.TOWR | 40862115 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.4430 | BUCKS CREEK-ROCK CREEK-CRESTA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40862115 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0019842 | 6663.9917 | 13.2228
121724201 | E | LC | ETL.1400.POLE.WDPS | 44922053 | VICTOR | YOSEMITE | 2021-07-07 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40808192 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017827 | 31.7334 | 0.056571
121724202 | E | LC | ETL.1400.POLE.WDPS | 44922054 | VICTOR | YOSEMITE | 2021-07-07 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40808192 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017827 | 31.7334 | 0.056571
121731806 | B | LC | ETL.9250.INSL | 40881785 | MIDWAY | KERN | 2021-07-14 | 2021-08-31 | ETL.9250 | TEJON-LEBEC | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860211 | 1966-01-01 | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | Other |  |  |  |  | 0.013508 | 5260.3872
121738680 | E | LC | ETL.8300.POLE.NWOD | 40700132 | TABLEMTN | NORTH VALLEY | 2021-07-13 | 2021-08-04 | ETL.8300 | VOLTA-SOUTH | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40700132 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Non Ceramic | Pin |  |  |  |  | 0.00043073 | 4039.3728
121742937 | F | LC | ETL.1820.POLE.NWOD | 44976955 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44976955 | 2020-03-09 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-03-09 | Glass | Suspension |  |  |  |  | 0.00044363 | 348.0238
121745632 | E | LC | ETL.5330.INSL | 40724548 | MOSSLNDG | CENTRAL COAST | 2021-07-14 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40681549 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 8.9437e-06 | 4717.8997 | 0.042195
121745632 | E | LC | ETL.5330.INSL | 40724548 | MOSSLNDG | CENTRAL COAST | 2021-07-14 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40681549 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 8.9437e-06 | 4717.8997 | 0.042195
121749049 | E | LC | ETL.1820.POLE.NWOD | 45102852 | EUREKA | HUMBOLDT | 2021-07-14 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45102852 | 2014-09-20 | Light Duty Steel Pole | 3P SV - 3 Pole Single Vertical | 2014-09-20 | Ceramic | Suspension |  |  |  |  | 0.15192 | 47.5118 | 7.2182
121749732 | B | LC | ETL.7212.INSL.NCER | 45004780 | METCALF | PENINSULA | 2021-07-17 | 2021-08-16 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40867266 |  | Single Wood Pole | WB - Wishbone | 2020-11-24 | Glass | Dead End |  |  |  |  | 0.97513 | 602.2181
121750703 | F | LC | ETL.6220.POLE.WOOD | 40875275 | EUREKA | HUMBOLDT | 2021-07-17 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40875275 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Porcelain | [5 empty] | 0.059519
121754963 | F | LC | ETL.6880.POLE.NWOD | 45074104 | LAKEVLLE | NORTH BAY | 2021-07-19 |  | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45074104 | 2020-03-05 | Lattice Steel Pole | DC-DDE - Double Circuit Double Dead End | 2020-03-05 | Glass | Dead End |  |  |  |  | 2.6581e-07 | 31.7184
121755805 | F | LC | ETL.6020.TOWR | 40689267 | TABLEMTN | NORTH VALLEY | 2021-07-19 |  | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40689267 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.0061837 | 221.5655
121781809 | E | LC | ETL.2390.POLE.WDPS | 44391047 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391046 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.001057 | 3292.7512 | 3.4803
121785195 | E | LC | ETL.2395.POLE.WOOD | 44987811 | TABLEMTN | NORTH VALLEY | 2021-07-21 | 2021-07-29 | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44987811 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.00039397 | 2769.5249
121785872 | B | LC | ETL.6020.TOWR | 40576661 | TABLEMTN | NORTH VALLEY | 2021-07-22 | 2021-08-05 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40576661 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00013831 | 221.5655
121793951 | B | LC | ETL.9240.TOWR | 43249747 | PISMOBCH | LOS PADRES | 2021-07-25 | 2021-11-09 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 43249747 |  | LATTICE STEEL TOWER | [9 empty] | 197.9564
121796687 | F | LC | ETL.9240.TOWR | 43249526 | PISMOBCH | LOS PADRES | 2021-07-26 | 2021-10-14 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 43249526 |  | LATTICE STEEL TOWER | [9 empty] | 2931.7146
121801638 | E | LC | ETL.6480.POLE.WOOD | 40815339 | SACTO | SIERRA | 2021-07-26 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40815339 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.33853 | 3859.7815 | 1306.6371
121812955 | E | LC | ETL.8630.POLE.WDPS | 44565520 | PISMOBCH | LOS PADRES | 2021-07-28 |  | ETL.8630 | DIVIDE-VANDENBERG #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564229 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0004801 | 2924.0354 | 1.4038
121824437 | E | LC | ETL.1810.TOWR | 40598279 | EUREKA | HUMBOLDT | 2021-07-30 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Hardware-Tower | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40598279 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Porcelain | Suspension |  |  |  |  | 9.7335e-05
121824795 | F | LC | ETL.5630.POLE.NWOD | 40599069 | TABLEMTN | NORTH VALLEY | 2021-07-30 |  | ETL.5630 | ROCK CREEK-POE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40599069 |  | Lattice Steel Pole | DDE - Double Dead End | 1958-01-01 | Non Ceramic | Dead End |  |  |  |  | 2.8446e-05 | 1804.4395
121847315 | A | LC | ETL.6760.POLE.WOOD | 40824342 | SACTO | SACRAMENTO | 2021-08-05 | 2021-08-12 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
121879352 | E | LC | ETL.4040.POLE.WDPS | 44557652 | TABLEMTN | NORTH VALLEY | 2021-07-31 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553989 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.006721 | 2155.7725 | 14.4889
121882665 | B | LC | ETL.6300.POLE.WOOD | 40698896 | TABLEMTN | NORTH VALLEY | 2021-08-10 | 2021-09-08 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0013896 | 15.9447
122035897 | B | LC | ETL.7030.POLE.WOOD | 40616880 | TABLEMTN | NORTH VALLEY | 2021-09-10 | 2021-10-04 | ETL.7030 | HAT CREEK #1-WESTWOOD | Emergency | Fire | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40616880 |  | Single Wood Pole | T2N | 2021-05-14 | Polymer | Post |  |  |  |  | 0.047643 | 47.5207
122107256 | B | LC | ETL.6980.POLE.STPS | 44992229 | LAKEVLLE | SONOMA | 2021-07-30 | 2021-11-01 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44992220 | 2020-10-13 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.14065 | 47.5317 | 6.6853
122162814 | E | LC | ETL.4392.INSL.NCER | 40835405 | LAKEVLLE | SONOMA | 2021-10-07 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Emergency | Storm Related | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40808851 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 2.2018e-07 | 31.7331 | 6.9869e-06
122421794 | E | LC | ETL.1480.POLE.WOOD | 40585046 | LAKEVLLE | SONOMA | 2021-11-29 |  | ETL.1480 | EAGLE ROCK-REDBUD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40585046 | 1978-01-01 | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.00027628 | 0.065149 | 1.7999e-05
118437576 | E | LC | ETL.1240.POLE.WDPS | 44386179 | TABLEMTN | NORTH VALLEY | 2020-01-11 | 2020-04-28 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118527250 | E | LC | ETL.3742.POLE.NWOD | 40575709 | CONCORD | DIABLO | 2020-02-12 | 2020-04-10 | ETL.3742 | SOBRANTE-MORAGA | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40575709 | 1947-01-01 | Lattice Steel Pole | DDE-A - Double Dead End Angle | 1947-01-01 | Ceramic | Other |  |  |  |  | 3.9776e-08 | 98.1414
118777384 | F | LC | ETL.5090.TOWR | 40862870 | MOSSLNDG | DE ANZA | 2020-04-03 |  | ETL.5090 | MONTA VISTA-COYOTE SW STA | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40862870 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.21343 | 189.9226 | 40.5343
118796512 | F | LC | ETL.4392.TOWR | 41129363 | LAKEVLLE | SONOMA | 2020-04-08 | 2020-05-11 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129363 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 5.2075e-05 | 1175.8542
118796512 | F | LC | ETL.4392.TOWR | 41129363 | LAKEVLLE | SONOMA | 2020-04-08 | 2020-05-11 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129363 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2021-04-22 | Glass | Dead End |  |  |  |  | 5.2075e-05 | 1175.8542
118899830 | E | LC | ETL.4391.POLE.NWOD | 40770880 | LAKEVLLE | SONOMA | 2020-04-09 | 2020-06-24 | ETL.4391 | GEYSERS #11-EAGLE ROCK | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40770880 | 1999-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 4.87e-05 | 4672.6953
118910276 | E | LC | ETL.4050.POLE.WOOD | 40619198 | LAKEVLLE | SONOMA | 2020-04-10 | 2020-07-01 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40619198 | 1970-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1970-01-01 | Ceramic | Post |  |  |  |  | 1.3291e-05 | 5573.2285
118920641 | F | LC | ETL.6880.POLE.NWOD | 40700895 | LAKEVLLE | SONOMA | 2020-04-13 | 2020-11-10 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 |  |  | DLFL
118960668 | E | LC | ETL.8350.POLE.WOOD | 40768204 | VICTOR | STOCKTON | 2020-04-28 | 2021-06-28 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40768204 |  | Single Wood Pole | DDE - Double Dead End |  | Glass | [5 empty] | 0.00016313 | 300.6168
118979913 | E | LC | ETL.6220.POLE.WOOD | 40586717 | EUREKA | HUMBOLDT | 2020-05-04 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40586717 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.043781 | 1284.2095 | 56.2233
119005264 | E | LC | ETL.1420.TOWR | 40589593 | SACTO | SIERRA | 2020-05-06 | 2021-06-28 | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40589593 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm |  | Polymer | [5 empty] | 0.00059755 | 158.285
119057072 | F | LC | ETL.6440.POLE.WOOD | 40601815 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-08-25 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40601815 |  | Single Wood Pole | LB - Line and Buck | 2015-01-15 | Ceramic | Suspension |  |  |  |  | 0.0020253 | 3898.925
119100178 | E | LC | ETL.6520.POLE.NWOD | 44231831 | SACTO | SIERRA | 2020-06-02 | 2021-06-07 | ETL.6520 | COLGATE-SMARTVILLE #2 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44231831 | 2014-07-25 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2014-07-25 | Non Ceramic | Dead End |  |  |  |  | 4.0094e-05 | 794.5712
119105198 | E | LC | ETL.1450.POLE.WDPS | 44549968 | SACTO | SACRAMENTO | 2020-05-19 | 2020-07-21 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44549505 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0024785 | 2056.7583
119105441 | E | LC | ETL.5490.TOWR | 40581142 | CONCORD | DIABLO | 2020-05-21 | 2021-04-05 | ETL.5490 | PITTSBURG-SAN RAMON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581142 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 9.545e-05 | 4943.5347
119111387 | F | LC | ETL.1400.POLE.STPS | 44382139 | VICTOR | YOSEMITE | 2020-05-22 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44382137 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.6183e-05 | 79.1977
119115159 | F | LC | ETL.7380.POLE.WOOD | 40701573 | MOSSLNDG | CENTRAL COAST | 2020-05-29 |  | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40701573 |  | Single Wood Pole | FIG4W - Wood X Arm |  | Ceramic | [5 empty] | 0.63185 | 31.6978
119126066 | E | LC | ETL.7930.POLE.WOOD | 40824172 | MOSSLNDG | CENTRAL COAST | 2020-06-03 | 2020-11-12 | ETL.7930 | SALINAS-LAURELES | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824172 |  | Single Wood Pole | FIG4W - Wood X Arm |  | Ceramic | Other |  |  |  |  | 0.008766 | 0.066432
119126208 | F | LC | ETL.6280.POLE.WOOD | 40768757 | TABLEMTN | NORTH VALLEY | 2020-06-03 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40768757 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00019589 | 237.3097
119162657 | F | LC | ETL.7260.POLE.WOOD | 40586362 | TABLEMTN | NORTH VALLEY | 2020-06-09 |  | ETL.7260 | KESWICK-CASCADE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40586362 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 1.1925e-05 | 1076.2739
119172703 | A | LC | ETL.8170.INSL.CERA | 40885914 | EUREKA | HUMBOLDT | 2020-06-12 | 2020-07-13 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564266 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 0.079393
119172703 | A | LC | ETL.8170.INSL.CERA | 40885914 | EUREKA | HUMBOLDT | 2020-06-12 | 2020-07-13 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564266 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 0.079393
119172703 | A | LC | ETL.8170.INSL.CERA | 40885914 | EUREKA | HUMBOLDT | 2020-06-12 | 2020-07-13 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564266 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Ceramic | Dead End |  |  |  |  | 0.079393
119181506 | F | LC | ETL.1422.TOWR | 40586112 | SACTO | SIERRA | 2020-06-15 | 2021-03-01 | ETL.1422 | BRUNSWICK #1 TAP | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40586112 | 1975-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.9084e-07 | 427.1649
119197989 | E | LC | ETL.6470.POLE.WOOD | 40822738 | SACTO | SIERRA | 2020-06-22 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822738 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.11416 | 221.5931
119200413 | B | LC | ETL.4220.POLE.NWOD | 44272858 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-10-26 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44272858 | 2014-10-27 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2014-10-27 | Ceramic | Suspension |  |  |  |  | 7.9924e-05 | 1600.0325
119203179 | E | LC | ETL.4220.POLE.WOOD | 40591077 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-08-20 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119205498 | E | LC | ETL.8350.POLE.WOOD | 40643238 | VICTOR | STOCKTON | 2020-03-31 | 2020-11-18 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Rotten | [Stub, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40643238 | 1943-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2016-12-23 | Polymer | Post |  |  |  |  | 0.0011208 | 300.6168
119220921 | E | LC | ETL.7550.POLE.WDPS | 44211110 | LAKEVLLE | SONOMA | 2020-06-26 | 2021-03-15 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44211108 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.0932e-05 | 79.2083
119233831 | E | LC | ETL.8170.POLE.WOOD | 40751117 | EUREKA | HUMBOLDT | 2020-06-29 | 2020-10-28 | ETL.8170 | TRINITY-MAPLE CREEK | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40751117 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.66365 | 253.1639
119234722 | F | LC | ETL.8060.POLE.WOOD | 40809681 | SACTO | SIERRA | 2020-06-29 | 2021-08-23 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809681 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.020003 | 411.4417
119235195 | F | LC | ETL.7270.POLE.WOOD | 40908542 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40908542 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0049078 | 4067.0386
119292672 | E | LC | ETL.5660.TOWR | 40805039 | CONCORD | DIABLO | 2020-07-01 | 2021-04-26 | ETL.5660 | SAN RAMON-MORAGA | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805039 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.8579e-08 | 3043.1921
119292672 | E | LC | ETL.5660.TOWR | 40805039 | CONCORD | DIABLO | 2020-07-01 | 2021-04-26 | ETL.5660 | SAN RAMON-MORAGA | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805039 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Suspension |  |  |  |  | 5.8579e-08 | 3043.1921
119293546 | B | LC | ETL.4680.TOWR | 40604941 | LAKEVLLE | SONOMA | 2020-07-01 | 2020-10-20 | ETL.4680 | FULTON-IGNACIO #1 | Other | Customer Issue | [Customer Refusal, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40604941 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.8667e-05 | 142.516
119295844 | E | LC | ETL.9330.TOWR | 40872019 | FRESNO | FRESNO | 2020-06-29 |  | ETL.9330 | WISHON-COPPERMINE | Structure-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40872019 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 5.0349e-05
119300108 | F | LC | ETL.1400.POLE.STPS | 44379625 | VICTOR | YOSEMITE | 2020-07-01 | 2021-02-09 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44379624 | 2017-08-17 | 3-Pole Non Wood | DV-DE - Double Vertical Dead End | [7 empty] | 0.00033822 | 79.1977
119300248 | E | LC | ETL.7300.POLE.WOOD | 40771364 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-03-18 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Rotten | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119303033 | E | LC | ETL.7300.POLE.WOOD | 40619315 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-09-02 | ETL.7300 | KILARC-DESCHUTES | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier2 |  |  | DLFL
119310415 | F | LC | ETL.2500.TOWR | 40762456 | METCALF | SAN JOSE | 2020-07-02 |  | ETL.2500 | METCALF-EL PATIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762456 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-08-08 | Glass | Double Dead End |  |  |  |  | 0.0065083 | 2374.251 | 15.4524
119310415 | F | LC | ETL.2500.TOWR | 40762456 | METCALF | SAN JOSE | 2020-07-02 |  | ETL.2500 | METCALF-EL PATIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762456 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2003-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 0.0065083 | 2374.251 | 15.4524
119315457 | E | LC | ETL.7300.POLE.WOOD | 40770437 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-03-04 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770437 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0012689 | 3200.7368
119316921 | F | LC | ETL.7270.POLE.WOOD | 40906068 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906068 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0091086 | 4936.5352
119323545 | F | LC | ETL.7270.POLE.WOOD | 40701701 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40701701 | 2013-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.036905 | 1076.101
119325064 | E | LC | ETL.4750.INSL.CERA | 40609332 | LAKEVLLE |  | 2020-07-07 | 2021-01-28 | ETL.4750 | GEYSERS #12-FULTON | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129171 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2019-12-16 | Glass | Dead End |  |  |  |  | 0.0040823 | 1725.5695
119325064 | E | LC | ETL.4750.INSL.CERA | 40609332 | LAKEVLLE |  | 2020-07-07 | 2021-01-28 | ETL.4750 | GEYSERS #12-FULTON | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129171 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | Dead End |  |  |  |  | 0.0040823 | 1725.5695
119329883 | F | LC | ETL.6760.POLE.WOOD | 40822660 | SACTO | SACRAMENTO | 2020-07-08 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40822660 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.028451 | 126.7574
119332158 | E | LC | ETL.1110.POLE.WDPS | 44423195 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-03-31 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423194 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.001737 | 104.4867
119332688 | E | LC | ETL.5300.INSL | 40782015 | PISMOBCH | LOS PADRES | 2020-07-08 | 2021-07-06 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40753282 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00010785 | 1913.6598
119335513 | E | LC | ETL.1110.TOWR | 40657046 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2020-09-03 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40657046 | 1952-01-01 | LATTICE STEEL TOWER | SUSP-A - Suspension Angle (TWR) |  | Porcelain | Suspension |  |  |  |  | 1.5284e-05 | 3916.6689
119356623 | E | LC | ETL.5934.TOWR | 40593877 | FRESNO | LOS PADRES | 2020-07-10 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40593877 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.0042315
119356623 | E | LC | ETL.5934.TOWR | 40593877 | FRESNO | LOS PADRES | 2020-07-10 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40593877 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0042315
119363409 | E | LC | ETL.7590.POLE.WOOD | 40657780 | MOSSLNDG | CENTRAL COAST | 2020-07-13 | 2020-09-24 | ETL.7590 | MONTA VISTA-BURNS | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119365522 | E | LC | ETL.5140.POLE.STPS | 44553851 | SACTO | SIERRA | 2020-07-13 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 44141874 | 2015-10-26 | 3-Pole Non Wood | DE - Dead End | [7 empty] | 4.5216e-07 | 239.1195 | 0.00010812
119365546 | E | LC | ETL.7030.POLE.WOOD | 40756786 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-07-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756786 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0094042 | 459.4211
119373460 | B | LC | ETL.6861.POLE.WOOD | 40698947 | LAKEVLLE | SONOMA | 2020-07-15 | 2020-08-14 | ETL.6861 | KONOCTI-EAGLE ROCK | Other | Customer Issue | [Access Issue] | Tier3 | Tier 3 | Within Both | DLFL | 40698947 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-11-06 | Polymer | Dead End |  |  |  |  | 3.3718e-05 | 4733.5092
119468193 | F | LC | ETL.6290.POLE.WOOD | 40769627 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-02-11 | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40769627 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.048047 | 221.4934
119471038 | F | LC | ETL.7030.POLE.WOOD | 40656690 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40656690 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0062153 | 118.8961
119488024 | E | LC | ETL.1370.POLE.WOOD | 40591102 | PISMOBCH | LOS PADRES | 2020-07-22 | 2021-08-24 | ETL.1370 | DIVIDE-CABRILLO #2 | Jumper-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591102 | 1960-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-08-16 | Glass | Dead End |  |  |  |  | 0.018472 | 1139.9856
119495094 | E | LC | ETL.6240.INSL.NCER | 44425202 | MOSSLNDG | CENTRAL COAST | 2020-07-23 | 2020-09-23 | ETL.6240 | BURNS-LONE STAR #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119505741 | F | LC | ETL.6880.POLE.NWOD | 45071350 | LAKEVLLE | SONOMA | 2020-07-24 |  | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45071350 | 2020-03-05 | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 2020-03-05 | Glass | Suspension |  |  |  |  | 8.4341e-05 | 142.5287
119582159 | A | LC | ETL.6050.TOWR | 40664443 | MOSSLNDG | CENTRAL COAST | 2020-08-09 | 2020-08-12 | ETL.6050 | MOSS LANDING-METCALF | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40664443 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.4796e-08 | 300.6727
119601420 | B | LC | ETL.7930.POLE.WOOD | 40864647 | MOSSLNDG | CENTRAL COAST | 2020-08-11 | 2020-11-09 | ETL.7930 | SALINAS-LAURELES | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40864647 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0040796 | 174.585
119609657 | F | LC | ETL.1112.TOWR | 40582633 | FRESNO | FRESNO | 2020-08-13 | 2020-09-25 | ETL.1112 | INDIAN FLAT-YOSEMITE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | DLFL | 40582633 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.00070846 | 6933.3555
119627562 | E | LC | ETL.5463.INSL | 40879223 | CONCORD | EAST BAY | 2020-08-17 | 2021-05-14 | ETL.5463 | PITTSBURG-SAN MATEO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857956 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 1.201e-06 | 2754.8582
119627562 | E | LC | ETL.5463.INSL | 40879223 | CONCORD | EAST BAY | 2020-08-17 | 2021-05-14 | ETL.5463 | PITTSBURG-SAN MATEO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857956 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-10 | Glass | Suspension |  |  |  |  | 1.201e-06 | 2754.8582
119630528 | F | LC | ETL.6900.POLE.WOOD | 40825348 | LAKEVLLE | SONOMA | 2020-08-14 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40825348 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0010286 | 3332.2297
119644992 | B | LC | ETL.8650.POLE.NWOD | 44420191 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420191 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0051176 | 15.88
119659274 | E | LC | ETL.3500.TOWR | 40744666 | VICTOR | STOCKTON | 2020-08-23 | 2021-06-28 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40744666 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 0.00033588 | 5967.086
119677937 | E | LC | ETL.3800.INSL | 40848555 | CONCORD | EAST BAY | 2020-08-26 | 2021-07-13 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119694723 | E | LC | ETL.6690.INSL.NCER | 40898270 | SACTO | SACRAMENTO | 2020-08-29 | 2021-03-29 | ETL.6690 | DEER CREEK-DRUM | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119705744 | F | LC | ETL.5440.POLE.NWOD | 44968848 | TABLEMTN | NORTH VALLEY | 2020-09-02 | 2020-12-01 | ETL.5440 | PIT #6 JCT-ROUND MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44968848 | 2020-08-16 | Light Duty Steel Pole | DDE - Double Dead End | 2020-08-16 | Glass | Dead End | [5 empty] | 693.7659
119720760 | E | LC | ETL.7510.POLE.WOOD | 40576185 | LAKEVLLE | HUMBOLDT | 2020-07-27 | 2020-09-08 | ETL.7510 | MENDOCINO-HARTLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40576185 | 2002-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 5.6197e-06 | 974.6474
119762499 | B | LC | ETL.6220.INSL.CERA | 40640384 | EUREKA | HUMBOLDT | 2020-09-14 | 2020-10-22 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119781216 | F | LC | ETL.8240.POLE.NWOD | 44969339 | VICTOR | STOCKTON | 2020-09-12 |  | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44969339 | 2019-09-12 | Light Duty Steel Pole | T-1 - Tri Post | 2019-09-12 | Polymer | Post |  |  |  |  | 0.00013512 | 2425.3579
119782600 | E | LC | ETL.6310.POLE.WOOD | 40600705 | TABLEMTN | NORTH VALLEY | 2020-09-14 | 2021-04-19 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40600705 |  | Single Wood Pole | T2N | 2020-11-05 | Polymer | Post |  |  |  |  | 3.1302e-05 | 7306.2056
119785370 | E | LC | ETL.6220.POLE.WOOD | 40614661 | EUREKA | HUMBOLDT | 2020-09-14 | 2021-10-26 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40614661 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.021279 | 1284.2095 | 27.3272
119788237 | E | LC | ETL.6610.INSL.NCER | 44214178 | SACTO | SACRAMENTO | 2020-09-17 |  | ETL.6610 | CORTINA #4 | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Non-HFTD | Non-HFRA | PEND | 44214150 | 2013-11-11 | Single Wood Pole | TH - TriAngle Post 70 | 2013-11-11 | Polymer | Post |  |  |  |  | 3.0514e-06
119809680 | F | LC | ETL.7270.POLE.WOOD | 40909539 | TABLEMTN | NORTH VALLEY | 2020-08-12 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40909539 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.002979 | 933.5561
119810092 | F | LC | ETL.6280.POLE.NWOD | 44259097 | TABLEMTN | NORTH VALLEY | 2020-08-25 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44259097 | 2018-09-23 | Light Duty Steel Pole | T2N | 2018-09-23 | Polymer | Post |  |  |  |  | 6.1927e-11 | 537.8195
119812211 | F | LC | ETL.6690.POLE.WOOD | 40597179 | SACTO | SIERRA | 2020-08-28 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40597179 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.092587 | 126.6309
119816380 | F | LC | ETL.1650.POLE.STPS | 44298399 | LAKEVLLE |  | 2020-08-29 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44298398 |  | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 1.7146e-08 | 3278.8411
119889948 | E | LC | ETL.6030.TOWR | 40807881 | MIDWAY | KERN | 2020-10-08 | 2021-06-22 | ETL.6030 | MIDWAY-WHIRLWIND | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40807881 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 1.0143e-06 | 6099.3638
119915764 | E | LC | ETL.6980.INSL.NCER | 44992224 | LAKEVLLE | SONOMA | 2020-10-16 | 2021-06-22 | ETL.6980 | FORT ROSS-GUALALA | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44992220 | 2020-10-13 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-10-13 | Glass | Dead End |  |  |  |  | 0.14065
119915764 | E | LC | ETL.6980.INSL.NCER | 44992224 | LAKEVLLE | SONOMA | 2020-10-16 | 2021-06-22 | ETL.6980 | FORT ROSS-GUALALA | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44992220 | 2020-10-13 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-10-13 | Glass | Dead End |  |  |  |  | 0.14065
119915764 | E | LC | ETL.6980.INSL.NCER | 44992224 | LAKEVLLE | SONOMA | 2020-10-16 | 2021-06-22 | ETL.6980 | FORT ROSS-GUALALA | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44992220 | 2020-10-13 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-10-13 | Glass | Dead End |  |  |  |  | 0.14065
119916917 | E | LC | ETL.8960.POLE.WOOD | 40687119 | FRESNO | YOSEMITE | 2020-10-15 | 2021-04-27 | ETL.8960 | LOS BANOS-PACHECO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40687119 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.9698e-05
119927209 | E | LC | ETL.7780.POLE.WOOD | 40605863 | LAKEVLLE | HUMBOLDT | 2020-10-19 | 2021-01-11 | ETL.7780 | PHILO JCT-ELK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40605863 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 4.0117e-05 | 94.9762
119965199 | F | LC | ETL.1110.POLE.WDPS | 44561153 | TABLEMTN | HUMBOLDT | 2020-08-25 | 2021-02-10 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44515884 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0015697 | 4037.9333
119978735 | E | LC | ETL.8960.POLE.WOOD | 40754937 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40754937 | 1979-01-01 | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0016536
119995844 | F | LC | ETL.6880.POLE.WOOD | 40912455 | LAKEVLLE | NORTH BAY | 2020-10-06 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40912455 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | [7 empty] | 0.0096848 | 4444.5719
120012438 | E | LC | ETL.6060.TOWR | 40759734 | TABLEMTN | NORTH VALLEY | 2020-11-11 | 2021-06-14 | ETL.6060 | ROUND MTN-TABLE MTN #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40759734 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.0080073 | 190.8412
120088561 | E | LC | ETL.3180.TOWR | 40857608 | CONCORD | EAST BAY | 2020-11-19 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40857608 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 6.8512e-05 | 16.3243 | 0.0011184
120088561 | E | LC | ETL.3180.TOWR | 40857608 | CONCORD | EAST BAY | 2020-11-19 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40857608 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-03-25 | Glass Silicone Coated | Suspension |  |  |  |  | 6.8512e-05 | 16.3243 | 0.0011184
120097199 | E | LC | ETL.7212.POLE.WDPS | 44384422 | METCALF | SAN JOSE | 2020-11-25 | 2021-07-13 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Vegetation | Overgrown | [Remove, Completed] |  | Tier 3 | HFRA Removal | COMP | 44384419 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.058118 | 617.5648
120118186 | E | LC | ETL.8961.INSL.NCER | 40642681 | FRESNO | FRESNO | 2020-11-23 |  | ETL.8961 | DINOSAUR POINT TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44231070 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Polymer | Suspension |  |  |  |  | 0.00087586
120118186 | E | LC | ETL.8961.INSL.NCER | 40642681 | FRESNO | FRESNO | 2020-11-23 |  | ETL.8961 | DINOSAUR POINT TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44231070 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Polymer | Suspension |  |  |  |  | 0.00087586
120118186 | E | LC | ETL.8961.INSL.NCER | 40642681 | FRESNO | FRESNO | 2020-11-23 |  | ETL.8961 | DINOSAUR POINT TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44231070 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical |  | Polymer | Suspension |  |  |  |  | 0.00087586
120418558 | B | LC | ETL.6880.POLE.NWOD | 44928866 | LAKEVLLE | SONOMA | 2021-01-08 | 2021-07-07 | ETL.6880 | FULTON-CALISTOGA | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44928866 | 2020-06-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-06-11 | Glass | Dead End |  |  |  |  | 5.0707e-06 | 3852.5246
120419118 | E | LC | ETL.1200.POLE.NWOD | 40809778 | PISMOBCH | LOS PADRES | 2021-01-11 |  | ETL.1200 | CABRILLO-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40809778 | 2010-01-01 | Light Duty Steel Pole | T-1 - Tri Post | 1989-01-01 | Ceramic | Other |  |  |  |  | 3.7242e-08 | 2391.6853 | 8.9071e-05
120471919 | A | LC | ETL.7390.POLE.WOOD | 40824455 | LAKEVLLE | SONOMA | 2021-01-27 | 2021-01-29 | ETL.7390 | LAYTONVILLE-COVELO | Emergency-Wood | Other | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824455 |  | Single Wood Pole | T2N | 2021-01-28 | Polymer | Post |  |  |  |  | 0.24944 | 458.8146
120495789 | B | LC | ETL.8405.POLE.WOOD | 40664802 | SACTO | SACRAMENTO | 2021-02-03 | 2021-02-11 | ETL.8405 | MIDDLE FORK #1 | Non-Routine Patrol | Investigate | [Air Patrol, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664802 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0023638 | 2452.4026
120639274 | F | LC | ETL.9100.POLE.WOOD | 44191893 | PISMOBCH | LOS PADRES | 2021-03-11 | 2021-08-26 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.0001934 | 2326.5281
120647084 | F | LC | ETL.5630.TOWR | 40598072 | TABLEMTN | NORTH VALLEY | 2021-03-16 |  | ETL.5630 | ROCK CREEK-POE | Structure-Steel | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40598072 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 3.7448e-05 | 537.9698
120652240 | E | LC | ETL.4870.INSL | 40881232 | FRESNO | FRESNO | 2021-03-16 |  | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40858333 | 1985-01-01 | LATTICE STEEL TOWER | SUSP-A - Suspension Angle (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 1.0453e-06 | 6094.3804 | 0.0063706
120653205 | F | LC | ETL.4680.TOWR | 40587445 | LAKEVLLE | SONOMA | 2021-03-17 |  | ETL.4680 | FULTON-IGNACIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40587445 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.6458e-07 | 174.2387 | 2.8676e-05
120662682 | F | LC | ETL.2395.POLE.WOOD | 45013478 | TABLEMTN | NORTH VALLEY | 2021-03-19 | 2021-08-02 | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45013478 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00077089 | 300.6002
120667199 | E | LC | ETL.1350.POLE.WDPS | 44552551 | TABLEMTN | NORTH VALLEY | 2021-03-20 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 44551562 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 0.055855 | 1422.5072 | 79.4547
120680407 | F | LC | ETL.4440.TOWR | 40758297 | TABLEMTN | NORTH VALLEY | 2021-03-22 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40758297 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Porcelain | Suspension |  |  |  |  | 1.4856e-08 | 2630.96 | 3.9086e-05
120681221 | E | LC | ETL.7630.INSL.CERA | 40608924 | LAKEVLLE |  | 2021-03-23 |  | ETL.7630 | MONTE RIO-FULTON | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40584635 | 1952-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.030509 | 79.1651 | 2.4152
120694984 | E | LC | ETL.3840.INSL.NCER | 40877441 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40856507 | 1910-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post | 1989-01-01 | Polymer | Suspension |  |  |  |  | 4.8795e-07 | 351.61 | 0.00017157
120698241 | E | LC | ETL.5630.TOWR | 40605388 | TABLEMTN | NORTH VALLEY | 2021-03-26 |  | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40605388 | 1958-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 4.7417e-05 | 6110.1685 | 0.28973
120700673 | E | LC | ETL.1530.TOWR | 40857878 | SACTO | SACRAMENTO | 2021-03-27 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40857878 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1980-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.8327e-06 | 1819.3202 | 0.017889
120704986 | F | LC | ETL.3830.TOWR | 40596299 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40596299 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.6254e-05 | 5967.0518 | 0.276
120708432 | F | LC | ETL.6880.POLE.WOOD | 40658453 | LAKEVLLE | SONOMA | 2021-03-24 |  | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40658453 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | [5 empty] | 0.00090379 | 1534.6033
120713743 | F | LC | ETL.1350.POLE.WDPS | 44512207 | TABLEMTN | NORTH VALLEY | 2021-03-30 |  | ETL.1350 | CRAG VIEW-CASCADE | Road | Brush Fuel | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40759402 | 1993-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.0030777 | 74.426
120717467 | F | LC | ETL.6760.POLE.WOOD | 40767263 | SACTO | SACRAMENTO | 2021-03-31 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40767263 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0063185 | 0.066432
120726804 | F | LC | ETL.7390.POLE.WDPS | 44412010 | LAKEVLLE | SONOMA | 2021-04-01 | 2021-04-05 | ETL.7390 | LAYTONVILLE-COVELO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44412009 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.053448 | 2652.9001
120735331 | F | LC | ETL.6040.TOWR | 40858421 | MOSSLNDG | CENTRAL COAST | 2021-04-02 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40858421 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 0.0088012
120742935 | E | LC | ETL.1720.POLE.WDPS | 44513690 | MOSSLNDG | CENTRAL COAST | 2021-04-03 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | Rotten | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44512210 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00011566 | 791.1378 | 0.091501
120757488 | E | LC | ETL.6880.POLE.WOOD | 40912486 | LAKEVLLE | SONOMA | 2021-04-07 | 2021-07-21 | ETL.6880 | FULTON-CALISTOGA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40912486 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0011476 | 5781.4629
120785644 | F | LC | ETL.5330.TOWR | 40604871 | MOSSLNDG | CENTRAL COAST | 2021-04-09 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40604871 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1969-01-01 | Ceramic | Other |  |  |  |  | 1.502e-06 | 110.769 | 0.00016637
120785644 | F | LC | ETL.5330.TOWR | 40604871 | MOSSLNDG | CENTRAL COAST | 2021-04-09 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40604871 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1969-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.502e-06 | 110.769 | 0.00016637
120798433 | B | LC | ETL.3830.INSL | 40785149 | VICTOR | STOCKTON | 2021-04-09 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40756100 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 3.5497e-06 | 3577.5825
120799373 | E | LC | ETL.8250.POLE.WOOD | 40912851 | VICTOR | STOCKTON | 2021-04-12 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40912851 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0044938 | 2931.7273 | 13.1745
120804866 | E | LC | ETL.7590.POLE.WDPS | 44965630 | MOSSLNDG | SAN JOSE | 2021-04-13 |  | ETL.7590 | MONTA VISTA-BURNS | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42565758 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.44389 | 126.6368 | 56.2132
120808867 | E | LC | ETL.6020.TOWR | 40759855 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40759855 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.5556e-10 | 1537.5861 | 3.9295e-07
120817467 | E | LC | ETL.5850.TOWR | 40872780 | LAKEVLLE | SACRAMENTO | 2021-04-14 | 2021-11-30 | ETL.5850 | VACA-PARKWAY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40872780 | 1946-01-01 | LATTICE STEEL TOWER | Unknown | 2020-02-27 | Glass | Suspension |  |  |  |  | 1.1149e-06 | 6178.9241 | 0.0068886
120817467 | E | LC | ETL.5850.TOWR | 40872780 | LAKEVLLE | SACRAMENTO | 2021-04-14 | 2021-11-30 | ETL.5850 | VACA-PARKWAY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40872780 | 1946-01-01 | LATTICE STEEL TOWER | Unknown | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.1149e-06 | 6178.9241 | 0.0068886
120818785 | E | LC | ETL.7270.POLE.WOOD | 40617597 | TABLEMTN | NORTH VALLEY | 2021-04-14 | 2021-05-04 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40617597 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.25873 | 3563.1055
120821461 | E | LC | ETL.5850.TOWR | 40866215 | LAKEVLLE | SACRAMENTO | 2021-04-15 | 2021-11-03 | ETL.5850 | VACA-PARKWAY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40866215 | 1946-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.7495e-06 | 4006.7839 | 0.011017
120821465 | E | LC | ETL.5850.TOWR | 40764333 | LAKEVLLE | SACRAMENTO | 2021-04-15 |  | ETL.5850 | VACA-PARKWAY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40764333 | 1946-01-01 | LATTICE STEEL TOWER | Unknown | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 6.3882e-07 | 4972.4482 | 0.0031765
120828938 | E | LC | ETL.1450.INSL.CERA | 40856144 | SACTO | SACRAMENTO | 2021-04-16 |  | ETL.1450 | DRUM-SUMMIT #2 | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44549482 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00014437
120828938 | E | LC | ETL.1450.INSL.CERA | 40856144 | SACTO | SACRAMENTO | 2021-04-16 |  | ETL.1450 | DRUM-SUMMIT #2 | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44549482 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00014437
120848902 | E | LC | ETL.3960.INSL.NCER | 45036800 | PISMOBCH | LOS PADRES | 2021-04-19 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40861814 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-04-10 | Glass | Suspension |  |  |  |  | 6.4042e-05 | 79.1593 | 0.0050696
120849027 | B | LC | ETL.7590.INSL | 40673113 | MOSSLNDG | DE ANZA | 2021-04-19 | 2021-07-22 | ETL.7590 | MONTA VISTA-BURNS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40645493 |  | Single Wood Pole | 3P DDE-A - 3 Pole Double Dead End Angle |  | Non Ceramic | Double Dead End |  |  |  |  | 0.973 | 126.6368
120850796 | F | LC | ETL.1820.POLE.NWOD | 45070135 | EUREKA | HUMBOLDT | 2021-04-20 | 2021-08-02 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 45070135 | 2021-03-19 | Light Duty Steel Pole | 3P SV - 3 Pole Single Vertical | 2021-03-19 | Glass | Suspension |  |  |  |  | 0.0048039 | 0.065148
120873168 | E | LC | ETL.1450.POLE.NWOD | 45125367 | SACTO | SIERRA | 2021-04-23 |  | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45125367 | 2020-06-19 | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper | 2020-06-19 | Glass | Double Dead End | [5 empty] | 550.7045
120874053 | E | LC | ETL.1250.INSL.NCER | 40684549 | FRESNO | FRESNO | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40655091 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0034423 | 5793.8223 | 19.9441
120874889 | E | LC | ETL.9250.POLE.WOOD | 40749544 | MIDWAY | KERN | 2021-04-22 | 2021-08-25 | ETL.9250 | TEJON-LEBEC | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40749544 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.044573 | 4848.7817
120880624 | E | LC | ETL.2030.INSL.NCER | 40577680 | FRESNO | FRESNO | 2021-04-24 |  | ETL.2030 | KINGS RIVER-SANGER-REEDLEY | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44191955 |  | Lattice Steel Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 1.3064e-05 | 4149.042 | 0.054203
120884781 | E | LC | ETL.1250.INSL | 40856098 | FRESNO | FRESNO | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40828396 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | [5 empty] | 3.2393e-06 | 5050.3735 | 0.01636
120913687 | E | LC | ETL.3830.INSL.NCER | 40639680 | VICTOR | STOCKTON | 2021-05-01 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40612634 | 1927-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 2.2242e-07 | 2376.9839 | 0.00052868
120914608 | E | LC | ETL.5930.TOWR | 40600042 | LAKEVLLE | DIABLO | 2021-05-01 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40600042 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.899e-08 | 316.3912 | 6.0081e-06
120914608 | E | LC | ETL.5930.TOWR | 40600042 | LAKEVLLE | DIABLO | 2021-05-01 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40600042 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-01 | Glass | Suspension |  |  |  |  | 1.899e-08 | 316.3912 | 6.0081e-06
120923273 | E | LC | ETL.8060.POLE.WOOD | 44349564 | SACTO | SACRAMENTO | 2021-05-03 |  | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44349564 | 2018-09-06 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-09-06 | Ceramic | Dead End |  |  |  |  | 0.18234 | 1260.556 | 229.8497
120924126 | E | LC | ETL.7550.POLE.WOOD | 40769245 | LAKEVLLE | SONOMA | 2021-05-03 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40769245 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 7.3412e-06 | 110.7947 | 0.00081337
121336913 | F | LC | ETL.4410.TOWR | 40873285 | CONCORD | DIABLO | 2021-04-26 |  | ETL.4410 | BRENTWOOD-KELSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40873285 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 2.8279e-07 | 4086.0105 | 0.0011555
121347623 | E | LC | ETL.1820.POLE.WDPS | 44557696 | EUREKA | HUMBOLDT | 2021-05-17 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44553968 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.026804 | 63.351 | 1.6981
121361008 | F | LC | ETL.5330.TOWR | 40869789 | MOSSLNDG | CENTRAL COAST | 2021-04-27 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40869789 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 3.8025e-05 | 238.11 | 0.0090541
121361008 | F | LC | ETL.5330.TOWR | 40869789 | MOSSLNDG | CENTRAL COAST | 2021-04-27 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40869789 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 3.8025e-05 | 238.11 | 0.0090541
121362623 | E | LC | ETL.6500.INSL | 40787233 | SACTO | SACRAMENTO | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40757193 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0054548 | 443.072 | 2.4169
121362665 | E | LC | ETL.4870.TOWR | 40576737 | FRESNO | FRESNO | 2021-05-19 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576737 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.5567e-06 | 94.963 | 0.00043272
121381231 | E | LC | ETL.6500.POLE.WOOD | 40815253 | SACTO | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40815253 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | Pin |  |  |  |  | 0.018019 | 2250.7314 | 40.557
121381699 | E | LC | ETL.6500.POLE.NWOD | 44203995 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44203995 | 2014-07-13 | Light Duty Steel Pole | T-1 - Tri Post | 2014-07-13 | Polymer | Post |  |  |  |  | 0.00015819 | 2010.2684 | 0.318
121393249 | E | LC | ETL.1420.TOWR | 40756302 | SACTO | SIERRA | 2021-05-15 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40756302 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-05 | Glass | Suspension |  |  |  |  | 1.714e-05 | 269.0173 | 0.0046109
121397389 | F | LC | ETL.6660.POLE.NWOD | 45086319 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45086319 | 2021-03-04 | Light Duty Steel Pole | T2N | 2021-03-04 | Polymer | Post |  |  |  |  | 1.7733e-11 | 1396.3485
121403926 | E | LC | ETL.6870.POLE.WOOD | 40589916 | SACTO | SIERRA | 2021-05-19 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40589916 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.10535 | 94.9894 | 10.0074
121404446 | F | LC | ETL.7290.POLE.NWOD | 44175303 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.7290 | KILARC-CEDAR CREEK | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44175303 | 2014-10-15 | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.0014264 | 126.625
121405599 | E | LC | ETL.7290.POLE.WOOD | 40824226 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40824226 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.0039784 | 1158.6814 | 4.6097
121422324 | B | LC | ETL.4392.TOWR | 41129322 | LAKEVLLE | SONOMA | 2021-05-26 | 2021-08-26 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 41129322 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.00021313 | 2470.457
121422324 | B | LC | ETL.4392.TOWR | 41129322 | LAKEVLLE | SONOMA | 2021-05-26 | 2021-08-26 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 41129322 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.00021313 | 2470.457
121430867 | F | LC | ETL.4393.POLE.STPS | 45100612 | SACTO | SIERRA | 2021-05-26 |  | ETL.4393 | DRUM-HIGGINS | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45100528 | 2021-03-31 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00012425 | 1503.0458
121438769 | E | LC | ETL.1600.TOWR | 40650798 | LAKEVLLE | SONOMA | 2021-06-01 |  | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40650798 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 3.6047e-09 | 712.2047 | 2.5673e-06
121483118 | B | LC | ETL.5390.INSL.NCER | 45114605 | TABLEMTN | NORTH VALLEY | 2021-06-07 | 2021-08-17 | ETL.5390 | PIT #1-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40759687 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.5088e-05 | 475.7527
121485864 | E | LC | ETL.2540.POLE.WDPS | 44401575 | METCALF | CENTRAL COAST | 2021-05-29 |  | ETL.2540 | METCALF-GREEN VALLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44401574 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0011225 | 3997.7278 | 4.4875
121485959 | E | LC | ETL.5463.TOWR | 40857950 | CONCORD | DIABLO | 2021-06-01 |  | ETL.5463 | PITTSBURG-SAN MATEO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857950 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 5.7545e-08 | 3798.8403 | 0.0002186
121486110 | F | LC | ETL.7550.POLE.WOOD | 40768582 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40768582 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 4.5941e-06 | 2962.2891
121490778 | E | LC | ETL.4316.INSL.NCER | 45102927 | TABLEMTN | NORTH VALLEY | 2021-05-29 | 2021-08-30 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 45102887 | 2021-04-21 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2021-04-21 | Glass | Dead End |  |  |  |  | 0.00012667
121490778 | E | LC | ETL.4316.INSL.NCER | 45102927 | TABLEMTN | NORTH VALLEY | 2021-05-29 | 2021-08-30 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 45102887 | 2021-04-21 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2021-04-21 | Glass | Dead End |  |  |  |  | 0.00012667
121490778 | E | LC | ETL.4316.INSL.NCER | 45102927 | TABLEMTN | NORTH VALLEY | 2021-05-29 | 2021-08-30 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 45102887 | 2021-04-14 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2021-04-21 | Glass | Dead End |  |  |  |  | 0.00012667
121492827 | E | LC | ETL.6890.POLE.WOOD | 40598493 | LAKEVLLE | SONOMA | 2021-06-01 | 2021-07-02 | ETL.6890 | FULTON-HOPLAND | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40598493 | 1948-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0033889 | 1361.9498
121516323 | F | LC | ETL.6760.POLE.NWOD | 45096582 | SACTO | SIERRA | 2021-06-05 | 2021-08-09 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 45096582 | 2021-03-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-03-16 | Glass | Dead End |  |  |  |  | 0.092373 | 2233.9502
121516461 | F | LC | ETL.1680.POLE.WDPS | 44298667 | LAKEVLLE |  | 2021-06-04 | 2021-09-10 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44298666 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0018828 | 2708.3875
121516652 | E | LC | ETL.7560.POLE.STPS | 45078167 | SACTO | SIERRA | 2021-06-04 | 2021-06-29 | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 45078167 | 2021-04-07 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2021-04-07 | Glass | Double Dead End |  |  |  |  | 0.037473
121516652 | E | LC | ETL.7560.POLE.STPS | 45078167 | SACTO | SIERRA | 2021-06-04 | 2021-06-29 | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 45078167 | 2021-04-07 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2021-04-07 | Glass | Double Dead End |  |  |  |  | 0.037473
121516652 | E | LC | ETL.7560.POLE.STPS | 45078167 | SACTO | SIERRA | 2021-06-04 | 2021-06-29 | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 45078167 | 2021-04-07 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2021-04-07 | Glass | Double Dead End |  |  |  |  | 0.037473
121521514 | E | LC | ETL.1710.INSL.CERA | 40802828 | MOSSLNDG | CENTRAL COAST | 2021-06-11 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44509646 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0011403
121521514 | E | LC | ETL.1710.INSL.CERA | 40802828 | MOSSLNDG | CENTRAL COAST | 2021-06-11 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44509646 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0011403
121522268 | E | LC | ETL.4221.POLE.NWOD | 44820242 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4221 | SLY CREEK TAP | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44820242 | 2019-05-23 | Light Duty Steel Pole | DDE - Double Dead End | 2019-05-23 | Glass | Double Dead End |  |  |  |  | 1.2401e-05 | 316.3912 | 0.0039237
121523633 | F | LC | ETL.4040.POLE.WDPS | 44460947 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908624 | 1949-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.08348 | 2329.6245
121523878 | B | LC | ETL.1350.POLE.WDPS | 44513804 | TABLEMTN |  | 2021-06-09 | 2021-08-02 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121523879 | B | LC | ETL.1350.POLE.WDPS | 44513782 | TABLEMTN |  | 2021-06-09 | 2021-08-03 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121523899 | F | LC | ETL.6760.POLE.NWOD | 45072117 | SACTO | SIERRA | 2021-06-05 | 2021-06-28 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 45072117 | 2020-05-22 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-22 | Polymer | Dead End |  |  |  |  | 0.017157 | 110.8102
121525958 | F | LC | ETL.6500.POLE.WOOD | 40610968 | SACTO | SIERRA | 2021-06-09 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40610968 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0044991 | 6284.8086
121525958 | F | LC | ETL.6500.POLE.WOOD | 40610968 | SACTO | SIERRA | 2021-06-09 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40610968 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0044991 | 6284.8086
121525958 | F | LC | ETL.6500.POLE.WOOD | 40610968 | SACTO | SIERRA | 2021-06-09 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40610968 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0044991 | 6284.8086
121535915 | F | LC | ETL.7575.POLE.WDPS | 44384740 | METCALF | SAN FRANCISCO | 2021-06-09 |  | ETL.7575 | SNEATH LANE-PACIFICA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44384739 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.24475 | 316.4883 | 77.4611
121536200 | E | LC | ETL.1820.POLE.WDPS | 44560631 | EUREKA | HUMBOLDT | 2021-06-10 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560089 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.69333 | 87.0508 | 60.355
121536670 | F | LC | ETL.4550.TOWR | 40678178 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40678178 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.9969e-08 | 2219.104 | 0.00013308
121551629 | F | LC | ETL.6020.TOWR | 40868961 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40868961 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 3.8151e-10 | 997.3687
121553477 | E | LC | ETL.6020.TOWR | 40657568 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40657568 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.2614e-07 | 1412.6931 | 0.00031946
121565392 | E | LC | ETL.2390.POLE.WDPS | 44391261 | VICTOR | STOCKTON | 2021-06-13 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391260 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00051405 | 3150.0508 | 1.6193
121567741 | F | LC | ETL.5930.TOWR | 44426962 | CONCORD | DIABLO | 2021-06-15 |  | ETL.5930 | PARKWAY-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44426962 | 2017-10-27 | LATTICE STEEL TOWER | DE - Dead End | 2017-10-27 | Glass | Dead End |  |  |  |  | 1.0227e-06 | 728.1564 | 0.00074472
121568024 | F | LC | ETL.7490.POLE.NWOD | 44977495 | EUREKA | HUMBOLDT | 2021-06-15 |  | ETL.7490 | MAPLE CREEK-HOOPA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44977495 | 2020-07-11 | Light Duty Steel Pole | DDE - Double Dead End | 2020-07-11 | Glass | Dead End |  |  |  |  | 0.22585 | 142.4498
121585723 | E | LC | ETL.7550.POLE.WOOD | 40750963 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40750963 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00030636 | 601.6387 | 0.18432
121598851 | E | LC | ETL.1450.POLE.WDPS | 44557646 | SACTO | SACRAMENTO | 2021-06-11 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44554055 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.060109 | 31.7066 | 1.9059
121605783 | F | LC | ETL.4223.POLE.STPS | 44375480 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.4223 | KANAKA TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44375478 | 2017-09-20 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.4285e-08 | 142.4703
121606521 | F | LC | ETL.1183.TOWR | 45098588 | LAKEVLLE | SONOMA | 2021-06-26 | 2021-09-10 | ETL.1183 | CALPINE-WEST FORD FLAT | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45098588 |  | LATTICE STEEL TOWER | Unknown |  | Unknown | Unknown | [5 empty] | 253.9757
121606814 | F | LC | ETL.7550.POLE.WOOD | 40585236 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40585236 |  | Single Wood Pole | THDE - Tri Post Dead End 60 |  | Polymer | [5 empty] | 0.00012759 | 63.3392 | 0.0080811
121639445 | B | LC | ETL.1073.POLE.WDPS | 44779571 | VICTOR | YOSEMITE | 2021-06-30 | 2021-08-17 | ETL.1073 | MI-WUK-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40803725 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00070015 | 31.7081
121648660 | E | LC | ETL.6870.POLE.NWOD | 40767452 | SACTO | SACRAMENTO | 2021-07-01 | 2021-10-25 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40767452 |  | Light Duty Steel Pole | T-1 - Tri Post | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.0046698 | 0.065152 | 0.00030425
121649363 | F | LC | ETL.8310.POLE.WDPS | 44564919 | MOSSLNDG | CENTRAL COAST | 2021-06-28 | 2021-07-14 | ETL.8310 | WATSONVILLE-SALINAS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44564327 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.017947 | 3291.4099
121653690 | E | LC | ETL.3700.POLE.NWOD | 44960363 | PISMOBCH | LOS PADRES | 2021-06-28 | 2021-10-11 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44960363 | 2020-07-24 | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2020-07-24 | Glass | Dead End |  |  |  |  | 1.1527e-07 | 3453.2021
121662570 | E | LC | ETL.3700.POLE.WDPS | 44296828 | PISMOBCH | LOS PADRES | 2021-06-30 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44296825 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00016233 | 4022.5613 | 0.65299
121662578 | E | LC | ETL.5430.POLE.WOOD | 44562659 | TABLEMTN | NORTH VALLEY | 2021-07-01 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562354 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0031671 | 858.7344 | 2.7197
121676217 | E | LC | ETL.5420.POLE.WDPS | 44565811 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44557923 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.017329 | 2329.4255 | 40.366
121685153 | E | LC | ETL.1720.POLE.WDPS | 44401033 | METCALF | CENTRAL COAST | 2021-07-05 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44401031 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0019005 | 1560.0969 | 2.965
121706999 | E | LC | ETL.1440.POLE.WOOD | 40865985 | SACTO | SIERRA | 2021-06-14 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40865985 | 1956-01-01 | Single Wood Pole | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0006656 | 1344.8513 | 0.89513
121707025 | F | LC | ETL.6750.POLE.WDPS | 44374919 | TABLEMTN |  | 2021-07-06 | 2021-07-14 | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44374918 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0003691 | 205.744
121741350 | E | LC | ETL.2420.POLE.WDPS | 44226620 | LAKEVLLE |  | 2021-07-09 |  | ETL.2420 | MENDOCINO-UKIAH | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44226618 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00019263 | 1059.9559 | 0.20418
121742677 | F | LC | ETL.1820.POLE.WDPS | 44562927 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44562486 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.22397 | 142.4119
121746521 | E | LC | ETL.2390.POLE.WDPS | 44391235 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391234 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.431e-05 | 412.5413 | 0.030656
121748656 | F | LC | ETL.2390.POLE.WDPS | 44195228 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44195227 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.7805e-05 | 3150.0508
121778116 | E | LC | ETL.2390.POLE.WDPS | 44195260 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44195258 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.6093e-06 | 713.7063 | 0.0054308
121781034 | E | LC | ETL.4040.INSL.NCER | 42682161 | TABLEMTN |  | 2021-07-21 |  | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40910715 |  | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | 1949-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.0018027
121781034 | E | LC | ETL.4040.INSL.NCER | 42682161 | TABLEMTN |  | 2021-07-21 |  | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40910715 |  | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | 1949-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.0018027
121783276 | E | LC | ETL.6020.TOWR | 40868974 | TABLEMTN | NORTH VALLEY | 2021-07-22 |  | ETL.6020 | MALIN-ROUND MTN #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40868974 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00022946 | 126.6368 | 0.029058
121794559 | E | LC | ETL.6660.POLE.WOOD | 45087057 | TABLEMTN | NORTH VALLEY | 2021-07-23 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45087057 | 2021-03-04 | Single Wood Pole | T-1 - Tri Post | 2021-03-04 | Polymer | Post |  |  |  |  | 3.9886e-06 | 1253.0741 | 0.004998
121796419 | E | LC | ETL.8365.POLE.WOOD | 40912503 | EUREKA | HUMBOLDT | 2021-07-24 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40912503 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.26396
121801630 | E | LC | ETL.6480.POLE.NWOD | 45099362 | SACTO | SIERRA | 2021-07-26 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45099362 | 2021-01-01 | Light Duty Steel Pole | T2N | 2021-01-01 | Polymer | Post |  |  |  |  | 0.058393 | 268.9798 | 15.7066
121805189 | E | LC | ETL.6290.POLE.WOOD | 40758604 | TABLEMTN | NORTH VALLEY | 2021-07-27 | 2021-11-16 | ETL.6290 | CARIBOU-PLUMAS JCT | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40758604 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.048047 | 1363.4305
121807392 | F | LC | ETL.8620.POLE.WDPS | 44564939 | PISMOBCH | LOS PADRES | 2021-07-26 |  | ETL.8620 | DIVIDE-VANDENBERG #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44564350 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0016251 | 2645.1401 | 4.2987
121810316 | E | LC | ETL.8365.POLE.WDPS | 44403628 | EUREKA | HUMBOLDT | 2021-07-28 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44403627 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0012435 | 2077.2241 | 2.5831
121813050 | B | LC | ETL.7570.SWIT | 40743947 | METCALF | PENINSULA | 2021-07-29 | 2021-10-13 | ETL.7570 | MILLBRAE-SNEATH LANE | Switch | Out of Adjustment | [Repair, Completed] | Tier2 |  |  | COMP | [8 empty] | Other | ARCHING HORNS ONLY | SCADA Only
121815605 | E | LC | ETL.6470.POLE.WOOD | 40823279 | SACTO | SIERRA | 2021-07-29 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40823279 |  | Single Wood Pole | T-1 - Tri Post | 2021-07-19 | Polymer | Post |  |  |  |  | 0.0044322 | 237.3428 | 1.0519
121820845 | E | LC | ETL.6760.POLE.NWOD | 45096585 | SACTO | SIERRA | 2021-07-29 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45096585 | 2021-03-04 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-04 | Polymer | Post |  |  |  |  | 0.030591 | 189.9137 | 5.8097
121942182 | E | LC | ETL.7140.POLE.WOOD | 40648881 | LAKEVLLE | SONOMA | 2021-08-23 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40648881 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2020-06-21 | Glass | Suspension |  |  |  |  | 0.036322 | 2185.4529 | 79.379
122058153 | E | LC | ETL.4780.INSL.NCER | 45129013 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129357 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 1.8675e-05 | 3897.7966 | 0.07279
122058153 | E | LC | ETL.4780.INSL.NCER | 45129013 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129357 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 1.8675e-05 | 3897.7966 | 0.07279
122079183 | E | LC | ETL.8210.POLE.WOOD | 40911574 | VICTOR | STOCKTON | 2021-09-21 |  | ETL.8210 | VALLEY SPRINGS #1 | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | PEND | [11 empty] | 0.0071026 | 2859.6412 | 20.311
118475242 | F | LC | ETL.1110.POLE.WDPS | 44423945 | TABLEMTN | HUMBOLDT | 2020-01-28 | 2020-03-04 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP | [12 empty] | 7125.6149
118735110 | E | LC | ETL.7140.INSL.NCER | 44893473 | LAKEVLLE | NORTH BAY | 2020-03-23 | 2021-07-29 | ETL.7140 | IGNACIO-BOLINAS #1 | Damper-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44893450 | 2020-01-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-01-18 | Polymer | Dead End |  |  |  |  | 0.00034386 | 174.0849
118900307 | E | LC | ETL.7780.POLE.WOOD | 40875196 | LAKEVLLE | SONOMA | 2020-04-09 | 2020-11-10 | ETL.7780 | PHILO JCT-ELK | Non-Routine Patrol | Investigate | [Ground Patrol] | Tier2 | Tier 2 | Within Both | DLFL | 40875196 |  | Single Wood Pole | T-1 - Tri Post | 2016-05-16 | Polymer | Post |  |  |  |  | 2.2395e-06 | 1842.2696
118956862 | E | LC | ETL.6220.POLE.WOOD | 40698435 | EUREKA | HUMBOLDT | 2020-04-28 | 2021-03-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40698435 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.065273 | 570.0973
118963999 | E | LC | ETL.2060.POLE.WOOD | 40648270 | LAKEVLLE | SONOMA | 2020-04-30 | 2020-07-29 | ETL.2060 | FORT BRAGG-ELK | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648270 | 1961-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2020-07-14 | Glass | Suspension |  |  |  |  | 0.28156 | 15.8807
119030583 | E | LC | ETL.7055.POLE.WOOD | 40804459 | CONCORD | DIABLO | 2020-05-12 | 2021-10-26 | ETL.7055 | BRIONES TAP | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40804459 | 1982-01-01 | Single Wood Pole | FSS - Field Switch Structure | 1982-01-01 | Ceramic | Pin |  |  |  |  | 0.40039 | 4769.5273
119038444 | E | LC | ETL.1710.INSL.CERA | 40853574 | MOSSLNDG | CENTRAL COAST | 2020-05-12 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 44510837 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End - Suspension |  |  |  |  | 0.0007611
119038444 | E | LC | ETL.1710.INSL.CERA | 40853574 | MOSSLNDG | CENTRAL COAST | 2020-05-12 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 44510837 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End - Suspension |  |  |  |  | 0.0007611
119038444 | E | LC | ETL.1710.INSL.CERA | 40853574 | MOSSLNDG | CENTRAL COAST | 2020-05-12 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 44510837 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End - Suspension |  |  |  |  | 0.0007611
119040036 | E | LC | ETL.5960.INSL | 40614760 | PISMOBCH | LOS PADRES | 2020-05-18 |  | ETL.5960 | DIABLO-GATES #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40589505 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 3.2742e-08 | 2975.9231 | 9.7437e-05
119084516 | E | LC | ETL.1400.INSL.NCER | 40670182 | VICTOR | YOSEMITE | 2020-05-22 | 2021-05-12 | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119094782 | E | LC | ETL.7300.POLE.WOOD | 40600426 | TABLEMTN | NORTH VALLEY | 2020-06-02 | 2021-03-24 | ETL.7300 | KILARC-DESCHUTES | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600426 |  | Single Wood Pole | T2N | 2018-06-03 | Polymer | Post |  |  |  |  | 0.00016918 | 5085.0723
119100724 | E | LC | ETL.6950.POLE.WOOD | 40666244 | SACTO | SIERRA | 2020-05-28 | 2021-04-26 | ETL.6950 | GOLD HILL #1 | Vegetation | Overgrown | [Trim, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40666244 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0003921 | 3313.3969
119102340 | F | LC | ETL.3530.TOWR | 40651036 | PISMOBCH | LOS PADRES | 2020-05-18 | 2021-01-28 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40651036 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 1.4167e-06 | 2576.9339
119111050 | E | LC | ETL.8300.POLE.WOOD | 40868017 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-08-03 | ETL.8300 | VOLTA-SOUTH | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40868017 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Pin |  |  |  |  | 0.035954 | 4276.5586
119112781 | F | LC | ETL.1050.TOWR | 40869241 | FRESNO | FRESNO | 2020-05-26 |  | ETL.1050 | BALCH-SANGER | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40869241 | 1961-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1961-01-01 | Porcelain | Suspension |  |  |  |  | 0.0011974 | 9097.8947 | 10.8937
119115673 | E | LC | ETL.5650.TOWR | 40868288 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2021-06-14 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40868288 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 0.00013523 | 905.5491
119118642 | F | LC | ETL.1450.POLE.WOOD | 40761541 | SACTO | SIERRA | 2020-06-01 | 2021-04-21 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40761541 | 1948-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 1948-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.00078411 | 47.5526
119118680 | E | LC | ETL.6330.POLE.WOOD | 40867563 | TABLEMTN | NORTH VALLEY | 2020-06-02 | 2021-09-14 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40867563 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0025372 | 3659.7241
119118780 | F | LC | ETL.6760.POLE.NWOD | 44764260 | SACTO | SIERRA | 2020-05-27 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44764260 | 2019-05-06 | Light Duty Steel Pole | T-1 - Tri Post | 2019-05-06 | Polymer | Post |  |  |  |  | 0.0073687 | 1503.0458
119119656 | F | LC | ETL.8170.POLE.WOOD | 44962156 | EUREKA | HUMBOLDT | 2020-06-03 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44962156 | 2020-04-30 | Single Wood Pole | DDE - Double Dead End | 2020-04-30 | Glass | Dead End |  |  |  |  | 0.14235 | 4131.4126
119144943 | F | LC | ETL.7930.POLE.WOOD | 42564790 | MOSSLNDG | CENTRAL COAST | 2020-06-03 |  | ETL.7930 | SALINAS-LAURELES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 42564790 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.020942 | 15.9053
119173412 | E | LC | ETL.1110.POLE.WDPS | 44561191 | TABLEMTN | HUMBOLDT | 2020-05-29 | 2021-04-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44515916 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0011394 | 5824.7817
119179323 | F | LC | ETL.5660.TOWR | 40822977 | CONCORD | MISSION | 2020-06-16 | 2021-01-21 | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822977 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 7.1779e-07 | 2754.8582
119179323 | F | LC | ETL.5660.TOWR | 40822977 | CONCORD | MISSION | 2020-06-16 | 2021-01-21 | ETL.5660 | SAN RAMON-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822977 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 7.1779e-07 | 2754.8582
119183636 | F | LC | ETL.6280.POLE.WOOD | 40599682 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-09-14 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40599682 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 6.0205e-06 | 1739.9091
119188436 | F | LC | ETL.5790.TOWR | 40645135 | VICTOR | STOCKTON | 2020-06-18 | 2021-06-01 | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40645135 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 3.2819e-06 | 110.8074
119195541 | F | LC | ETL.6470.POLE.WOOD | 40868958 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40868958 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.046335 | 474.9903
119195929 | E | LC | ETL.6470.POLE.WOOD | 40760451 | SACTO | SIERRA | 2020-06-22 | 2021-07-15 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.047175 | 79.2067
119200831 | E | LC | ETL.1370.INSL.NCER | 40685429 | PISMOBCH | LOS PADRES | 2020-06-23 | 2021-06-23 | ETL.1370 | DIVIDE-CABRILLO #2 | Jumper-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40655840 | 1960-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1988-01-01 | Polymer | Dead End |  |  |  |  | 0.0031265 | 1376.9107
119204211 | F | LC | ETL.7321.POLE.WOOD | 44212732 | MOSSLNDG | CENTRAL COAST | 2020-06-22 |  | ETL.7321 | JOLON TAP | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44212732 | 2014-12-16 | Fiberglass | T-1 - Tri Post | 2014-12-16 | Non Ceramic | Post |  |  |  |  | 9.4298e-06 | 413.1489
119232557 | B | LC | ETL.4220.POLE.NWOD | 44388413 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2020-08-19 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119237533 | E | LC | ETL.6880.POLE.WOOD | 40658395 | LAKEVLLE | SONOMA | 2020-06-30 | 2021-08-11 | ETL.6880 | FULTON-CALISTOGA | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40658395 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.019301 | 569.8757
119296051 | F | LC | ETL.1450.POLE.WDPS | 44552507 | SACTO | SACRAMENTO | 2020-06-30 | 2020-08-18 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44551603 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00028114 | 450.9556
119308134 | F | LC | ETL.6300.POLE.WOOD | 40826511 | TABLEMTN |  | 2020-07-01 | 2021-02-10 | ETL.6300 | CARIBOU-WESTWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40826511 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Pin |  |  |  |  | 6.1291e-06 | 0.065148
119310006 | E | LC | ETL.8170.POLE.WOOD | 44948565 | EUREKA | HUMBOLDT | 2020-07-03 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44948565 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End | [5 empty] | 269.0562
119311413 | B | LC | ETL.1402.POLE.WDPS | 44550823 | VICTOR | STOCKTON | 2020-07-02 | 2021-06-01 | ETL.1402 | SPRING GAP TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119314484 | F | LC | ETL.7270.POLE.WOOD | 40909538 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-04-13 | ETL.7270 | KESWICK-TRINITY | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40909538 |  | Single Wood Pole | TCDE - Tap Construction Dead End |  | Porcelain | [5 empty] | 0.0039545 | 933.5561
119325731 | B | LC | ETL.7270.INSL.NCER | 40919271 | TABLEMTN |  | 2020-07-06 | 2020-07-24 | ETL.7270 | KESWICK-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40909532 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Unknown |  |  |  |  | 0.0015497 | 5300.8838
119327702 | E | LC | ETL.6470.POLE.WOOD | 40822602 | SACTO | SACRAMENTO | 2020-07-07 | 2021-08-04 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822602 |  | Single Wood Pole | T2N | 2021-07-20 | Polymer | Post |  |  |  |  | 0.014805 | 1439.967
119328259 | F | LC | ETL.1350.POLE.WDPS | 44550026 | TABLEMTN |  | 2020-07-06 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44549435 |  | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.03657 | 411.4229
119328910 | F | LC | ETL.7030.POLE.WOOD | 40667985 | TABLEMTN | NORTH VALLEY | 2020-07-07 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40667985 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.015985 | 0.06515
119334417 | F | LC | ETL.6890.POLE.WOOD | 40825324 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-05-05 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40825324 | 1967-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Other |  |  |  |  | 0.0023391 | 982.4404
119334774 | E | LC | ETL.1430.INSL.NCER | 44305013 | SACTO | SACRAMENTO | 2020-07-08 | 2021-01-21 | ETL.1430 | DRUM-RIO OSO #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40672397 | 1913-01-01 | LATTICE STEEL TOWER | Unknown | 2016-11-14 | Non Ceramic | Post |  |  |  |  | 0.002243 | 1977.4294
119341484 | E | LC | ETL.7030.POLE.WOOD | 40877587 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-11 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40877587 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0053269 | 47.5839
119341560 | E | LC | ETL.1431.INSL | 40885585 | SACTO | SACRAMENTO | 2020-07-09 | 2021-03-18 | ETL.1431 | BRUNSWICK #2 TAP | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40862192 | 1975-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Ceramic | Suspension |  |  |  |  | 1.2082e-06 | 31.7022
119354789 | E | LC | ETL.6861.POLE.WOOD | 40809243 | LAKEVLLE | SONOMA | 2020-07-10 | 2021-09-13 | ETL.6861 | KONOCTI-EAGLE ROCK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809243 |  | Single Wood Pole | T2N | 2018-11-06 | Polymer | Post |  |  |  |  | 0.0028581 | 4752.3721
119357216 | E | LC | ETL.1110.TOWR | 40909286 | EUREKA | HUMBOLDT | 2020-07-09 | 2021-01-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40909286 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-06-18 | Glass | Double Dead End |  |  |  |  | 0.00012745 | 506.8068
119357672 | F | LC | ETL.7980.POLE.WOOD | 40593022 | SACTO | SIERRA | 2020-07-08 |  | ETL.7980 | SMARTVILLE-MARYSVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40593022 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 0.0015035 | 1440.1678
119366506 | E | LC | ETL.7590.POLE.WOOD | 42565792 | MOSSLNDG | CENTRAL COAST | 2020-07-14 | 2020-12-16 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Rotten | [Replace, Completed] | Tier3 |  |  | COMP
119368619 | F | LC | ETL.7490.POLE.WDPS | 44743787 | EUREKA | HUMBOLDT | 2020-07-13 |  | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
119371552 | E | LC | ETL.7030.POLE.WOOD | 40671153 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-05-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119404378 | E | LC | ETL.6222.POLE.WOOD | 40667645 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6222 | FORT SEWARD TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40667645 | 1952-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0061393
119494235 | F | LC | ETL.1450.POLE.WDPS | 44558946 | SACTO | SACRAMENTO | 2020-07-22 | 2020-11-12 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44558489 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0063751 | 31.7066
119495046 | F | LC | ETL.2060.POLE.WOOD | 40860675 | LAKEVLLE | SONOMA | 2020-07-23 | 2021-01-22 | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40860675 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.10261 | 205.794
119495422 | E | LC | ETL.1110.POLE.WDPS | 44509664 | EUREKA | HUMBOLDT | 2020-07-22 | 2021-06-25 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44509664 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0039232
119495422 | E | LC | ETL.1110.POLE.WDPS | 44509664 | EUREKA | HUMBOLDT | 2020-07-22 | 2021-06-25 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44509664 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0039232
119514674 | F | LC | ETL.4040.POLE.NWOD | 43688511 | TABLEMTN | NORTH VALLEY | 2020-07-28 |  | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | PEND
119560171 | F | LC | ETL.8170.POLE.WOOD | 40770470 | EUREKA | HUMBOLDT | 2020-08-04 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40770470 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.16195 | 31.6978
119574069 | E | LC | ETL.1050.TOWR | 40862354 | FRESNO | FRESNO | 2020-08-06 | 2021-06-23 | ETL.1050 | BALCH-SANGER | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862354 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1923-01-01 | Porcelain | Suspension |  |  |  |  | 0.0028628 | 4069.9172
119574069 | E | LC | ETL.1050.TOWR | 40862354 | FRESNO | FRESNO | 2020-08-06 | 2021-06-23 | ETL.1050 | BALCH-SANGER | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862354 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-06-16 | Glass | Suspension |  |  |  |  | 0.0028628 | 4069.9172
119576972 | B | LC | ETL.8365.POLE.WOOD | 40912624 | EUREKA | HUMBOLDT | 2020-08-07 | 2020-11-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912624 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.18307
119591849 | F | LC | ETL.7590.POLE.WOOD | 40592831 | MOSSLNDG | CENTRAL COAST | 2020-08-10 | 2021-01-12 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119599301 | F | LC | ETL.8365.POLE.WOOD | 40906597 | EUREKA | HUMBOLDT | 2020-08-11 | 2021-02-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40906597 | 2010-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.022299
119605796 | B | LC | ETL.7490.POLE.NWOD | 44837783 | EUREKA | HUMBOLDT | 2020-08-12 | 2020-08-18 | ETL.7490 | MAPLE CREEK-HOOPA | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44837783 | 2019-09-12 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-09-12 | Polymer | Dead End |  |  |  |  | 0.0014737 | 142.4119
119626714 | F | LC | ETL.6880.POLE.WOOD | 40912430 | LAKEVLLE | NORTH BAY | 2020-08-17 | 2021-06-08 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119632036 | E | LC | ETL.6870.POLE.WOOD | 40649987 | SACTO | SIERRA | 2020-08-17 | 2021-04-28 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40649987 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.081813 | 126.6562
119635925 | E | LC | ETL.8270.POLE.WOOD | 40876148 | MOSSLNDG | CENTRAL COAST | 2020-08-18 | 2021-03-11 | ETL.8270 | VIEJO-MONTEREY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40876148 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.27958 | 0.065148
119677833 | F | LC | ETL.1450.POLE.WDPS | 44559082 | SACTO | SACRAMENTO | 2020-08-19 | 2020-08-28 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44558484 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.7977e-05 | 0.065152
119678312 | E | LC | ETL.5140.POLE.WDPS | 44553723 | SACTO | SACRAMENTO | 2020-08-25 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 3 | Within Both | PEND | 44553209 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0019616 | 205.7817 | 0.40367
119678427 | E | LC | ETL.7560.POLE.WOOD | 40598730 | SACTO | SACRAMENTO | 2020-08-27 | 2021-04-05 | ETL.7560 | WEIMAR #1 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40598730 |  | Single Wood Pole | T2N | 2021-03-30 | Polymer | Post |  |  |  |  | 0.14681 | 490.5528
119679150 | B | LC | ETL.1330.TOWR | 40750597 | LAKEVLLE | SONOMA | 2020-08-27 | 2020-10-29 | ETL.1330 | CORTINA-MENDOCINO #1 | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750597 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00015491 | 1522.7161
119679150 | B | LC | ETL.1330.TOWR | 40750597 | LAKEVLLE | SONOMA | 2020-08-27 | 2020-10-29 | ETL.1330 | CORTINA-MENDOCINO #1 | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750597 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Ceramic | Dead End |  |  |  |  | 0.00015491 | 1522.7161
119687177 | F | LC | ETL.6490.POLE.WOOD | 44190861 | SACTO | SIERRA | 2020-08-25 | 2021-03-01 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44190861 |  | Single Wood Pole | Unknown | [7 empty] | 0.0088881 | 428.1771
119688339 | E | LC | ETL.1440.POLE.WDPS | 44768922 | SACTO | SACRAMENTO | 2020-08-25 | 2021-08-09 | ETL.1440 | DRUM-SUMMIT #1 | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [12 empty] | 31.7066
119700470 | E | LC | ETL.6690.POLE.WOOD | 40824502 | SACTO | SACRAMENTO | 2020-09-01 | 2021-10-14 | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40824502 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.064091 | 63.3607
119702283 | F | LC | ETL.7780.POLE.WOOD | 40820707 | LAKEVLLE | HUMBOLDT | 2020-08-25 | 2021-04-15 | ETL.7780 | PHILO JCT-ELK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40820707 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Other |  |  |  |  | 5.99e-08 | 2423.4854
119719818 | F | LC | ETL.7780.POLE.WOOD | 40605866 | LAKEVLLE | HUMBOLDT | 2020-06-22 | 2021-01-20 | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40605866 |  | Single Wood Pole | 3P DV - 3 Pole Double Vertical |  | Non Ceramic | [5 empty] | 0.00053131 | 158.2502
119721801 | E | LC | ETL.8480.POLE.WOOD | 40660691 | PISMOBCH | LOS PADRES | 2020-07-30 | 2021-07-22 | ETL.8480 | ATASCADERO-CAYUCOS | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660691 | 1954-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 2021-07-14 | Polymer | Post |  |  |  |  | 0.00028796 | 3273.925
119722805 | E | LC | ETL.6880.POLE.WOOD | 40658466 | LAKEVLLE | NORTH BAY | 2020-08-06 | 2020-10-02 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119723140 | E | LC | ETL.7321.POLE.WOOD | 44212737 | MOSSLNDG | CENTRAL COAST | 2020-06-23 | 2021-03-01 | ETL.7321 | JOLON TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44212737 | 2014-12-16 | Fiberglass | SV2 - Angle 30-80 Degrees | 2014-12-16 | Non Ceramic | Suspension |  |  |  |  | 7.4894e-06 | 1198.2018
119723145 | E | LC | ETL.1112.TOWR | 40661992 | FRESNO | YOSEMITE | 2020-08-10 |  | ETL.1112 | INDIAN FLAT-YOSEMITE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40661992 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1929-01-01 | Ceramic | Suspension |  |  |  |  | 5.4644e-05 | 6806.8955 | 0.37196
119727758 | A | LC | ETL.7590.POLE.WOOD | 40599208 | MOSSLNDG | CENTRAL COAST | 2020-09-08 | 2020-10-21 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119751328 | E | LC | ETL.7140.POLE.WDPS | 44942606 | LAKEVLLE | NORTH BAY | 2020-08-11 | 2021-05-19 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111807 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.023199 | 79.2167
119780540 | E | LC | ETL.1073.POLE.WOOD | 44963356 | VICTOR | STOCKTON | 2020-09-17 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 44963356 | 1956-01-01 | Single Wood Pole | 3P TRP D - 3 Pole Tramp Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0024346 | 15.88 | 0.038661
119782113 | E | LC | ETL.7270.POLE.WOOD | 40906117 | TABLEMTN | NORTH VALLEY | 2020-09-17 | 2021-11-08 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906117 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.003335 | 4067.0386 | 13.5635
119783406 | E | LC | ETL.5630.TOWR | 40762419 | TABLEMTN | NORTH VALLEY | 2020-09-14 | 2021-03-29 | ETL.5630 | ROCK CREEK-POE | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762419 | 1950-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2019-06-13 | Glass | Dead End |  |  |  |  | 2.0295e-06 | 254.0199
119787069 | F | LC | ETL.7212.POLE.WOOD | 40612350 | METCALF | PENINSULA | 2020-08-27 | 2021-09-14 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40612350 |  | Single Wood Pole | WB - Wishbone |  | Ceramic | Post |  |  |  |  | 0.62112 | 602.2181
119805445 | F | LC | ETL.7290.POLE.WOOD | 40693125 | TABLEMTN | NORTH VALLEY | 2020-08-10 | 2021-08-19 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693125 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.015713 | 591.9693
119835381 | F | LC | ETL.2740.TOWR | 40857638 | CONCORD | EAST BAY | 2020-09-04 | 2021-09-27 | ETL.2740 | MORAGA-OAKLAND #3 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40857638 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 2.8893e-05 | 0.065158
119845287 | F | LC | ETL.7300.POLE.WOOD | 40771291 | TABLEMTN |  | 2020-09-16 |  | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40771291 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00078285 | 731.3142
119850165 | E | LC | ETL.7030.POLE.WOOD | 40827471 | TABLEMTN | NORTH VALLEY | 2020-10-02 | 2021-05-24 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827471 |  | Single Wood Pole | T2N | 2021-05-20 | Polymer | Post |  |  |  |  | 0.024506 | 206.4995
119873698 | E | LC | ETL.7030.POLE.WOOD | 40617056 | TABLEMTN | NORTH VALLEY | 2020-10-05 | 2021-08-17 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40617056 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.056762 | 63.3304
119917795 | F | LC | ETL.5290.TOWR | 40865518 | PISMOBCH | LOS PADRES | 2020-09-25 | 2021-05-10 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40865518 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-01-26 | Ceramic | Suspension |  |  |  |  | 1.6635e-07 | 1870.6561
119917795 | F | LC | ETL.5290.TOWR | 40865518 | PISMOBCH | LOS PADRES | 2020-09-25 | 2021-05-10 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40865518 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-07-18 | Ceramic | Suspension |  |  |  |  | 1.6635e-07 | 1870.6561
119934288 | E | LC | ETL.1820.POLE.WDPS | 44560504 | EUREKA | HUMBOLDT | 2020-10-22 | 2021-02-23 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119946821 | F | LC | ETL.5240.TOWR | 40593847 | METCALF | DE ANZA | 2020-10-22 |  | ETL.5240 | MONTA VISTA-SARATOGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40593847 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1957-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.21379 | 1711.0358 | 365.8103
119963089 | F | LC | ETL.8960.POLE.NWOD | 40820334 | FRESNO | YOSEMITE | 2020-10-27 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40820334 |  | Tubular Steel Pole | DV-DE - Double Vertical Dead End | 1974-01-01 | Polymer | Dead End |  |  |  |  | 9.681e-07
119968126 | B | LC | ETL.8580.TOWR | 40597697 | FRESNO | FRESNO | 2020-10-31 | 2020-11-16 | ETL.8580 | COALINGA #1-SAN MIGUEL | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40597697 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-10-31 | Glass | Suspension |  |  |  |  | 0.00019863
119973950 | F | LC | ETL.8580.TOWR | 40663527 | FRESNO | FRESNO | 2020-10-29 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Structure-Steel | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40663527 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Glass | [5 empty] | 2.9984e-06
119985596 | E | LC | ETL.8170.POLE.WOOD | 44948567 | EUREKA | HUMBOLDT | 2020-11-05 | 2021-08-26 | ETL.8170 | TRINITY-MAPLE CREEK | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44948567 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | Dead End |  |  |  |  | 0.038532 | 6300.0015
119993475 | E | LC | ETL.8960.POLE.WOOD | 44231462 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44231462 |  | Single Wood Pole | SUSP - Suspension (TWR) |  | Glass | [5 empty] | 0.00016258
120044480 | F | LC | ETL.7212.POLE.WOOD | 40665339 | METCALF | PENINSULA | 2020-10-06 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40665339 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Post |  |  |  |  | 0.28203 | 680.9633
120085382 | B | LC | ETL.8365.POLE.WOOD | 40912561 | EUREKA | HUMBOLDT | 2020-11-20 | 2021-01-27 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912561 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-08-20 | Glass | Dead End |  |  |  |  | 0.006174
120108118 | F | LC | ETL.7212.POLE.NWOD | 44947417 | METCALF | SAN JOSE | 2020-11-30 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44947417 | 2015-06-26 | Light Duty Steel Pole | DDE - Double Dead End | 2015-06-26 | Polymer | Suspension |  |  |  |  | 0.096414 | 460.5361
120128298 | F | LC | ETL.7780.POLE.WOOD | 40611735 | LAKEVLLE | HUMBOLDT | 2020-10-19 |  | ETL.7780 | PHILO JCT-ELK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40611735 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 1.5125e-05 | 4568.4863
120136328 | F | LC | ETL.7590.POLE.WDPS | 44985732 | MOSSLNDG | DE ANZA | 2020-11-30 | 2021-02-09 | ETL.7590 | MONTA VISTA-BURNS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 2 | Within Both | DLFL | 42565532 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.23518 | 1424.8561
120210237 | F | LC | ETL.4040.POLE.NWOD | 44874419 | TABLEMTN | NORTH VALLEY | 2020-11-06 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44874419 | 2020-01-18 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2020-01-18 | Polymer | Dead End |  |  |  |  | 0.00027576 | 253.2084
120237255 | F | LC | ETL.1350.POLE.STPS | 44994609 | TABLEMTN | NORTH VALLEY | 2020-11-30 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44993924 | 2020-06-16 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 5.1506e-05 | 411.4229
120240652 | F | LC | ETL.9340.POLE.NWOD | 44180723 | FRESNO | YOSEMITE | 2020-12-04 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44180723 | 2015-06-18 | Light Duty Steel Pole | T-1 - Tri Post | 2015-06-18 | Non Ceramic | Post |  |  |  |  | 0.00060561 | 5445.5674
120254690 | F | LC | ETL.7170.POLE.WOOD | 44871205 | LAKEVLLE | NORTH BAY | 2020-12-17 |  | ETL.7170 | IGNACIO-ALTO-SAUSALITO #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871205 | 2019-09-19 | Single Wood Pole | 3HP - 3 Horizontal Post | 2019-09-19 | Polymer | Post |  |  |  |  | 0.23091 | 580.7642
120485825 | E | LC | ETL.1420.TOWR | 40865474 | SACTO | SIERRA | 2021-02-01 | 2021-11-23 | ETL.1420 | DRUM-RIO OSO #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | DLFL | 40865474 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-08-08 | Porcelain | Dead End |  |  |  |  | 2.2971e-07 | 1360.4569
120486841 | E | LC | ETL.1650.POLE.WOOD | 40585258 | LAKEVLLE | SONOMA | 2021-02-01 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40585258 | 1991-01-01 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper |  | Porcelain | Dead End |  |  |  |  | 0.00067945 | 5243.5029 | 3.5627
120634384 | F | LC | ETL.5290.TOWR | 40863200 | PISMOBCH | LOS PADRES | 2021-03-11 |  | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40863200 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-23 | Glass | Suspension |  |  |  |  | 2.5972e-05 | 1870.6561 | 0.048584
120634384 | F | LC | ETL.5290.TOWR | 40863200 | PISMOBCH | LOS PADRES | 2021-03-11 |  | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40863200 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-19 | Glass | Suspension |  |  |  |  | 2.5972e-05 | 1870.6561 | 0.048584
120661886 | F | LC | ETL.4680.TOWR | 40651559 | LAKEVLLE | SONOMA | 2021-03-17 | 2021-07-14 | ETL.4680 | FULTON-IGNACIO #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40651559 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-07 | Glass | Double Dead End |  |  |  |  | 0.038768 | 221.8368
120661886 | F | LC | ETL.4680.TOWR | 40651559 | LAKEVLLE | SONOMA | 2021-03-17 | 2021-07-14 | ETL.4680 | FULTON-IGNACIO #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40651559 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.038768 | 221.8368
120689120 | E | LC | ETL.5790.INSL.CERA | 40895644 | VICTOR | STOCKTON | 2021-03-24 |  | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40870622 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 2.548e-06 | 126.8157 | 0.00032312
120691905 | F | LC | ETL.6621.TOWR | 42580656 | TABLEMTN | NORTH VALLEY | 2021-03-25 |  | ETL.6621 | OROVILLE-THERMALITO-TABLE MTN #1 (CDWR) | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 42580656 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 9.5507e-08 | 8420.0293
120695046 | F | LC | ETL.5630.TOWR | 40815723 | TABLEMTN | NORTH VALLEY | 2021-03-25 |  | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40815723 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End - Suspension |  |  |  |  | 1.1753e-05 | 6806.3008 | 0.079994
120696617 | E | LC | ETL.5140.POLE.WDPS | 44553752 | SACTO | SACRAMENTO | 2021-03-26 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | PEND
120706617 | E | LC | ETL.3820.TOWR | 40642811 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40642811 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 8.5967e-07 | 1962.8882 | 0.0016874
120715093 | B | LC | ETL.8480.INSL.NCER | 44917667 | PISMOBCH | LOS PADRES | 2021-03-30 | 2021-04-05 | ETL.8480 | ATASCADERO-CAYUCOS | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40684718 | 1954-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2020-05-15 | Glass | Post |  |  |  |  | 7.8563e-05 | 2879.8447
120735138 | E | LC | ETL.1650.POLE.WOOD | 40750639 | LAKEVLLE | SONOMA | 2021-04-02 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40750639 | 1966-01-01 | Single Wood Pole | WB - Wishbone | 1966-01-01 | Porcelain | Suspension |  |  |  |  | 0.00014986 | 4055.4705 | 0.60774
120740505 | F | LC | ETL.6880.POLE.WOOD | 40912471 | LAKEVLLE | SONOMA | 2021-04-03 | 2021-04-26 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40912471 |  | Single Wood Pole | T2N | 2021-04-15 | Polymer | Post |  |  |  |  | 0.01603 | 476.0715
120752545 | F | LC | ETL.3820.TOWR | 40860910 | VICTOR | STOCKTON | 2021-04-06 | 2021-07-19 | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40860910 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 2.0601e-07 | 533.0465
120763830 | E | LC | ETL.6880.POLE.WOOD | 40905730 | LAKEVLLE | SONOMA | 2021-04-08 | 2021-08-30 | ETL.6880 | FULTON-CALISTOGA | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40905730 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0018425 | 3880.3723
120770464 | E | LC | ETL.4100.INSL.NCER | 40781276 | LAKEVLLE | SACRAMENTO | 2021-04-09 |  | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40752810 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1913-01-01 | Non Ceramic | Suspension |  |  |  |  | 4.781e-05 | 5399.8154 | 0.25817
120789411 | F | LC | ETL.8250.POLE.WOOD | 40908866 | VICTOR | STOCKTON | 2021-04-10 | 2021-09-28 | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40908866 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00019854 | 3042.1279
120806922 | A | LC | ETL.4590.TOWR | 40910132 | TABLEMTN | NORTH VALLEY | 2021-04-13 | 2021-04-14 | ETL.4590 | CRESTA-RIO OSO | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910132 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.0057e-05 | 3986.9912
120807629 | E | LC | ETL.3830.INSL | 40794311 | VICTOR | STOCKTON | 2021-04-12 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40763946 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 2.4415e-05 | 4187.5937 | 0.10224
120812919 | F | LC | ETL.4392.TOWR | 41129311 | LAKEVLLE | SONOMA | 2021-04-14 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 41129311 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.0085536 | 3391.9678
120812919 | F | LC | ETL.4392.TOWR | 41129311 | LAKEVLLE | SONOMA | 2021-04-14 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 41129311 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.0085536 | 3391.9678
120814932 | E | LC | ETL.8365.POLE.WOOD | 40587735 | EUREKA | HUMBOLDT | 2021-04-14 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40587735 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0034804
120833336 | E | LC | ETL.3830.TOWR | 40803332 | VICTOR | STOCKTON | 2021-04-17 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40803332 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.2675e-05 | 7492.2583 | 0.094967
120839722 | E | LC | ETL.4440.INSL.CERA | 40616994 | TABLEMTN | NORTH VALLEY | 2021-04-12 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591416 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Porcelain | Suspension |  |  |  |  | 4.6176e-08 | 842.2069 | 3.889e-05
120850280 | F | LC | ETL.1400.POLE.NWOD | 44948557 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44948557 | 2019-07-15 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2019-07-15 | Glass | Suspension |  |  |  |  | 2.0639e-05 | 4145.3232
120851297 | E | LC | ETL.4050.POLE.NWOD | 44965638 | LAKEVLLE | SONOMA | 2021-04-20 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44965638 | 2020-04-02 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-04-02 | Glass | Dead End |  |  |  |  | 2.0668e-05 | 4230.5894 | 0.087436
120857487 | E | LC | ETL.1400.INSL.NCER | 40623106 | VICTOR | YOSEMITE | 2021-04-21 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40596732 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0026299
120857487 | E | LC | ETL.1400.INSL.NCER | 40623106 | VICTOR | YOSEMITE | 2021-04-21 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40596732 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0026299
120860659 | E | LC | ETL.3830.TOWR | 40860791 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40860791 | 1927-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1999-01-01 | Polymer | Dead End |  |  |  |  | 7.7118e-07 | 10386.085 | 0.0080096
120863684 | E | LC | ETL.9340.POLE.NWOD | 44663904 | FRESNO | FRESNO | 2021-04-21 | 2021-06-04 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44663904 | 2018-10-03 | Light Duty Steel Pole | T-1 - Tri Post | 2018-10-03 | Polymer | Post |  |  |  |  | 0.00062538 | 5445.5674
120864033 | E | LC | ETL.2720.INSL | 40878734 | CONCORD | DIABLO | 2021-04-21 |  | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | HFRA Removal | PEND | 40857634 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1980-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.00013677 | 0.065147 | 8.9102e-06
120866198 | F | LC | ETL.6470.POLE.WOOD | 40760693 | SACTO | SACRAMENTO | 2021-04-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40760693 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.0091479 | 696.2946
120878673 | E | LC | ETL.3820.TOWR | 40822483 | VICTOR | STOCKTON | 2021-04-24 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40822483 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 0.00022438 | 428.7104 | 0.096195
120894138 | E | LC | ETL.5300.TOWR | 40762342 | PISMOBCH | LOS PADRES | 2021-04-14 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40762342 | 1960-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 8.1943e-07 | 4654.7246 | 0.0038142
120903744 | F | LC | ETL.7550.POLE.NWOD | 40768549 | LAKEVLLE | SONOMA | 2021-04-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40768549 | 2010-01-01 | Tubular Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 5.7486e-07 | 3608.3047
120911527 | E | LC | ETL.5930.TOWR | 40676028 | LAKEVLLE | DIABLO | 2021-04-30 | 2021-10-25 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676028 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.7398e-08 | 142.9306 | 2.4867e-06
120911527 | E | LC | ETL.5930.TOWR | 40676028 | LAKEVLLE | DIABLO | 2021-04-30 | 2021-10-25 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676028 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-24 | Glass | Suspension |  |  |  |  | 1.7398e-08 | 142.9306 | 2.4867e-06
120914636 | E | LC | ETL.5930.TOWR | 40656833 | LAKEVLLE | DIABLO | 2021-05-01 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40656833 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 7.6705e-09 | 284.7965 | 2.1845e-06
120914636 | E | LC | ETL.5930.TOWR | 40656833 | LAKEVLLE | DIABLO | 2021-05-01 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40656833 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-11-06 | Glass | Suspension |  |  |  |  | 7.6705e-09 | 284.7965 | 2.1845e-06
120930806 | E | LC | ETL.8060.POLE.WOOD | 40702051 | SACTO | SACRAMENTO | 2021-05-04 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40702051 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.077758 | 617.0731
120932444 | B | LC | ETL.6500.POLE.NWOD | 44153662 | SACTO | SACRAMENTO | 2021-05-04 | 2021-06-30 | ETL.6500 | COLGATE-PALERMO | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44153662 |  | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | Suspension |  |  |  |  | 4.932e-05 | 428.1771
120941880 | F | LC | ETL.6890.POLE.NWOD | 44963411 | LAKEVLLE | SONOMA | 2021-05-06 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44963411 | 2019-11-09 | Light Duty Steel Pole | T-1 - Tri Post | 2019-11-09 | Polymer | Post |  |  |  |  | 0.00019244 | 3170.8542
120953605 | F | LC | ETL.1820.POLE.WDPS | 44565588 | EUREKA | HUMBOLDT | 2021-05-08 | 2021-07-01 | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44564260 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.21109 | 5073.1993
121116456 | E | LC | ETL.4590.TOWR | 40906788 | TABLEMTN | NORTH VALLEY | 2021-04-19 |  | ETL.4590 | CRESTA-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40906788 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.7209e-05 | 15.8851 | 0.00059106
121186766 | E | LC | ETL.7550.POLE.NWOD | 40876350 | LAKEVLLE | SONOMA | 2021-05-11 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40876350 |  | Light Duty Steel Pole | T-1 - Tri Post | 2011-02-27 | Polymer | Post |  |  |  |  | 9.4446e-11 | 15.8807
121187108 | E | LC | ETL.7610.POLE.WOOD | 40874210 | METCALF | SAN JOSE | 2021-05-11 |  | ETL.7610 | MONTA VISTA-LOS GATOS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40874210 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Non Ceramic | Post |  |  |  |  | 0.00047304 | 0.066432 | 3.1425e-05
121332942 | E | LC | ETL.4440.INSL.CERA | 40691245 | TABLEMTN | NORTH VALLEY | 2021-05-14 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40660506 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.00016132 | 3638.1943 | 0.58691
121345141 | F | LC | ETL.8480.POLE.WOOD | 40819609 | PISMOBCH | LOS PADRES | 2021-04-23 | 2021-10-07 | ETL.8480 | ATASCADERO-CAYUCOS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40819609 | 1954-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1954-01-01 | Polymer | Suspension |  |  |  |  | 0.00030533 | 648.5239
121383389 | F | LC | ETL.6500.POLE.NWOD | 44665703 | SACTO | SIERRA | 2021-05-10 | 2021-07-08 | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44665703 | 2018-07-06 | Light Duty Steel Pole | T2N | 2018-07-06 | Polymer | Post |  |  |  |  | 1.2655e-05 | 712.8596
121384289 | E | LC | ETL.6110.INSL.CERA | 40851076 | METCALF | MISSION | 2021-05-21 | 2021-07-12 | ETL.6110 | TESLA-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40822145 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 7.8359e-05 | 4246.6318
121384875 | F | LC | ETL.6760.POLE.WOOD | 40766658 | SACTO | SIERRA | 2021-05-13 | 2021-06-25 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40766658 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.10166 | 332.3255
121385211 | F | LC | ETL.1420.TOWR | 40670134 | SACTO | SIERRA | 2021-05-12 | 2021-07-19 | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40670134 | 1913-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2019-08-30 | Glass | Dead End |  |  |  |  | 4.8222e-07 | 0.075274
121385507 | E | LC | ETL.1430.TOWR | 40746580 | SACTO | SIERRA | 2021-05-12 |  | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40746580 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2016-11-14 | Ceramic | Suspension |  |  |  |  | 0.0010538 | 15.9216 | 0.016778
121396644 | E | LC | ETL.1400.INSL | 40670171 | VICTOR | YOSEMITE | 2021-05-13 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40643179 | 1956-01-01 | Single Wood Pole | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.0018621 | 2626.426 | 4.8906
121405381 | F | LC | ETL.6870.POLE.NWOD | 44340601 | SACTO | SIERRA | 2021-05-19 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44340601 | 2014-10-01 | Light Duty Steel Pole | T-1 - Tri Post | 2014-10-01 | Non Ceramic | Post |  |  |  |  | 0.0016816 | 0.065152
121405531 | E | LC | ETL.5540.TOWR | 40655509 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40655509 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 1.0109e-06 | 1824.0908 | 0.001844
121418282 | E | LC | ETL.8290.POLE.WOOD | 40867830 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40867830 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.09292 | 795.1825 | 73.8884
121420258 | F | LC | ETL.1401.POLE.WDPS | 44390868 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1401 | BEARDSLEY TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44390867 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.022794 | 348.1624 | 7.936
121423129 | E | LC | ETL.1400.POLE.STPS | 44806646 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44789703 | 2019-06-21 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00020168 | 158.2923 | 0.031924
121430936 | F | LC | ETL.7000.POLE.WOOD | 40868225 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40868225 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00013599 | 47.5141
121443235 | A | LC | ETL.1440.INSL | 40784570 | SACTO | SIERRA | 2021-06-01 | 2021-06-07 | ETL.1440 | DRUM-SUMMIT #1 | Emergency | Storm Related | [Repair, Completed] | Tier2 |  |  | COMP
121443283 | B | LC | ETL.6979.INSL.NCER | 40577889 | LAKEVLLE |  | 2021-06-01 | 2021-06-14 | ETL.6979 | MONTE RIO-FORT ROSS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40575979 | 1998-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.2543 | 1737.1464
121450313 | B | LC | ETL.5640.TOWR | 40758172 | TABLEMTN | NORTH VALLEY | 2021-06-02 | 2021-07-26 | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758172 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 6.6115e-09 | 4167.8633
121451530 | E | LC | ETL.3830.INSL.NCER | 40639674 | VICTOR | STOCKTON | 2021-06-03 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40612625 | 1927-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1999-01-01 | Polymer | Dead End |  |  |  |  | 5.5338e-07 | 6219.292 | 0.0034416
121467817 | E | LC | ETL.1350.POLE.WDPS | 44512161 | TABLEMTN |  | 2021-05-29 | 2021-08-09 | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40657292 | 2012-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.012475 | 2918.4626
121483113 | B | LC | ETL.6880.INSL.CERA | 44286195 | LAKEVLLE |  | 2021-06-07 | 2021-07-08 | ETL.6880 | FULTON-CALISTOGA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40905743 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00094514 | 4800.3047
121485763 | F | LC | ETL.1820.POLE.STPS | 44395526 | EUREKA | HUMBOLDT | 2021-05-28 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395525 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.020877 | 405.5042
121485867 | E | LC | ETL.4050.POLE.WOOD | 40581127 | LAKEVLLE | SONOMA | 2021-05-31 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40581127 | 1970-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1970-01-01 | Ceramic | Post |  |  |  |  | 0.00052108 | 1554.2012 | 0.80986
121486100 | F | LC | ETL.7550.POLE.NWOD | 40698091 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40698091 |  | Light Duty Steel Pole | T1-1A |  | Polymer | Post |  |  |  |  | 2.6697e-08 | 665.5179
121489485 | E | LC | ETL.6030.TOWR | 40584218 | MIDWAY | KERN | 2021-06-07 |  | ETL.6030 | MIDWAY-WHIRLWIND | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40584218 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 8.9773e-05 | 6859.2124 | 0.61577
121492593 | F | LC | ETL.6890.POLE.WOOD | 40824189 | LAKEVLLE | SONOMA | 2021-06-02 | 2021-07-12 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 0.00090649 | 2867.9473
121493484 | F | LC | ETL.6890.POLE.WOOD | 40692993 | LAKEVLLE | SONOMA | 2021-06-02 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40692993 | 1986-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0034846 | 870.6168
121493695 | F | LC | ETL.2790.TOWR | 40580828 | CONCORD | EAST BAY | 2021-06-03 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40580828 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.9672e-08 | 0.066303 | 1.9673e-09
121493695 | F | LC | ETL.2790.TOWR | 40580828 | CONCORD | EAST BAY | 2021-06-03 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40580828 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 2.9672e-08 | 0.066303 | 1.9673e-09
121497768 | B | LC | ETL.4440.INSL | 40890183 | TABLEMTN | NORTH VALLEY | 2021-06-08 | 2021-07-08 | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40867214 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 6.0733e-05 | 253.1639
121500249 | F | LC | ETL.5650.TOWR | 40810156 | TABLEMTN | NORTH VALLEY | 2021-06-03 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40810156 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-09-14 | Ceramic | Suspension |  |  |  |  | 8.5753e-08 | 6640.8916 | 0.00056948
121513975 | E | LC | ETL.1220.INSL.CERA | 40792714 | MOSSLNDG | CENTRAL COAST | 2021-06-03 |  | ETL.1220 | CAMP EVERS-PAUL SWEET | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40762462 |  | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 8.2997e-06 | 4.8096 | 3.9918e-05
121516737 | E | LC | ETL.6030.TOWR | 40749810 | MIDWAY | KERN | 2021-06-05 |  | ETL.6030 | MIDWAY-WHIRLWIND | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40749810 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 5.4989e-05 | 6700.9697 | 0.36848
121516791 | E | LC | ETL.4392.INSL.CERA | 40718525 | LAKEVLLE | SONOMA | 2021-06-03 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40670680 | 1973-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 2.2995e-07 | 1837.5829 | 0.00042256
121521774 | E | LC | ETL.1350.POLE.WDPS | 44552557 | TABLEMTN |  | 2021-06-11 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44551567 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 0.20927 | 348.1497 | 72.8563
121523289 | E | LC | ETL.1810.POLE.WDPS | 44322590 | EUREKA | HUMBOLDT | 2021-06-08 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44322589 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.037845 | 28.5482 | 1.0804
121541395 | E | LC | ETL.6722.POLE.WOOD | 44190970 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.6722 | FORKS OF THE BUTTE TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44190970 | 1997-01-01 | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.00024172 | 237.3649 | 0.057376
121543886 | E | LC | ETL.6500.POLE.WOOD | 40874639 | SACTO | SIERRA | 2021-06-10 |  | ETL.6500 | COLGATE-PALERMO | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40874639 |  | Single Wood Pole | T2N | 2018-06-29 | Polymer | Post |  |  |  |  | 0.0010655 | 95.0648 | 0.10129
121544956 | F | LC | ETL.5420.POLE.STPS | 44400021 | TABLEMTN | NORTH VALLEY | 2021-06-14 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44400019 | 2017-11-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.8269e-05 | 316.5195
121562573 | F | LC | ETL.6880.POLE.NWOD | 45070110 | LAKEVLLE | SONOMA | 2021-06-15 |  | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45070110 | 2019-08-14 | Lattice Steel Pole | DDE - Double Dead End | 2019-08-14 | Glass | Dead End |  |  |  |  | 3.2025e-06 | 142.5961
121567665 | F | LC | ETL.4040.POLE.NWOD | 44999543 | TABLEMTN | NORTH VALLEY | 2021-06-12 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44999543 | 2020-08-06 | Light Duty Steel Pole | 3P SV - 3 Pole Single Vertical | 2020-08-06 | Glass | Suspension |  |  |  |  | 2.3902e-05 | 838.6274
121572403 | F | LC | ETL.6880.POLE.STPS | 44647528 | LAKEVLLE | NORTH BAY | 2021-06-15 | 2021-07-09 | ETL.6880 | FULTON-CALISTOGA | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44647528 | 2018-08-26 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2019-10-31 | Glass | Dead End |  |  |  |  | 3.4212e-05
121572403 | F | LC | ETL.6880.POLE.STPS | 44647528 | LAKEVLLE | NORTH BAY | 2021-06-15 | 2021-07-09 | ETL.6880 | FULTON-CALISTOGA | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44647528 | 2018-08-26 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2019-10-31 | Glass | Dead End |  |  |  |  | 3.4212e-05
121572403 | F | LC | ETL.6880.POLE.STPS | 44647528 | LAKEVLLE | NORTH BAY | 2021-06-15 | 2021-07-09 | ETL.6880 | FULTON-CALISTOGA | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44647528 | 2018-08-26 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | 2019-10-31 | Glass | Dead End |  |  |  |  | 3.4212e-05
121573673 | F | LC | ETL.5140.POLE.STPS | 45112063 | SACTO | SIERRA | 2021-06-17 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45111952 | 2020-10-10 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [8 empty] | 0.06515
121607271 | F | LC | ETL.7212.POLE.STPS | 44264957 | METCALF | PENINSULA | 2021-06-23 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44264956 | 2009-11-20 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.14481 | 704.4957
121662741 | E | LC | ETL.2395.POLE.WOOD | 45013477 | TABLEMTN | NORTH VALLEY | 2021-06-28 |  | ETL.2395 | GRIZZLY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45013477 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 0.00017633 | 3021.0042 | 0.5327
121662890 | E | LC | ETL.6861.POLE.WOOD | 40615042 | LAKEVLLE | HUMBOLDT | 2021-07-01 | 2021-09-14 | ETL.6861 | KONOCTI-EAGLE ROCK | Hardware-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40615042 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.00040547 | 300.6788
121679085 | E | LC | ETL.9240.TOWR | 43249510 | PISMOBCH | LOS PADRES | 2021-07-07 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier3 | Tier 3 | Within Both | PEND | 43249510 |  | LATTICE STEEL TOWER | [9 empty] | 2470.1736
121690054 | E | LC | ETL.1720.POLE.WDPS | 44401050 | MOSSLNDG | CENTRAL COAST | 2021-07-05 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44401049 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0007381 | 490.6567 | 0.36215
121691500 | B | LC | ETL.4040.POLE.NWOD | 45100465 | TABLEMTN | NORTH VALLEY | 2021-07-08 | 2021-08-12 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45100465 | 2020-09-23 | Light Duty Steel Pole | DDE - Double Dead End | 2020-09-23 | Ceramic | Dead End |  |  |  |  | 0.00013274 | 174.1138
121707187 | E | LC | ETL.7820.POLE.WOOD | 40826209 | LAKEVLLE | HUMBOLDT | 2021-07-06 |  | ETL.7820 | POTTER VALLEY-WILLITS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40826209 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Pin |  |  |  |  | 0.001192 | 650.3827 | 0.77527
121717956 | E | LC | ETL.3770.TOWR | 40746157 | CONCORD | DIABLO | 2021-07-07 |  | ETL.3770 | SOBRANTE-R #1 | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40746157 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1923-01-01 | Ceramic | Suspension |  |  |  |  | 0.00024733 | 443.3865 | 0.10966
121731291 | E | LC | ETL.1400.POLE.WDPS | 44770772 | VICTOR | STOCKTON | 2021-07-07 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40643188 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.015993 | 2246.7366 | 35.9329
121738507 | F | LC | ETL.1820.POLE.NWOD | 45092601 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45092601 | 2017-09-12 | Light Duty Steel Pole | 3P DDE - 3 Pole Double Dead End | 2017-09-12 | Polymer | Dead End |  |  |  |  | 0.059859 | 0.065148
121750020 | E | LC | ETL.7550.POLE.WOOD | 40768543 | LAKEVLLE | HUMBOLDT | 2021-07-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40768543 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0039594 | 3284.7499 | 13.0056
121764526 | F | LC | ETL.1820.POLE.WDPS | 44562889 | EUREKA | HUMBOLDT | 2021-07-13 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562378 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.23795 | 47.5295 | 11.3095
121778552 | E | LC | ETL.1820.POLE.WDPS | 44560557 | EUREKA | HUMBOLDT | 2021-07-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Right of Way | Encroachment | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44560104 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.043289 | 23.8531
121781801 | E | LC | ETL.5420.POLE.WDPS | 44558963 | TABLEMTN | NORTH VALLEY | 2021-07-20 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44558527 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0051346 | 649.1145 | 3.3329
121781807 | E | LC | ETL.2390.POLE.WDPS | 44391255 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391254 |  | 2-Pole Wood | FSS - Field Switch Structure | [7 empty] | 5.8388e-05 | 4273.2705 | 0.24951
121783189 | E | LC | ETL.2390.INSL.NCER | 40827975 | VICTOR | STOCKTON | 2021-07-20 | 2021-08-09 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44391208 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 0.00013765
121783189 | E | LC | ETL.2390.INSL.NCER | 40827975 | VICTOR | STOCKTON | 2021-07-20 | 2021-08-09 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44391208 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Polymer | Dead End |  |  |  |  | 0.00013765
121810530 | B | LC | ETL.6760.INSL.CERA | 40898171 | SACTO | SACRAMENTO | 2021-07-27 | 2021-09-30 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873765 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | [5 empty] | 0.1228 | 237.3428 | 29.1447
121811610 | F | LC | ETL.6480.POLE.NWOD | 45120521 | SACTO | NORTH VALLEY | 2021-07-27 | 2021-08-09 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45120521 | 2021-06-20 | Light Duty Steel Pole | T-1 - Tri Post | 2021-06-20 | Polymer | Post | [5 empty] | 253.3131
121813037 | E | LC | ETL.8405.POLE.WOOD | 40874885 | SACTO | SIERRA | 2021-07-26 | 2021-08-23 | ETL.8405 | MIDDLE FORK #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL | [11 empty] | 0.42896 | 142.4895
121814972 | E | LC | ETL.4316.INSL.CERA | 40691000 | TABLEMTN | NORTH VALLEY | 2021-07-29 |  | ETL.4316 | PARADISE-TABLE MTN | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | PEND
121820057 | F | LC | ETL.6480.POLE.NWOD | 45120515 | SACTO | NORTH VALLEY | 2021-07-27 | 2021-08-23 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 45120515 | 2021-06-20 | Light Duty Steel Pole | T-1 - Tri Post | 2021-06-20 | Polymer | Post | [5 empty] | 253.3119
121824783 | F | LC | ETL.7212.POLE.WDPS | 44761217 | METCALF | PENINSULA | 2021-07-31 | 2021-08-11 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40591470 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.31918 | 1519.1747
121860125 | B | LC | ETL.6300.POLE.WOOD | 40615000 | TABLEMTN | NORTH VALLEY | 2021-08-07 | 2021-09-23 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.8859e-06 | 15.8815
121883934 | E | LC | ETL.2390.POLE.NWOD | 40575680 | VICTOR | STOCKTON | 2021-08-11 | 2021-10-24 | ETL.2390 | MELONES-CURTIS | Switch | Out of Adjustment | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40575680 | 2010-01-01 | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 2.2267e-08 | 2437.8394 | 5.4285e-05
121908841 | E | LC | ETL.6470.POLE.NWOD | 45133126 | SACTO | SIERRA | 2021-08-16 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45133126 | 2021-07-13 | Light Duty Steel Pole | FSS - Field Switch Structure | [8 empty] | 142.4516
121934474 | E | LC | ETL.8170.POLE.WOOD | 40642855 | EUREKA | HUMBOLDT | 2021-08-22 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40642855 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.0069074 | 47.5295 | 0.3283
122014781 | E | LC | ETL.6750.POLE.WOOD | 42611956 | TABLEMTN | NORTH VALLEY | 2021-09-08 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 42611956 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 2.4052e-05 | 79.1724 | 0.0019043
122019147 | F | LC | ETL.8650.POLE.NWOD | 44420167 | FRESNO | FRESNO | 2021-09-09 |  | ETL.8650 | EXCHEQUER-INDIAN FLAT | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44420167 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0024618 | 5678.02
122021951 | E | LC | ETL.1180.POLE.WOOD | 44399902 | TABLEMTN | NORTH VALLEY | 2021-09-09 |  | ETL.1180 | BUTTE VALLEY-CARIBOU | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44399902 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper |  | Porcelain | [5 empty] | 0.0023649 | 5538.7192 | 13.0985
122282459 | E | LC | ETL.5400.TOWR | 40762212 | TABLEMTN | NORTH VALLEY | 2021-11-01 |  | ETL.5400 | PIT #3-PIT #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40762212 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0069928 | 1679.5538 | 11.7448
118797486 | B | LC | ETL.4590.TOWR | 40910127 | TABLEMTN | NORTH VALLEY | 2020-04-08 | 2020-06-11 | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910127 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-02 | Glass | Suspension |  |  |  |  | 2.7244e-05 | 267.8125
118910489 | E | LC | ETL.4590.TOWR | 40910167 | TABLEMTN | NORTH VALLEY | 2020-04-10 | 2020-09-24 | ETL.4590 | CRESTA-RIO OSO | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40910167 |  | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-03-15 | Ceramic | Suspension |  |  |  |  | 2.8218e-05 | 142.7942
118926631 | E | LC | ETL.6440.POLE.WOOD | 40760018 | TABLEMTN | NORTH VALLEY | 2020-04-16 | 2020-06-29 | ETL.6440 | COLEMAN-RED BLUFF | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760018 |  | Single Wood Pole | T2N | 2020-05-14 | Polymer | Post |  |  |  |  | 0.0025381 | 3265.0894
118961073 | E | LC | ETL.6220.POLE.WOOD | 40614612 | EUREKA | HUMBOLDT | 2020-04-29 | 2021-04-21 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118964373 | F | LC | ETL.7520.POLE.NWOD | 40750147 | LAKEVLLE | HUMBOLDT | 2020-04-24 |  | ETL.7520 | MENDOCINO-PHILO JCT-HOPLAND | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40750147 |  | Lattice Steel Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 1.8631e-05 | 1112.0168
119026485 | F | LC | ETL.8410.POLE.WOOD | 40763071 | LAKEVLLE | HUMBOLDT | 2020-05-07 |  | ETL.8410 | ELK-GUALALA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40763071 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Porcelain | Suspension |  |  |  |  | 0.0645 | 0.065148
119083412 | E | LC | ETL.1050.TOWR | 40806883 | FRESNO | FRESNO | 2020-05-27 | 2021-04-19 | ETL.1050 | BALCH-SANGER | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40806883 | 1961-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1923-01-01 | Porcelain | Suspension |  |  |  |  | 0.0030644 | 4655.1548
119085435 | E | LC | ETL.3770.TOWR | 40746157 | CONCORD | EAST BAY | 2020-05-18 | 2021-04-08 | ETL.3770 | SOBRANTE-R #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746157 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1923-01-01 | Ceramic | Suspension |  |  |  |  | 0.00024733 | 443.3865
119088231 | E | LC | ETL.5430.POLE.WDPS | 44561518 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2020-07-14 | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119093826 | F | LC | ETL.6880.POLE.WOOD | 44922946 | LAKEVLLE | HUMBOLDT | 2020-05-19 | 2021-04-05 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44922946 | 2020-03-02 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2020-03-02 | Glass | Suspension |  |  |  |  | 0.00065557 | 696.472
119096851 | E | LC | ETL.7790.POLE.WOOD | 40674158 | TABLEMTN | NORTH VALLEY | 2020-06-02 | 2020-12-01 | ETL.7790 | PIT #1-MCARTHUR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40674158 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | Dead End |  |  |  |  | 0.040074 | 4131.7891
119102920 | F | LC | ETL.1430.TOWR | 40815314 | SACTO | SIERRA | 2020-05-19 | 2021-01-27 | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40815314 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.0029035 | 269.0173
119108730 | E | LC | ETL.6760.POLE.WOOD | 40589537 | SACTO | SIERRA | 2020-05-28 | 2021-03-11 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40589537 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.070016 | 63.348
119110446 | E | LC | ETL.1401.POLE.WOOD | 42834637 | VICTOR | YOSEMITE | 2020-05-26 | 2021-04-15 | ETL.1401 | BEARDSLEY TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42834637 |  | Single Wood Pole | DE - Dead End |  | Porcelain | [5 empty] | 0.0054257 | 2246.7366
119115267 | E | LC | ETL.7290.POLE.WOOD | 40677185 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-03-18 | ETL.7290 | KILARC-CEDAR CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40677185 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Unknown |  |  |  |  | 0.0056293 | 666.5034
119166113 | F | LC | ETL.6480.POLE.WOOD | 40655138 | SACTO | SIERRA | 2020-06-15 | 2021-06-14 | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40655138 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.22184 | 664.4426
119179062 | F | LC | ETL.6280.POLE.WOOD | 40758673 | TABLEMTN | NORTH VALLEY | 2020-06-16 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758673 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00023641 | 6705.0029
119179329 | E | LC | ETL.6310.POLE.WOOD | 40759466 | TABLEMTN | NORTH VALLEY | 2020-06-16 | 2021-08-11 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759466 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 5.2169e-06 | 4087.3262
119181039 | F | LC | ETL.6280.POLE.WOOD | 40758802 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758802 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 9.6347e-05 | 5934.9365
119189105 | F | LC | ETL.1073.POLE.WDPS | 44769569 | VICTOR | YOSEMITE | 2020-06-17 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40643217 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00014147 | 917.3254
119201069 | E | LC | ETL.9340.POLE.NWOD | 43680877 | FRESNO | FRESNO | 2020-06-23 | 2020-08-06 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 43680877 | 2016-02-11 | Light Duty Steel Pole | T-1 - Tri Post | 2016-02-11 | Polymer | Post |  |  |  |  | 0.00060553 | 5445.5674
119201518 | F | LC | ETL.6470.POLE.WOOD | 40869669 | SACTO | SIERRA | 2020-06-23 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40869669 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.24444 | 110.8102
119222765 | E | LC | ETL.8290.POLE.WOOD | 40700104 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2021-04-21 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119236690 | E | LC | ETL.6220.POLE.WOOD | 40769355 | EUREKA | HUMBOLDT | 2020-06-30 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40769355 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.054248 | 300.5862 | 16.3062
119290398 | E | LC | ETL.1370.POLE.WOOD | 40669002 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-06-23 | ETL.1370 | DIVIDE-CABRILLO #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40669002 | 1960-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1988-01-01 | Porcelain | Suspension |  |  |  |  | 0.001766 | 3446.0557
119291043 | E | LC | ETL.7180.POLE.WOOD | 40577322 | LAKEVLLE | SONOMA | 2020-07-01 | 2021-04-07 | ETL.7180 | IGNACIO-BOLINAS #2 | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40577322 |  | Single Wood Pole | T-1 - Tri Post | 2021-04-03 | Polymer | Post |  |  |  |  | 2.3218e-05 | 412.5442
119300324 | B | LC | ETL.4220.INSL.NCER | 40840868 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2020-08-12 | ETL.4220 | WOODLEAF-PALERMO | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119308059 | B | LC | ETL.7140.POLE | 40701374 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-20 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] |  | Tier 3 | Within Both | COMP | 40701374 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.36745 | 3102.6682
119311201 | F | LC | ETL.8060.POLE.WOOD | 40669472 | SACTO | SIERRA | 2020-07-02 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40669472 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.077758 | 617.0731
119325949 | F | LC | ETL.4040.POLE.STPS | 44647155 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44646908 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00020369 | 538.0957
119329743 | E | LC | ETL.5220.INSL.CERA | 44377028 | METCALF | SAN JOSE | 2020-07-08 | 2021-03-15 | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119333685 | E | LC | ETL.2060.POLE.WOOD | 40584472 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-08-12 | ETL.2060 | FORT BRAGG-ELK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40584472 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 2021-08-02 | Glass | Suspension |  |  |  |  | 0.096111 | 0.066432
119337038 | E | LC | ETL.6980.POLE.WOOD | 40750317 | LAKEVLLE | SONOMA | 2020-07-09 | 2021-06-17 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40750317 | 2003-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-06-09 | Glass | Dead End |  |  |  |  | 0.087025 | 0.065152
119341063 | F | LC | ETL.6980.POLE.WOOD | 40606927 | LAKEVLLE | SONOMA | 2020-07-09 | 2021-01-28 | ETL.6980 | FORT ROSS-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40606927 | 1986-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2021-06-11 | Glass | Suspension |  |  |  |  | 0.12989 | 15.8873
119353451 | F | LC | ETL.6280.POLE.NWOD | 44688366 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-02-10 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44688366 | 2018-11-24 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-24 | Polymer | Post |  |  |  |  | 4.1476e-07 | 4065.6267
119356635 | F | LC | ETL.6280.POLE.WOOD | 40649923 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40649923 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Other |  |  |  |  | 9.5208e-05 | 490.3705
119359687 | E | LC | ETL.1370.INSL.CERA | 40788151 | PISMOBCH | LOS PADRES | 2020-07-09 | 2021-07-13 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119367518 | B | LC | ETL.1110.POLE.WDPS | 44232671 | TABLEMTN | HUMBOLDT | 2020-07-13 | 2020-08-14 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44232670 | 2014-10-28 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017539 | 3692.7366
119367968 | E | LC | ETL.1110.POLE.WDPS | 44232662 | TABLEMTN | HUMBOLDT | 2020-07-14 | 2021-04-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44232659 | 2014-10-28 | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.0012206 | 3154.0374
119371227 | F | LC | ETL.6290.POLE.WOOD | 40698825 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-09-13 | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40698825 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2011-01-01 | Polymer | Post |  |  |  |  | 0.0097571 | 63.3304
119377984 | F | LC | ETL.1430.TOWR | 40805175 | SACTO | SACRAMENTO | 2020-07-15 | 2021-03-01 | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805175 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical | 1990-01-01 | Ceramic | Post |  |  |  |  | 0.0024669 | 205.7345
119381479 | E | LC | ETL.7130.POLE.WOOD | 40585368 | EUREKA | HUMBOLDT | 2020-07-16 | 2021-02-16 | ETL.7130 | HUMBOLDT-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40585368 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Non Ceramic | Pin |  |  |  |  | 0.033079
119383238 | F | LC | ETL.1820.POLE.STPS | 44395122 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395121 | 2020-03-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0036552 | 31.7081
119462109 | F | LC | ETL.6280.POLE.NWOD | 44644793 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44644793 | 2018-08-26 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-26 | Polymer | Dead End - Suspension |  |  |  |  | 9.3226e-08 | 6110.2441
119468561 | E | LC | ETL.1370.POLE.WOOD | 40866910 | PISMOBCH | LOS PADRES | 2020-07-16 | 2021-07-13 | ETL.1370 | DIVIDE-CABRILLO #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40866910 | 1960-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 2021-06-18 | Glass | Suspension |  |  |  |  | 0.025373 | 739.2226
119468569 | E | LC | ETL.6290.POLE.WOOD | 40589802 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-10-04 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40589802 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.20024 | 47.5141
119468786 | E | LC | ETL.2060.POLE.WOOD | 40586945 | LAKEVLLE | SONOMA | 2020-07-17 | 2021-08-24 | ETL.2060 | FORT BRAGG-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586945 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.30441 | 284.7454
119480168 | E | LC | ETL.4393.TOWR | 41162659 | SACTO | SACRAMENTO | 2020-07-21 | 2021-03-11 | ETL.4393 | DRUM-HIGGINS | Damper-Steel | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41162659 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-01-16 | Glass | Suspension |  |  |  |  | 8.6178e-05 | 269.0557
119505040 | F | LC | ETL.4393.POLE.WDPS | 44172114 | SACTO | SACRAMENTO | 2020-07-24 | 2021-02-12 | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44172112 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00064727 | 269.0937
119510199 | E | LC | ETL.7570.TOWR | 41162747 | METCALF | SAN JOSE | 2020-07-27 |  | ETL.7570 | MILLBRAE-SNEATH LANE | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | HFRA Removal | PEND | 41162747 |  | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | [5 empty] | 1.5374e-05 | 213.6666 | 0.003285
119512348 | E | LC | ETL.6030.TOWR | 40860578 | MIDWAY | KERN | 2020-07-27 | 2020-12-22 | ETL.6030 | MIDWAY-WHIRLWIND | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40860578 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-12-09 | Glass Silicone Coated | Suspension |  |  |  |  | 5.8828e-05 | 6985.7988
119529367 | F | LC | ETL.1470.POLE.WOOD | 41176347 | LAKEVLLE | HUMBOLDT | 2020-07-30 | 2021-02-02 | ETL.1470 | EAGLE ROCK-CORTINA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 41176347 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Porcelain | Post |  |  |  |  | 0.03031 | 5193.0776
119536307 | E | LC | ETL.5650.TOWR | 40599912 | TABLEMTN | NORTH VALLEY | 2020-07-31 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40599912 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 9.9143e-06 | 920.8503 | 0.0091296
119538954 | F | LC | ETL.6380.POLE.WOOD | 40577268 | LAKEVLLE | HUMBOLDT | 2020-07-31 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | PEND
119570690 | F | LC | ETL.9340.POLE.NWOD | 44180720 | FRESNO | YOSEMITE | 2020-08-06 | 2021-02-09 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44180720 | 2015-06-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2015-06-18 | Non Ceramic | Dead End |  |  |  |  | 0.0026748 | 5524.4275
119575381 | B | LC | ETL.7780.POLE.WOOD | 40619442 | LAKEVLLE | SONOMA | 2020-08-07 | 2020-10-19 | ETL.7780 | PHILO JCT-ELK | Other | Customer Issue | [Access Issue] | Tier2 | Tier 2 | Within Both | COMP | 40619442 |  | Single Wood Pole | 3P DV - 3 Pole Double Vertical |  | Ceramic | [5 empty] | 0.00011436 | 0.065148
119600653 | F | LC | ETL.9210.POLE.WOOD | 40595781 | MIDWAY | KERN | 2020-08-11 |  | ETL.9210 | TAFT-CUYAMA #2 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40595781 | 1946-01-01 | Single Wood Pole | TPAT - Tri Pin Arm Tramp | 1946-01-01 | Ceramic | Pin |  |  |  |  | 0.062233
119607622 | E | LC | ETL.6222.POLE.WOOD | 40616324 | EUREKA | HUMBOLDT | 2020-08-12 |  | ETL.6222 | FORT SEWARD TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40616324 | 1952-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 1952-01-01 | Ceramic | Dead End |  |  |  |  | 0.0015368
119608473 | E | LC | ETL.7490.POLE.WDPS | 44145859 | EUREKA | HUMBOLDT | 2020-08-13 | 2020-11-04 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Pole-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | DLFL | 44145856 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.029639 | 142.4119
119617873 | E | LC | ETL.6240.POLE.WOOD | 40874266 | MOSSLNDG | CENTRAL COAST | 2020-08-14 | 2020-10-21 | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119631869 | E | LC | ETL.6870.POLE.WOOD | 40809614 | SACTO | SIERRA | 2020-08-17 | 2021-06-02 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119632531 | F | LC | ETL.6870.POLE.WOOD | 40874891 | SACTO | SIERRA | 2020-08-17 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40874891 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.11237 | 63.386
119649171 | E | LC | ETL.1420.TOWR | 40870507 | SACTO | SACRAMENTO | 2020-08-21 | 2021-02-16 | ETL.1420 | DRUM-RIO OSO #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40870507 | 1913-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 1.2243e-05 | 126.6435
119649200 | E | LC | ETL.8365.POLE.WOOD | 40912516 | EUREKA | HUMBOLDT | 2020-08-21 | 2021-04-21 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912516 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-04-19 | Glass | Dead End |  |  |  |  | 0.021997
119677832 | B | LC | ETL.7780.INSL.NCER | 40697933 | LAKEVLLE | HUMBOLDT | 2020-08-25 | 2020-10-20 | ETL.7780 | PHILO JCT-ELK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119692991 | F | LC | ETL.7290.POLE.NWOD | 44837803 | TABLEMTN | NORTH VALLEY | 2020-08-28 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44837803 | 2019-06-07 | Light Duty Steel Pole | T-1 - Tri Post | 2019-06-07 | Polymer | Post |  |  |  |  | 0.0056003 | 126.6376
119701282 | F | LC | ETL.1440.POLE.WDPS | 40590126 | SACTO | SIERRA | 2020-08-27 | 2021-02-12 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | DLFL | [11 empty] | 0.01018
119702102 | E | LC | ETL.6890.POLE.WOOD | 40616494 | LAKEVLLE | SONOMA | 2020-08-27 | 2021-04-21 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119706858 | E | LC | ETL.6300.POLE.WOOD | 40876678 | TABLEMTN |  | 2020-08-31 | 2021-09-23 | ETL.6300 | CARIBOU-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876678 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-09-18 | Glass | Dead End |  |  |  |  | 0.00064063 | 5538.7192
119709897 | E | LC | ETL.6300.POLE.WOOD | 44191058 | TABLEMTN | NORTH VALLEY | 2020-08-31 | 2021-08-18 | ETL.6300 | CARIBOU-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191058 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | [7 empty] | 5.3084e-06 | 31.6978
119720712 | E | LC | ETL.3190.TOWR | 41082472 | TABLEMTN | NORTH VALLEY | 2020-07-27 |  | ETL.3190 | CARIBOU-PALERMO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41082472 |  | LATTICE STEEL TOWER | DDE - Double Dead End | [7 empty] | 0.00063184 | 2531.262 | 1.5994
119721155 | E | LC | ETL.4771.TOWR | 40650466 | LAKEVLLE | HUMBOLDT | 2020-07-27 | 2021-04-19 | ETL.4771 | BOTTLE ROCK TAP D.W.R. | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40650466 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.4936e-07 | 3276.6768
119722801 | E | LC | ETL.7560.INSL.CERA | 40630457 | SACTO | SIERRA | 2020-08-06 | 2021-04-12 | ETL.7560 | WEIMAR #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40589963 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.17878 | 189.9556
119722991 | E | LC | ETL.6490.POLE.WOOD | 40768374 | SACTO | SIERRA | 2020-08-07 | 2021-03-02 | ETL.6490 | COLGATE-GRASS VALLEY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768374 |  | Single Wood Pole | T2N | 2021-02-17 | Polymer | Post |  |  |  |  | 0.013631 | 54.72
119743476 | A | LC | ETL.4223.POLE.WOOD | 44271528 | TABLEMTN | NORTH VALLEY | 2020-09-10 | 2020-09-17 | ETL.4223 | KANAKA TAP | Emergency-Wood | Other | [Replace, Completed] | Tier2 |  |  | COMP
119752123 | B | LC | ETL.5790.TOWR | 40805532 | VICTOR | STOCKTON | 2020-09-11 | 2020-11-25 | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805532 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 5.5781e-05 | 537.8945
119754569 | F | LC | ETL.1110.POLE.NWOD | 42603423 | TABLEMTN | NORTH VALLEY | 2020-08-14 | 2021-02-10 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42603423 |  | Lattice Steel Pole | DDE - Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.00034681 | 221.5655
119765440 | E | LC | ETL.6480.POLE.WOOD | 40597563 | SACTO | NORTH VALLEY | 2020-09-08 | 2021-05-23 | ETL.6480 | COLGATE-CHALLENGE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119773948 | E | LC | ETL.1110.POLE.WDPS | 44423863 | TABLEMTN | HUMBOLDT | 2020-08-25 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44423862 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0031038 | 5461.4707
119780485 | F | LC | ETL.1073.POLE.WDPS | 44385267 | VICTOR | YOSEMITE | 2020-09-17 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44385266 | 2017-08-17 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00072916 | 15.88
119794606 | E | LC | ETL.5140.INSL.CERA | 40615858 | SACTO | SIERRA | 2020-09-18 | 2021-11-04 | ETL.5140 | MIDDLE FORK-GOLD HILL | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119813486 | B | LC | ETL.1110.TOWR | 40752267 | EUREKA | HUMBOLDT | 2020-08-27 | 2020-10-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752267 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Suspension |  |  |  |  | 2.5375e-05 | 0.065152
119822444 | B | LC | ETL.8580.TOWR | 40690774 | FRESNO | FRESNO | 2020-09-25 | 2020-12-17 | ETL.8580 | COALINGA #1-SAN MIGUEL | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40690774 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Porcelain | Dead End |  |  |  |  | 9.182e-07
119829910 | B | LC | ETL.1110.TOWR | 40592235 | TABLEMTN | HUMBOLDT | 2020-09-28 | 2020-11-04 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592235 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 2.7661e-05 | 712.1317
119835303 | F | LC | ETL.1450.POLE.WDPS | 44947122 | SACTO | SIERRA | 2020-09-08 | 2021-04-22 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42572869 | 1948-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0007842 | 1344.8513
119838433 | E | LC | ETL.5960.TOWR | 40873355 | PISMOBCH | LOS PADRES | 2020-10-01 | 2021-07-08 | ETL.5960 | DIABLO-GATES #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40873355 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 1.4226e-07 | 2373.7322
119851700 | F | LC | ETL.7270.POLE.NWOD | 44649317 | TABLEMTN | NORTH VALLEY | 2020-09-18 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44649317 | 2018-08-17 | Light Duty Steel Pole | T2N | 2018-08-17 | Polymer | Post |  |  |  |  | 0.00039602 | 94.9939
119926497 | E | LC | ETL.5970.TOWR | 40818886 | PISMOBCH | LOS PADRES | 2020-10-20 | 2021-04-29 | ETL.5970 | DIABLO-MIDWAY #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40818886 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2012-09-19 | Ceramic | Suspension |  |  |  |  | 1.1997e-11 | 2565.1169
120135358 | E | LC | ETL.8650.TOWR | 40584411 | FRESNO | YOSEMITE | 2020-12-04 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40584411 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1929-01-01 | Porcelain | Suspension |  |  |  |  | 0.0033644 | 6915.5117
120212428 | B | LC | ETL.1200.POLE.NWOD | 40751493 | PISMOBCH | LOS PADRES | 2020-12-16 | 2021-02-24 | ETL.1200 | CABRILLO-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40751493 | 2010-01-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 2.4498e-07 | 1845.3171
120638702 | E | LC | ETL.7820.POLE.WOOD | 40666634 | LAKEVLLE | SONOMA | 2021-03-12 |  | ETL.7820 | POTTER VALLEY-WILLITS | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40666634 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 3.8371e-08 | 917.5893 | 3.5209e-05
120707809 | E | LC | ETL.1530.TOWR | 40660247 | SACTO | SACRAMENTO | 2021-03-29 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40660247 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 0.0001293 | 704.0812 | 0.091039
120707834 | F | LC | ETL.6760.POLE.WOOD | 40598599 | SACTO | SACRAMENTO | 2021-03-29 | 2021-10-12 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40598599 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.017558 | 31.7022
120710911 | A | LC | ETL.6220.POLE.WOOD | 40614584 | EUREKA | HUMBOLDT | 2021-03-30 | 2021-04-05 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Emergency | Storm Related | [Repair, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40614584 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.071698
120715430 | E | LC | ETL.3020.TOWR | 40644301 | CONCORD | DIABLO | 2021-03-30 |  | ETL.3020 | NEWARK-JARVIS #1 | Structure-Steel | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40644301 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.7919e-06
120715430 | E | LC | ETL.3020.TOWR | 40644301 | CONCORD | DIABLO | 2021-03-30 |  | ETL.3020 | NEWARK-JARVIS #1 | Structure-Steel | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40644301 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-11-03 | Ceramic | Dead End |  |  |  |  | 3.7919e-06
120717255 | E | LC | ETL.1110.POLE.WDPS | 44424383 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-05-04 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120726501 | E | LC | ETL.6750.POLE.STPS | 44932587 | TABLEMTN | NORTH VALLEY | 2021-04-01 |  | ETL.6750 | DELTA-MTN GATE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44932562 | 2020-02-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.3682e-06 | 466.798 | 0.00063867
120735316 | E | LC | ETL.1070.POLE.WOOD | 40819621 | VICTOR | STOCKTON | 2021-04-02 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40819621 | 1957-01-01 | Single Wood Pole | WB - Wishbone | 1998-01-01 | Polymer | Post |  |  |  |  | 4.6487e-05 | 2393.3862 | 0.11126
120737372 | E | LC | ETL.3820.TOWR | 40579601 | VICTOR | STOCKTON | 2021-04-01 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40579601 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 2.6396e-05 | 47.6362 | 0.0012574
120757653 | E | LC | ETL.2720.INSL.NCER | 45100598 | CONCORD | EAST BAY | 2021-04-07 |  | ETL.2720 | MORAGA-OAKLAND #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40805690 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-03 | Polymer | Suspension |  |  |  |  | 6.1461e-05 | 0.065158 | 4.0047e-06
120757653 | E | LC | ETL.2720.INSL.NCER | 45100598 | CONCORD | EAST BAY | 2021-04-07 |  | ETL.2720 | MORAGA-OAKLAND #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40805690 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-01 | Polymer | Suspension |  |  |  |  | 6.1461e-05 | 0.065158 | 4.0047e-06
120771603 | E | LC | ETL.4000.INSL.NCER | 40922577 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.4000 | TESLA-SALADO-MANTECA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40912768 | 1964-01-01 | Single Wood Pole | DDE - Double Dead End | 1964-01-01 | Polymer | [5 empty] | 0.014378 | 686.8128 | 9.8752
120787933 | E | LC | ETL.6880.POLE.WOOD | 40911332 | LAKEVLLE | SONOMA | 2021-04-10 | 2021-07-12 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120803492 | F | LC | ETL.5330.TOWR | 40587150 | MOSSLNDG | CENTRAL COAST | 2021-04-12 | 2021-05-24 | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40587150 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 3.4511e-08 | 3072.0266
120803492 | F | LC | ETL.5330.TOWR | 40587150 | MOSSLNDG | CENTRAL COAST | 2021-04-12 | 2021-05-24 | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40587150 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-04-29 | Glass | Suspension |  |  |  |  | 3.4511e-08 | 3072.0266
120806247 | E | LC | ETL.7270.POLE.WDPS | 44421136 | TABLEMTN | NORTH VALLEY | 2021-04-13 | 2021-06-09 | ETL.7270 | KESWICK-TRINITY | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL | [12 empty] | 3104.2327
120813437 | E | LC | ETL.5310.INSL | 40631417 | PISMOBCH | LOS PADRES | 2021-04-14 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40592048 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 2.6754e-07 | 1333.1163 | 0.00035667
120813680 | F | LC | ETL.1430.INSL | 40922943 | SACTO | SACRAMENTO | 2021-04-14 |  | ETL.1430 | DRUM-RIO OSO #2 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40913099 | 1991-01-01 | Tubular Steel Pole | 2PS - 2 Pole SUSP | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 0.0011534 | 490.5074
120814664 | E | LC | ETL.1250.POLE.NWOD | 40582990 | FRESNO | FRESNO | 2021-04-14 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40582990 |  | Lattice Steel Pole | 3WV-T - Three Way Vertical Tap |  | Polymer | [5 empty] | 3.3517e-06 | 5129.5112 | 0.017192
120833838 | E | LC | ETL.6890.POLE.WOOD | 40759954 | LAKEVLLE | SONOMA | 2021-04-07 | 2021-11-09 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0013793 | 1806.5382 | 2.4918
120839882 | E | LC | ETL.3750.TOWR | 40818432 | CONCORD | DIABLO | 2021-04-19 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40818432 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1944-01-01 | Ceramic | Suspension |  |  |  |  | 8.8721e-06 | 1045.262 | 0.0092737
120842738 | E | LC | ETL.1070.POLE.WOOD | 40580896 | VICTOR | STOCKTON | 2021-04-12 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40580896 | 1998-01-01 | Single Wood Pole | DDE - Double Dead End | 1957-01-01 | Polymer | Dead End |  |  |  |  | 1.4282e-05 | 2978.6118 | 0.042542
120850730 | F | LC | ETL.6470.POLE.WOOD | 40817327 | SACTO | SACRAMENTO | 2021-04-20 | 2021-08-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40817327 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2018-07-20 | Ceramic | Dead End - Suspension |  |  |  |  | 0.0067663 | 479.409
120873225 | F | LC | ETL.9250.POLE.WOOD | 40647732 | MIDWAY | KERN | 2021-04-22 |  | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40647732 | 1967-01-01 | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Other |  |  |  |  | 0.070881 | 5260.3872
120882043 | F | LC | ETL.1820.POLE.STPS | 44395197 | EUREKA | HUMBOLDT | 2021-04-24 | 2021-09-27 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44395195 | 2017-09-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017267
120889055 | E | LC | ETL.4870.TOWR | 40858337 | FRESNO | FRESNO | 2021-04-27 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40858337 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 5.1256e-07 | 8439.7969 | 0.0043259
120912082 | E | LC | ETL.6470.POLE.WOOD | 40874694 | SACTO | SACRAMENTO | 2021-04-29 | 2021-08-10 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40874694 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.016815 | 791.0033
120913496 | E | LC | ETL.5330.TOWR | 40752978 | MOSSLNDG | CENTRAL COAST | 2021-04-15 | 2021-10-19 | ETL.5330 | MOSS LANDING-COBURN | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752978 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 3.5379e-06 | 1994.1763 | 0.0070551
120913496 | E | LC | ETL.5330.TOWR | 40752978 | MOSSLNDG | CENTRAL COAST | 2021-04-15 | 2021-10-19 | ETL.5330 | MOSS LANDING-COBURN | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752978 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 3.5379e-06 | 1994.1763 | 0.0070551
120914999 | E | LC | ETL.1250.POLE.NWOD | 40765067 | FRESNO | FRESNO | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40765067 |  | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 2.8774e-07 | 5825.4395 | 0.0016762
120931394 | E | LC | ETL.7550.POLE.WOOD | 40600377 | LAKEVLLE | SONOMA | 2021-05-04 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | PEND | 40600377 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0025517 | 47.5118 | 0.12124
120939903 | E | LC | ETL.2720.INSL | 40878734 | CONCORD | DIABLO | 2021-05-05 | 2021-05-24 | ETL.2720 | MORAGA-OAKLAND #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | HFRA Removal | DLFL | 40857634 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1980-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.00013677 | 0.065147
121319068 | F | LC | ETL.5300.TOWR | 40857966 | PISMOBCH | LOS PADRES | 2021-04-20 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40857966 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-04-29 | Glass | Suspension |  |  |  |  | 6.7776e-05 | 3927.1462 | 0.26617
121325165 | E | LC | ETL.1650.POLE.NWOD | 40740186 | LAKEVLLE | SONOMA | 2021-05-12 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40740186 | 2011-01-01 | Light Duty Steel Pole | 3HP - 3 Horizontal Post | 1989-01-01 | Polymer | Dead End |  |  |  |  | 6.5575e-07 | 3278.8411 | 0.0021501
121330784 | F | LC | ETL.9100.POLE.WOOD | 44191388 | PISMOBCH | LOS PADRES | 2021-04-19 | 2021-06-29 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL | [11 empty] | 2.3132e-05 | 1281.5726
121338964 | F | LC | ETL.3210.TOWR | 40659276 | SACTO | NORTH VALLEY | 2021-04-21 |  | ETL.3210 | PALERMO-NICOLAUS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40659276 | 1962-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | Dead End |  |  |  |  | 1.8219e-07 | 5787.9745 | 0.0010545
121345321 | E | LC | ETL.4620.INSL | 40713916 | PISMOBCH | LOS PADRES | 2021-04-28 |  | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40662618 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-08-15 | Glass Silicone Coated | Double Dead End |  |  |  |  | 8.6303e-07 | 619.8801 | 0.00053497
121345321 | E | LC | ETL.4620.INSL | 40713916 | PISMOBCH | LOS PADRES | 2021-04-28 |  | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40662618 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1969-01-01 | Ceramic | Double Dead End |  |  |  |  | 8.6303e-07 | 619.8801 | 0.00053497
121352944 | E | LC | ETL.5300.TOWR | 40762346 | PISMOBCH | LOS PADRES | 2021-04-26 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762346 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.5039e-06 | 5477.5894 | 0.019193
121364408 | E | LC | ETL.4590.INSL | 40685032 | TABLEMTN | NORTH VALLEY | 2021-04-26 |  | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40655507 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 3.0104e-07 | 4276.3525 | 0.0012873
121364408 | E | LC | ETL.4590.INSL | 40685032 | TABLEMTN | NORTH VALLEY | 2021-04-26 |  | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40655507 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-06-13 | Glass | Suspension |  |  |  |  | 3.0104e-07 | 4276.3525 | 0.0012873
121367091 | E | LC | ETL.2700.INSL.CERA | 42581980 | CONCORD | EAST BAY | 2021-05-19 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44188777 | 2008-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 2.9651e-07 | 398.0443 | 0.00011803
121369251 | E | LC | ETL.1820.INSL.CERA | 40579069 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560159 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.11287
121369251 | E | LC | ETL.1820.INSL.CERA | 40579069 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560159 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.11287
121369251 | E | LC | ETL.1820.INSL.CERA | 40579069 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560159 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.11287
121370817 | F | LC | ETL.4680.TOWR | 40597132 | LAKEVLLE | SONOMA | 2021-05-01 |  | ETL.4680 | FULTON-IGNACIO #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40597132 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.7843e-06 | 213.7858
121378372 | E | LC | ETL.6320.INSL.NCER | 44820284 | TABLEMTN | NORTH VALLEY | 2021-05-07 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44820179 | 2019-06-30 | Fiberglass | T-1 - Tri Post | 2019-06-30 | Polymer | Post |  |  |  |  | 0.00061774 | 862.7981 | 0.53298
121381067 | F | LC | ETL.8350.POLE.NWOD | 44918798 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44918798 | 2020-03-03 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-03 | Polymer | Post |  |  |  |  | 3.9095e-07 | 933.6463
121383313 | F | LC | ETL.6500.POLE.WOOD | 44153671 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44153671 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 0.003888 | 158.2502
121383729 | F | LC | ETL.8250.POLE.WOOD | 40912844 | VICTOR | STOCKTON | 2021-05-10 |  | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40912844 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00061189 | 2425.2947
121397221 | E | LC | ETL.6660.POLE.NWOD | 45058626 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45058626 | 2020-05-08 | Light Duty Steel Pole | T2N | 2020-05-08 | Polymer | Post |  |  |  |  | 3.8214e-10 | 4940.2572 | 1.8879e-06
121404010 | E | LC | ETL.7550.POLE.WOOD | 40875210 | LAKEVLLE | HUMBOLDT | 2021-05-19 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40875210 |  | Single Wood Pole | SV-1B - Single Vertical Light Angle BR |  | Porcelain | [5 empty] | 0.0031111 | 1238.8812 | 3.8543
121428326 | E | LC | ETL.7560.POLE.WDPS | 44414818 | SACTO | SACRAMENTO | 2021-05-26 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44414815 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.22103 | 1202.2719 | 265.7393
121474900 | F | LC | ETL.4316.POLE.STPS | 44561312 | TABLEMTN | NORTH VALLEY | 2021-05-28 | 2021-08-03 | ETL.4316 | PARADISE-TABLE MTN | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44559134 | 2018-03-14 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00018886 | 2995.1147
121489142 | F | LC | ETL.7550.POLE.WOOD | 40585234 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40585234 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | [5 empty] | 8.7031e-05 | 110.7947 | 0.0096426
121492701 | F | LC | ETL.6890.POLE.WOOD | 40875978 | LAKEVLLE | SONOMA | 2021-06-02 | 2021-07-26 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL
121495762 | B | LC | ETL.8350.POLE.NWOD | 44918775 | VICTOR | STOCKTON | 2021-06-08 | 2021-07-07 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44918775 | 2020-03-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-03-03 | Polymer | Dead End |  |  |  |  | 4.2856e-08 | 2161.0107
121499770 | E | LC | ETL.6852.POLE.WOOD | 40750182 | LAKEVLLE | SONOMA | 2021-06-09 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40750182 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.039315 | 6348.395 | 249.59
121514867 | F | LC | ETL.4392.TOWR | 41129349 | LAKEVLLE | SONOMA | 2021-06-03 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129349 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 3.335e-05 | 1332.3551
121514867 | F | LC | ETL.4392.TOWR | 41129349 | LAKEVLLE | SONOMA | 2021-06-03 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129349 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 3.335e-05 | 1332.3551
121519758 | B | LC | ETL.7550.INSL.CERA | 40677118 | LAKEVLLE | HUMBOLDT | 2021-06-10 | 2021-08-31 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40657953 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | Dead End |  |  |  |  | 3.1166e-05 | 15.8807
121520393 | F | LC | ETL.6870.POLE.NWOD | 44431463 | SACTO | SIERRA | 2021-06-07 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44431463 | 2017-08-24 | Light Duty Steel Pole | Unknown | 2017-08-24 | Polymer | Post |  |  |  |  | 0.0020572 | 4287.5171
121521113 | F | LC | ETL.1480.TOWR | 40585023 | LAKEVLLE | SONOMA | 2021-06-11 | 2021-07-12 | ETL.1480 | EAGLE ROCK-REDBUD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40585023 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1978-01-01 | Glass | Dead End |  |  |  |  | 0.00038821 | 3738.1865
121523359 | F | LC | ETL.7212.POLE.WDPS | 40867264 | METCALF | PENINSULA | 2021-06-04 | 2021-07-12 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40867264 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.5781
121523359 | F | LC | ETL.7212.POLE.WDPS | 40867264 | METCALF | PENINSULA | 2021-06-04 | 2021-07-12 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40867264 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.5781
121523359 | F | LC | ETL.7212.POLE.WDPS | 40867264 | METCALF | PENINSULA | 2021-06-04 | 2021-07-12 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40867264 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.5781
121523502 | E | LC | ETL.1350.POLE.WDPS | 44201747 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44201744 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.01226 | 411.4229 | 5.0441
121527753 | E | LC | ETL.5430.POLE.WDPS | 44561442 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560781 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0022472 | 665.1749 | 1.4948
121528554 | E | LC | ETL.5420.POLE.WDPS | 44559029 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44558510 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0056163 | 2361.4426 | 13.2627
121548096 | F | LC | ETL.7640.POLE.WDPS | 44565574 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564244 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 4.3612e-06 | 3373.8892
121557602 | E | LC | ETL.5630.TOWR | 40867169 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5630 | ROCK CREEK-POE | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40867169 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 5.2628e-05 | 4794.1747 | 0.25231
121561704 | F | LC | ETL.7640.POLE.WDPS | 44565417 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564195 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0021043 | 79.1851
121588107 | F | LC | ETL.1400.POLE.WDPS | 45095805 | VICTOR | STOCKTON | 2021-06-23 | 2021-07-09 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40580177 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.008921 | 31.7207
121603345 | F | LC | ETL.7550.POLE.NWOD | 45036774 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45036774 | 2020-05-29 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-29 | Glass | Dead End |  |  |  |  | 6.7255e-08 | 348.958
121605967 | F | LC | ETL.4040.POLE.STPS | 44647513 | TABLEMTN |  | 2021-06-23 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44646841 | 2018-08-17 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 5.0249e-05 | 96.1193
121607603 | E | LC | ETL.7550.POLE.WOOD | 40702876 | LAKEVLLE | HUMBOLDT | 2021-06-18 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40702876 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00019171 | 110.7947 | 0.02124
121623300 | E | LC | ETL.1450.POLE.NWOD | 45125372 | SACTO | SIERRA | 2021-06-28 |  | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45125372 | 2020-07-25 | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper | 2020-07-25 | Glass | Double Dead End | [5 empty] | 648.7145
121634886 | F | LC | ETL.3770.TOWR | 40581867 | CONCORD | DIABLO | 2021-06-22 |  | ETL.3770 | SOBRANTE-R #1 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40581867 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-08-29 | Glass | Suspension |  |  |  |  | 1.6303e-06 | 316.3912 | 0.00051581
121643656 | E | LC | ETL.6690.POLE.NWOD | 44203628 | SACTO | SIERRA | 2021-06-18 |  | ETL.6690 | DEER CREEK-DRUM | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44203628 | 2014-09-05 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2014-09-05 | Ceramic | Suspension |  |  |  |  | 0.042159 | 126.6309 | 5.3387
121662620 | F | LC | ETL.6230.POLE.WOOD | 40771527 | MOSSLNDG | CENTRAL COAST | 2021-07-01 | 2021-09-29 | ETL.6230 | BURNS-LONE STAR #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771527 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.61672 | 79.1724
121662627 | E | LC | ETL.5980.TOWR | 40812093 | PISMOBCH | LOS PADRES | 2021-06-30 | 2021-07-09 | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40812093 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.0822e-07 | 286.2883
121678378 | B | LC | ETL.6020.INSL | 40887334 | TABLEMTN | NORTH VALLEY | 2021-07-06 | 2021-07-14 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863447 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.5306e-08 | 174.1517
121729387 | E | LC | ETL.4393.POLE.NWOD | 44258715 | SACTO | SIERRA | 2021-06-12 |  | ETL.4393 | DRUM-HIGGINS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44258715 |  | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2016-08-08 | Ceramic | Dead End |  |  |  |  | 6.2714e-07 | 349.6656 | 0.00021929
121741437 | E | LC | ETL.7180.INSL.CERA | 40737596 | LAKEVLLE | NORTH BAY | 2021-07-14 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40737579 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 0.0017581 | 31.7201 | 0.055766
121749230 | B | LC | ETL.7212.INSL.NCER | 40720757 | METCALF | PENINSULA | 2021-07-17 | 2021-08-16 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40674734 |  | Single Wood Pole | DV - Double Vertical |  | Non Ceramic | [5 empty] | 0.58287 | 680.9633
121749716 | E | LC | ETL.7590.POLE.WDPS | 45041305 | MOSSLNDG | CENTRAL COAST | 2021-07-15 |  | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45041262 | 2020-09-17 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.39236 | 15.8866 | 6.2332
121758739 | B | LC | ETL.6280.POLE.WOOD | 40698589 | TABLEMTN | NORTH VALLEY | 2021-07-19 | 2021-10-11 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40698589 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 3.1954e-05 | 490.3705
121759702 | E | LC | ETL.1820.POLE.WDPS | 44560512 | EUREKA | HUMBOLDT | 2021-07-19 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560165 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.12292 | 150.3689 | 18.4834
121781442 | E | LC | ETL.4050.POLE.WOOD | 44310999 | LAKEVLLE | SONOMA | 2021-07-21 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44310999 | 2014-12-18 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2014-12-18 | Polymer | Suspension |  |  |  |  | 2.231e-05 | 2248.4673 | 0.050164
121809437 | B | LC | ETL.1820.POLE.WDPS | 40662077 | EUREKA | HUMBOLDT | 2021-07-28 | 2021-08-04 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662077 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 0.80044
121809437 | B | LC | ETL.1820.POLE.WDPS | 40662077 | EUREKA | HUMBOLDT | 2021-07-28 | 2021-08-04 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662077 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 0.80044
121809437 | B | LC | ETL.1820.POLE.WDPS | 40662077 | EUREKA | HUMBOLDT | 2021-07-28 | 2021-08-04 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662077 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 0.80044
121810588 | E | LC | ETL.6950.INSL.CERA | 44174912 | SACTO | SACRAMENTO | 2021-07-28 |  | ETL.6950 | GOLD HILL #1 | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44174899 |  | Fiberglass | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00039786 | 617.0629 | 0.2455
121810702 | F | LC | ETL.5390.TOWR | 40759512 | TABLEMTN | NORTH VALLEY | 2021-07-27 | 2021-08-19 | ETL.5390 | PIT #1-COTTONWOOD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40759512 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-01-13 | Glass | Suspension |  |  |  |  | 3.5657e-07 | 358.9875
121813061 | B | LC | ETL.6280.POLE.WOOD | 40666867 | TABLEMTN | NORTH VALLEY | 2021-07-29 | 2021-10-04 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 3.4202e-05 | 876.2883
121882696 | B | LC | ETL.6300.POLE.WDPS | 44976228 | TABLEMTN | NORTH VALLEY | 2021-08-10 | 2021-09-23 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 174.1204
121985940 | F | LC | ETL.4310.POLE.WOOD | 44732850 | VICTOR | YOSEMITE | 2021-09-01 | 2021-09-16 | ETL.4310 | VIERRA-TRACY-KASSON | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Non-HFTD | Non-HFRA | DLFL | 44732850 | 2019-04-01 | Single Wood Pole | T-1 - Tri Post | 2019-04-01 | Polymer | Post
122191829 | E | LC | ETL.7490.POLE.NWOD | 44977481 | EUREKA | HUMBOLDT | 2021-10-12 |  | ETL.7490 | MAPLE CREEK-HOOPA | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44977481 | 2020-07-11 | Light Duty Steel Pole | DDE - Double Dead End | 2020-07-11 | Glass | Dead End |  |  |  |  | 0.18419 | 142.4498 | 26.2375
118442469 | E | LC | ETL.5440.POLE.WDPS | 44558269 | TABLEMTN |  | 2020-01-18 | 2020-06-16 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118605992 | E | LC | ETL.8210.SWIT | 43242665 | VICTOR | STOCKTON | 2020-03-05 | 2020-11-19 | ETL.8210 | VALLEY SPRINGS #1 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 |  |  | COMP
118725742 | E | LC | ETL.7575.POLE.WOOD | 40599267 | METCALF | SAN JOSE | 2020-03-19 | 2020-09-28 | ETL.7575 | SNEATH LANE-PACIFICA | Vegetation | Overgrown | [Remove, Completed] | Tier3 |  |  | COMP
118758386 | E | LC | ETL.5790.TOWR | 40585747 | VICTOR | STOCKTON | 2020-03-31 | 2021-06-09 | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585747 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 8.4032e-07 | 571.9987
118961052 | F | LC | ETL.4220.POLE.NWOD | 44272858 | TABLEMTN | NORTH VALLEY | 2020-04-27 | 2020-05-22 | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44272858 | 2014-10-27 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2014-10-27 | Ceramic | Suspension |  |  |  |  | 7.9924e-05 | 1600.0325
118992121 | E | LC | ETL.8650.TOWR | 40651170 | FRESNO | YOSEMITE | 2020-05-04 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40651170 |  | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-12-17 | Glass | Suspension |  |  |  |  | 0.0079381 | 50.2805
119004889 | E | LC | ETL.8480.POLE.WDPS | 44319830 | PISMOBCH | LOS PADRES | 2020-05-05 | 2021-07-22 | ETL.8480 | ATASCADERO-CAYUCOS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44319827 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.8241e-05 | 47.5476
119041041 | E | LC | ETL.1470.INSL.CERA | 40796412 | SACTO |  | 2020-05-14 | 2021-03-09 | ETL.1470 | EAGLE ROCK-CORTINA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119056874 | E | LC | ETL.6440.POLE.WOOD | 44191495 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-08-14 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191495 |  | Single Wood Pole | TP - Tri Pin | [7 empty] | 0.0037266 | 3740.5452
119057484 | E | LC | ETL.6440.POLE.WOOD | 41144197 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-06-10 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41144197 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.0039399 | 4911.8149
119082371 | B | LC | ETL.6722.POLE.WOOD | 44190964 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2020-06-17 | ETL.6722 | FORKS OF THE BUTTE TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119083662 | E | LC | ETL.1600.INSL.NCER | 40796382 | LAKEVLLE | SONOMA | 2020-05-27 | 2021-03-25 | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119086846 | E | LC | ETL.8410.POLE.WOOD | 40825524 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-01-20 | ETL.8410 | ELK-GUALALA | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825524 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 2019-08-05 | Glass | Suspension |  |  |  |  | 0.23966 | 665.6348
119100532 | F | LC | ETL.2540.POLE.WDPS | 44401518 | MOSSLNDG | CENTRAL COAST | 2020-05-20 | 2021-07-26 | ETL.2540 | METCALF-GREEN VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44401516 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.15372 | 253.2084
119104213 | E | LC | ETL.5250.TOWR | 40670657 | CONCORD | DIABLO | 2020-05-21 | 2021-02-08 | ETL.5250 | MORAGA-CASTRO VALLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40670657 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 2.3504e-07 | 525.4913
119116945 | E | LC | ETL.5290.INSL | 40886908 | PISMOBCH | LOS PADRES | 2020-05-27 | 2021-09-09 | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119117504 | F | LC | ETL.6760.POLE.NWOD | 40867115 | SACTO | SIERRA | 2020-05-27 | 2021-10-14 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40867115 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.041566 | 95.0268
119119541 | F | LC | ETL.6950.POLE.NWOD | 44172724 | SACTO | SIERRA | 2020-06-02 |  | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44172724 |  | Fiberglass | TPA - Tri Pin Arm |  | Porcelain | Post |  |  |  |  | 1.721e-05 | 917.5387
119127027 | E | LC | ETL.7300.POLE.WOOD | 40602045 | TABLEMTN |  | 2020-06-03 | 2021-03-05 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119132424 | F | LC | ETL.7300.POLE.WOOD | 44141995 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-03-23 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44141995 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.00018199 | 6446.7676
119142493 | F | LC | ETL.6490.POLE.WOOD | 40679368 | SACTO | SIERRA | 2020-06-02 |  | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40679368 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.010027 | 569.5441
119147743 | F | LC | ETL.6470.POLE.WOOD | 40869658 | SACTO | SIERRA | 2020-06-10 | 2020-07-15 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40869658 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.020278 | 284.8633
119162839 | F | LC | ETL.5440.POLE.WDPS | 44558322 | TABLEMTN |  | 2020-06-13 | 2020-08-19 | ETL.5440 | PIT #6 JCT-ROUND MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 |  |  | COMP
119163068 | F | LC | ETL.7300.POLE.NWOD | 44809977 | TABLEMTN | NORTH VALLEY | 2020-06-04 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44809977 | 2019-05-24 | Light Duty Steel Pole | T1-1A | 2019-05-24 | Polymer | Post |  |  |  |  | 3.2849e-08 | 2853.7749
119175041 | E | LC | ETL.8170.POLE.WDPS | 44420661 | EUREKA | HUMBOLDT | 2020-06-15 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44420658 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.029769 | 0.065152 | 0.0019395
119177655 | E | LC | ETL.6750.POLE.WOOD | 40817276 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2021-05-19 | ETL.6750 | DELTA-MTN GATE JCT | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119182107 | E | LC | ETL.7300.POLE.WOOD | 40809935 | TABLEMTN |  | 2020-06-16 | 2021-08-17 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809935 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00025217 | 2838.0014
119182515 | F | LC | ETL.6310.POLE.WOOD | 40657165 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40657165 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.1364e-05 | 5196.2129
119183106 | E | LC | ETL.6310.POLE.WOOD | 40759287 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-06-22 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759287 | 2011-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 9.9855e-07 | 4022.0014
119198757 | F | LC | ETL.6470.POLE.WOOD | 40602537 | SACTO | SIERRA | 2020-06-23 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40602537 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 0.087167 | 110.8102
119219679 | E | LC | ETL.8290.POLE.NWOD | 44186927 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2020-12-01 | ETL.8290 | VOLTA-DESCHUTES | Vegetation | Overgrown | [Trim, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44186927 | 2013-10-14 | Light Duty Steel Pole | T-1 - Tri Post | 2013-10-14 | Non Ceramic | Post |  |  |  |  | 4.4237e-07 | 554.7007
119222426 | E | LC | ETL.4050.POLE.NWOD | 40750650 | LAKEVLLE | SONOMA | 2020-06-26 | 2021-04-17 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750650 | 2012-01-01 | Light Duty Steel Pole | T-1 - Tri Post | 1970-01-01 | Ceramic | Post |  |  |  |  | 1.7455e-08 | 2750.789
119230356 | E | LC | ETL.1400.INSL.NCER | 44810073 | VICTOR | STOCKTON | 2020-06-26 | 2021-05-10 | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44810009 | 2019-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2019-08-08 | Glass | Suspension |  |  |  |  | 5.6327e-05
119230356 | E | LC | ETL.1400.INSL.NCER | 44810073 | VICTOR | STOCKTON | 2020-06-26 | 2021-05-10 | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44810009 | 2019-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2019-08-08 | Glass | Suspension |  |  |  |  | 5.6327e-05
119231917 | E | LC | ETL.8170.POLE.WOOD | 40876572 | EUREKA | HUMBOLDT | 2020-06-29 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40876572 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.16712 | 31.6978 | 5.2974
119233593 | F | LC | ETL.8060.POLE.WOOD | 40828127 | SACTO | SIERRA | 2020-06-29 | 2021-02-11 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40828127 |  | Single Wood Pole | T2N | 2021-05-04 | Polymer | Post |  |  |  |  | 0.015317 | 95.1488
119289950 | F | LC | ETL.7300.POLE.WOOD | 40759099 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40759099 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0015881 | 1218.3302
119291260 | B | LC | ETL.6490.POLE.WOOD | 40823561 | SACTO | SIERRA | 2020-07-01 | 2020-09-23 | ETL.6490 | COLGATE-GRASS VALLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119304438 | E | LC | ETL.6980.POLE.WOOD | 40872351 | LAKEVLLE | SONOMA | 2020-07-02 |  | ETL.6980 | FORT ROSS-GUALALA | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40872351 | 1953-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1953-01-01 | Polymer | Suspension |  |  |  |  | 0.50336 | 74.4037 | 37.452
119312665 | F | LC | ETL.1440.POLE.STPS | 44815119 | SACTO | SACRAMENTO | 2020-07-02 | 2021-05-08 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44815088 | 2019-08-07 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.4449e-06 | 965.3439
119318231 | F | LC | ETL.7270.POLE.WOOD | 40906074 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-08-17 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906074 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0020802 | 5300.8838
119328674 | F | LC | ETL.6300.POLE.WOOD | 40591700 | TABLEMTN |  | 2020-07-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40591700 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 8.0832e-06 | 47.5141
119330749 | E | LC | ETL.7180.POLE.WOOD | 41124303 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-05-03 | ETL.7180 | IGNACIO-BOLINAS #2 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41124303 |  | Single Wood Pole | T-1 - Tri Post | 2021-04-13 | Polymer | Post |  |  |  |  | 1.1416e-05 | 3247.3364
119334403 | F | LC | ETL.4040.POLE.STPS | 44784272 | TABLEMTN | NORTH VALLEY | 2020-07-07 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44784126 | 2019-07-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.6429e-05 | 3310.937
119334860 | F | LC | ETL.1820.POLE.STPS | 44395137 | EUREKA | HUMBOLDT | 2020-07-08 |  | ETL.1820 | HUMBOLDT-TRINITY | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395136 | 2020-03-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00096384 | 63.351 | 0.06106
119354785 | F | LC | ETL.6861.POLE.WOOD | 44409704 | LAKEVLLE | SONOMA | 2020-07-10 |  | ETL.6861 | KONOCTI-EAGLE ROCK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44409704 | 2018-10-14 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-10-14 | Polymer | Dead End |  |  |  |  | 0.0007196 | 4752.3721
119357646 | E | LC | ETL.5960.INSL.CERA | 44374365 | PISMOBCH | LOS PADRES | 2020-07-08 |  | ETL.5960 | DIABLO-GATES #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40741756 |  | LATTICE STEEL TOWER | DDE - Double Dead End | 2013-04-12 | Ceramic | Dead End |  |  |  |  | 8.3652e-07 | 821.6836 | 0.00068735
119368463 | F | LC | ETL.1440.POLE.WOOD | 42572645 | SACTO | SIERRA | 2020-07-14 | 2020-11-12 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42572645 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees | [7 empty] | 5.5674e-05 | 648.7145
119368854 | E | LC | ETL.8410.POLE.STPS | 44810763 | LAKEVLLE | HUMBOLDT | 2020-07-13 | 2021-03-29 | ETL.8410 | ELK-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44810763 | 2019-07-14 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2019-07-14 | Polymer | Dead End |  |  |  |  | 0.0085443
119368854 | E | LC | ETL.8410.POLE.STPS | 44810763 | LAKEVLLE | HUMBOLDT | 2020-07-13 | 2021-03-29 | ETL.8410 | ELK-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44810763 | 2019-07-14 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2019-07-14 | Polymer | Dead End |  |  |  |  | 0.0085443
119368854 | E | LC | ETL.8410.POLE.STPS | 44810763 | LAKEVLLE | HUMBOLDT | 2020-07-13 | 2021-03-29 | ETL.8410 | ELK-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44810763 | 2019-07-14 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2019-07-14 | Polymer | Dead End |  |  |  |  | 0.0085443
119378293 | E | LC | ETL.6280.POLE.WOOD | 44259123 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-06-16 | ETL.6280 | CARIBOU #2 | Anchor-Wood | Missing | [Install] | Tier2 |  |  | DLFL | [11 empty] | 4.1639e-06 | 695.9825
119470028 | F | LC | ETL.7030.POLE.WOOD | 40825579 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40825579 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0085436 | 47.5839
119471352 | F | LC | ETL.7030.POLE.WOOD | 40616945 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2020-10-29 | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40616945 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 2016-08-10 | Polymer | Post |  |  |  |  | 0.0059614
119478342 | F | LC | ETL.6280.POLE.WOOD | 40614758 | TABLEMTN | NORTH VALLEY | 2020-07-20 | 2021-07-13 | ETL.6280 | CARIBOU #2 | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40614758 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00082973 | 174.0445
119487356 | F | LC | ETL.6440.POLE.WOOD | 40770033 | TABLEMTN | NORTH VALLEY | 2020-07-22 | 2021-01-05 | ETL.6440 | COLEMAN-RED BLUFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770033 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.00031024 | 3992.9106
119494706 | E | LC | ETL.1110.POLE.WDPS | 44550800 | TABLEMTN | HUMBOLDT | 2020-07-22 | 2021-04-06 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44550077 | 2011-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0026274 | 1946.3441
119495538 | F | LC | ETL.1110.POLE.WDPS | 44424438 | TABLEMTN | NORTH VALLEY | 2020-07-22 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44424437 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014879 | 3180.1895
119551460 | E | LC | ETL.1530.TOWR | 40751920 | SACTO | SACRAMENTO | 2020-08-03 | 2021-07-06 | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40751920 | 1923-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2019-02-12 | Glass | Double Dead End |  |  |  |  | 6.505e-06 | 332.3128
119596531 | E | LC | ETL.8365.POLE.WOOD | 40906586 | EUREKA | HUMBOLDT | 2020-08-10 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Vegetation | Overgrown | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40906586 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.019477
119608853 | B | LC | ETL.8650.POLE.NWOD | 44436537 | FRESNO | FRESNO | 2020-08-13 | 2020-12-08 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44436537 | 1929-01-01 | Lattice Steel Pole | DDE - Double Dead End | 2019-11-18 | Glass | Dead End |  |  |  |  | 0.012591 | 7011.6152
119628295 | F | LC | ETL.7380.POLE.WOOD | 40701571 | MOSSLNDG | CENTRAL COAST | 2020-08-17 |  | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40701571 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.16647 | 0.065148
119629193 | F | LC | ETL.7380.POLE.NWOD | 40668280 | MOSSLNDG | CENTRAL COAST | 2020-08-17 | 2021-09-01 | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40668280 | 2009-01-01 | Light Duty Steel Pole | T-1 - Tri Post | 2020-05-10 | Polymer | Post |  |  |  |  | 0.090687 | 174.3987
119629426 | F | LC | ETL.1440.POLE.WDPS | 44765180 | SACTO | SACRAMENTO | 2020-08-17 | 2021-02-12 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40876967 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00058908 | 31.7066
119649430 | F | LC | ETL.6480.POLE.NWOD | 44695448 | SACTO | SACRAMENTO | 2020-08-21 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44695448 | 2018-12-10 | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper | 2018-12-10 | Polymer | Dead End |  |  |  |  | 0.0016676 | 428.1771
119666706 | E | LC | ETL.7490.POLE.WOOD | 40828009 | EUREKA | HUMBOLDT | 2020-08-25 | 2021-08-18 | ETL.7490 | MAPLE CREEK-HOOPA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40828009 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-07-30 | Glass | Dead End |  |  |  |  | 0.0010188 | 221.4934
119668470 | A | LC | ETL.7590.POLE.WDPS | 44950340 | MOSSLNDG | CENTRAL COAST | 2020-08-25 | 2020-09-24 | ETL.7590 | MONTA VISTA-BURNS | Emergency-Wood | Other | [Replace, Completed] |  | Tier 3 | Within Both | COMP | 44949089 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.34141 | 15.8866
119675431 | E | LC | ETL.4100.TOWR | 40812936 | SACTO | SACRAMENTO | 2020-08-26 | 2021-03-22 | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40812936 | 1913-01-01 | LATTICE STEEL TOWER | DE - Dead End | 2018-05-28 | Glass | Dead End |  |  |  |  | 7.9262e-07 | 5399.8154
119677277 | F | LC | ETL.7180.POLE.WOOD | 40751195 | LAKEVLLE | SONOMA | 2020-08-24 | 2021-02-10 | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40751195 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 3.9013e-05 | 2315.3281
119723403 | B | LC | ETL.4620.TOWR | 40862769 | PISMOBCH | LOS PADRES | 2020-08-07 | 2020-09-28 | ETL.4620 | DIABLO-MESA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40862769 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 1.1156e-06 | 521.9926
119723403 | B | LC | ETL.4620.TOWR | 40862769 | PISMOBCH | LOS PADRES | 2020-08-07 | 2020-09-28 | ETL.4620 | DIABLO-MESA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40862769 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-03 | Glass | Suspension |  |  |  |  | 1.1156e-06 | 521.9926
119723483 | E | LC | ETL.6770.POLE.WOOD | 40770252 | SACTO | SIERRA | 2020-08-07 | 2021-05-03 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119723742 | F | LC | ETL.1240.POLE.WDPS | 44386062 | TABLEMTN | NORTH VALLEY | 2020-08-04 |  | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44386060 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.7616e-05 | 2419.7553
119754131 | E | LC | ETL.8350.POLE.WOOD | 40643843 | VICTOR | STOCKTON | 2020-08-31 | 2021-02-22 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40643843 | 1993-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Glass | [5 empty] | 1.1268e-05 | 4759.0768
119756414 | F | LC | ETL.7212.POLE.WDPS | 44384385 | METCALF | PENINSULA | 2020-08-26 | 2021-10-04 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44384383 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.063442 | 760.1513
119769410 | E | LC | ETL.6470.POLE.WOOD | 40874206 | SACTO | SIERRA | 2020-06-19 | 2021-08-04 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.052404 | 79.2067
119788620 | E | LC | ETL.7590.INSL.CERA | 42565789 | MOSSLNDG | CENTRAL COAST | 2020-09-17 | 2021-01-12 | ETL.7590 | MONTA VISTA-BURNS | Insulator | Contaminated | [Ground Wash] | Tier3 |  |  | DLFL
119791054 | F | LC | ETL.4220.POLE.STPS | 44388382 | TABLEMTN |  | 2020-07-30 |  | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44388380 | 2017-09-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.4925e-05 | 411.5997
119810054 | F | LC | ETL.7560.POLE.NWOD | 44662499 | SACTO | SIERRA | 2020-08-14 | 2021-10-19 | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44662499 | 2018-09-29 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-09-29 | Polymer | Dead End - Suspension |  |  |  |  | 0.016637 | 3116.3115
119829428 | E | LC | ETL.7340.INSL.NCER | 40641292 | LAKEVLLE |  | 2020-09-28 | 2021-05-25 | ETL.7340 | LAKEVILLE #2 | Insulator | Contaminated | [Ground Wash, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40617312 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0023818 | 523.984
119857402 | F | LC | ETL.7490.POLE.NWOD | 44963388 | EUREKA | HUMBOLDT | 2020-09-24 | 2021-02-09 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44963388 | 2020-07-15 | Light Duty Steel Pole | DDE - Double Dead End | 2020-07-15 | Polymer | Dead End |  |  |  |  | 4.3463e-05 | 174.0445
119892563 | F | LC | ETL.6240.POLE.WOOD | 44991775 | MOSSLNDG | CENTRAL COAST | 2020-10-12 |  | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44991775 | 2020-09-19 | Single Wood Pole | T2N | 2020-09-19 | Polymer | Post |  |  |  |  | 0.18805 | 0.065152
119896871 | E | LC | ETL.5970.TOWR | 40753879 | PISMOBCH | LOS PADRES | 2020-10-13 | 2021-05-11 | ETL.5970 | DIABLO-MIDWAY #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40753879 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 1.7655e-07 | 490.3249
119917020 | E | LC | ETL.1110.INSL.CERA | 40678632 | TABLEMTN | HUMBOLDT | 2020-10-13 | 2021-05-11 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119927466 | E | LC | ETL.6050.TOWR | 40870822 | MOSSLNDG | CENTRAL COAST | 2020-10-20 | 2021-05-04 | ETL.6050 | MOSS LANDING-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870822 | 1966-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2020-05-16 | Glass Silicone Coated | Suspension |  |  |  |  | 2.3638e-07 | 2595.8459
119973897 | A | LC | ETL.5970.TOWR | 40604994 | PISMOBCH | LOS PADRES | 2020-11-02 | 2020-11-07 | ETL.5970 | DIABLO-MIDWAY #2 | Hardware-Tower | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40604994 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 1.7858e-08 | 4115.2769
119993207 | F | LC | ETL.5390.TOWR | 40595055 | TABLEMTN | NORTH VALLEY | 2020-11-06 |  | ETL.5390 | PIT #1-COTTONWOOD | Road | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40595055 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.04e-07 | 4690.1665
120129769 | F | LC | ETL.6870.POLE.WOOD | 40611453 | SACTO | SIERRA | 2020-10-22 | 2021-07-21 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40611453 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post | 1966-01-01 | Polymer | Post |  |  |  |  | 0.030328 | 332.3381
120129769 | F | LC | ETL.6870.POLE.WOOD | 40611453 | SACTO | SIERRA | 2020-10-22 | 2021-07-21 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40611453 | 1966-01-01 | Single Wood Pole | T-1 - Tri Post | 1966-01-01 | Ceramic | Post |  |  |  |  | 0.030328 | 332.3381
120493057 | E | LC | ETL.1340.POLE.WOOD | 40819247 | TABLEMTN | NORTH VALLEY | 2021-02-02 | 2021-11-15 | ETL.1340 | COTTONWOOD-PANORAMA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40819247 | 1964-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2021-11-04 | Glass | Dead End |  |  |  |  | 6.8426e-05 | 4104.0635 | 0.28082
120633202 | E | LC | ETL.6330.INSL.NCER | 40844703 | TABLEMTN | NORTH VALLEY | 2021-03-10 | 2021-09-14 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40816794 |  | Tubular Steel Pole | SV1 - Angle 0-30 Degrees |  | Non Ceramic | Pin |  |  |  |  | 4.2914e-06 | 253.1848
120634151 | E | LC | ETL.4316.INSL.NCER | 40617158 | TABLEMTN |  | 2021-03-10 | 2021-08-12 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120654612 | E | LC | ETL.1650.POLE.NWOD | 45059213 | LAKEVLLE | SONOMA | 2021-03-17 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45059213 | 2021-03-12 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-03-12 | Glass | Dead End |  |  |  |  | 3.7097e-09 | 4970.959 | 1.8441e-05
120664092 | E | LC | ETL.1350.POLE.WDPS | 44551502 | TABLEMTN | NORTH VALLEY | 2021-03-19 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759412 | 1993-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.059566 | 3817.3882
120689522 | F | LC | ETL.3700.POLE.WOOD | 40602966 | PISMOBCH | LOS PADRES | 2021-03-24 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40602966 | 1989-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1989-01-01 | Porcelain | Suspension |  |  |  |  | 2.0682e-05 | 5477.0957
120691847 | E | LC | ETL.3820.INSL.CERA | 40694470 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Damper-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40663252 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 3.076e-07 | 158.4159 | 4.8729e-05
120694889 | B | LC | ETL.8650.POLE.NWOD | 44420210 | FRESNO | FRESNO | 2021-03-26 | 2021-04-19 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Conductor-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420210 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.013591 | 369.2492
120713742 | B | LC | ETL.5140.POLE.STPS | 44690643 | SACTO | SACRAMENTO | 2021-03-30 | 2021-04-15 | ETL.5140 | MIDDLE FORK-GOLD HILL | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44141415 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.1194e-07 | 1075.8865
120724500 | E | LC | ETL.4040.POLE.STPS | 44647135 | TABLEMTN | NORTH VALLEY | 2021-04-01 | 2021-09-15 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44646919 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00045863 | 676.0986
120727413 | E | LC | ETL.2540.POLE.WDPS | 44401484 | MOSSLNDG | CENTRAL COAST | 2021-04-01 | 2021-07-08 | ETL.2540 | METCALF-GREEN VALLEY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44401482 |  | 2-Pole Wood | 2P DDE-A - 2 Pole Double Dead End Angle | [7 empty] | 0.071492 | 158.2797
120743564 | E | LC | ETL.3700.INSL.CERA | 40889410 | PISMOBCH | LOS PADRES | 2021-04-01 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40865326 | 1956-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1989-01-01 | Porcelain | Dead End |  |  |  |  | 0.00028451 | 3499.8623 | 0.99574
120743589 | B | LC | ETL.8170.POLE.WOOD | 40744498 | EUREKA | HUMBOLDT | 2021-04-05 | 2021-06-29 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | Missing | [Install, Completed, Completed] | Tier2 |  |  | COMP
120757473 | E | LC | ETL.7560.INSL.NCER | 40635056 | SACTO | SIERRA | 2021-04-07 | 2021-08-31 | ETL.7560 | WEIMAR #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120770264 | F | LC | ETL.1350.POLE.WDPS | 44515161 | TABLEMTN |  | 2021-04-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44513824 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0083316 | 189.9226
120771860 | E | LC | ETL.4040.POLE.STPS | 44976193 | TABLEMTN | NORTH VALLEY | 2021-04-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Vegetation | Overgrown | [Trim] | Tier3 | Tier 3 | Within Both | PEND | 43688510 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0023885 | 1440.0197 | 3.4395
120786660 | E | LC | ETL.9250.INSL.NCER | 40777409 | MIDWAY | KERN | 2021-04-10 | 2021-08-23 | ETL.9250 | TEJON-LEBEC | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40749544 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.044573 | 4848.7817
120787155 | E | LC | ETL.9250.POLE.WOOD | 40662630 | MIDWAY | KERN | 2021-04-10 | 2021-04-15 | ETL.9250 | TEJON-LEBEC | Vegetation | Overgrown | [Trim] | Tier2 | Tier 2 | Within Both | DLFL | 40662630 | 1967-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | [5 empty] | 0.019634 | 4848.7817
120794903 | A | LC | ETL.7360.POLE.NWOD | 44963429 | LAKEVLLE | SONOMA | 2021-04-12 | 2021-04-14 | ETL.7360 | LAKEVILLE #1 | Emergency | Storm Related | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44963429 | 2020-08-10 | Light Duty Steel Pole | T-1 - Tri Post | 2020-08-10 | Polymer | Post |  |  |  |  | 0.00019139 | 1111.2394
120811786 | F | LC | ETL.4392.TOWR | 41129308 | LAKEVLLE | SONOMA | 2021-04-14 | 2021-08-04 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129308 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.022407 | 5164.5723
120811786 | F | LC | ETL.4392.TOWR | 41129308 | LAKEVLLE | SONOMA | 2021-04-14 | 2021-08-04 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129308 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.022407 | 5164.5723
120812243 | F | LC | ETL.5300.TOWR | 40762340 | PISMOBCH | LOS PADRES | 2021-04-14 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762340 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 7.3545e-07 | 652.484 | 0.00047987
120817540 | E | LC | ETL.5850.TOWR | 40664069 | LAKEVLLE | SACRAMENTO | 2021-04-14 | 2021-10-19 | ETL.5850 | VACA-PARKWAY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40664069 | 1946-01-01 | LATTICE STEEL TOWER | Unknown | 1946-01-01 | Ceramic | Dead End |  |  |  |  | 7.1404e-09 | 4861.7715 | 3.4715e-05
120826279 | E | LC | ETL.3750.TOWR | 40761866 | CONCORD | DIABLO | 2021-04-16 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761866 | 1922-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 7.0716e-08 | 31.6978 | 2.2415e-06
120834998 | E | LC | ETL.9340.POLE.WOOD | 44190780 | FRESNO | FRESNO | 2021-04-17 | 2021-10-27 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44190780 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.033093 | 5176.5
120834998 | E | LC | ETL.9340.POLE.WOOD | 44190780 | FRESNO | FRESNO | 2021-04-17 | 2021-10-27 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44190780 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.033093 | 5176.5
120850030 | F | LC | ETL.5300.TOWR | 40660527 | PISMOBCH | LOS PADRES | 2021-04-12 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40660527 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 3.2586e-06 | 930.3098 | 0.0030315
120864708 | B | LC | ETL.4440.INSL | 40720705 | TABLEMTN | NORTH VALLEY | 2021-04-21 | 2021-05-03 | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40674621 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 4.0255e-06 | 1044.361
120874718 | B | LC | ETL.3960.INSL.CERA | 40610688 | PISMOBCH | LOS PADRES | 2021-04-22 | 2021-07-19 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40586148 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 1.1352e-08 | 4958.5791
120874718 | B | LC | ETL.3960.INSL.CERA | 40610688 | PISMOBCH | LOS PADRES | 2021-04-22 | 2021-07-19 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40586148 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 1.1352e-08 | 4958.5791
120875076 | F | LC | ETL.6050.TOWR | 40870822 | MOSSLNDG | CENTRAL COAST | 2021-04-23 |  | ETL.6050 | MOSS LANDING-METCALF | Road | Brush Fuel | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40870822 | 1966-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 2020-05-16 | Glass Silicone Coated | Suspension |  |  |  |  | 2.3638e-07 | 2595.8459
120880324 | F | LC | ETL.5463.POLE.NWOD | 41136386 | CONCORD | DIABLO | 2021-04-24 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41136386 | 2002-01-01 | Tubular Steel Pole | SVDE - Single Vertical Dead End | 2001-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 5.1223e-08 | 5624.2686 | 0.00028809
120901201 | E | LC | ETL.5390.TOWR | 40674086 | TABLEMTN | NORTH VALLEY | 2021-04-29 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40674086 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 6.9232e-06 | 1428.0112 | 0.0098865
120906580 | B | LC | ETL.5933.TOWR | 40762765 | PISMOBCH | LOS PADRES | 2021-04-29 | 2021-05-24 | ETL.5933 | MORRO BAY-TEMPLETON | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40762765 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 9.3179e-07 | 142.5251
120921156 | E | LC | ETL.7000.POLE.WOOD | 40617023 | TABLEMTN | NORTH VALLEY | 2021-05-03 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40617023 | 1998-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0012119 | 205.6771 | 0.24925
121002069 | E | LC | ETL.7610.POLE.WOOD | 40767914 | METCALF | SAN JOSE | 2021-05-10 |  | ETL.7610 | MONTA VISTA-LOS GATOS | Vegetation | Overgrown | [Trim] | Tier2 | Tier 2 | HFRA Removal | PEND | 40767914 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00013658 | 0.065147 | 8.8976e-06
121343019 | E | LC | ETL.1430.TOWR | 40866284 | SACTO | SIERRA | 2021-05-15 |  | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40866284 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.040301 | 142.4642 | 5.7415
121347998 | F | LC | ETL.1420.TOWR | 40756310 | SACTO | SIERRA | 2021-04-24 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40756310 | 1913-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1913-01-01 | Porcelain | Double Dead End |  |  |  |  | 0.0028952 | 316.4859 | 0.91629
121351366 | E | LC | ETL.3500.TOWR | 40744662 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40744662 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 3.9961e-05 | 95.0148 | 0.0037969
121364875 | E | LC | ETL.6870.POLE.WOOD | 44190847 | SACTO | SIERRA | 2021-05-19 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44190847 |  | Single Wood Pole | T-1 - Tri Post | 2020-05-14 | Polymer | Post |  |  |  |  | 0.11255 | 332.3381 | 37.4059
121370099 | E | LC | ETL.1600.TOWR | 40582777 | LAKEVLLE | SONOMA | 2021-05-03 |  | ETL.1600 | FULTON-PUEBLO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40582777 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 1.6844e-06 | 190.6293 | 0.00032109
121379443 | B | LC | ETL.1070.POLE.WOOD | 40643757 | VICTOR | STOCKTON | 2021-05-21 | 2021-07-20 | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121380563 | B | LC | ETL.6470.POLE.WOOD | 40873684 | SACTO | SIERRA | 2021-05-19 | 2021-08-09 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40873684 |  | Single Wood Pole | T2N | 2021-07-10 | Polymer | Post |  |  |  |  | 0.084026 | 110.8481
121380563 | B | LC | ETL.6470.POLE.WOOD | 40873684 | SACTO | SIERRA | 2021-05-19 | 2021-08-09 | ETL.6470 | COLGATE-ALLEGHANY | Tie Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40873684 |  | Single Wood Pole | T2N | 2021-07-10 | Polymer | Post |  |  |  |  | 0.084026 | 110.8481
121380655 | F | LC | ETL.6760.POLE.WOOD | 40664735 | SACTO | SIERRA | 2021-05-06 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40664735 |  | Single Wood Pole | T-1 - Tri Post | 2019-05-30 | Polymer | Post |  |  |  |  | 0.0095562 | 1060.4241
121381979 | F | LC | ETL.6500.POLE.WOOD | 43689857 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 43689857 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Other |  |  |  |  | 0.0014261 | 2820.3911
121382058 | F | LC | ETL.8250.POLE.WOOD | 40908836 | VICTOR | STOCKTON | 2021-05-11 | 2021-06-23 | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40908836 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00053222 | 1664.5133
121384012 | F | LC | ETL.6500.POLE.NWOD | 45165693 | SACTO | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45165693 | 2020-07-27 | Light Duty Steel Pole | T-1 - Tri Post | 2020-07-27 | Polymer | Post
121384537 | E | LC | ETL.8350.POLE.NWOD | 44885873 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44885873 | 2019-10-03 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2019-10-03 | Polymer | Post |  |  |  |  | 1.5792e-06 | 1427.2969 | 0.002254
121387106 | E | LC | ETL.7550.POLE.WOOD | 40698050 | LAKEVLLE | HUMBOLDT | 2021-05-21 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40698050 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 7.224e-05 | 2958.8982 | 0.21375
121388124 | E | LC | ETL.6220.POLE.WOOD | 40698413 | EUREKA | HUMBOLDT | 2021-05-24 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40698413 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.12974 | 522.5851 | 67.8021
121418094 | E | LC | ETL.5540.TOWR | 40673091 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40673091 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1950-01-01 | Porcelain | Suspension |  |  |  |  | 3.811e-08 | 1997.6632 | 7.6131e-05
121421671 | E | LC | ETL.7040.POLE.WOOD | 40591253 | TABLEMTN | NORTH VALLEY | 2021-05-24 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40591253 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.18023 | 144.0314 | 25.9592
121428403 | F | LC | ETL.1420.POLE.STPS | 44337065 | SACTO | SACRAMENTO | 2021-05-25 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44337064 | 2016-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.2054e-07 | 316.4733
121428454 | F | LC | ETL.4316.POLE.STPS | 44209595 | TABLEMTN |  | 2021-05-26 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 43696796 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.7365e-05 | 0.077803
121428851 | E | LC | ETL.6470.POLE.WOOD | 40817361 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40817361 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.12912 | 269.0426 | 34.7387
121470858 | B | LC | ETL.4950.INSL | 40782289 | LAKEVLLE |  | 2021-06-03 | 2021-06-21 | ETL.4950 | FULTON-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594213 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0037861 | 411.6203
121470858 | B | LC | ETL.4950.INSL | 40782289 | LAKEVLLE |  | 2021-06-03 | 2021-06-21 | ETL.4950 | FULTON-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594213 | 1984-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.0037861 | 411.6203
121475405 | E | LC | ETL.1250.POLE.WDPS | 44319507 | FRESNO | FRESNO | 2021-05-28 | 2021-06-30 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44319506 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.2086e-06 | 4323.0181
121481578 | F | LC | ETL.7130.POLE.WDPS | 44315157 | EUREKA | HUMBOLDT | 2021-06-05 | 2021-08-02 | ETL.7130 | HUMBOLDT-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44315155 | 2013-10-26 | 3-Pole Wood | SVDE - Single Vertical Dead End | [7 empty] | 0.17715 | 0.065148
121483481 | F | LC | ETL.7630.POLE.WOOD | 40873119 | LAKEVLLE | SONOMA | 2021-06-03 | 2021-10-18 | ETL.7630 | MONTE RIO-FULTON | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40873119 | 1997-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.034957 | 31.7051
121484950 | F | LC | ETL.4782.POLE.STPS | 45099299 | LAKEVLLE | HUMBOLDT | 2021-06-07 |  | ETL.4782 | SANTA FE GEOTHERMAL TAP | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40584987 |  | 3-Pole Non Wood | DDE-A - Double Dead End Angle | [7 empty] | 2.3657e-05 | 284.9657
121485046 | F | LC | ETL.5140.POLE.STPS | 44690688 | SACTO | SIERRA | 2021-05-29 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44141441 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.0712e-09 | 5272.4746
121485071 | F | LC | ETL.7550.POLE.WOOD | 40876385 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40876385 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 7.3718e-06 | 3342.5151
121488450 | F | LC | ETL.6760.POLE.WOOD | 40822654 | SACTO | SIERRA | 2021-06-07 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40822654 |  | Single Wood Pole | T-1 - Tri Post | 2020-05-26 | Polymer | Post |  |  |  |  | 0.022195 | 110.8102
121498228 | E | LC | ETL.8170.POLE.NWOD | 44846605 | EUREKA | HUMBOLDT | 2021-06-02 |  | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44846605 | 2019-05-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-05-17 | Glass | Dead End |  |  |  |  | 0.0012773 | 5637.5752 | 7.2009
121498228 | E | LC | ETL.8170.POLE.NWOD | 44846605 | EUREKA | HUMBOLDT | 2021-06-02 |  | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44846605 | 2019-05-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-05-17 | Glass | Dead End |  |  |  |  | 0.0012773 | 5637.5752 | 7.2009
121514250 | B | LC | ETL.6890.INSL.NCER | 44635339 | LAKEVLLE |  | 2021-06-09 | 2021-08-02 | ETL.6890 | FULTON-HOPLAND | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44635333 | 2018-08-01 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2018-08-01 | Polymer | Suspension |  |  |  |  | 9.9443e-07 | 126.6897
121520071 | F | LC | ETL.6880.POLE.WOOD | 40912418 | LAKEVLLE | NORTH BAY | 2021-06-07 |  | ETL.6880 | FULTON-CALISTOGA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40912418 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0022896 | 1836.4817 | 4.2047
121523500 | E | LC | ETL.4040.POLE.WDPS | 44552482 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44551571 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.045394 | 1426.2432 | 64.7425
121544961 | E | LC | ETL.5420.POLE.STPS | 44400026 | TABLEMTN | NORTH VALLEY | 2021-06-14 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44400025 | 2017-11-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.7313e-08 | 1028.4974 | 3.8376e-05
121553214 | E | LC | ETL.6650.POLE.WDPS | 44386920 | TABLEMTN | NORTH VALLEY | 2021-06-17 | 2021-06-23 | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44386919 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.022504 | 2441.9417
121553815 | B | LC | ETL.8360.INSL.CERA | 40698027 | LAKEVLLE |  | 2021-06-17 | 2021-08-02 | ETL.8360 | LAYTONVILLE-WILLITS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44412048 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Double Dead End |  |  |  |  | 0.0035111
121553815 | B | LC | ETL.8360.INSL.CERA | 40698027 | LAKEVLLE |  | 2021-06-17 | 2021-08-02 | ETL.8360 | LAYTONVILLE-WILLITS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44412048 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Double Dead End |  |  |  |  | 0.0035111
121553815 | B | LC | ETL.8360.INSL.CERA | 40698027 | LAKEVLLE |  | 2021-06-17 | 2021-08-02 | ETL.8360 | LAYTONVILLE-WILLITS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44412048 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Double Dead End |  |  |  |  | 0.0035111
121557687 | E | LC | ETL.7490.INSL | 40802697 | EUREKA | HUMBOLDT | 2021-06-16 |  | ETL.7490 | MAPLE CREEK-HOOPA | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40771317 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 0.023573 | 189.8608 | 4.4757
121560083 | E | LC | ETL.6240.POLE.WOOD | 40823332 | MOSSLNDG | CENTRAL COAST | 2021-06-16 | 2021-08-09 | ETL.6240 | BURNS-LONE STAR #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40823332 |  | Single Wood Pole | TPAF - Flat Pin Arm | 2021-08-01 | Polymer | Post |  |  |  |  | 0.60757 | 0.065152
121573058 | E | LC | ETL.7550.POLE.WOOD | 40698000 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40698000 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 5.3221e-06 | 0.065148 | 3.4672e-07
121574387 | E | LC | ETL.1350.POLE.STPS | 45021990 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45021959 | 2020-10-07 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.001353 | 316.5195 | 0.42826
121603840 | F | LC | ETL.4040.POLE.STPS | 45006538 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-07-19 | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 45006453 | 2020-09-17 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.6921e-05 | 2294.1755
121606542 | B | LC | ETL.4960.INSL | 40897036 | CONCORD |  | 2021-06-16 | 2021-08-05 | ETL.4960 | LAKEVILLE-SOBRANTE #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40872696 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 5.3248e-05 | 1427.1888
121629566 | E | LC | ETL.6650.POLE.WDPS | 45099302 | TABLEMTN | NORTH VALLEY | 2021-06-29 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40616021 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0050596 | 903.4213 | 4.571
121634319 | E | LC | ETL.5140.POLE.WDPS | 44552567 | SACTO | SACRAMENTO | 2021-06-23 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44551676 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0024331 | 205.7471 | 0.50061
121641794 | E | LC | ETL.2700.TOWR | 40857616 | CONCORD | DIABLO | 2021-06-22 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857616 | 1944-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.1831e-06 | 1370.5471 | 0.0016215
121641794 | E | LC | ETL.2700.TOWR | 40857616 | CONCORD | DIABLO | 2021-06-22 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857616 | 1944-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-03-30 | Glass | Suspension |  |  |  |  | 1.1831e-06 | 1370.5471 | 0.0016215
121691126 | F | LC | ETL.6430.POLE.WOOD | 40667368 | TABLEMTN | NORTH VALLEY | 2021-07-05 |  | ETL.6430 | COLEMAN-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40667368 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Pin |  |  |  |  | 0.0072473 | 3954.0575
121706671 | B | LC | ETL.7550.POLE.NWOD | 45012929 | LAKEVLLE | HUMBOLDT | 2021-07-07 | 2021-07-27 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45012929 | 2019-11-18 | Light Duty Steel Pole | TPS - Tri Post & Susp (1-3) |  | Glass | Suspension |  |  |  |  | 1.205e-10 | 806.9501
121714827 | E | LC | ETL.5400.INSL | 40722072 | TABLEMTN | NORTH VALLEY | 2021-07-12 |  | ETL.5400 | PIT #3-PIT #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40677307 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 0.011356 | 4243.0601 | 48.1846
121716471 | F | LC | ETL.4050.POLE.WDPS | 44558388 | LAKEVLLE |  | 2021-07-06 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44557895 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00012225 | 2187.8147
121717212 | E | LC | ETL.6050.INSL.CERA | 40741080 | METCALF | SAN JOSE | 2021-07-12 |  | ETL.6050 | MOSS LANDING-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40740232 |  | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End |  | Ceramic | Dead End |  |  |  |  | 2.9847e-07 | 2595.8459 | 0.00077479
121722717 | A | LC | ETL.1820.POLE.WDPS | 44562693 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-07-15 | ETL.1820 | HUMBOLDT-TRINITY | Emergency | Storm Related | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44562443 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.05269 | 221.983
121731298 | E | LC | ETL.2395.POLE.WOOD | 44948578 | TABLEMTN | NORTH VALLEY | 2021-06-12 | 2021-09-29 | ETL.2395 | GRIZZLY TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44948578 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Unknown | Suspension |  |  |  |  | 0.0011295 | 189.8861
121734164 | B | LC | ETL.1810.POLE.WDPS | 44322432 | EUREKA | HUMBOLDT | 2021-07-14 | 2021-08-12 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322431 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0012584
121742589 | E | LC | ETL.3720.INSL.CERA | 40671721 | CONCORD | EAST BAY | 2021-07-13 |  | ETL.3720 | SOBRANTE-G #1 | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40644471 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1968-01-01 | Porcelain | Suspension |  |  |  |  | 6.0395e-05 | 269.6005 | 0.016283
121743232 | F | LC | ETL.6950.POLE.NWOD | 44944255 | SACTO | SIERRA | 2021-07-15 | 2021-08-02 | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44944255 | 2020-05-08 | Light Duty Steel Pole | T-1 - Tri Post | 2020-05-08 | Polymer | Post |  |  |  |  | 0.00016959 | 1313.0015
121745630 | E | LC | ETL.4316.POLE.NWOD | 45102878 | TABLEMTN | NORTH VALLEY | 2021-07-14 |  | ETL.4316 | PARADISE-TABLE MTN | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 45102878 | 2021-04-30 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2021-04-30 | Glass | Suspension |  |  |  |  | 3.449e-05 | 1982.3486 | 0.06837
121753649 | B | LC | ETL.6040.INSL | 40724091 | MOSSLNDG | CENTRAL COAST | 2021-07-16 | 2021-09-01 | ETL.6040 | MOSS LANDING-LOS BANOS | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40680865 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 7.8797e-08
121783807 | E | LC | ETL.9240.TOWR | 43249715 | PISMOBCH | LOS PADRES | 2021-07-22 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249715 |  | LATTICE STEEL TOWER | [9 empty] | 2470.1736
121788211 | B | LC | ETL.6280.POLE.WOOD | 40698755 | TABLEMTN | NORTH VALLEY | 2021-07-23 | 2021-09-16 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.5033e-05 | 31.7091
121797923 | B | LC | ETL.6020.TOWR | 41191655 | TABLEMTN | NORTH VALLEY | 2021-07-26 | 2021-08-11 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41191655 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00012436 | 221.5655
121829483 | E | LC | ETL.1110.SWIT | 45016446 | TABLEMTN | NORTH VALLEY | 2021-07-31 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Switch | Out of Adjustment | [Repair] | Tier2 |  |  | PEND | [7 empty] | 2020-11-30 | SEECO | VACUUM INTERRUPTERS (5 GAPS) | SCADA Only
122064806 | E | LC | ETL.4780.INSL | 40724664 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40681705 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 2.826e-05 | 221.7097 | 0.0062656
118603242 | E | LC | ETL.9090.POLE.WDPS | 44565351 | PISMOBCH | LOS PADRES | 2020-03-04 | 2021-05-05 | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118652246 | E | LC | ETL.3180.TOWR | 40646332 | CONCORD | DIABLO | 2020-03-09 | 2021-07-07 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | DLFL | 40646332 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.0723e-06 | 16.3369
118652251 | E | LC | ETL.3180.TOWR | 40579964 | CONCORD | DIABLO | 2020-03-09 | 2020-04-30 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator | Contaminated | [Ground Wash, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40579964 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1944-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.2522e-06 | 16.2382
118652251 | E | LC | ETL.3180.TOWR | 40579964 | CONCORD | DIABLO | 2020-03-09 | 2020-04-30 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Insulator | Contaminated | [Ground Wash, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40579964 | 1941-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-03-27 | Glass | Dead End |  |  |  |  | 3.2522e-06 | 16.2382
118683843 | E | LC | ETL.6640.POLE.NWOD | 40593599 | TABLEMTN | NORTH VALLEY | 2020-03-12 | 2020-05-05 | ETL.6640 | COTTONWOOD-BENTON #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40593599 | 2010-01-01 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-10 | Polymer | Post |  |  |  |  | 0.00040957 | 3249.6929
118781633 | E | LC | ETL.6980.POLE.WDPS | 44312229 | LAKEVLLE | SONOMA | 2020-04-06 | 2020-11-10 | ETL.6980 | FORT ROSS-GUALALA | Anchor-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | DLFL | 44312226 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.044642 | 126.7015
118923802 | E | LC | ETL.3500.TOWR | 40744661 | VICTOR | STOCKTON | 2020-04-14 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40744661 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 5.7317e-05 | 348.2221 | 0.019959
118939974 | E | LC | ETL.7510.POLE.WDPS | 44218388 | LAKEVLLE | SONOMA | 2020-04-22 | 2020-07-03 | ETL.7510 | MENDOCINO-HARTLEY | Ground Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44218387 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00015326 | 4355.1782
118949763 | F | LC | ETL.4750.TOWR | 40594204 | LAKEVLLE | SONOMA | 2020-04-26 | 2020-05-11 | ETL.4750 | GEYSERS #12-FULTON | Structure-Steel | Anti-Climbing Guard | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594204 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 3.3443e-07 | 3054.8015
118960135 | E | LC | ETL.7212.POLE.WOOD | 40601801 | METCALF | SAN JOSE | 2020-04-20 | 2021-05-19 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40601801 |  | Single Wood Pole | 3P DDE-A - 3 Pole Double Dead End Angle |  | Ceramic | [5 empty] | 0.64151 | 538.9081
118975671 | E | LC | ETL.8253.POLE.WOOD | 40821941 | VICTOR | STOCKTON | 2020-04-23 |  | ETL.8253 | IONE TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40821941 | 1987-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Other |  |  |  |  | 0.00042632 | 1001.5823 | 0.42699
118999802 | F | LC | ETL.4392.TOWR | 41129373 | LAKEVLLE | SONOMA | 2020-05-08 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Road | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129373 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.00033265 | 740.6124
118999802 | F | LC | ETL.4392.TOWR | 41129373 | LAKEVLLE | SONOMA | 2020-05-08 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Road | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129373 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.00033265 | 740.6124
119016357 | E | LC | ETL.8650.TOWR | 40859316 | FRESNO | YOSEMITE | 2020-05-04 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40859316 | 1929-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2019-11-18 | Glass | Suspension |  |  |  |  | 0.012896 | 7011.6152
119084349 | B | LC | ETL.6760.POLE.WOOD | 40611241 | SACTO | SIERRA | 2020-05-29 | 2020-11-09 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611241 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Dead End |  |  |  |  | 0.0090718 | 109.2179
119084653 | E | LC | ETL.3750.INSL.CERA | 40622389 | CONCORD | EAST BAY | 2020-05-22 | 2021-03-22 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119086107 | E | LC | ETL.7980.POLE.WOOD | 40694046 | SACTO | SACRAMENTO | 2020-06-01 |  | ETL.7980 | SMARTVILLE-MARYSVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40694046 |  | Single Wood Pole | DV - Double Vertical |  | Ceramic | [5 empty] | 0.014527 | 1839.6332 | 26.725
119112090 | E | LC | ETL.6760.POLE.WOOD | 40654105 | SACTO | SIERRA | 2020-05-27 | 2021-03-18 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40654105 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.10616 | 47.5526
119112260 | F | LC | ETL.6490.POLE.WOOD | 40603839 | SACTO | SIERRA | 2020-06-02 | 2021-09-13 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40603839 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-08-31 | Glass | Dead End |  |  |  |  | 0.0045085 | 4144.5146
119114933 | E | LC | ETL.1240.POLE.STPS | 44197148 | TABLEMTN |  | 2020-06-02 | 2020-07-15 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Tier 2 | Within Both | COMP | 44197146 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.4379e-09 | 2691.6716
119115086 | E | LC | ETL.1112.POLE.NWOD | 44420218 | FRESNO | YOSEMITE | 2020-06-02 |  | ETL.1112 | INDIAN FLAT-YOSEMITE | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44420218 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Glass | Suspension |  |  |  |  | 0.00011343 | 6710.374 | 0.76117
119124873 | E | LC | ETL.8170.POLE.WOOD | 40906430 | EUREKA | HUMBOLDT | 2020-06-03 | 2021-09-07 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906430 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | [5 empty] | 0.031019 | 189.9226
119128830 | F | LC | ETL.6280.POLE.WOOD | 40599649 | TABLEMTN | NORTH VALLEY | 2020-06-03 |  | ETL.6280 | CARIBOU #2 | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40599649 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 8.5139e-06 | 0.065148
119155870 | E | LC | ETL.1420.TOWR | 40750985 | SACTO | SIERRA | 2020-06-04 | 2021-02-01 | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750985 | 1913-01-01 | LATTICE STEEL TOWER | FDDE - Flat Dead End Construction | 2021-02-23 | Glass | Double Dead End |  |  |  |  | 1.0202e-05 | 1993.4753
119166722 | F | LC | ETL.6280.POLE.WOOD | 40826434 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2021-09-14 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 1.5033e-05 | 36.4515
119168512 | B | LC | ETL.6280.INSL | 40892601 | TABLEMTN | NORTH VALLEY | 2020-06-15 | 2020-06-30 | ETL.6280 | CARIBOU #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40868137 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 4.9819e-06 | 569.452
119183632 | E | LC | ETL.6280.POLE.WOOD | 40826407 | TABLEMTN | NORTH VALLEY | 2020-06-16 | 2021-07-08 | ETL.6280 | CARIBOU #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | DLFL
119198753 | E | LC | ETL.6470.INSL.CERA | 40849862 | SACTO | SACRAMENTO | 2020-06-22 | 2021-08-03 | ETL.6470 | COLGATE-ALLEGHANY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119199203 | F | LC | ETL.2660.POLE.NWOD | 40861991 | SACTO | SIERRA | 2020-06-22 | 2021-07-06 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40861991 | 1967-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Porcelain | Suspension |  |  |  |  | 1.552e-09 | 15.8837
119199203 | F | LC | ETL.2660.POLE.NWOD | 40861991 | SACTO | SIERRA | 2020-06-22 | 2021-07-06 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40861991 | 1967-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Ceramic | Suspension |  |  |  |  | 1.552e-09 | 15.8837
119206023 | F | LC | ETL.6870.POLE.NWOD | 44361748 | SACTO | SIERRA | 2020-06-23 | 2021-07-06 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44361748 |  | Light Duty Steel Pole | FSS - Field Switch Structure | [7 empty] | 0.013137 | 63.3733
119210464 | B | LC | ETL.6720.POLE.WOOD | 42578819 | TABLEMTN | NORTH VALLEY | 2020-06-24 | 2020-10-26 | ETL.6720 | DESABLA-CENTERVILLE | Other | Customer Issue | [Customer Refusal, Completed] | Tier3 |  |  | COMP
119210635 | F | LC | ETL.7270.POLE.WOOD | 40862147 | TABLEMTN | NORTH VALLEY | 2020-06-25 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40862147 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.048886 | 744.5844
119219345 | E | LC | ETL.4680.TOWR | 40872361 | LAKEVLLE | SONOMA | 2020-06-26 | 2020-11-24 | ETL.4680 | FULTON-IGNACIO #1 | Vegetation | Overgrown | [Trim, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40872361 | 1966-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.3677e-06 | 174.5292
119231937 | E | LC | ETL.7180.POLE.WOOD | 40861081 | LAKEVLLE | SONOMA | 2020-06-29 | 2021-04-21 | ETL.7180 | IGNACIO-BOLINAS #2 | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861081 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 4.4021e-06 | 71.6461
119234457 | E | LC | ETL.1402.POLE.STPS | 44915896 | VICTOR | YOSEMITE | 2020-06-29 | 2021-01-14 | ETL.1402 | SPRING GAP TAP | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 3 | Within Both | COMP | 44915830 | 2019-11-21 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 4.4685e-06 | 1329.0924
119237340 | E | LC | ETL.6220.POLE.WOOD | 40600514 | EUREKA | HUMBOLDT | 2020-06-30 | 2021-10-24 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.39286 | 316.1304 | 124.1952
119238054 | E | LC | ETL.7270.POLE.WOOD | 40906113 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2021-08-07 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906113 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0031954 | 3119.219
119295614 | F | LC | ETL.8060.POLE.WOOD | 40810157 | SACTO | SIERRA | 2020-06-29 | 2021-08-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810157 |  | Single Wood Pole | T2N | 2021-08-02 | Polymer | Post |  |  |  |  | 0.003398 | 95.1488
119295630 | F | LC | ETL.5540.POLE.STPS | 44383624 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.5540 | POE-RIO OSO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44383623 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.1186e-09 | 395.8822
119300335 | E | LC | ETL.1110.POLE.STPS | 44899402 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-04-13 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44899381 | 2020-01-30 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 9.4476e-06 | 9019.2051
119304930 | F | LC | ETL.1180.POLE.WOOD | 44879461 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-01-29 | ETL.1180 | BUTTE VALLEY-CARIBOU | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44879461 |  | Single Wood Pole | SV-DE-90 - Single Vertical Dead End 90 |  | Unknown | Unknown |  |  |  |  | 0.050008 | 5538.7192
119307767 | F | LC | ETL.8170.POLE.WOOD | 40906449 | EUREKA | HUMBOLDT | 2020-07-02 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40906449 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.078044 | 94.9939
119313155 | E | LC | ETL.7300.POLE.WOOD | 40602045 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-03-11 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119317385 | F | LC | ETL.7030.POLE.WOOD | 40758923 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758923 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.030851 | 0.06515
119325046 | E | LC | ETL.7180.POLE.WOOD | 40585472 | LAKEVLLE | SONOMA | 2020-07-07 | 2021-04-08 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585472 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.5221e-05 | 2537.4253
119325778 | F | LC | ETL.6300.POLE.WOOD | 40698888 | TABLEMTN |  | 2020-07-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40698888 | 2013-01-01 | Single Wood Pole | T-1 - Tri Post | 2014-11-07 | Non Ceramic | Post |  |  |  |  | 0.00047613 | 126.6209
119350214 | F | LC | ETL.1110.POLE.WDPS | 44561178 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-02-10 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install] |  | Tier 2 | Within Both | DLFL | 44515894 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00096821 | 4417.5273
119358068 | F | LC | ETL.6280.POLE.WOOD | 40826483 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Non-HFTD | Non-HFRA | PEND | 40826483 |  | Single Wood Pole | LB - Line and Buck |  | Ceramic | Other |  |  |  |  | 0.00013859 | 522.9415
119359598 | F | LC | ETL.7030.POLE.WOOD | 40877579 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40877579 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.0053217 | 0.065151
119369383 | E | LC | ETL.6380.POLE.WOOD | 40752566 | LAKEVLLE | SONOMA | 2020-07-14 | 2021-03-09 | ETL.6380 | KONOCTI-MIDDLETOWN | Switch-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752566 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 3.7377e-05 | 1729.3945
119399329 | E | LC | ETL.6222.POLE.WOOD | 40808736 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.6222 | FORT SEWARD TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40808736 | 2010-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 0.00045017
119461635 | F | LC | ETL.7030.POLE.WOOD | 40591885 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591885 |  | Single Wood Pole | T2N | 2020-06-29 | Polymer | Post |  |  |  |  | 0.016082 | 0.06515
119470432 | A | LC | ETL.1440.POLE.WOOD | 40866547 | SACTO | SACRAMENTO | 2020-07-18 | 2020-08-03 | ETL.1440 | DRUM-SUMMIT #1 | Emergency-Wood | Other | [Replace, Completed] | Tier2 |  |  | COMP
119479210 | E | LC | ETL.1450.TOWR | 40602591 | SACTO | SIERRA | 2020-07-20 | 2021-05-13 | ETL.1450 | DRUM-SUMMIT #2 | Switch | Out of Adjustment | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602591 | 1955-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | 1955-01-01 | Ceramic | Dead End |  |  |  |  | 4.3035e-06 | 348.1462
119485284 | B | LC | ETL.2470.POLE.WOOD | 40658943 | MOSSLNDG | CENTRAL COAST | 2020-07-22 | 2020-09-30 | ETL.2470 | METCALF-COYOTE PUMPING PLANT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40658943 | 1986-01-01 | Single Wood Pole | DV - Double Vertical | 1986-01-01 | Ceramic | Dead End |  |  |  |  | 9.3164e-05
119487343 | E | LC | ETL.1370.INSL.CERA | 40856115 | PISMOBCH | LOS PADRES | 2020-07-22 | 2021-06-29 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119496012 | F | LC | ETL.3190.TOWR | 40761090 | TABLEMTN | NORTH VALLEY | 2020-07-23 | 2021-02-01 | ETL.3190 | CARIBOU-PALERMO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40761090 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-07-30 | Porcelain | Suspension |  |  |  |  | 0.00086174 | 3832.9919
119511860 | E | LC | ETL.8060.POLE.WOOD | 40809675 | SACTO | SACRAMENTO | 2020-07-27 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809675 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0052244 | 291.1663
119534763 | F | LC | ETL.4393.POLE.WDPS | 44172174 | SACTO | SACRAMENTO | 2020-07-31 | 2021-06-21 | ETL.4393 | DRUM-HIGGINS | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44172172 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00075752 | 664.5352
119562041 | F | LC | ETL.7780.POLE.WOOD | 40660560 | LAKEVLLE | HUMBOLDT | 2020-08-05 |  | ETL.7780 | PHILO JCT-ELK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40660560 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 6.1589e-06 | 3110.5322
119599302 | E | LC | ETL.8365.POLE.WOOD | 40906597 | EUREKA | HUMBOLDT | 2020-08-11 | 2021-04-29 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906597 | 2010-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.022299
119615218 | B | LC | ETL.1112.POLE.NWOD | 44420235 | FRESNO | FRESNO | 2020-08-14 | 2020-12-14 | ETL.1112 | INDIAN FLAT-YOSEMITE | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420235 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.00059495 | 2803.7676
119615386 | E | LC | ETL.1810.POLE.STPS | 44322238 | EUREKA | HUMBOLDT | 2020-08-14 | 2021-11-15 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Crossarm-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | DLFL | 44322237 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.4663e-05
119623263 | E | LC | ETL.7490.POLE.NWOD | 44707296 | EUREKA | HUMBOLDT | 2020-08-16 | 2021-10-14 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44707296 | 2019-02-25 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-02-25 | Polymer | Dead End |  |  |  |  | 0.00020953 | 47.5141 | 0.0099556
119643314 | B | LC | ETL.8650.POLE.NWOD | 44420194 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420194 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0039383 | 3843.0691
119660640 | A | LC | ETL.7180.INSL.CERA | 40833147 | LAKEVLLE | SONOMA | 2020-08-17 | 2020-09-10 | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119665872 | F | LC | ETL.3800.TOWR | 40764274 | CONCORD | EAST BAY | 2020-08-20 | 2021-02-09 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40764274 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.4858e-08 | 174.8163
119680784 | F | LC | ETL.3800.TOWR | 40650623 | CONCORD | EAST BAY | 2020-08-20 | 2021-04-19 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650623 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Ceramic | Suspension |  |  |  |  | 1.4851e-07 | 1395.4297
119701857 | E | LC | ETL.8060.POLE.WOOD | 40761663 | SACTO | SIERRA | 2020-08-28 | 2021-04-03 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 0.0055812 | 30.1245
119715994 | B | LC | ETL.6710.POLE.WOOD | 40613861 | MOSSLNDG | CENTRAL COAST | 2020-08-31 | 2020-11-21 | ETL.6710 | DEL MONTE-VIEJO | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40613861 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Ceramic | [5 empty] | 0.16278 | 0.065148
119718966 | F | LC | ETL.1680.POLE.WOOD | 40741958 | LAKEVLLE | SONOMA | 2020-07-30 | 2021-01-20 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40741958 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2020-11-13 | Glass | Dead End |  |  |  |  | 0.00068683 | 5129.7943
119720428 | E | LC | ETL.2410.INSL | 40791989 | LAKEVLLE |  | 2020-06-23 | 2021-08-16 | ETL.2410 | MENDOCINO-REDBUD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119720478 | B | LC | ETL.1530.TOWR | 40862225 | SACTO | SIERRA | 2020-08-25 | 2020-11-19 | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862225 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-11-10 | Ceramic | Suspension |  |  |  |  | 0.00089309 | 601.4848
119728657 | B | LC | ETL.8170.INSL | 40735637 | EUREKA | HUMBOLDT | 2020-09-09 | 2020-10-13 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40701802 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.60539 | 253.1639
119756198 | E | LC | ETL.1810.POLE.STPS | 44322454 | EUREKA | HUMBOLDT | 2020-08-18 | 2020-11-09 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Crossarm-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | DLFL | 44322453 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.6516e-06
119781237 | F | LC | ETL.7030.POLE.WOOD | 40825645 | TABLEMTN | NORTH VALLEY | 2020-09-12 | 2021-06-23 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825645 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.023488 | 63.4531
119785865 | E | LC | ETL.7930.POLE.NWOD | 40824188 | MOSSLNDG | CENTRAL COAST | 2020-09-18 | 2020-11-20 | ETL.7930 | SALINAS-LAURELES | Switch | Out of Adjustment | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40824188 |  | Tubular Steel Pole | FSS - Field Switch Structure |  | Non Ceramic | Other |  |  |  |  | 0.00094429 | 63.3245
119788195 | E | LC | ETL.7300.INSL.NCER | 44957562 | TABLEMTN | NORTH VALLEY | 2020-09-16 | 2021-03-22 | ETL.7300 | KILARC-DESCHUTES | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44957542 | 2019-10-01 | Light Duty Steel Pole | T-1 - Tri Post | 2019-10-01 | Polymer | Post |  |  |  |  | 3.2844e-08 | 2853.7749
119791685 | F | LC | ETL.6440.POLE.WOOD | 44191477 | TABLEMTN | NORTH VALLEY | 2020-08-04 |  | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44191477 |  | Single Wood Pole | T-1 - Tri Post | [7 empty] | 0.002673 | 2652.9794
119803590 | E | LC | ETL.2740.TOWR | 40746996 | CONCORD | EAST BAY | 2020-09-22 | 2021-03-10 | ETL.2740 | MORAGA-OAKLAND #3 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746996 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-06-08 | Glass Silicone Coated | Suspension |  |  |  |  | 3.7406e-06 | 0.065152
119803590 | E | LC | ETL.2740.TOWR | 40746996 | CONCORD | EAST BAY | 2020-09-22 | 2021-03-10 | ETL.2740 | MORAGA-OAKLAND #3 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746996 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-06-10 | Glass Silicone Coated | Suspension |  |  |  |  | 3.7406e-06 | 0.065152
119818184 | F | LC | ETL.7290.POLE.WOOD | 41119877 | TABLEMTN | NORTH VALLEY | 2020-08-29 | 2021-09-29 | ETL.7290 | KILARC-CEDAR CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41119877 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.4601 | 2436.0542
119850946 | F | LC | ETL.8365.POLE.NWOD | 44356203 | EUREKA | HUMBOLDT | 2020-09-17 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44356203 | 2016-06-21 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2016-06-21 | Polymer | Post |  |  |  |  | 0.023209
119890044 | E | LC | ETL.6030.TOWR | 40762999 | MIDWAY | KERN | 2020-10-09 | 2021-05-17 | ETL.6030 | MIDWAY-WHIRLWIND | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40762999 | 1973-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1973-01-01 | Ceramic | Dead End |  |  |  |  | 4.8974e-06 | 5624.5342
119914624 | F | LC | ETL.1721.TOWR | 44181023 | MOSSLNDG | CENTRAL COAST | 2020-10-16 |  | ETL.1721 | METCALF-SALINAS #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44181023 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 2.6798e-08
119914624 | F | LC | ETL.1721.TOWR | 44181023 | MOSSLNDG | CENTRAL COAST | 2020-10-16 |  | ETL.1721 | METCALF-SALINAS #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44181023 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 2.6798e-08
119914624 | F | LC | ETL.1721.TOWR | 44181023 | MOSSLNDG | CENTRAL COAST | 2020-10-16 |  | ETL.1721 | METCALF-SALINAS #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44181023 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Non Ceramic | Suspension |  |  |  |  | 2.6798e-08
119920407 | B | LC | ETL.6220.POLE.WOOD | 40591058 | EUREKA | HUMBOLDT | 2020-10-16 | 2021-01-04 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40591058 |  | Single Wood Pole | T2N | 2020-12-20 | Polymer | Post |  |  |  |  | 0.20627 | 554.6226
119961150 | E | LC | ETL.6060.TOWR | 40601310 | TABLEMTN | NORTH VALLEY | 2020-10-29 | 2021-06-14 | ETL.6060 | ROUND MTN-TABLE MTN #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40601310 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Non Ceramic | Suspension |  |  |  |  | 9.6191e-06 | 1800.2244
119961150 | E | LC | ETL.6060.TOWR | 40601310 | TABLEMTN | NORTH VALLEY | 2020-10-29 | 2021-06-14 | ETL.6060 | ROUND MTN-TABLE MTN #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40601310 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 9.6191e-06 | 1800.2244
119973763 | F | LC | ETL.8580.POLE.WOOD | 40663521 | FRESNO | FRESNO | 2020-10-29 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40663521 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Other |  |  |  |  | 0.00017441
119974473 | B | LC | ETL.8580.INSL.NCER | 40694788 | FRESNO | FRESNO | 2020-11-02 | 2020-12-15 | ETL.8580 | COALINGA #1-SAN MIGUEL | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40663533 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 3.5243e-07
120044889 | F | LC | ETL.6240.POLE.WOOD | 40767337 | MOSSLNDG | CENTRAL COAST | 2020-10-06 | 2021-08-09 | ETL.6240 | BURNS-LONE STAR #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40767337 |  | Single Wood Pole | FDDE - Flat Dead End Construction | 2020-09-18 | Glass | Dead End |  |  |  |  | 0.22099 | 15.8866
120050264 | E | LC | ETL.2394.INSL.CERA | 40631842 | PISMOBCH | LOS PADRES | 2020-11-17 | 2021-09-23 | ETL.2394 | OCEANO-CALLENDER SW STA | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | DLFL | 40593079 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Porcelain | Dead End - Suspension |  |  |  |  | 6.0487e-06 | 1092.1489
120139345 | F | LC | ETL.7930.POLE.WOOD | 40861740 | MOSSLNDG | CENTRAL COAST | 2020-10-28 |  | ETL.7930 | SALINAS-LAURELES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40861740 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Other |  |  |  |  | 0.00347 | 31.6948
120143824 | E | LC | ETL.8650.POLE.NWOD | 44420140 | FRESNO | FRESNO | 2020-12-08 |  | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44420140 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.010077 | 6900.5825 | 69.5402
120241321 | F | LC | ETL.4440.POLE.NWOD | 41162690 | TABLEMTN | NORTH VALLEY | 2020-12-04 |  | ETL.4440 | CARIBOU-TABLE MTN | Structure-Steel | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 41162690 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | Dead End |  |  |  |  | 6.215e-12 | 713.1375
120243384 | E | LC | ETL.4393.POLE.WDPS | 44172134 | SACTO | SACRAMENTO | 2020-12-31 | 2021-04-01 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
120423250 | E | LC | ETL.3742.POLE.NWOD | 40575709 | CONCORD | DIABLO | 2021-01-12 |  | ETL.3742 | SOBRANTE-MORAGA | Guy Wire-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40575709 | 1947-01-01 | Lattice Steel Pole | DDE-A - Double Dead End Angle | 1947-01-01 | Ceramic | Other |  |  |  |  | 3.9776e-08 | 98.1414 | 3.9037e-06
120471263 | A | LC | ETL.8360.POLE.WOOD | 40656782 | LAKEVLLE | SONOMA | 2021-01-27 | 2021-02-08 | ETL.8360 | LAYTONVILLE-WILLITS | Emergency | Storm Related | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656782 |  | Single Wood Pole | TP - Tri Pin | 2017-03-14 | Ceramic | Dead End |  |  |  |  | 0.010521 | 237.3428
120475984 | A | LC | ETL.1110.POLE.WDPS | 44423250 | EUREKA | HUMBOLDT | 2021-01-28 | 2021-02-01 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Emergency | Storm Related | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423250 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.00117
120475984 | A | LC | ETL.1110.POLE.WDPS | 44423250 | EUREKA | HUMBOLDT | 2021-01-28 | 2021-02-01 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Emergency | Storm Related | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423250 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.00117
120487241 | B | LC | ETL.3500.POLE.NWOD | 44400221 | VICTOR | STOCKTON | 2021-02-01 | 2021-02-02 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44400221 |  | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 0.0016702 | 5982.1558
120499405 | A | LC | ETL.8405.POLE.WOOD | 40826832 | SACTO | SACRAMENTO | 2021-02-04 | 2021-02-09 | ETL.8405 | MIDDLE FORK #1 | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40826832 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.13896 | 205.7471
120697003 | F | LC | ETL.3820.TOWR | 40687280 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40687280 | 1910-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1989-01-01 | Porcelain | Suspension |  |  |  |  | 2.6192e-08 | 3247.5388
120697003 | F | LC | ETL.3820.TOWR | 40687280 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40687280 | 1910-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-10-16 | Polymer | Post |  |  |  |  | 2.6192e-08 | 3247.5388
120700391 | E | LC | ETL.6720.POLE.STPS | 44984423 | TABLEMTN | NORTH VALLEY | 2021-03-27 | 2021-06-24 | ETL.6720 | DESABLA-CENTERVILLE | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL | [12 empty] | 47.5251
120706874 | E | LC | ETL.1810.POLE.WDPS | 44322686 | EUREKA | HUMBOLDT | 2021-03-29 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44322684 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0035136 | 79.143 | 0.27808
120712740 | F | LC | ETL.1890.TOWR | 40748480 | FRESNO | FRESNO | 2021-03-29 | 2021-07-19 | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40748480 | 1986-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 2.4819e-07 | 5240.2971
120745223 | F | LC | ETL.5790.TOWR | 40651658 | VICTOR | STOCKTON | 2021-03-24 |  | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40651658 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 5.1261e-05 | 1202.2845 | 0.061631
120745724 | F | LC | ETL.1720.POLE.WDPS | 44845112 | MOSSLNDG | CENTRAL COAST | 2021-04-05 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Road | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44825343 | 2019-06-24 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00070711 | 1218.3296
120757415 | F | LC | ETL.1730.POLE.WOOD | 40702144 | MOSSLNDG | CENTRAL COAST | 2021-03-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40702144 | 1972-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1972-01-01 | Ceramic | Post |  |  |  |  | 0.00015671 | 0.065147
120762990 | F | LC | ETL.6760.POLE.WOOD | 40693365 | SACTO | SACRAMENTO | 2021-04-08 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Road | Brush Fuel | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40693365 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.016463 | 221.5243
120764439 | E | LC | ETL.5300.INSL | 40631432 | PISMOBCH | LOS PADRES | 2021-04-08 | 2021-11-15 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | DLFL | 40592072 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 3.4273e-07 | 4987.3418
120765947 | F | LC | ETL.4750.TOWR | 40866255 | LAKEVLLE | SONOMA | 2021-04-08 |  | ETL.4750 | GEYSERS #12-FULTON | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40866255 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Porcelain | Suspension |  |  |  |  | 2.5512e-08 | 1252.5039 | 3.1954e-05
120766379 | E | LC | ETL.7590.POLE.STPS | 44985776 | MOSSLNDG | CENTRAL COAST | 2021-04-08 |  | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44985747 | 2020-09-18 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.066121 | 15.8866 | 1.0504
120770373 | E | LC | ETL.2540.POLE.WDPS | 44401580 | MOSSLNDG | CENTRAL COAST | 2021-04-08 | 2021-08-17 | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [12 empty] | 2455.0217
120792903 | E | LC | ETL.3820.INSL.NCER | 40878868 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40856494 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 4.6724e-05 | 95.2198 | 0.004449
120794508 | B | LC | ETL.3830.INSL | 40885153 | VICTOR | STOCKTON | 2021-04-09 | 2021-06-01 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861800 | 1989-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 3.7342e-05 | 5823.2505
120805205 | F | LC | ETL.1710.POLE.NWOD | 40591170 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40591170 | 1971-01-01 | Lattice Steel Pole | DDE - Double Dead End | 1971-01-01 | Ceramic | Dead End |  |  |  |  | 3.1955e-07 | 0.066431
120805205 | F | LC | ETL.1710.POLE.NWOD | 40591170 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40591170 | 1971-01-01 | Lattice Steel Pole | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.1955e-07 | 0.066431
120814774 | E | LC | ETL.8480.POLE.WOOD | 40817235 | VICTOR | LOS PADRES | 2021-04-07 |  | ETL.8480 | ATASCADERO-CAYUCOS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40817235 | 1954-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1954-01-01 | Polymer | Suspension |  |  |  |  | 0.00028795 | 5488.6089 | 1.5805
120819436 | B | LC | ETL.4680.TOWR | 40597134 | LAKEVLLE | SONOMA | 2021-04-15 | 2021-05-04 | ETL.4680 | FULTON-IGNACIO #1 | Other | Customer Issue | [Access Issue] | Tier3 | Tier 3 | Within Both | COMP | 40597134 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.3131e-05 | 965.4728
120828369 | E | LC | ETL.1400.POLE.WDPS | 45078145 | VICTOR | YOSEMITE | 2021-04-16 |  | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40579918 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0010964 | 47.5548 | 0.052138
120830869 | E | LC | ETL.3500.INSL | 40603338 | VICTOR | STOCKTON | 2021-04-16 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40579792 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.053654 | 5982.1558 | 320.9636
120839206 | E | LC | ETL.7290.POLE.NWOD | 44175299 | TABLEMTN | NORTH VALLEY | 2021-04-17 | 2021-11-29 | ETL.7290 | KILARC-CEDAR CREEK | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | COMP | 44175299 | 2014-10-15 | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.054811 | 31.7051 | 1.7378
120859882 | F | LC | ETL.1820.POLE.STPS | 44763083 | EUREKA | HUMBOLDT | 2021-04-21 |  | ETL.1820 | HUMBOLDT-TRINITY | Right of Way | Encroachment | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44763053 | 2019-04-28 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0013505 | 63.3274
120863333 | F | LC | ETL.3720.TOWR | 40857820 | CONCORD | DIABLO | 2021-04-21 |  | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40857820 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 6.2927e-06 | 316.3912 | 0.001991
120863333 | F | LC | ETL.3720.TOWR | 40857820 | CONCORD | DIABLO | 2021-04-21 |  | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40857820 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 6.2927e-06 | 316.3912 | 0.001991
120864704 | B | LC | ETL.4590.INSL.CERA | 40782364 | TABLEMTN | NORTH VALLEY | 2021-04-21 | 2021-07-20 | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120864749 | B | LC | ETL.4590.INSL.CERA | 40891686 | TABLEMTN | NORTH VALLEY | 2021-04-21 | 2021-07-27 | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
120873245 | B | LC | ETL.1820.INSL.NCER | 40735657 | EUREKA | HUMBOLDT | 2021-04-23 | 2021-05-26 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
120875693 | F | LC | ETL.1820.POLE.STPS | 44395178 | EUREKA | HUMBOLDT | 2021-04-23 | 2021-08-10 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44395176 | 2017-09-15 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.063019 | 94.9585
120875693 | F | LC | ETL.1820.POLE.STPS | 44395178 | EUREKA | HUMBOLDT | 2021-04-23 | 2021-08-10 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44395176 | 2017-09-15 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.063019 | 94.9585
120880393 | E | LC | ETL.1810.POLE.WDPS | 44322253 | EUREKA | HUMBOLDT | 2021-04-24 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Anchor-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44322252 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0012259
120906887 | F | LC | ETL.3830.TOWR | 40803325 | VICTOR | STOCKTON | 2021-04-30 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40803325 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.8861e-08 | 95.2198 | 5.6047e-06
120912298 | E | LC | ETL.6890.POLE.WOOD | 40877330 | LAKEVLLE | SONOMA | 2021-05-01 | 2021-05-24 | ETL.6890 | FULTON-HOPLAND | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40877330 | 1986-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.00010396 | 3658.7083
120941890 | B | LC | ETL.4550.TOWR | 40678288 | TABLEMTN | NORTH VALLEY | 2021-05-04 | 2021-06-17 | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40678288 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 8.2847e-08 | 4690.1665
120949015 | F | LC | ETL.6621.TOWR | 42580652 | TABLEMTN | NORTH VALLEY | 2021-04-16 |  | ETL.6621 | OROVILLE-THERMALITO-TABLE MTN #1 (CDWR) | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 42580652 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 4.1528e-06 | 7350.3149
121116455 | F | LC | ETL.7590.POLE.WOOD | 40747197 | METCALF | DE ANZA | 2021-04-19 | 2021-09-30 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40747197 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | Double Dead End |  |  |  |  | 0.80116 | 126.6368
121186583 | E | LC | ETL.1820.POLE.WDPS | 44562823 | EUREKA | HUMBOLDT | 2021-05-11 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562420 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.22896 | 789.5898 | 180.7863
121318320 | E | LC | ETL.3700.INSL.NCER | 44946533 | PISMOBCH | LOS PADRES | 2021-04-27 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44946514 | 2020-07-01 | Light Duty Steel Pole | T-1 - Tri Post | 2020-07-01 | Polymer | Post |  |  |  |  | 1.1153e-05 | 3878.2041 | 0.043255
121318437 | F | LC | ETL.1720.TOWR | 40751267 | MOSSLNDG | SAN JOSE | 2021-04-28 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40751267 | 1928-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1986-01-01 | Porcelain | Dead End |  |  |  |  | 7.6356e-05 | 8439.1357 | 0.64438
121331168 | F | LC | ETL.3500.TOWR | 40856704 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40856704 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0021429 | 6665.3057 | 14.283
121336002 | E | LC | ETL.3750.INSL.CERA | 44651149 | CONCORD | EAST BAY | 2021-04-23 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44188774 | 2008-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-01-16 | Ceramic | Dead End |  |  |  |  | 2.1728e-06 | 603.2272 | 0.0013107
121336880 | E | LC | ETL.1820.INSL.CERA | 40884594 | EUREKA | HUMBOLDT | 2021-05-14 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562465 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.10498
121336880 | E | LC | ETL.1820.INSL.CERA | 40884594 | EUREKA | HUMBOLDT | 2021-05-14 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562465 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.10498
121336880 | E | LC | ETL.1820.INSL.CERA | 40884594 | EUREKA | HUMBOLDT | 2021-05-14 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562465 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.10498
121338249 | E | LC | ETL.2770.TOWR | 40870565 | CONCORD | MISSION | 2021-04-23 |  | ETL.2770 | MORAGA-SAN LEANDRO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40870565 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 0.00015247 | 15.8932 | 0.0024233
121338281 | E | LC | ETL.2770.INSL | 40895571 | CONCORD | EAST BAY | 2021-04-23 |  | ETL.2770 | MORAGA-SAN LEANDRO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40870565 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 0.00015247 | 15.8932 | 0.0024233
121340517 | E | LC | ETL.6470.POLE.WOOD | 40767224 | SACTO | SACRAMENTO | 2021-05-15 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40767224 |  | Single Wood Pole | T2N | 2021-07-16 | Polymer | Post |  |  |  |  | 0.087167 | 126.6309 | 11.038
121348627 | E | LC | ETL.6130.TOWR | 40592764 | VICTOR | YOSEMITE | 2021-04-28 |  | ETL.6130 | TRACY-LOS BANOS | Raptor Guard-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40592764 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Glass | Suspension |  |  |  |  | 3.4456e-10 | 1935.4041 | 6.6686e-07
121357635 | E | LC | ETL.8210.POLE.WOOD | 40908234 | VICTOR | STOCKTON | 2021-05-19 |  | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40908234 | 1991-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.015587 | 1854.4864 | 28.9055
121359020 | F | LC | ETL.5630.POLE.NWOD | 40819093 | TABLEMTN | NORTH VALLEY | 2021-04-23 |  | ETL.5630 | ROCK CREEK-POE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40819093 | 2011-01-01 | Tubular Steel Pole | DV-DE - Double Vertical Dead End | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 8.4014e-09 | 1171.7432
121384528 | F | LC | ETL.6760.POLE.WOOD | 40611300 | SACTO | SIERRA | 2021-05-13 | 2021-06-23 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40611300 |  | Single Wood Pole | T-1 - Tri Post | 2019-08-03 | Polymer | Post |  |  |  |  | 0.054482 | 1503.0458
121384528 | F | LC | ETL.6760.POLE.WOOD | 40611300 | SACTO | SIERRA | 2021-05-13 | 2021-06-23 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40611300 |  | Single Wood Pole | T-1 - Tri Post | 2019-08-03 | Polymer | Post |  |  |  |  | 0.054482 | 1503.0458
121395581 | E | LC | ETL.1450.INSL.CERA | 40630552 | SACTO | SACRAMENTO | 2021-05-25 |  | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553957 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064757
121395581 | E | LC | ETL.1450.INSL.CERA | 40630552 | SACTO | SACRAMENTO | 2021-05-25 |  | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553957 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064757
121395581 | E | LC | ETL.1450.INSL.CERA | 40630552 | SACTO | SACRAMENTO | 2021-05-25 |  | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553957 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064757
121399755 | E | LC | ETL.1710.POLE.WDPS | 44513711 | MOSSLNDG | CENTRAL COAST | 2021-05-25 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44512232 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.005666 | 31.6948 | 0.17958
121404971 | E | LC | ETL.2700.INSL.CERA | 42581974 | CONCORD | EAST BAY | 2021-05-19 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44188844 | 2008-01-01 | LATTICE STEEL TOWER | Unknown |  | Ceramic | Unknown |  |  |  |  | 4.3482e-06 | 445.731 | 0.0019381
121407861 | F | LC | ETL.8405.POLE.WOOD | 40861919 | SACTO | SIERRA | 2021-05-20 | 2021-11-02 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40861919 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.023855 | 1075.8865
121418315 | E | LC | ETL.6640.POLE.WOOD | 40650269 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40650269 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Non Ceramic | [5 empty] | 0.015948 | 3249.6929 | 51.8249
121427105 | E | LC | ETL.6220.POLE.WOOD | 40768707 | EUREKA | HUMBOLDT | 2021-05-26 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40768707 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.29975 | 522.446 | 156.6012
121453649 | E | LC | ETL.7030.POLE.WOOD | 40592092 | TABLEMTN | NORTH VALLEY | 2021-06-03 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40592092 |  | Single Wood Pole | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Pin |  |  |  |  | 0.03808 | 1044.1121 | 39.76
121481854 | E | LC | ETL.6770.POLE.WOOD | 40770265 | SACTO | SIERRA | 2021-06-05 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40770265 |  | Single Wood Pole | DDE - Double Dead End |  | Non Ceramic | [5 empty] | 0.067484 | 1329.6379 | 89.7296
121481854 | E | LC | ETL.6770.POLE.WOOD | 40770265 | SACTO | SIERRA | 2021-06-05 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40770265 |  | Single Wood Pole | DDE - Double Dead End | 2017-08-02 | Polymer | Dead End |  |  |  |  | 0.067484 | 1329.6379 | 89.7296
121489916 | F | LC | ETL.7550.POLE.WOOD | 40600367 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40600367 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00018068 | 221.5243 | 0.040024
121494543 | B | LC | ETL.8060.INSL.CERA | 40678214 | SACTO | SACRAMENTO | 2021-06-08 | 2021-08-17 | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650055 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | [5 empty] | 0.023881 | 31.7066
121500457 | E | LC | ETL.4450.TOWR | 40589822 | CONCORD | MISSION | 2021-06-04 | 2021-09-27 | ETL.4450 | CASTRO VALLEY-NEWARK | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40589822 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.794e-05 | 2960.0791
121512539 | E | LC | ETL.6880.POLE.WOOD | 40912470 | LAKEVLLE | NORTH BAY | 2021-06-05 |  | ETL.6880 | FULTON-CALISTOGA | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40912470 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.0035255 | 395.8694 | 1.3956
121514752 | E | LC | ETL.1610.INSL | 40630961 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1610 | SILVERADO-FULTON JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591166 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 0.00024456 | 2438.3081 | 0.5963
121516880 | F | LC | ETL.5390.TOWR | 40608991 | TABLEMTN | NORTH VALLEY | 2021-06-07 | 2021-10-04 | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40608991 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 0.00010341 | 159.5934
121518217 | F | LC | ETL.1440.POLE.STPS | 44338135 | SACTO | SIERRA | 2021-06-04 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44338134 | 2018-09-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.6252e-06 | 47.5526
121524675 | E | LC | ETL.5390.TOWR | 40759682 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40759682 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 3.9691e-06 | 604.3115 | 0.0023986
121536058 | E | LC | ETL.6852.POLE.WOOD | 40699035 | LAKEVLLE | HUMBOLDT | 2021-06-09 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40699035 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.054354 | 5982.4478
121538200 | F | LC | ETL.5390.TOWR | 40867670 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40867670 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 7.8343e-09 | 4626.835
121546416 | F | LC | ETL.1110.POLE.WOOD | 45082071 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45082071 | 2018-02-09 | Single Wood Pole | DE - Dead End | 2018-02-09 | Ceramic | Dead End |  |  |  |  | 0.0018001 | 332.3156
121550488 | F | LC | ETL.4040.POLE.NWOD | 44878708 | TABLEMTN | NORTH VALLEY | 2021-06-12 | 2021-08-11 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44878708 | 2020-01-25 | Light Duty Steel Pole | 3P DV - 3 Pole Double Vertical | 2020-01-25 | Polymer | Dead End |  |  |  |  | 0.00022391 | 2468.2368
121561411 | E | LC | ETL.5390.TOWR | 40600996 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40600996 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.9902e-06 | 4041.2002 | 0.012084
121562457 | F | LC | ETL.6110.TOWR | 40760557 | METCALF | SAN JOSE | 2021-06-16 | 2021-07-02 | ETL.6110 | TESLA-METCALF | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40760557 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.6346e-08 | 4627.0366
121581632 | E | LC | ETL.5980.INSL.NCER | 45089796 | PISMOBCH | LOS PADRES | 2021-06-22 |  | ETL.5980 | DIABLO-MIDWAY #3 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40811437 | 1975-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-05-04 | Glass Silicone Coated | Dead End |  |  |  |  | 2.6871e-07 | 3437.3396 | 0.00092364
121590986 | B | LC | ETL.8170.INSL | 40916103 | EUREKA | HUMBOLDT | 2021-06-22 | 2021-08-30 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906434 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.13534 | 189.9226
121628277 | F | LC | ETL.4316.POLE.NWOD | 42567095 | TABLEMTN | NORTH VALLEY | 2021-06-22 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 42567095 | 2011-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | Unknown |  |  |  |  | 0.012867 | 238.4023
121642284 | F | LC | ETL.4440.POLE.NWOD | 40757705 | TABLEMTN | NORTH VALLEY | 2021-06-27 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40757705 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 4.2889e-07 | 0.065148
121660336 | E | LC | ETL.2540.POLE.WDPS | 44401442 | METCALF | CENTRAL COAST | 2021-06-29 |  | ETL.2540 | METCALF-GREEN VALLEY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44401440 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.015117 | 1565.8347 | 23.6709
121661616 | F | LC | ETL.1450.POLE.WOOD | 44159090 | SACTO | SIERRA | 2021-07-02 |  | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44159090 | 2013-09-30 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2013-09-30 | Ceramic | Suspension |  |  |  |  | 7.8157e-05 | 427.3257
121673313 | E | LC | ETL.7630.POLE.WOOD | 40808640 | LAKEVLLE | SONOMA | 2021-07-05 |  | ETL.7630 | MONTE RIO-FULTON | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40808640 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.66545 | 94.985 | 63.2082
121689015 | F | LC | ETL.5140.POLE.STPS | 44690692 | SACTO | SIERRA | 2021-07-05 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44141443 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.2439e-08 | 6079.75
121705900 | E | LC | ETL.5970.INSL | 40846243 | PISMOBCH | LOS PADRES | 2021-07-09 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40819441 | 1972-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1972-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.2308e-05 | 4512.3296 | 0.10066
121715777 | E | LC | ETL.1820.POLE.NWOD | 45089716 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45089716 |  | Light Duty Steel Pole | TRP DE - Tramp Dead End |  | Ceramic | Dead End |  |  |  |  | 0.038506 | 2753.0989 | 106.0105
121741318 | B | LC | ETL.6020.INSL | 40726259 | TABLEMTN | NORTH VALLEY | 2021-07-14 | 2021-09-01 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40684090 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00042658 | 316.4942
121743659 | E | LC | ETL.1820.POLE.WDPS | 44562638 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562369 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.27229 | 189.9226 | 51.7138
121744369 | E | LC | ETL.2390.INSL.NCER | 40772610 | VICTOR | STOCKTON | 2021-07-13 | 2021-07-28 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44391123 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.00018876
121744369 | E | LC | ETL.2390.INSL.NCER | 40772610 | VICTOR | STOCKTON | 2021-07-13 | 2021-07-28 | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44391123 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 0.00018876
121749331 | F | LC | ETL.2390.POLE.WDPS | 44195282 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44195281 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.1786e-05 | 475.4843
121749331 | F | LC | ETL.2390.POLE.WDPS | 44195282 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44195281 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.1786e-05 | 475.4843
121780850 | F | LC | ETL.1110.POLE.WOOD | 45082072 | TABLEMTN | NORTH VALLEY | 2021-07-21 | 2021-08-05 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 45082072 | 2018-02-09 | Single Wood Pole | DE - Dead End | 2018-02-09 | Ceramic | Dead End |  |  |  |  | 0.0018001 | 332.3156
121780857 | F | LC | ETL.6020.TOWR | 41162683 | TABLEMTN | NORTH VALLEY | 2021-07-21 |  | ETL.6020 | MALIN-ROUND MTN #2 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41162683 | 1965-01-01 | LATTICE STEEL TOWER | Unknown | [7 empty] | 1.9769e-08 | 1202.6853
121781596 | F | LC | ETL.6480.POLE.NWOD | 45099369 | SACTO | SIERRA | 2021-07-19 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Rotten | [Stub] | Tier3 | Tier 3 | Within Both | PEND | 45099369 | 2020-11-14 | Light Duty Steel Pole | T2N | 2020-11-14 | Polymer | Post |  |  |  |  | 0.011705 | 664.4426 | 7.7776
121789409 | E | LC | ETL.4040.POLE.STPS | 45173226 | TABLEMTN | NORTH VALLEY | 2021-07-21 | 2021-12-02 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 45173181 | 2021-09-22 | 2-Pole Non Wood | 2PS - 2 Pole SUSP
121792268 | E | LC | ETL.6230.POLE.WDPS | 44958670 | MOSSLNDG | CENTRAL COAST | 2021-07-24 |  | ETL.6230 | BURNS-LONE STAR #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40602886 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.21807 | 284.8766 | 62.1237
121800821 | B | LC | ETL.6280.POLE.WOOD | 44259133 | TABLEMTN | NORTH VALLEY | 2021-07-26 | 2021-09-21 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 3.2961e-05 | 1292.2571
121806511 | E | LC | ETL.7490.POLE.WOOD | 40602127 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40602127 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.71316 | 20.6453 | 14.7234
121810030 | F | LC | ETL.4870.TOWR | 40576886 | FRESNO | FRESNO | 2021-07-27 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] |  | Zone 1 | HFRA Removal | PEND | 40576886 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.0001152 | 15.8815 | 0.0018295
121814540 | E | LC | ETL.6230.POLE.WDPS | 45099493 | MOSSLNDG | CENTRAL COAST | 2021-07-26 |  | ETL.6230 | BURNS-LONE STAR #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42565850 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.52877 | 284.8766 | 150.6345
121816465 | B | LC | ETL.8365.INSL.CERA | 40922517 | EUREKA | HUMBOLDT | 2021-07-27 | 2021-08-23 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40912708 |  | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.016678 | 2151.1467
121838465 | E | LC | ETL.7800.POLE.WOOD | 40820912 | SACTO | SACRAMENTO | 2021-08-03 |  | ETL.7800 | PLACER-DEL MAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | PEND | [11 empty] | 1.3176e-05 | 2677.1912 | 0.035274
121882474 | B | LC | ETL.1820.POLE.WDPS | 44560561 | EUREKA | HUMBOLDT | 2021-08-10 | 2021-09-02 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 3943.1492
121897317 | B | LC | ETL.8170.POLE.WOOD | 40809961 | EUREKA | HUMBOLDT | 2021-08-11 | 2021-09-13 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.004435
122019101 | E | LC | ETL.6980.POLE.WOOD | 40825488 | LAKEVLLE | SONOMA | 2021-09-09 |  | ETL.6980 | FORT ROSS-GUALALA | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40825488 | 1968-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.47074 | 0.065147 | 0.030667
122053482 | E | LC | ETL.4780.INSL.NCER | 45128997 | LAKEVLLE | SONOMA | 2021-09-15 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40750668 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.0031234 | 4562.5039 | 14.2503
122053482 | E | LC | ETL.4780.INSL.NCER | 45128997 | LAKEVLLE | SONOMA | 2021-09-15 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40750668 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.0031234 | 4562.5039 | 14.2503
122058123 | E | LC | ETL.4780.INSL.NCER | 45129011 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129355 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 2.8718e-05 | 3628.7817 | 0.10421
122058123 | E | LC | ETL.4780.INSL.NCER | 45129011 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129355 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 2.8718e-05 | 3628.7817 | 0.10421
122161949 | E | LC | ETL.4392.INSL.NCER | 40623803 | LAKEVLLE | SONOMA | 2021-10-07 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Emergency | Storm Related | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40582777 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 1.6844e-06 | 190.6293 | 0.00032109
118528001 | E | LC | ETL.6390.POLE.WOOD | 40648304 | LAKEVLLE | HUMBOLDT | 2020-02-12 | 2020-11-20 | ETL.6390 | CLEAR LAKE-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118937892 | E | LC | ETL.6220.POLE.WOOD | 40810335 | EUREKA | HUMBOLDT | 2020-04-21 | 2021-03-22 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Idle | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40810335 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.21462 | 1028.302
118946455 | E | LC | ETL.8220.POLE.WOOD | 40613666 | VICTOR | STOCKTON | 2020-04-23 | 2020-07-15 | ETL.8220 | VALLEY SPRINGS-CALAVERAS CEMENT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40613666 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Other |  |  |  |  | 0.001179 | 810.9612
118951226 | E | LC | ETL.7520.POLE.NWOD | 40595526 | LAKEVLLE | HUMBOLDT | 2020-04-23 |  | ETL.7520 | MENDOCINO-PHILO JCT-HOPLAND | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40595526 |  | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 5.2691e-06 | 3642.5862 | 0.019193
118951226 | E | LC | ETL.7520.POLE.NWOD | 40595526 | LAKEVLLE | HUMBOLDT | 2020-04-23 |  | ETL.7520 | MENDOCINO-PHILO JCT-HOPLAND | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40595526 |  | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 2020-06-08 | Glass | Suspension |  |  |  |  | 5.2691e-06 | 3642.5862 | 0.019193
118971998 | F | LC | ETL.2060.POLE.NWOD | 44141377 | LAKEVLLE | HUMBOLDT | 2020-04-30 |  | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | PEND
118975868 | E | LC | ETL.2060.POLE.WOOD | 40750131 | LAKEVLLE | HUMBOLDT | 2020-04-29 | 2021-11-15 | ETL.2060 | FORT BRAGG-ELK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.34198 | 0.065148
119016608 | B | LC | ETL.8560.POLE.WOOD | 40652919 | PISMOBCH | LOS PADRES | 2020-05-06 | 2020-07-08 | ETL.8560 | CAYUCOS-CAMBRIA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40652919 |  | Single Wood Pole | FIG4W - Wood X Arm | 2019-09-12 | Glass | Suspension |  |  |  |  | 0.0070202 | 382.8347
119044086 | E | LC | ETL.7590.POLE.WOOD | 40694938 | MOSSLNDG | DE ANZA | 2020-05-11 | 2020-08-06 | ETL.7590 | MONTA VISTA-BURNS | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119070713 | F | LC | ETL.8490.TOWR | 40754931 | PISMOBCH | LOS PADRES | 2020-05-21 | 2020-11-10 | ETL.8490 | ATASCADERO-SAN LUIS OBISPO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40754931 | 1932-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1932-01-01 | Ceramic | Suspension |  |  |  |  | 0.0021331 | 1851.2734
119080706 | B | LC | ETL.4392.INSL.CERA | 40620214 | LAKEVLLE |  | 2020-05-26 | 2020-07-15 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40594199 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | [5 empty] | 5.6725e-07 | 2114.9343
119085321 | E | LC | ETL.5290.INSL | 40792005 | PISMOBCH | LOS PADRES | 2020-05-15 | 2021-02-04 | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119088957 | E | LC | ETL.7140.POLE.WOOD | 40762994 | LAKEVLLE | NORTH BAY | 2020-05-18 | 2021-04-28 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762994 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.11267 | 348.1174
119095867 | E | LC | ETL.1420.TOWR | 40765091 | SACTO | SIERRA | 2020-05-19 | 2021-03-23 | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40765091 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 7.2581e-05 | 2753.5613
119095867 | E | LC | ETL.1420.TOWR | 40765091 | SACTO | SIERRA | 2020-05-19 | 2021-03-23 | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40765091 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-05-11 | Glass | Suspension |  |  |  |  | 7.2581e-05 | 2753.5613
119107908 | E | LC | ETL.7130.POLE.WOOD | 40700544 | EUREKA | HUMBOLDT | 2020-06-04 |  | ETL.7130 | HUMBOLDT-MAPLE CREEK | Damper-Steel | Missing | [Install] | Tier2 |  |  | PEND
119116353 | E | LC | ETL.1050.TOWR | 40583099 | FRESNO | FRESNO | 2020-05-26 | 2021-06-29 | ETL.1050 | BALCH-SANGER | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40583099 | 1923-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1923-01-01 | Porcelain | Dead End |  |  |  |  | 0.0051859 | 6585.0371
119116937 | F | LC | ETL.8405.POLE.WOOD | 40874900 | SACTO | SIERRA | 2020-05-28 | 2021-04-20 | ETL.8405 | MIDDLE FORK #1 | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40874900 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0031317 | 2610.7236
119118608 | E | LC | ETL.6520.POLE.WOOD | 40602839 | SACTO | SIERRA | 2020-06-03 | 2021-06-08 | ETL.6520 | COLGATE-SMARTVILLE #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602839 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.0067445 | 1887.8925
119119239 | E | LC | ETL.1430.TOWR | 40672175 | SACTO | SIERRA | 2020-05-22 | 2021-03-22 | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40672175 | 1913-01-01 | LATTICE STEEL TOWER | Unknown | 2016-11-14 | Non Ceramic | Post |  |  |  |  | 0.0024225 | 94.9894
119125656 | F | LC | ETL.7930.POLE.WOOD | 42564781 | MOSSLNDG | CENTRAL COAST | 2020-06-03 | 2020-11-12 | ETL.7930 | SALINAS-LAURELES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42564781 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 0.0031014 | 237.3476
119125725 | F | LC | ETL.3190.POLE.NWOD | 44374356 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.3190 | CARIBOU-PALERMO | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44374356 | 2013-10-22 | Light Duty Steel Pole | DDE - Double Dead End | 2013-10-22 | Polymer | Dead End |  |  |  |  | 0.0026602 | 537.9698
119125965 | E | LC | ETL.8405.POLE.WOOD | 40824479 | SACTO | SIERRA | 2020-05-28 | 2021-09-27 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40824479 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.19574 | 537.9821
119144779 | E | LC | ETL.7260.POLE.NWOD | 44960381 | TABLEMTN | NORTH VALLEY | 2020-06-09 |  | ETL.7260 | KESWICK-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44960381 | 2020-08-03 | Light Duty Steel Pole | T2N | 2020-08-03 | Polymer | Post |  |  |  |  | 2.0016e-05 | 411.5568 | 0.0082376
119159483 | E | LC | ETL.1050.TOWR | 40646822 | FRESNO | FRESNO | 2020-06-12 | 2021-08-04 | ETL.1050 | BALCH-SANGER | Connector | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40646822 | 1923-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1923-01-01 | Porcelain | Dead End |  |  |  |  | 0.0031925 | 5354.4616
119162324 | F | LC | ETL.6220.POLE.WDPS | 44402633 | EUREKA | HUMBOLDT | 2020-06-11 | 2021-08-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | DLFL | 44402632 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0076991
119163162 | F | LC | ETL.7380.POLE.WDPS | 44562882 | MOSSLNDG | CENTRAL COAST | 2020-06-12 | 2020-11-12 | ETL.7380 | LAURELES-OTTER | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 3 | Within Both | DLFL | 44562374 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.12694 | 47.5141
119172701 | E | LC | ETL.8170.POLE.WDPS | 44565596 | EUREKA | HUMBOLDT | 2020-06-12 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564266 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.079393 | 1174.8506 | 93.275
119179189 | F | LC | ETL.7300.POLE.WOOD | 40759317 | TABLEMTN |  | 2020-06-16 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40759317 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0017394 | 3991.2373
119181035 | F | LC | ETL.6280.POLE.NWOD | 40698726 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40698726 |  | Light Duty Steel Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 5.5324e-06 | 5270.2847
119194238 | F | LC | ETL.6470.POLE.WOOD | 40658299 | SACTO | SIERRA | 2020-06-19 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40658299 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.048338 | 474.9903
119197969 | E | LC | ETL.6470.POLE.WOOD | 40590447 | SACTO | SIERRA | 2020-06-22 | 2021-07-14 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.060001 | 110.8355
119232420 | F | LC | ETL.8170.POLE.WOOD | 40826067 | EUREKA | HUMBOLDT | 2020-06-29 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40826067 |  | Single Wood Pole | TPAT - Tri Pin Arm Tramp |  | Ceramic | [5 empty] | 0.018393 | 95.0389
119291715 | F | LC | ETL.7270.POLE.NWOD | 44649314 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44649314 | 2018-08-17 | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2018-08-17 | Polymer | Dead End |  |  |  |  | 2.0401e-07 | 0.065152
119294066 | F | LC | ETL.1110.POLE.WDPS | 44423290 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-01-29 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 2 | Within Both | DLFL | 44423289 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0020869 | 5132.3877
119300305 | F | LC | ETL.8060.POLE.WOOD | 40593596 | SACTO | SIERRA | 2020-06-29 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40593596 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.059897 | 31.7066
119300976 | E | LC | ETL.4393.POLE.WDPS | 44172273 | SACTO | SACRAMENTO | 2020-07-01 | 2020-07-28 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119308049 | B | LC | ETL.7140.POLE.WOOD | 41111775 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-26 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111775 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.55042
119308049 | B | LC | ETL.7140.POLE.WOOD | 41111775 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-26 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111775 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.55042
119308049 | B | LC | ETL.7140.POLE.WOOD | 41111775 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-10-26 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111775 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 0.55042
119309822 | E | LC | ETL.7180.POLE.WOOD | 44376899 | LAKEVLLE | SONOMA | 2020-07-03 | 2021-05-19 | ETL.7180 | IGNACIO-BOLINAS #2 | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44376899 | 2013-04-02 | Single Wood Pole | T-1 - Tri Post | 2013-04-02 | Polymer | Post |  |  |  |  | 1.3412e-05 | 285.4144
119323344 | E | LC | ETL.5970.INSL | 40897218 | PISMOBCH | LOS PADRES | 2020-07-07 | 2021-07-22 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119325563 | E | LC | ETL.1110.TOWR | 40761532 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-09-03 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Vegetation-Tower | Overgrown | [Cage Clearing, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40761532 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 0.00016185 | 379.78
119333564 | E | LC | ETL.6280.POLE.WOOD | 40675402 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-08-02 | ETL.6280 | CARIBOU #2 | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40675402 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00030069 | 490.3705
119334384 | E | LC | ETL.7030.POLE.WOOD | 40667963 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-06-07 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119334444 | E | LC | ETL.7030.POLE.WOOD | 40816890 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-06-30 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40816890 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.01638 | 0.066432
119341812 | E | LC | ETL.3190.TOWR | 40863363 | TABLEMTN | NORTH VALLEY | 2020-07-08 |  | ETL.3190 | CARIBOU-PALERMO | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40863363 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.0086864 | 857.7261 | 7.4505
119359419 | E | LC | ETL.7030.POLE.WOOD | 40770835 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40770835 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.015633 | 5604.2109 | 87.6113
119359575 | F | LC | ETL.7030.POLE.WOOD | 40770743 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40770743 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0039891 | 5445.9722
119365541 | F | LC | ETL.7030.POLE.WOOD | 40671157 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-06-30 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40671157 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0092938 | 572.0204
119374065 | F | LC | ETL.7930.POLE.WOOD | 40768997 | MOSSLNDG | CENTRAL COAST | 2020-07-15 | 2021-02-04 | ETL.7930 | SALINAS-LAURELES | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40768997 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Other |  |  |  |  | 0.020123 | 48.2352
119378134 | E | LC | ETL.6290.POLE.WOOD | 40585991 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-08-15 | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40585991 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.068351 | 4811.106
119378449 | F | LC | ETL.6290.POLE.WOOD | 40675216 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40675216 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.092559 | 1376.0835
119378807 | F | LC | ETL.8170.POLE.WDPS | 44420649 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44420646 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0097533 | 189.9226
119379483 | F | LC | ETL.7030.POLE.WOOD | 40868474 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40868474 |  | Single Wood Pole | TPAT - Tri Pin Arm Tramp | 2013-06-15 | Ceramic | Pin |  |  |  |  | 0.0089806 | 5620.1401
119482445 | E | LC | ETL.1110.TOWR | 40608462 | TABLEMTN | HUMBOLDT | 2020-07-21 | 2021-07-30 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | Earth Covered Tower | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40608462 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-10-10 | Ceramic | Suspension |  |  |  |  | 1.4168e-06 | 63.351
119484121 | F | LC | ETL.4393.POLE.WDPS | 44172256 | SACTO | SACRAMENTO | 2020-07-21 | 2021-02-11 | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44172255 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.7183e-06 | 775.2101
119485672 | F | LC | ETL.8960.POLE.WOOD | 40652906 | FRESNO | FRESNO | 2020-07-22 | 2020-12-09 | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40652906 |  | Single Wood Pole | DDE - Double Dead End | 1974-01-01 | Porcelain | Dead End |  |  |  |  | 0.00067847
119486792 | E | LC | ETL.1820.POLE.WDPS | 44557580 | EUREKA | HUMBOLDT | 2020-07-01 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44553937 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.48797 | 71.3456 | 34.8141
119488816 | E | LC | ETL.7780.POLE.WOOD | 40763016 | LAKEVLLE | SONOMA | 2020-07-22 | 2021-04-12 | ETL.7780 | PHILO JCT-ELK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40763016 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 8.931e-05 | 5414.5503
119496383 | E | LC | ETL.7680.TOWR | 40911073 | SACTO | SIERRA | 2020-07-22 |  | ETL.7680 | NICOLAUS-CATLETT JCT | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Non-HFTD | Non-HFRA | PEND | 40911073 | 1909-01-01 | LATTICE STEEL TOWER | Unknown | 1909-01-01 | Ceramic | Suspension |  |  |  |  | 1.1674e-05
119511791 | F | LC | ETL.6880.POLE.WOOD | 40588911 | LAKEVLLE | SONOMA | 2020-07-27 | 2021-07-21 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119518599 | E | LC | ETL.6330.INSL | 40730919 | TABLEMTN | NORTH VALLEY | 2020-07-28 | 2021-09-14 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40692868 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0080885 | 2534.72
119578432 | E | LC | ETL.6490.INSL | 40636160 | SACTO | SACRAMENTO | 2020-08-07 | 2021-09-16 | ETL.6490 | COLGATE-GRASS VALLEY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119591422 | E | LC | ETL.7340.INSL.NCER | 43603674 | LAKEVLLE |  | 2020-08-07 | 2021-05-26 | ETL.7340 | LAKEVILLE #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 43219795 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Other |  |  |  |  | 0.0075293 | 4181.1831
119594284 | E | LC | ETL.6240.POLE.WOOD | 40754020 | MOSSLNDG | CENTRAL COAST | 2020-08-10 | 2020-09-23 | ETL.6240 | BURNS-LONE STAR #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40754020 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.3587 | 15.8866
119596497 | F | LC | ETL.8365.POLE.NWOD | 40861089 | EUREKA | HUMBOLDT | 2020-08-10 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40861089 | 2010-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 2.9192e-05
119598009 | F | LC | ETL.4309.POLE.WOOD | 41104276 | LAKEVLLE | SONOMA | 2020-08-10 |  | ETL.4309 | SANTA ROSA-CORONA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41104276 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Non Ceramic | Post |  |  |  |  | 0.0061911 | 142.7329
119613918 | E | LC | ETL.8365.POLE.WOOD | 40912593 | EUREKA | HUMBOLDT | 2020-08-13 | 2021-01-20 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Vegetation | Overgrown | [Trim, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912593 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Pin |  |  |  |  | 0.089183
119619508 | E | LC | ETL.6480.POLE.WOOD | 40693469 | SACTO | SACRAMENTO | 2020-08-14 | 2021-06-29 | ETL.6480 | COLGATE-CHALLENGE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119624163 | E | LC | ETL.6220.POLE.NWOD | 44414891 | EUREKA | HUMBOLDT | 2020-07-30 | 2021-08-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44414891 | 2018-07-22 | Light Duty Steel Pole | T-1 - Tri Post | 2018-07-22 | Polymer | Post |  |  |  |  | 0.020794 | 1737.1102
119626710 | E | LC | ETL.6870.POLE.WOOD | 40593745 | SACTO | SIERRA | 2020-08-17 | 2021-06-02 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119628656 | E | LC | ETL.6870.POLE.WOOD | 40603359 | SACTO | SIERRA | 2020-08-17 | 2021-06-07 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40603359 | 1966-01-01 | Single Wood Pole | T2N | 2021-05-20 | Polymer | Post |  |  |  |  | 0.052124 | 63.3733
119637867 | E | LC | ETL.1450.POLE.WDPS | 44557655 | SACTO | SACRAMENTO | 2020-08-18 | 2021-08-17 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44554012 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.246e-05 | 31.7066
119638568 | A | LC | ETL.7590.POLE.WOOD | 40824967 | MOSSLNDG | CENTRAL COAST | 2020-08-19 | 2020-09-24 | ETL.7590 | MONTA VISTA-BURNS | Emergency-Wood | Other | [Replace, Completed] | Tier3 |  |  | COMP
119639940 | B | LC | ETL.8650.TOWR | 40584433 | FRESNO | FRESNO | 2020-08-19 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40584433 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.016128 | 6283.7788
119660866 | E | LC | ETL.8365.POLE.NWOD | 40906626 | EUREKA | HUMBOLDT | 2020-08-22 | 2021-04-26 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906626 | 2010-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0032076
119667240 | B | LC | ETL.7180.POLE.WOOD | 40808629 | LAKEVLLE | NORTH BAY | 2020-08-24 | 2020-11-10 | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119685466 | B | LC | ETL.6870.POLE.WOOD | 40826821 | SACTO | SIERRA | 2020-07-16 | 2021-05-19 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Rotten | [Replace, Completed] | Tier3 |  |  | COMP
119687171 | E | LC | ETL.1110.POLE.WDPS | 44515790 | TABLEMTN | HUMBOLDT | 2020-08-25 | 2021-04-09 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44515191 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00081832 | 4828.9785
119693005 | E | LC | ETL.1440.INSL | 40845924 | SACTO | SIERRA | 2020-08-25 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40819191 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | 1956-01-01 | Ceramic | Dead End |  |  |  |  | 0.011379
119693005 | E | LC | ETL.1440.INSL | 40845924 | SACTO | SIERRA | 2020-08-25 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40819191 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | 1956-01-01 | Ceramic | Dead End |  |  |  |  | 0.011379
119693005 | E | LC | ETL.1440.INSL | 40845924 | SACTO | SIERRA | 2020-08-25 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40819191 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | 1956-01-01 | Ceramic | Dead End |  |  |  |  | 0.011379
119710411 | F | LC | ETL.6621.TOWR | 44812743 | TABLEMTN | NORTH VALLEY | 2020-09-03 |  | ETL.6621 | OROVILLE-THERMALITO-TABLE MTN #1 (CDWR) | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44812743 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | Suspension |  |  |  |  | 8.8192e-07 | 1849.6195
119719146 | B | LC | ETL.1110.POLE.WDPS | 44424397 | TABLEMTN | HUMBOLDT | 2020-09-04 | 2020-11-04 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424396 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012557 | 5069.9922
119720393 | A | LC | ETL.6240.POLE.WOOD | 40652077 | MOSSLNDG | CENTRAL COAST | 2020-09-05 | 2020-10-07 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119722806 | E | LC | ETL.1730.INSL.CERA | 40672602 | MOSSLNDG | CENTRAL COAST | 2020-08-06 | 2020-11-21 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119729450 | A | LC | ETL.4393.TOWR | 40822536 | SACTO | SACRAMENTO | 2020-09-09 | 2020-09-25 | ETL.4393 | DRUM-HIGGINS | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822536 |  | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Ceramic | [5 empty] | 9.652e-05 | 205.7977
119753205 | E | LC | ETL.2060.POLE.WOOD | 40614180 | LAKEVLLE | HUMBOLDT | 2020-08-18 | 2021-08-23 | ETL.2060 | FORT BRAGG-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40614180 | 1961-01-01 | Single Wood Pole | TPSR - Tri Post & Susp Light | 1961-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.18809 | 0.066432
119754036 | E | LC | ETL.1220.INSL | 40844054 | MOSSLNDG | CENTRAL COAST | 2020-09-03 |  | ETL.1220 | CAMP EVERS-PAUL SWEET | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40816123 |  | Lattice Steel Pole | DDE - Double Dead End | 2021-06-05 | Glass | Double Dead End |  |  |  |  | 0.0048917 | 0.065147 | 0.00031868
119754036 | E | LC | ETL.1220.INSL | 40844054 | MOSSLNDG | CENTRAL COAST | 2020-09-03 |  | ETL.1220 | CAMP EVERS-PAUL SWEET | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40816123 |  | Lattice Steel Pole | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.0048917 | 0.065147 | 0.00031868
119762155 | F | LC | ETL.1120.TOWR | 40857563 | CONCORD | DIABLO | 2020-09-04 | 2021-01-26 | ETL.1120 | BRIGHTON-CLAYTON #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40857563 | 1909-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-05-19 | Glass | Suspension |  |  |  |  | 3.2931e-05 | 7869.8662
119772232 | F | LC | ETL.7540.POLE.WOOD | 40826184 | LAKEVLLE | HUMBOLDT | 2020-08-20 |  | ETL.7540 | MENDOCINO-WILLITS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40826184 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.00019853 | 1063.8021
119775157 | B | LC | ETL.6760.INSL.CERA | 40787071 | SACTO | SACRAMENTO | 2020-09-08 | 2020-09-28 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Damper-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40757035 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Unknown |  |  |  |  | 0.2259 | 632.8055
119783930 | E | LC | ETL.7630.POLE.WOOD | 40750312 | LAKEVLLE | SONOMA | 2020-09-14 | 2021-08-24 | ETL.7630 | MONTE RIO-FULTON | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750312 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.012696 | 47.5251
119786458 | E | LC | ETL.3500.INSL | 40771860 | VICTOR | STOCKTON | 2020-09-15 | 2021-09-16 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40744665 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Non Ceramic | Suspension |  |  |  |  | 3.2507e-06 | 110.8102
119787457 | E | LC | ETL.1420.INSL.CERA | 40786130 | SACTO | SACRAMENTO | 2020-09-15 | 2021-03-11 | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119805067 | F | LC | ETL.4220.POLE.STPS | 44860164 | TABLEMTN | NORTH VALLEY | 2020-08-11 |  | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | PEND | 44860087 | 2019-11-13 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00079693 | 537.9951
119834959 | E | LC | ETL.1073.INSL.CERA | 40829526 | VICTOR | YOSEMITE | 2020-09-29 | 2021-11-15 | ETL.1073 | MI-WUK-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40803725 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00070015
119834959 | E | LC | ETL.1073.INSL.CERA | 40829526 | VICTOR | YOSEMITE | 2020-09-29 | 2021-11-15 | ETL.1073 | MI-WUK-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40803725 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 1956-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00070015
119836219 | F | LC | ETL.6870.POLE.NWOD | 40862117 | SACTO | SIERRA | 2020-09-15 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40862117 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 0.013661 | 0.065152
119844671 | A | LC | ETL.1110.INSL.CERA | 40721759 | TABLEMTN | HUMBOLDT | 2020-10-02 | 2020-12-02 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119927776 | E | LC | ETL.6290.POLE.WOOD | 40698784 | TABLEMTN | NORTH VALLEY | 2020-10-20 | 2021-11-29 | ETL.6290 | CARIBOU-PLUMAS JCT | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40698784 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.53381 | 15.8941
119930759 | E | LC | ETL.8560.POLE.WOOD | 42573746 | PISMOBCH | LOS PADRES | 2020-10-20 |  | ETL.8560 | CAYUCOS-CAMBRIA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 42573746 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | Suspension |  |  |  |  | 0.035935 | 382.8347 | 13.7572
119936035 | E | LC | ETL.8170.POLE.NWOD | 44988828 | EUREKA | HUMBOLDT | 2020-10-22 | 2021-10-14 | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44988828 | 2020-10-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-10-17 | Glass | Dead End |  |  |  |  | 0.012669 | 6475.8594
119954028 | E | LC | ETL.2911.POLE.WOOD | 40810982 | MOSSLNDG | CENTRAL COAST | 2020-10-28 |  | ETL.2911 | LLAGAS-HOLLISTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40810982 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 3.1506e-05
119978804 | F | LC | ETL.8960.POLE.WOOD | 40667142 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40667142 |  | Single Wood Pole | DDE - Double Dead End | 1974-01-01 | Porcelain | Dead End |  |  |  |  | 0.00014005
119993414 | F | LC | ETL.8960.POLE.WOOD | 40662884 | FRESNO | YOSEMITE | 2020-11-03 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40662884 | 1979-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1979-01-01 | Polymer | Post |  |  |  |  | 0.0020082
120044681 | E | LC | ETL.1710.POLE.WDPS | 44957513 | MOSSLNDG | CENTRAL COAST | 2020-11-16 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42567483 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.00177 | 15.88 | 0.028108
120083998 | E | LC | ETL.6060.TOWR | 40595126 | TABLEMTN | NORTH VALLEY | 2020-11-21 |  | ETL.6060 | ROUND MTN-TABLE MTN #1 | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier3 | Tier 3 | Within Both | PEND | 40595126 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00061293 | 142.5209 | 0.087356
120120787 | F | LC | ETL.1440.POLE.WOOD | 42572626 | SACTO | SIERRA | 2020-11-30 | 2021-06-14 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 7.1092e-05 | 237.4101
120124633 | F | LC | ETL.6720.POLE.WDPS | 44950334 | TABLEMTN | NORTH VALLEY | 2020-12-03 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | PEND | 42578837 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0025222 | 2104.1226
120210243 | F | LC | ETL.4040.POLE.NWOD | 44874426 | TABLEMTN | NORTH VALLEY | 2020-11-06 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44874426 | 2020-01-18 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2020-01-18 | Polymer | Dead End |  |  |  |  | 6.4224e-05 | 253.2084
120586055 | F | LC | ETL.8410.POLE.NWOD | 44946529 | LAKEVLLE | SONOMA | 2021-03-01 | 2021-08-19 | ETL.8410 | ELK-GUALALA | Road | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44946529 | 2020-07-07 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2020-07-07 | Glass | Suspension |  |  |  |  | 0.054812 | 219.9952
120633401 | E | LC | ETL.4316.INSL.NCER | 41118694 | TABLEMTN | NORTH VALLEY | 2021-03-10 | 2021-08-16 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120661885 | B | LC | ETL.4392.POLE.NWOD | 44191335 | LAKEVLLE | SONOMA | 2021-03-17 | 2021-04-06 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44191335 |  | Tubular Steel Pole | SV-DE-90 - Single Vertical Dead End 90 |  | Polymer | Suspension |  |  |  |  | 0.0013354 | 886.3674
120669649 | E | LC | ETL.6520.INSL.NCER | 44964350 | SACTO | SIERRA | 2021-03-19 | 2021-06-07 | ETL.6520 | COLGATE-SMARTVILLE #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120673277 | F | LC | ETL.4920.TOWR | 40817211 | LAKEVLLE | SONOMA | 2021-03-22 |  | ETL.4920 | IGNACIO-SOBRANTE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40817211 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 7.5919e-05 | 1427.1888 | 0.10835
120695953 | E | LC | ETL.4040.POLE.WOOD | 40592786 | TABLEMTN | NORTH VALLEY | 2021-03-26 | 2021-09-23 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0013474 | 2010.385
120695986 | E | LC | ETL.6720.INSL.CERA | 44647554 | TABLEMTN | NORTH VALLEY | 2021-03-26 |  | ETL.6720 | DESABLA-CENTERVILLE | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42578810 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-08-30 | Ceramic | Dead End |  |  |  |  | 0.0015781
120695986 | E | LC | ETL.6720.INSL.CERA | 44647554 | TABLEMTN | NORTH VALLEY | 2021-03-26 |  | ETL.6720 | DESABLA-CENTERVILLE | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42578810 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-08-30 | Ceramic | Dead End |  |  |  |  | 0.0015781
120695986 | E | LC | ETL.6720.INSL.CERA | 44647554 | TABLEMTN | NORTH VALLEY | 2021-03-26 |  | ETL.6720 | DESABLA-CENTERVILLE | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42578810 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-08-30 | Ceramic | Dead End |  |  |  |  | 0.0015781
120712178 | F | LC | ETL.6720.POLE.STPS | 44893477 | TABLEMTN | NORTH VALLEY | 2021-03-30 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44893445 | 2019-12-06 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 1.1513e-05 | 0.065151
120721272 | E | LC | ETL.4392.TOWR | 41129338 | LAKEVLLE | SONOMA | 2021-03-31 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129338 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 2.4608e-05 | 3818.9065 | 0.093976
120721272 | E | LC | ETL.4392.TOWR | 41129338 | LAKEVLLE | SONOMA | 2021-03-31 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129338 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 2.4608e-05 | 3818.9065 | 0.093976
120721279 | E | LC | ETL.4392.TOWR | 41129364 | LAKEVLLE | SONOMA | 2021-03-31 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41129364 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.0038549 | 1175.8542 | 4.5328
120721279 | E | LC | ETL.4392.TOWR | 41129364 | LAKEVLLE | SONOMA | 2021-03-31 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41129364 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.0038549 | 1175.8542 | 4.5328
120741220 | E | LC | ETL.1450.POLE.WDPS | 44552574 | SACTO | SACRAMENTO | 2021-04-03 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44551657 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00013594 | 205.7724 | 0.027973
120747950 | E | LC | ETL.7140.INSL | 40779411 | LAKEVLLE | NORTH BAY | 2021-04-06 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40750602 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0047317 | 720.4106 | 3.4088
120769033 | B | LC | ETL.3190.TOWR | 40910322 | TABLEMTN | NORTH VALLEY | 2021-04-08 | 2021-06-24 | ETL.3190 | CARIBOU-PALERMO | Other | Land/Enviro Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910322 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Other |  |  |  |  | 0.17963 | 4742.367
120796344 | E | LC | ETL.8250.POLE.WOOD | 40908880 | VICTOR | STOCKTON | 2021-04-12 | 2021-09-08 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0010183 | 2614.054
120812525 | F | LC | ETL.9100.POLE.WOOD | 44191883 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191883 |  | Single Wood Pole | WB - Wishbone |  | Porcelain | [5 empty] | 1.9794e-05 | 2882.5776
120829189 | E | LC | ETL.1073.POLE.WOOD | 40580219 | VICTOR | STOCKTON | 2021-04-16 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40580219 | 1956-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1956-01-01 | Ceramic | Dead End |  |  |  |  | 0.00097856 | 17.4687 | 0.017094
120829375 | B | LC | ETL.4316.POLE.NWOD | 42567106 | TABLEMTN | NORTH VALLEY | 2021-04-16 | 2021-04-27 | ETL.4316 | PARADISE-TABLE MTN | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42567106 | 2011-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.0003507 | 238.4023
120843617 | F | LC | ETL.8365.POLE.NWOD | 40906667 | EUREKA | HUMBOLDT | 2021-04-19 | 2021-06-02 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40906667 | 2011-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.010632
120844898 | E | LC | ETL.1073.POLE.WDPS | 44385268 | VICTOR | STOCKTON | 2021-04-19 | 2021-10-26 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44385266 | 2017-08-17 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00072916 | 15.88 | 0.011579
120850399 | F | LC | ETL.5540.TOWR | 40663013 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40663013 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 4.8781e-06 | 2883.9575 | 0.014068
120871953 | E | LC | ETL.5780.TOWR | 40752888 | VICTOR | STOCKTON | 2021-04-22 |  | ETL.5780 | TIGER CREEK-ELECTRA | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40752888 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 0.00010571 | 1202.2845 | 0.1271
120877929 | F | LC | ETL.5463.TOWR | 40805053 | CONCORD | DIABLO | 2021-04-23 |  | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40805053 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 1.0848e-07 | 4841.9011 | 0.00052526
120913824 | E | LC | ETL.1820.POLE.STPS | 45002623 | EUREKA | HUMBOLDT | 2021-05-01 |  | ETL.1820 | HUMBOLDT-TRINITY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45002593 | 2020-06-13 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0004638 | 79.1724 | 0.03672
120920192 | E | LC | ETL.6470.POLE.WOOD | 40611127 | SACTO | SIERRA | 2021-04-28 | 2021-08-11 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [12 empty] | 632.8055
120922806 | E | LC | ETL.1250.INSL | 40674409 | FRESNO | FRESNO | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40646745 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.00032935 | 6647.8232 | 2.1895
120930260 | E | LC | ETL.5300.TOWR | 40753336 | PISMOBCH | LOS PADRES | 2021-05-04 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753336 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 1.0207e-05 | 3642.3188 | 0.037179
121191632 | E | LC | ETL.2900.TOWR | 40805727 | MOSSLNDG | CENTRAL COAST | 2021-04-20 | 2021-10-11 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Raptor Guard-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40805727 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0037712 | 825.5362 | 3.1133
121191632 | E | LC | ETL.2900.TOWR | 40805727 | MOSSLNDG | CENTRAL COAST | 2021-04-20 | 2021-10-11 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Raptor Guard-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40805727 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Polymer | Suspension |  |  |  |  | 0.0037712 | 825.5362 | 3.1133
121319826 | E | LC | ETL.3500.TOWR | 40579800 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40579800 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 9.0211e-06 | 316.5427 | 0.0028556
121329429 | F | LC | ETL.2395.POLE.WDPS | 44551465 | TABLEMTN | NORTH VALLEY | 2021-05-13 |  | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44550854 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0046791 | 189.8861
121331289 | B | LC | ETL.7060.INSL.CERA | 44410478 | METCALF | SAN JOSE | 2021-05-12 | 2021-08-05 | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121341019 | F | LC | ETL.8405.POLE.WOOD | 40602856 | SACTO | SIERRA | 2021-05-15 | 2021-09-23 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40602856 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Polymer | [5 empty] | 0.057815 | 6774.7476
121348625 | F | LC | ETL.9040.POLE.WOOD | 40655081 | MIDWAY | FRESNO | 2021-04-20 |  | ETL.9040 | TULE-SPRINGVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40655081 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 1.1899e-05 | 6394.647
121350015 | F | LC | ETL.3720.POLE.NWOD | 44359232 | CONCORD | EAST BAY | 2021-05-17 |  | ETL.3720 | SOBRANTE-G #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | PEND | 44359232 |  | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2021-05-18 | Glass | Suspension |  |  |  |  | 0.0090087 | 0.066432 | 0.00059847
121350212 | E | LC | ETL.8990.POLE.NWOD | 40596438 | FRESNO | FRESNO | 2021-05-18 |  | ETL.8990 | MERCED FALLS-EXCHEQUER | Raptor Guard-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40596438 | 1929-01-01 | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 2020-11-08 | Glass | Suspension |  |  |  |  | 5.7226e-08 | 49.7364 | 2.8462e-06
121363305 | F | LC | ETL.1250.POLE.WOOD | 40682182 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40682182 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.00032563 | 6647.8232
121365123 | E | LC | ETL.1820.INSL.NCER | 40884596 | EUREKA | HUMBOLDT | 2021-05-19 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562349 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.32474
121365123 | E | LC | ETL.1820.INSL.NCER | 40884596 | EUREKA | HUMBOLDT | 2021-05-19 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562349 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.32474
121370916 | E | LC | ETL.1250.POLE.WOOD | 40807037 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40807037 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 5.752e-05 | 4148.9409 | 0.23865
121374514 | E | LC | ETL.5970.INSL.NCER | 45113099 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40753809 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-04-26 | Glass Silicone Coated | Suspension |  |  |  |  | 5.8396e-11 | 2469.6398 | 1.4422e-07
121377733 | F | LC | ETL.1600.TOWR | 40604097 | LAKEVLLE | SONOMA | 2021-05-21 |  | ETL.1600 | FULTON-PUEBLO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40604097 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 1.7125e-05 | 158.4545
121377733 | F | LC | ETL.1600.TOWR | 40604097 | LAKEVLLE | SONOMA | 2021-05-21 |  | ETL.1600 | FULTON-PUEBLO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40604097 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 1.7125e-05 | 158.4545
121380308 | F | LC | ETL.8350.POLE.NWOD | 44853240 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44853240 | 2019-11-27 | Light Duty Steel Pole | T1-1A | 2019-11-27 | Polymer | Post |  |  |  |  | 5.1943e-07 | 95.3431
121383154 | E | LC | ETL.1430.TOWR | 40757312 | SACTO | SIERRA | 2021-05-12 |  | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40757312 | 1913-01-01 | LATTICE STEEL TOWER | Unknown | 2016-11-14 | Non Ceramic | Post |  |  |  |  | 0.00013487 | 1507.6083 | 0.20333
121383540 | E | LC | ETL.4590.TOWR | 40910130 | TABLEMTN | NORTH VALLEY | 2021-05-12 |  | ETL.4590 | CRESTA-RIO OSO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40910130 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-10-30 | Ceramic | Dead End |  |  |  |  | 3.3336e-05 | 3986.9912 | 0.13291
121384608 | F | LC | ETL.1420.TOWR | 40750989 | SACTO | SIERRA | 2021-05-12 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40750989 | 1965-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm | 1989-01-01 | Polymer | Post |  |  |  |  | 8.1697e-08 | 0.090454 | 7.3898e-09
121391551 | E | LC | ETL.1420.TOWR | 40866003 | SACTO | SIERRA | 2021-05-15 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40866003 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-05 | Glass | Suspension |  |  |  |  | 1.2756e-05 | 142.4642 | 0.0018172
121392055 | F | LC | ETL.6760.POLE.WOOD | 40598618 | SACTO | SIERRA | 2021-05-17 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40598618 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0377 | 632.8055
121395444 | E | LC | ETL.6660.POLE.NWOD | 44358502 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44358502 | 2016-10-23 | Light Duty Steel Pole | T2N | 2021-03-04 | Polymer | Post |  |  |  |  | 5.1778e-11 | 2996.0371 | 1.5513e-07
121397209 | F | LC | ETL.6690.POLE.WOOD | 40597179 | SACTO | SIERRA | 2021-05-15 |  | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40597179 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.092587 | 126.6309
121397641 | F | LC | ETL.6770.POLE.NWOD | 44273107 | SACTO | SIERRA | 2021-05-19 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44273107 | 2014-05-14 | Light Duty Steel Pole | T-1 - Tri Post | 2014-05-14 | Polymer | Post |  |  |  |  | 2.1947e-06 | 933.5001
121403659 | B | LC | ETL.1400.SWIT | 44402645 | VICTOR | STOCKTON | 2021-05-26 | 2021-08-12 | ETL.1400 | DONNELLS-MI-WUK | Switch | Out of Adjustment | [Repair, Completed] | Tier3 |  |  | COMP | [7 empty] | 2017-01-23 | SEECO | HIGH SPEED INTERRUPTER | SCADA Only
121421090 | F | LC | ETL.5463.TOWR | 40646991 | CONCORD | DIABLO | 2021-05-27 |  | ETL.5463 | PITTSBURG-SAN MATEO | Structure-Tower | Anti-Climbing Guard | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40646991 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 4.48e-06 | 728.4601
121422084 | B | LC | ETL.6020.TOWR | 40759704 | TABLEMTN | NORTH VALLEY | 2021-05-28 | 2021-06-03 | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759704 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 5.1073e-09 | 1397.0818
121428098 | E | LC | ETL.1402.INSL.CERA | 40772943 | VICTOR | STOCKTON | 2021-05-25 |  | ETL.1402 | SPRING GAP TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550069 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.006849
121428098 | E | LC | ETL.1402.INSL.CERA | 40772943 | VICTOR | STOCKTON | 2021-05-25 |  | ETL.1402 | SPRING GAP TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44550069 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.006849
121443538 | E | LC | ETL.6220.POLE.WOOD | 40862832 | EUREKA | HUMBOLDT | 2021-06-01 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40862832 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.088122 | 332.2834 | 29.2816
121468330 | B | LC | ETL.2770.INSL | 40671343 | CONCORD | EAST BAY | 2021-06-03 | 2021-07-26 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40644212 | 1925-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1991-01-01 | Ceramic | Dead End |  |  |  |  | 4.4711e-06 | 0.065147
121468330 | B | LC | ETL.2770.INSL | 40671343 | CONCORD | EAST BAY | 2021-06-03 | 2021-07-26 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40644212 | 1925-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1991-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.4711e-06 | 0.065147
121493015 | F | LC | ETL.6890.POLE.WOOD | 40874585 | LAKEVLLE | SONOMA | 2021-06-02 |  | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40874585 | 1965-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Other |  |  |  |  | 0.00025078 | 2236.0244
121493095 | F | LC | ETL.5640.TOWR | 40663705 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40663705 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 1.2247e-08 | 3407.9209 | 4.1738e-05
121493439 | E | LC | ETL.1720.POLE.WDPS | 44401104 | MOSSLNDG | CENTRAL COAST | 2021-05-28 | 2021-10-07 | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44401102 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.1697e-05 | 76.2623 | 0.0039425
121500063 | E | LC | ETL.5650.INSL | 40621324 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40595050 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 7.1797e-07 | 1871.8424 | 0.0013439
121511221 | B | LC | ETL.1350.POLE.WDPS | 44512309 | TABLEMTN | NORTH VALLEY | 2021-06-09 | 2021-06-21 | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44512309 |  | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.042743
121511221 | B | LC | ETL.1350.POLE.WDPS | 44512309 | TABLEMTN | NORTH VALLEY | 2021-06-09 | 2021-06-21 | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44512309 |  | 2-Pole Wood | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.042743
121511346 | A | LC | ETL.1820.INSL.CERA | 40790541 | EUREKA | HUMBOLDT | 2021-06-08 | 2021-06-14 | ETL.1820 | HUMBOLDT-TRINITY | Emergency-Wood | Other | [Replace, Completed] | Tier2 |  |  | COMP
121512257 | F | LC | ETL.8060.POLE.WDPS | 44420792 | SACTO | SACRAMENTO | 2021-06-09 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
121516305 | E | LC | ETL.8170.INSL.NCER | 45142905 | EUREKA | HUMBOLDT | 2021-06-10 |  | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40903783 |  | Single Wood Pole | T1DE - Tri Post Dead End 115 | 2021-06-02 | Glass | Dead End |  |  |  |  | 0.0093661 | 284.8513 | 2.6679
121519790 | E | LC | ETL.7550.POLE.NWOD | 44837775 | LAKEVLLE | HUMBOLDT | 2021-06-07 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44837775 | 2019-09-14 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-09-14 | Glass | Dead End |  |  |  |  | 1.9743e-09 | 0.065148 | 1.2862e-10
121523468 | E | LC | ETL.1350.POLE.WDPS | 44201743 | TABLEMTN | NORTH VALLEY | 2021-06-09 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44201741 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.14209 | 490.5302 | 69.6996
121524594 | E | LC | ETL.1710.POLE.WDPS | 44510824 | MOSSLNDG | CENTRAL COAST | 2021-06-12 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44509642 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 8.1282e-05 | 174.0283 | 0.014145
121534205 | E | LC | ETL.1600.INSL.CERA | 40781836 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40752656 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 1.4163e-08 | 838.7772 | 1.188e-05
121543941 | F | LC | ETL.4440.POLE.NWOD | 41162681 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41162681 |  | Lattice Steel Pole | SUSP - Suspension (TWR) |  | Non Ceramic | [5 empty] | 0.0001454 | 5999.3906
121563150 | B | LC | ETL.8250.INSL.NCER | 42833886 | VICTOR | STOCKTON | 2021-06-17 | 2021-07-15 | ETL.8250 | CLAY-MARTEL | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44254762 |  | 3-Pole Wood | 1VP - 1 Vertical |  | Polymer | Suspension |  |  |  |  | 0.016874
121563150 | B | LC | ETL.8250.INSL.NCER | 42833886 | VICTOR | STOCKTON | 2021-06-17 | 2021-07-15 | ETL.8250 | CLAY-MARTEL | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44254762 |  | 3-Pole Wood | 1VP - 1 Vertical |  | Polymer | Suspension |  |  |  |  | 0.016874
121563150 | B | LC | ETL.8250.INSL.NCER | 42833886 | VICTOR | STOCKTON | 2021-06-17 | 2021-07-15 | ETL.8250 | CLAY-MARTEL | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44254762 |  | 3-Pole Wood | 1VP - 1 Vertical |  | Polymer | Suspension |  |  |  |  | 0.016874
121563150 | B | LC | ETL.8250.INSL.NCER | 42833886 | VICTOR | STOCKTON | 2021-06-17 | 2021-07-15 | ETL.8250 | CLAY-MARTEL | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44254762 |  | 3-Pole Wood | 1VP - 1 Vertical |  | Polymer | Suspension |  |  |  |  | 0.016874
121563150 | B | LC | ETL.8250.INSL.NCER | 42833886 | VICTOR | STOCKTON | 2021-06-17 | 2021-07-15 | ETL.8250 | CLAY-MARTEL | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44254762 |  | 3-Pole Wood | 1VP - 1 Vertical |  | Polymer | Suspension |  |  |  |  | 0.016874
121563150 | B | LC | ETL.8250.INSL.NCER | 42833886 | VICTOR | STOCKTON | 2021-06-17 | 2021-07-15 | ETL.8250 | CLAY-MARTEL | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44254762 |  | 3-Pole Wood | 1VP - 1 Vertical |  | Polymer | Suspension |  |  |  |  | 0.016874
121574078 | E | LC | ETL.6240.INSL.NCER | 44175576 | MOSSLNDG | CENTRAL COAST | 2021-06-16 |  | ETL.6240 | BURNS-LONE STAR #2 | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44175558 | 2014-05-13 | Single Wood Pole | TH - TriAngle Post 70 | 2014-05-13 | Polymer | Post |  |  |  |  | 0.50715 | 15.8866 | 8.0569
121580874 | E | LC | ETL.7550.POLE.WOOD | 40750980 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40750980 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.00091359 | 15.8807 | 0.014509
121581169 | E | LC | ETL.7550.INSL.NCER | 40779077 | LAKEVLLE |  | 2021-06-18 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40750973 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0001416 | 602.6383 | 0.085337
121582433 | E | LC | ETL.6040.INSL | 40783480 | MOSSLNDG | CENTRAL COAST | 2021-06-22 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40753855 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 0.00013013 | 3115.7767 | 0.40545
121583067 | E | LC | ETL.4440.TOWR | 40867845 | TABLEMTN | NORTH VALLEY | 2021-06-22 |  | ETL.4440 | CARIBOU-TABLE MTN | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier2 | Tier 2 | Within Both | PEND | 40867845 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 0.0038179 | 1170.4968 | 4.4689
121585115 | F | LC | ETL.8365.POLE.STPS | 44915259 | EUREKA | HUMBOLDT | 2021-06-18 | 2021-11-29 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44915229 | 2019-06-22 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00053994 | 648.7126
121585246 | E | LC | ETL.8365.POLE.STPS | 44915260 | EUREKA | HUMBOLDT | 2021-06-18 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | PEND | 44915229 | 2019-06-22 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00053994 | 648.7126 | 0.35026
121594042 | E | LC | ETL.5140.POLE.WDPS | 44552353 | SACTO | SACRAMENTO | 2021-06-17 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44551683 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00024144 | 1075.8865 | 0.25976
121605538 | E | LC | ETL.4750.TOWR | 41129179 | LAKEVLLE | SONOMA | 2021-06-22 |  | ETL.4750 | GEYSERS #12-FULTON | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129179 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1979-01-01 | Porcelain | Dead End |  |  |  |  | 0.0054538 | 1378.0675 | 7.5156
121605538 | E | LC | ETL.4750.TOWR | 41129179 | LAKEVLLE | SONOMA | 2021-06-22 |  | ETL.4750 | GEYSERS #12-FULTON | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129179 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1979-01-01 | Ceramic | Dead End |  |  |  |  | 0.0054538 | 1378.0675 | 7.5156
121605538 | E | LC | ETL.4750.TOWR | 41129179 | LAKEVLLE | SONOMA | 2021-06-22 |  | ETL.4750 | GEYSERS #12-FULTON | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 41129179 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | [5 empty] | 0.0054538 | 1378.0675 | 7.5156
121608543 | E | LC | ETL.1440.POLE.WDPS | 44149467 | SACTO | SACRAMENTO | 2021-06-23 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44149466 | 2013-11-06 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.015706 | 23.837 | 0.37438
121609160 | E | LC | ETL.7180.INSL.CERA | 40699486 | LAKEVLLE | NORTH BAY | 2021-06-18 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 40668085 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.00010577 | 126.5965 | 0.013391
121621707 | E | LC | ETL.6020.TOWR | 40753360 | TABLEMTN | NORTH VALLEY | 2021-06-26 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753360 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 6.1069e-07 | 79.1724 | 4.835e-05
121624366 | B | LC | ETL.1350.INSL.CERA | 42611954 | TABLEMTN | NORTH VALLEY | 2021-06-27 | 2021-07-26 | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
121642407 | E | LC | ETL.1610.INSL | 40835246 | LAKEVLLE | SONOMA | 2021-06-11 |  | ETL.1610 | SILVERADO-FULTON JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810366 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.6406e-07 | 6494.9727 | 0.0010656
121651761 | E | LC | ETL.6760.POLE.WOOD | 40766662 | SACTO | SIERRA | 2021-06-28 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40766662 |  | Single Wood Pole | TCDE - Tap Construction Dead End |  | Porcelain | [5 empty] | 0.094622 | 94.9889 | 8.9881
121723058 | E | LC | ETL.6020.TOWR | 40601178 | TABLEMTN | NORTH VALLEY | 2021-07-12 |  | ETL.6020 | MALIN-ROUND MTN #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40601178 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 9.5082e-05 | 221.5655 | 0.021067
121726529 | B | LC | ETL.6650.INSL.NCER | 40618655 | TABLEMTN | NORTH VALLEY | 2021-07-13 | 2021-09-08 | ETL.6650 | COTTONWOOD-BENTON #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44386694 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.0023919
121726529 | B | LC | ETL.6650.INSL.NCER | 40618655 | TABLEMTN | NORTH VALLEY | 2021-07-13 | 2021-09-08 | ETL.6650 | COTTONWOOD-BENTON #2 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44386694 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Non Ceramic | Suspension |  |  |  |  | 0.0023919
121730342 | B | LC | ETL.1730.POLE.WDPS | 44413250 | MOSSLNDG | CENTRAL COAST | 2021-07-14 | 2021-07-27 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44413247 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.705e-05 | 63.3245
121731855 | F | LC | ETL.4220.POLE.STPS | 44388357 | TABLEMTN |  | 2021-07-07 |  | ETL.4220 | WOODLEAF-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44388356 | 2016-12-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0011569 | 269.106
121741173 | F | LC | ETL.2390.POLE.STPS | 44905900 | VICTOR | YOSEMITE | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44905850 | 2020-03-03 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.35e-09 | 2645.3047
121746603 | F | LC | ETL.5430.POLE.STPS | 44659655 | TABLEMTN |  | 2021-07-14 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44148943 | 2016-12-07 | 2-Pole Non Wood | SS1 - Susp. Steel Single. CIR | [7 empty] | 1.3576e-06 | 364.0218
121748774 | E | LC | ETL.1820.INSL.CERA | 40694348 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562457 |  | Single Wood Pole | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.30195 | 4621.6372 | 1395.5088
121748989 | E | LC | ETL.1820.POLE.WOOD | 45102080 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45102080 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Ceramic | Suspension |  |  |  |  | 0.22936 | 5637.5752 | 1293.008
121763607 | F | LC | ETL.9240.TOWR | 43249795 | PISMOBCH | LOS PADRES | 2021-07-19 | 2021-10-04 | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 43249795 |  | LATTICE STEEL TOWER | [9 empty] | 950.9399
121771460 | E | LC | ETL.8365.INSL.NCER | 40922498 | EUREKA | HUMBOLDT | 2021-07-21 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40912689 | 2010-01-01 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 0.056089 | 4492.853 | 251.9992
121781612 | E | LC | ETL.4440.POLE.STPS | 45112504 | TABLEMTN | NORTH VALLEY | 2021-07-21 | 2021-08-09 | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44190865 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 3.4309e-05 | 5874.6039
121806900 | E | LC | ETL.8405.POLE.WOOD | 40822817 | SACTO | SIERRA | 2021-07-26 |  | ETL.8405 | MIDDLE FORK #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40822817 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2020-03-08 | Polymer | Dead End |  |  |  |  | 0.004133 | 1186.6189 | 4.9043
121813853 | F | LC | ETL.4590.TOWR | 41083092 | TABLEMTN | NORTH VALLEY | 2021-07-29 |  | ETL.4590 | CRESTA-RIO OSO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41083092 |  | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-07-13 | Glass | Dead End |  |  |  |  | 8.0427e-07 | 6066.4741
121815349 | F | LC | ETL.4440.POLE.NWOD | 40814896 | TABLEMTN | NORTH VALLEY | 2021-07-28 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40814896 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.00060701 | 4683.9302
121815678 | F | LC | ETL.2540.POLE.NWOD | 44987819 | MOSSLNDG | SAN JOSE | 2021-07-29 |  | ETL.2540 | METCALF-GREEN VALLEY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44987819 | 2014-05-06 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2014-05-06 | Porcelain | Dead End |  |  |  |  | 4.9902e-06 | 1853.4576
121815686 | F | LC | ETL.5400.POLE.STPS | 45114387 | TABLEMTN | NORTH VALLEY | 2021-07-27 |  | ETL.5400 | PIT #3-PIT #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Non-HFTD | Non-HFRA | PEND | 45114360 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [8 empty] | 4186.9331
121822705 | E | LC | ETL.8060.INSL.CERA | 42636528 | SACTO | SACRAMENTO | 2021-07-29 |  | ETL.8060 | SPAULDING-SUMMIT | Tie Wire-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40587811 |  | Light Duty Steel Pole | FSS - Field Switch Structure |  | Porcelain | [5 empty] | 0.018819 | 2110.5538 | 39.7183
121906739 | E | LC | ETL.1400.POLE.WDPS | 44779568 | VICTOR | YOSEMITE | 2021-06-01 |  | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40803710 | 2019-06-22 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.00037953 | 2626.426 | 0.99681
121973966 | E | LC | ETL.7270.POLE.WOOD | 40909533 | TABLEMTN | NORTH VALLEY | 2021-08-30 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40909533 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0030041 | 5300.8838 | 15.9244
122066035 | E | LC | ETL.4780.INSL | 40687892 | LAKEVLLE | SONOMA | 2021-09-17 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40658050 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.0011912 | 2193.1538 | 2.6125
118754469 | B | LC | ETL.8000.POLE.NWOD | 40912140 | SACTO | SACRAMENTO | 2020-03-28 | 2020-04-16 | ETL.8000 | SMARTVILLE-NICOLAUS #2 | Switch | Out of Adjustment | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40912140 |  | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 6.0731e-06 | 2125.1653
118913715 | E | LC | ETL.8210.POLE.WOOD | 40908281 | VICTOR | STOCKTON | 2020-04-13 | 2021-07-06 | ETL.8210 | VALLEY SPRINGS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908281 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0017118 | 3736.1409
118947136 | F | LC | ETL.3830.TOWR | 40856491 | VICTOR | STOCKTON | 2020-04-24 | 2021-02-16 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40856491 | 1927-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1999-01-01 | Non Ceramic | Suspension |  |  |  |  | 3.0349e-08 | 1364.5436
118963978 | E | LC | ETL.2390.POLE.WOOD | 44391580 | VICTOR | STOCKTON | 2020-04-30 | 2021-01-13 | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44391580 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | Dead End |  |  |  |  | 2.9412e-06 | 6710.7031
119004609 | E | LC | ETL.2720.TOWR | 40648544 | CONCORD | EAST BAY | 2020-05-04 | 2021-06-04 | ETL.2720 | MORAGA-OAKLAND #1 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40648544 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.5563e-05 | 0.065158
119004622 | E | LC | ETL.1710.POLE.WOOD | 42567479 | MOSSLNDG | CENTRAL COAST | 2020-04-20 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42567479 |  | Single Wood Pole | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00085507 | 0.065147 | 5.5705e-05
119035578 | E | LC | ETL.1650.POLE.WOOD | 40659189 | LAKEVLLE | SONOMA | 2020-05-11 | 2021-03-16 | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40659189 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 5.3451e-05 | 3938.675
119038666 | F | LC | ETL.2031.POLE.NWOD | 40746824 | FRESNO | FRESNO | 2020-05-07 |  | ETL.2031 | RAINBOW TAP | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Non-HFTD | Non-HFRA | PEND | 40746824 | 1979-01-01 | Lattice Steel Pole | SUSP - Suspension (TWR) | 1979-01-01 | Ceramic | Suspension |  |  |  |  | 3.4945e-09
119038952 | E | LC | ETL.7055.POLE.WOOD | 40804452 | CONCORD | DIABLO | 2020-05-12 | 2020-06-08 | ETL.7055 | BRIONES TAP | Insulator | Contaminated | [Ground Wash, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40804452 | 1982-01-01 | Single Wood Pole | DDE-A - Double Dead End Angle | 2020-05-30 | Glass | Dead End |  |  |  |  | 0.012615 | 4769.5273
119041804 | B | LC | ETL.1110.TOWR | 40657063 | EUREKA | HUMBOLDT | 2020-05-19 | 2020-05-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40657063 | 1952-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | [7 empty] | 1.9122e-05 | 126.6368
119083188 | E | LC | ETL.6980.POLE.WOOD | 40648493 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-06-17 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648493 | 1953-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2010-01-01 | Polymer | Suspension |  |  |  |  | 0.20902 | 0.065159
119083486 | B | LC | ETL.2060.INSL | 40608739 | LAKEVLLE | HUMBOLDT | 2020-05-22 | 2021-05-12 | ETL.2060 | FORT BRAGG-ELK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119105591 | F | LC | ETL.6720.POLE.WDPS | 44950335 | TABLEMTN | NORTH VALLEY | 2020-05-19 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 42578837 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0025222 | 2104.1226
119107648 | E | LC | ETL.6950.POLE.WOOD | 40600080 | SACTO | SIERRA | 2020-06-02 | 2021-04-03 | ETL.6950 | GOLD HILL #1 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40600080 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00067666 | 2914.9978
119109517 | E | LC | ETL.7560.POLE.WDPS | 44947120 | SACTO | SIERRA | 2020-06-01 | 2021-04-29 | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119113497 | E | LC | ETL.6760.POLE.WOOD | 40756938 | SACTO | SIERRA | 2020-05-27 | 2021-06-29 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756938 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.002189 | 1138.9978
119114516 | F | LC | ETL.6870.POLE.NWOD | 40693737 | SACTO | SIERRA | 2020-05-28 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40693737 |  | Light Duty Steel Pole | DDE - Double Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 0.0033913 | 126.6309
119116259 | F | LC | ETL.7290.POLE.WOOD | 40816386 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40816386 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | [7 empty] | 0.003745 | 1158.6814
119118334 | E | LC | ETL.6490.POLE.WOOD | 40825362 | SACTO | SIERRA | 2020-05-28 | 2021-03-03 | ETL.6490 | COLGATE-GRASS VALLEY | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40825362 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.019544 | 3591.0945
119118979 | F | LC | ETL.1400.POLE.WDPS | 45087025 | VICTOR | YOSEMITE | 2020-05-27 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40579644 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0085281 | 31.7207
119119848 | F | LC | ETL.6490.POLE.WOOD | 40679320 | SACTO | SIERRA | 2020-06-03 |  | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40679320 |  | Single Wood Pole | T-1 - Tri Post | 2020-06-03 | Polymer | Post |  |  |  |  | 0.013735 | 71.3642
119127350 | E | LC | ETL.9340.POLE.NWOD | 44761235 | FRESNO | FRESNO | 2020-06-09 | 2021-08-02 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44761235 | 2019-05-08 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-05-08 | Polymer | Dead End |  |  |  |  | 0.00037908 | 6948.3115
119128429 | E | LC | ETL.3690.INSL | 40782057 | PISMOBCH | LOS PADRES | 2020-06-09 |  | ETL.3690 | SISQUOC-GAREY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40752829 | 1986-01-01 | Single Wood Pole | DV - Double Vertical | 1986-01-01 | Ceramic | Other |  |  |  |  | 0.020608 | 5160.9634 | 106.3595
119163052 | F | LC | ETL.6440.POLE.NWOD | 44761239 | TABLEMTN | NORTH VALLEY | 2020-06-11 | 2020-09-03 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44761239 | 2019-04-04 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-04-04 | Glass | Dead End |  |  |  |  | 7.5504e-05 | 2917.0559
119165433 | E | LC | ETL.1420.TOWR | 40582454 | SACTO | SIERRA | 2020-06-11 | 2021-02-16 | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40582454 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-04 | Glass | Suspension |  |  |  |  | 4.7833e-05 | 142.4516
119171367 | E | LC | ETL.6280.POLE.WOOD | 40698677 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6280 | CARIBOU #2 | Crossarm-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40698677 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0010594 | 569.452 | 0.60327
119171602 | B | LC | ETL.5780.INSL | 40791814 | VICTOR | STOCKTON | 2020-04-14 | 2020-09-21 | ETL.5780 | TIGER CREEK-ELECTRA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119175069 | F | LC | ETL.6480.POLE.NWOD | 45122793 | SACTO | NORTH VALLEY | 2020-06-15 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45122793 | 2021-06-19 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-06-19 | Glass | Dead End | [5 empty] | 253.3131
119177870 | F | LC | ETL.6280.POLE.WOOD | 40666852 | TABLEMTN | NORTH VALLEY | 2020-06-16 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40666852 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 5.8877e-06 | 6187.9214
119179396 | F | LC | ETL.6770.POLE.NWOD | 44874802 | SACTO | SIERRA | 2020-06-17 | 2021-03-17 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44874802 | 2019-04-24 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-04-13 | Polymer | Dead End |  |  |  |  | 0.00019112 | 411.4038
119182832 | E | LC | ETL.5780.TOWR | 40593868 | VICTOR | STOCKTON | 2020-06-16 | 2021-06-01 | ETL.5780 | TIGER CREEK-ELECTRA | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593868 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Ceramic | Suspension |  |  |  |  | 1.2535e-07 | 1075.7617
119185016 | E | LC | ETL.6710.POLE.WOOD | 40876146 | MOSSLNDG | CENTRAL COAST | 2020-06-18 |  | ETL.6710 | DEL MONTE-VIEJO | Damper-Steel | Missing | [Install] | Tier2 |  |  | PEND
119194266 | F | LC | ETL.6470.POLE.WOOD | 40767352 | SACTO | SIERRA | 2020-06-19 | 2021-07-06 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40767352 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.15777 | 174.1689
119197861 | F | LC | ETL.6470.POLE.WOOD | 40598566 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40598566 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.034652 | 269.0553
119209689 | F | LC | ETL.8180.POLE.WOOD | 40876763 | LAKEVLLE | SACRAMENTO | 2020-06-24 |  | ETL.8180 | TULUCAY-NAPA #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40876763 | 1991-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | [5 empty] | 0.018962 | 1918.6997
119210462 | B | LC | ETL.6720.POLE.WOOD | 42578820 | TABLEMTN | NORTH VALLEY | 2020-06-24 | 2020-10-26 | ETL.6720 | DESABLA-CENTERVILLE | Other | Customer Issue | [Customer Refusal, Completed] | Tier3 |  |  | COMP
119236146 | F | LC | ETL.7270.POLE.WOOD | 40909477 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40909477 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Unknown |  |  |  |  | 0.02334 | 0.065152
119238735 | E | LC | ETL.6470.POLE.WOOD | 40905840 | SACTO | SACRAMENTO | 2020-06-30 | 2021-07-27 | ETL.6470 | COLGATE-ALLEGHANY | Damper-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40905840 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.16873 | 474.9903
119290985 | E | LC | ETL.1370.INSL.CERA | 40840502 | PISMOBCH | LOS PADRES | 2020-07-01 | 2021-07-08 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119294883 | F | LC | ETL.4430.POLE.NWOD | 44771056 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.4430 | BUCKS CREEK-ROCK CREEK-CRESTA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44771056 |  | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 7.3613e-05 | 2076.5681
119295657 | E | LC | ETL.4393.POLE.WDPS | 44172218 | SACTO | SACRAMENTO | 2020-06-30 | 2021-04-07 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119302923 | E | LC | ETL.1110.POLE.WDPS | 44424551 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-04-09 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 44424550 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014098 | 3344.0325
119310042 | F | LC | ETL.2395.POLE.WDPS | 44549858 | TABLEMTN |  | 2020-07-01 |  | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44549427 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0040869 | 2293.4417
119319443 | F | LC | ETL.7270.POLE.WOOD | 40906104 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906104 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0018033 | 1085.5622
119328099 | F | LC | ETL.2395.POLE.WDPS | 44550836 | TABLEMTN |  | 2020-07-07 |  | ETL.2395 | GRIZZLY TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
119337226 | E | LC | ETL.6980.POLE.WOOD | 40661485 | LAKEVLLE | SONOMA | 2020-07-09 | 2021-06-23 | ETL.6980 | FORT ROSS-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40661485 | 1953-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.82871 | 0.065153
119341877 | F | LC | ETL.6300.POLE.WDPS | 44989190 | TABLEMTN | NORTH VALLEY | 2020-07-08 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 42624216 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.002545 | 126.6209
119355798 | F | LC | ETL.1480.TOWR | 40585028 | LAKEVLLE | SONOMA | 2020-07-10 | 2021-01-28 | ETL.1480 | EAGLE ROCK-REDBUD | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40585028 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-11-05 | Glass | Suspension |  |  |  |  | 0.0010798 | 574.263
119355798 | F | LC | ETL.1480.TOWR | 40585028 | LAKEVLLE | SONOMA | 2020-07-10 | 2021-01-28 | ETL.1480 | EAGLE ROCK-REDBUD | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40585028 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 0.0010798 | 574.263
119356860 | F | LC | ETL.6280.POLE.NWOD | 44258959 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44258959 | 2020-05-27 | Light Duty Steel Pole | LB - Line and Buck | 2020-05-27 | Ceramic | Suspension |  |  |  |  | 1.4636e-07 | 2040.3936
119357596 | E | LC | ETL.1720.INSL.CERA | 40630825 | MOSSLNDG | SAN JOSE | 2020-07-09 | 2021-03-25 | ETL.1720 | GREEN VALLEY-LLAGAS | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119359715 | E | LC | ETL.7030.POLE.WOOD | 40827471 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-06-08 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827471 |  | Single Wood Pole | T2N | 2021-05-20 | Polymer | Post |  |  |  |  | 0.024506 | 206.4995
119362867 | E | LC | ETL.8560.INSL.CERA | 44652092 | PISMOBCH | LOS PADRES | 2020-07-13 | 2021-03-23 | ETL.8560 | CAYUCOS-CAMBRIA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119367657 | E | LC | ETL.1440.POLE.WDPS | 40671393 | SACTO | SIERRA | 2020-07-13 | 2021-02-18 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Rotten | [Replace] | Tier2 |  |  | DLFL
119367963 | E | LC | ETL.1110.POLE.WDPS | 44232660 | TABLEMTN | HUMBOLDT | 2020-07-14 | 2021-04-19 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44232659 | 2014-10-28 | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.0012206 | 3154.0374
119379699 | B | LC | ETL.6380.SWIT | 43249244 | LAKEVLLE | SONOMA | 2020-07-16 | 2020-11-24 | ETL.6380 | KONOCTI-MIDDLETOWN | Switch | Out of Adjustment | [Repair, Completed] | Tier2 |  |  | COMP | [8 empty] | Turner | ARCING HORNS WITH VACUUM BOTT* | Manual
119467865 | F | LC | ETL.7380.POLE.WOOD | 40666351 | MOSSLNDG | CENTRAL COAST | 2020-07-17 | 2021-04-12 | ETL.7380 | LAURELES-OTTER | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40666351 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0059928 | 15.88
119469062 | B | LC | ETL.8410.INSL.NCER | 40641079 | LAKEVLLE | HUMBOLDT | 2020-07-17 | 2020-12-01 | ETL.8410 | ELK-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119474855 | E | LC | ETL.6880.POLE.WOOD | 40667684 | LAKEVLLE | SONOMA | 2020-07-20 | 2020-12-29 | ETL.6880 | FULTON-CALISTOGA | Road | Brush Fuel | [Remove, Completed] | Tier3 |  |  | COMP
119475068 | F | LC | ETL.5440.POLE.STPS | 44313718 | TABLEMTN | NORTH VALLEY | 2020-07-20 | 2020-08-19 | ETL.5440 | PIT #6 JCT-ROUND MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44313716 | 2016-10-10 | 2-Pole Non Wood | Unknown | [7 empty] | 1.305e-05 | 696.9175
119477074 | B | LC | ETL.5290.INSL | 40793055 | PISMOBCH | LOS PADRES | 2020-07-20 | 2020-09-03 | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119480256 | F | LC | ETL.8960.POLE.STPS | 44236992 | FRESNO | FRESNO | 2020-07-21 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44236989 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.581e-07
119482688 | F | LC | ETL.8960.POLE.WOOD | 40754868 | FRESNO | FRESNO | 2020-07-21 | 2021-01-26 | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40754868 |  | Single Wood Pole | WB - Wishbone | 1974-01-01 | Porcelain | Suspension |  |  |  |  | 0.003073
119492705 | E | LC | ETL.4393.POLE.WDPS | 44172158 | SACTO | SACRAMENTO | 2020-07-23 | 2021-02-04 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44172156 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.2768e-05 | 1360.4569
119511955 | F | LC | ETL.6220.POLE.WOOD | 40826281 | EUREKA | HUMBOLDT | 2020-07-23 | 2020-08-14 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40826281 |  | Single Wood Pole | T2N | 2020-12-20 | Polymer | Post |  |  |  |  | 0.12505 | 1645.0619
119512192 | E | LC | ETL.7780.POLE.WDPS | 44837718 | LAKEVLLE | SONOMA | 2020-07-27 | 2021-01-20 | ETL.7780 | PHILO JCT-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40819535 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.0039418 | 15.8807
119539146 | F | LC | ETL.6380.POLE.WOOD | 40699027 | LAKEVLLE | HUMBOLDT | 2020-07-31 | 2021-03-08 | ETL.6380 | KONOCTI-MIDDLETOWN | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40699027 |  | Single Wood Pole | T2N | 2018-09-29 | Polymer | Post |  |  |  |  | 5.1266e-05 | 6300.8276
119555398 | F | LC | ETL.7180.POLE.WOOD | 40809060 | LAKEVLLE | NORTH BAY | 2020-08-04 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40809060 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 6.8445e-05 | 1834.5856
119560484 | F | LC | ETL.9340.POLE.WOOD | 44655747 | FRESNO | YOSEMITE | 2020-08-04 | 2021-04-26 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP
119575416 | B | LC | ETL.7780.POLE.WOOD | 40876332 | LAKEVLLE | SONOMA | 2020-08-07 | 2020-10-19 | ETL.7780 | PHILO JCT-ELK | Other | Customer Issue | [Customer Refusal] | Tier2 | Tier 2 | Within Both | COMP | 40876332 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Ceramic | [5 empty] | 0.00024451 | 79.143
119607595 | E | LC | ETL.6222.POLE.WOOD | 40860869 | EUREKA | HUMBOLDT | 2020-08-12 |  | ETL.6222 | FORT SEWARD TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40860869 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.00016526
119610176 | E | LC | ETL.4392.TOWR | 40756575 | LAKEVLLE | SONOMA | 2020-08-13 | 2021-03-24 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756575 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-05-12 | Porcelain | Suspension |  |  |  |  | 1.1142e-06 | 2789.2666
119610176 | E | LC | ETL.4392.TOWR | 40756575 | LAKEVLLE | SONOMA | 2020-08-13 | 2021-03-24 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756575 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-03-10 | Porcelain | Suspension |  |  |  |  | 1.1142e-06 | 2789.2666
119611117 | B | LC | ETL.1112.TOWR | 40748160 | FRESNO | FRESNO | 2020-08-13 | 2020-12-14 | ETL.1112 | INDIAN FLAT-YOSEMITE | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40748160 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1929-01-01 | Glass | Double Dead End - Suspension |  |  |  |  | 0.00081201 | 6806.8955
119611375 | E | LC | ETL.8650.TOWR | 40651187 | FRESNO | FRESNO | 2020-08-13 | 2020-11-06 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40651187 | 1929-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.008378 | 6900.5825
119638581 | A | LC | ETL.7590.POLE.WOOD | 40820792 | MOSSLNDG | CENTRAL COAST | 2020-08-19 | 2020-08-20 | ETL.7590 | MONTA VISTA-BURNS | Non-Routine Patrol | Investigate | [Ground Patrol] | Tier3 |  |  | DLFL
119682340 | E | LC | ETL.8170.POLE.WDPS | 44752429 | EUREKA | HUMBOLDT | 2020-08-25 |  | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40861547 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.2659 | 284.7712 | 75.7197
119714388 | F | LC | ETL.8290.POLE.WOOD | 40702894 | TABLEMTN | NORTH VALLEY | 2020-08-29 | 2021-03-31 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40702894 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 6.5786e-05 | 3010.644
119716110 | F | LC | ETL.8170.POLE.WOOD | 40751121 | EUREKA | HUMBOLDT | 2020-09-02 | 2021-11-29 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40751121 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.34157 | 253.2652
119718688 | B | LC | ETL.4950.INSL | 41130057 | LAKEVLLE |  | 2020-07-27 | 2020-09-21 | ETL.4950 | FULTON-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593051 | 1984-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1984-01-01 | Ceramic | Suspension |  |  |  |  | 0.0090983 | 1327.7751
119723303 | E | LC | ETL.7300.POLE.WOOD | 40828001 | TABLEMTN |  | 2020-08-11 | 2021-09-02 | ETL.7300 | KILARC-DESCHUTES | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40828001 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0029898 | 1519.6183
119753684 | F | LC | ETL.1240.POLE.WDPS | 44386111 | TABLEMTN | NORTH VALLEY | 2020-07-31 |  | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44386110 |  | 2-Pole Wood | 2PS TRP - 2 Pole SUSP. Transposition | [7 empty] | 2.9815e-05 | 3619.7201
119754033 | F | LC | ETL.7930.POLE.WOOD | 40585819 | MOSSLNDG | CENTRAL COAST | 2020-09-11 |  | ETL.7930 | SALINAS-LAURELES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40585819 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0034318 | 31.6948
119755258 | E | LC | ETL.2540.POLE.WDPS | 44401431 | MOSSLNDG | CENTRAL COAST | 2020-08-26 | 2021-01-15 | ETL.2540 | METCALF-GREEN VALLEY | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 3 | Within Both | COMP | 44401430 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.006563 | 1407.5852
119775551 | F | LC | ETL.6320.POLE | 44660735 | TABLEMTN | NORTH VALLEY | 2020-09-10 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44660735 | 2018-10-05 | Light Duty Steel Pole | T-1 - Tri Post | 2018-10-05 | Polymer | Post |  |  |  |  | 5.2254e-07 | 506.6714
119783667 | A | LC | ETL.7590.POLE.WDPS | 44632193 | MOSSLNDG | CENTRAL COAST | 2020-09-18 | 2020-10-16 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Storm Related | [Replace, Completed] |  | Tier 3 | Within Both | COMP | 44631825 | 2018-07-23 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.049429 | 110.8153
119789502 | F | LC | ETL.1400.POLE.STPS | 44381764 | VICTOR | YOSEMITE | 2020-07-29 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 3 | Within Both | PEND | 44381763 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00017549 | 79.1977
119800105 | F | LC | ETL.6480.POLE.NWOD | 44695478 | SACTO | SIERRA | 2020-08-07 | 2021-05-23 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44695478 | 2018-12-10 | Light Duty Steel Pole | T-1 - Tri Post | 2018-12-10 | Polymer | Post |  |  |  |  | 0.035129 | 3859.7815
119811217 | F | LC | ETL.6470.POLE.NWOD | 44683834 | SACTO | SIERRA | 2020-08-25 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44683834 | 2018-11-28 | Light Duty Steel Pole | T-1 - Tri Post | 2018-11-27 | Polymer | Post |  |  |  |  | 0.0056081 | 269.0553
119833593 | B | LC | ETL.7780.INSL.CERA | 40743998 | LAKEVLLE | HUMBOLDT | 2020-09-30 | 2020-11-12 | ETL.7780 | PHILO JCT-ELK | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41128129 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.00032017 | 450.6957
119869597 | E | LC | ETL.7030.POLE.WOOD | 40876183 | TABLEMTN | NORTH VALLEY | 2020-10-05 | 2021-07-08 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40876183 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.018738 | 0.24228
119898450 | E | LC | ETL.6520.POLE.WOOD | 40828234 | SACTO | SIERRA | 2020-10-07 | 2021-06-22 | ETL.6520 | COLGATE-SMARTVILLE #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40828234 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 0.083521 | 744.7016
120232486 | F | LC | ETL.6280.POLE.NWOD | 44259088 | TABLEMTN | NORTH VALLEY | 2020-11-25 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44259088 | 2018-09-24 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2018-11-01 | Ceramic | Suspension |  |  |  |  | 2.5241e-10 | 537.8195
120470958 | A | LC | ETL.7820.POLE.NWOD | 44629382 | LAKEVLLE | SONOMA | 2021-01-27 | 2021-02-01 | ETL.7820 | POTTER VALLEY-WILLITS | Emergency | Storm Related | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44629382 | 2018-06-29 | Light Duty Steel Pole | T2N | 2018-06-29 | Polymer | Post |  |  |  |  | 4.189e-08 | 569.8857
120649290 | F | LC | ETL.2395.POLE.WOOD | 45019107 | TABLEMTN | NORTH VALLEY | 2021-03-16 | 2021-07-09 | ETL.2395 | GRIZZLY TAP | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45019107 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.0066717 | 6679.8335
120668107 | E | LC | ETL.4040.POLE.STPS | 44783300 | TABLEMTN | NORTH VALLEY | 2021-03-20 | 2021-09-14 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44783246 | 2019-07-14 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00012492 | 5687.9312
120677270 | B | LC | ETL.3700.INSL.CERA | 40891679 | PISMOBCH | LOS PADRES | 2021-03-22 | 2021-06-01 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40868600 | 1989-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1989-01-01 | Porcelain | Unknown |  |  |  |  | 0.001567 | 5033.5718
120706502 | E | LC | ETL.5140.TOWR | 40659056 | SACTO | SACRAMENTO | 2021-03-29 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40659056 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Dead End |  |  |  |  | 5.8958e-11 | 1582.1367 | 9.328e-08
120717712 | E | LC | ETL.5540.INSL.CERA | 40638291 | TABLEMTN | NORTH VALLEY | 2021-03-31 |  | ETL.5540 | POE-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40608860 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | Suspension |  |  |  |  | 7.8825e-07 | 4513.7266 | 0.0035579
120718393 | F | LC | ETL.6880.POLE.NWOD | 44324057 | LAKEVLLE | SONOMA | 2021-03-31 |  | ETL.6880 | FULTON-CALISTOGA | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44324057 | 2014-12-10 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | [7 empty] | 1.1883e-06 | 4876.5742
120720493 | E | LC | ETL.5960.INSL | 40887931 | PISMOBCH | LOS PADRES | 2021-03-31 |  | ETL.5960 | DIABLO-GATES #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40863937 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 9.9922e-11 | 131.4725 | 1.3137e-08
120725152 | E | LC | ETL.4100.TOWR | 40653588 | LAKEVLLE | SACRAMENTO | 2021-04-01 |  | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40653588 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-05-29 | Glass Silicone Coated | Suspension |  |  |  |  | 4.3022e-06 | 3088.1243 | 0.013286
120735872 | E | LC | ETL.3830.TOWR | 40865915 | VICTOR | STOCKTON | 2021-03-31 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40865915 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 1.0137e-08 | 2156.2512 | 2.1858e-05
120737346 | E | LC | ETL.7390.POLE.WOOD | 44412207 | LAKEVLLE | SONOMA | 2021-04-02 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44412207 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | Suspension |  |  |  |  | 0.080209
120746575 | E | LC | ETL.8350.INSL.NCER | 45015294 | VICTOR | STOCKTON | 2021-04-05 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45015282 | 2020-05-07 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-05-07 | Glass | Dead End |  |  |  |  | 1.7083e-05
120746575 | E | LC | ETL.8350.INSL.NCER | 45015294 | VICTOR | STOCKTON | 2021-04-05 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45015282 | 2020-05-07 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-05-07 | Glass | Dead End |  |  |  |  | 1.7083e-05
120746575 | E | LC | ETL.8350.INSL.NCER | 45015294 | VICTOR | STOCKTON | 2021-04-05 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 45015282 | 2020-05-07 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-05-07 | Glass | Dead End |  |  |  |  | 1.7083e-05
120757381 | F | LC | ETL.1420.TOWR | 40814356 | SACTO | SACRAMENTO | 2021-04-07 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40814356 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.00011885 | 3071.4875
120757381 | F | LC | ETL.1420.TOWR | 40814356 | SACTO | SACRAMENTO | 2021-04-07 |  | ETL.1420 | DRUM-RIO OSO #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40814356 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-03-30 | Porcelain | Suspension |  |  |  |  | 0.00011885 | 3071.4875
120795725 | F | LC | ETL.5510.TOWR | 40764789 | CONCORD | DIABLO | 2021-04-12 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40764789 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 1.9073e-08 | 4927.8965 | 9.3991e-05
120797464 | E | LC | ETL.5540.TOWR | 40597443 | TABLEMTN | NORTH VALLEY | 2021-04-12 |  | ETL.5540 | POE-RIO OSO | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40597443 | 1950-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | Suspension |  |  |  |  | 1.0086e-06 | 4384.0257 | 0.0044219
120812244 | E | LC | ETL.5310.INSL | 40680115 | PISMOBCH | LOS PADRES | 2021-04-14 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40651382 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 2.7747e-07 | 652.484 | 0.00018104
120812250 | F | LC | ETL.9100.POLE.WOOD | 44191920 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191920 |  | Single Wood Pole | TAP - Tri Arm Post |  | Polymer | [5 empty] | 8.3175e-06 | 2203.3623
120813718 | F | LC | ETL.9100.POLE.WOOD | 44191434 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-26 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove, Completed] | Tier2 |  |  | COMP | [11 empty] | 1.9713e-05 | 2724.3408
120814122 | F | LC | ETL.6690.POLE.NWOD | 44916820 | SACTO | SACRAMENTO | 2021-04-14 | 2021-06-04 | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44916820 | 2020-04-27 | Light Duty Steel Pole | T2N | 2020-04-27 | Polymer | Post |  |  |  |  | 0.008953 | 63.3607
120834059 | F | LC | ETL.5090.TOWR | 40810729 | MOSSLNDG | CENTRAL COAST | 2021-04-17 |  | ETL.5090 | MONTA VISTA-COYOTE SW STA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40810729 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.41994 | 316.4942 | 132.9083
120852723 | E | LC | ETL.6050.TOWR | 40689530 | MOSSLNDG | CENTRAL COAST | 2021-04-20 | 2021-04-26 | ETL.6050 | MOSS LANDING-METCALF | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40689530 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.5574e-08 | 3359.552
120876103 | E | LC | ETL.6470.POLE.WOOD | 40602534 | SACTO | SIERRA | 2021-04-23 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40602534 |  | Single Wood Pole | T2N | 2021-07-16 | Polymer | Post |  |  |  |  | 0.25227 | 158.2723
120880468 | E | LC | ETL.2770.INSL.CERA | 44642307 | CONCORD | EAST BAY | 2021-04-23 |  | ETL.2770 | MORAGA-SAN LEANDRO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40764851 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-08-14 | Ceramic | Suspension |  |  |  |  | 5.3268e-07 | 474.9144 | 0.00025298
120889697 | E | LC | ETL.6890.POLE.NWOD | 44220668 | LAKEVLLE | SONOMA | 2021-04-27 |  | ETL.6890 | FULTON-HOPLAND | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44220668 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | Dead End |  |  |  |  | 0.00024097 | 899.3032 | 0.21671
120921872 | E | LC | ETL.1250.POLE.NWOD | 44770831 | FRESNO | FRESNO | 2021-05-03 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44770831 | 2019-05-31 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-05-31 | Glass | Suspension |  |  |  |  | 2.5261e-08 | 4148.9409 | 0.00010481
120935063 | F | LC | ETL.5330.TOWR | 40863057 | MOSSLNDG | CENTRAL COAST | 2021-04-15 |  | ETL.5330 | MOSS LANDING-COBURN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40863057 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 3.3231e-05 | 208.6439
120943713 | E | LC | ETL.1810.INSL.NCER | 40854183 | EUREKA | HUMBOLDT | 2021-05-05 | 2021-05-18 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
120948232 | E | LC | ETL.4316.TOWR | 40819272 | TABLEMTN | NORTH VALLEY | 2021-04-15 |  | ETL.4316 | PARADISE-TABLE MTN | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40819272 |  | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End |  | Porcelain | Unknown |  |  |  |  | 0.0043351 | 3798.3027 | 16.4661
121022885 | E | LC | ETL.7610.POLE.WOOD | 40691513 | METCALF | SAN JOSE | 2021-05-10 | 2021-11-12 | ETL.7610 | MONTA VISTA-LOS GATOS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40691513 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00066407 | 0.066432
121192124 | E | LC | ETL.3820.TOWR | 40642926 | VICTOR | STOCKTON | 2021-04-16 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40642926 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 5.7648e-05 | 253.1151 | 0.014592
121322941 | E | LC | ETL.4460.INSL | 40693781 | MOSSLNDG | CENTRAL COAST | 2021-04-22 | 2021-11-29 | ETL.4460 | COBURN-LAS AGUILAS SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662771 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 1.1845e-06 | 47.9778 | 5.6831e-05
121322941 | E | LC | ETL.4460.INSL | 40693781 | MOSSLNDG | CENTRAL COAST | 2021-04-22 | 2021-11-29 | ETL.4460 | COBURN-LAS AGUILAS SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662771 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 1.1845e-06 | 47.9778 | 5.6831e-05
121364100 | E | LC | ETL.3750.INSL | 40878971 | CONCORD | EAST BAY | 2021-04-24 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40857800 | 1932-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Dead End |  |  |  |  | 3.9536e-05 | 0.065158 | 2.5761e-06
121367078 | E | LC | ETL.1810.POLE.WDPS | 44322584 | EUREKA | HUMBOLDT | 2021-05-10 | 2021-06-11 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Anchor-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 44322581 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0070627 | 23.8261
121370122 | E | LC | ETL.1820.POLE.WDPS | 44560488 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | PEND
121377605 | F | LC | ETL.8350.POLE.NWOD | 44918809 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44918809 | 2020-03-03 | Light Duty Steel Pole | T-1 - Tri Post | 2020-03-03 | Polymer | Post |  |  |  |  | 6.273e-07 | 668.9188
121378056 | B | LC | ETL.1820.INSL.CERA | 44260561 | EUREKA | HUMBOLDT | 2021-05-21 | 2021-06-14 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562382 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2016-10-03 | Ceramic | Suspension |  |  |  |  | 0.020917
121378056 | B | LC | ETL.1820.INSL.CERA | 44260561 | EUREKA | HUMBOLDT | 2021-05-21 | 2021-06-14 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562382 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2016-10-03 | Ceramic | Suspension |  |  |  |  | 0.020917
121378056 | B | LC | ETL.1820.INSL.CERA | 44260561 | EUREKA | HUMBOLDT | 2021-05-21 | 2021-06-14 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44562382 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2016-10-03 | Ceramic | Suspension |  |  |  |  | 0.020917
121381819 | E | LC | ETL.6500.POLE.WOOD | 40597451 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40597451 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | Pin |  |  |  |  | 0.0012203 | 747.485 | 0.91215
121383518 | F | LC | ETL.8250.POLE.WOOD | 44836568 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44836568 | 2019-08-24 | Single Wood Pole | T-1 - Tri Post | 2019-08-24 | Polymer | Post |  |  |  |  | 1.605e-05 | 1096.4655
121383813 | F | LC | ETL.6760.POLE.WOOD | 40824319 | SACTO | SIERRA | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40824319 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0046279 | 332.2538
121384057 | E | LC | ETL.6760.POLE.WOOD | 40757035 | SACTO | SIERRA | 2021-05-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40757035 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Unknown |  |  |  |  | 0.2259 | 632.8055 | 142.951
121385518 | E | LC | ETL.1650.INSL.NCER | 40689447 | LAKEVLLE | SONOMA | 2021-05-14 | 2021-07-12 | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40659189 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 5.3451e-05 | 3938.675
121385523 | F | LC | ETL.6470.POLE.WOOD | 40760688 | SACTO | SIERRA | 2021-05-11 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40760688 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0036864 | 428.1771
121390911 | F | LC | ETL.6110.TOWR | 40870768 | METCALF | MISSION | 2021-05-15 |  | ETL.6110 | TESLA-METCALF | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40870768 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-11-05 | Glass Silicone Coated | Suspension |  |  |  |  | 2.5959e-07 | 7474.1577
121391936 | F | LC | ETL.6980.POLE.WOOD | 44261318 | LAKEVLLE | HUMBOLDT | 2021-05-17 |  | ETL.6980 | FORT ROSS-GUALALA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44261318 | 2018-09-06 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 2020-05-19 | Glass | Suspension |  |  |  |  | 0.024483 | 356.5904
121404664 | E | LC | ETL.7560.POLE.WOOD | 40870663 | SACTO | SIERRA | 2021-05-20 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40870663 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.095109 | 617.1262 | 58.6943
121405371 | E | LC | ETL.7290.POLE.WOOD | 40701749 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.7290 | KILARC-CEDAR CREEK | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40701749 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.11153 | 178.8524 | 19.9481
121421093 | E | LC | ETL.7290.POLE.WOOD | 40817422 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40817422 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Unknown |  |  |  |  | 0.025446 | 1634.3816 | 41.5882
121428161 | E | LC | ETL.7380.POLE.WOOD | 40771071 | MOSSLNDG | CENTRAL COAST | 2021-05-26 |  | ETL.7380 | LAURELES-OTTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40771071 |  | Single Wood Pole | WB - Wishbone |  | Ceramic | [5 empty] | 0.63167 | 31.6978 | 20.0226
121428748 | F | LC | ETL.1400.POLE.STPS | 44379636 | VICTOR | YOSEMITE | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44379635 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.9197e-05 | 2626.426
121445029 | F | LC | ETL.1400.POLE.STPS | 44806630 | VICTOR | YOSEMITE | 2021-06-01 | 2021-10-04 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44779589 | 2019-06-25 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.3911e-05 | 1242.0833
121474135 | E | LC | ETL.5140.POLE.WDPS | 44552259 | SACTO | SACRAMENTO | 2021-06-04 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44551627 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.011288 | 205.7471 | 2.3225
121475057 | E | LC | ETL.1430.INSL.CERA | 44305009 | SACTO | SACRAMENTO | 2021-06-04 |  | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44304991 | 2016-11-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2016-11-14 | Ceramic | Suspension |  |  |  |  | 0.010296
121475057 | E | LC | ETL.1430.INSL.CERA | 44305009 | SACTO | SACRAMENTO | 2021-06-04 |  | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44304991 | 2016-11-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2016-11-14 | Ceramic | Suspension |  |  |  |  | 0.010296
121486106 | E | LC | ETL.7550.POLE.WOOD | 40614306 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40614306 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00076273 | 2804.2429 | 2.1389
121499781 | E | LC | ETL.6470.POLE.WOOD | 40766639 | SACTO | SIERRA | 2021-05-27 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40766639 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.13309 | 237.4138 | 31.5973
121500279 | E | LC | ETL.5390.TOWR | 40873515 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40873515 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.1711e-06 | 1871.8424 | 0.0021922
121512080 | B | LC | ETL.1350.POLE.WDPS | 44513779 | TABLEMTN |  | 2021-06-09 | 2021-08-02 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121516048 | E | LC | ETL.3720.INSL.NCER | 45099537 | CONCORD | EAST BAY | 2021-06-10 |  | ETL.3720 | SOBRANTE-G #1 | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | HFRA Removal | PEND | 44359232 |  | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2021-05-18 | Glass | Suspension |  |  |  |  | 0.0090087 | 0.066432 | 0.00059847
121517070 | E | LC | ETL.5390.TOWR | 40677357 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40677357 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 3.2487e-06 | 1333.3085 | 0.0043316
121522675 | E | LC | ETL.1440.POLE.WDPS | 45087759 | SACTO | SIERRA | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40689699 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0030713 | 31.7066 | 0.097381
121522988 | B | LC | ETL.4440.POLE.NWOD | 40869374 | TABLEMTN | NORTH VALLEY | 2021-06-11 | 2021-07-08 | ETL.4440 | CARIBOU-TABLE MTN | Ground Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40869374 |  | Lattice Steel Pole | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 0.00014011 | 5999.3906
121524920 | E | LC | ETL.5390.TOWR | 40762590 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762590 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 0.016938 | 379.707 | 6.4314
121526448 | E | LC | ETL.6890.POLE.NWOD | 44712983 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44712983 | 2019-02-16 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-02-16 | Ceramic | Suspension |  |  |  |  | 1.6608e-07 | 3884.5432 | 0.00064514
121533134 | E | LC | ETL.1820.INSL.NCER | 45127546 | EUREKA | HUMBOLDT | 2021-06-14 |  | ETL.1820 | HUMBOLDT-TRINITY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45127512 | 2021-05-20 | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2021-05-20 | Glass | Double Dead End | [5 empty] | 158.2408
121536530 | E | LC | ETL.5510.TOWR | 40862420 | CONCORD | DIABLO | 2021-06-10 |  | ETL.5510 | PITTSBURG-TESLA #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40862420 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 3.7439e-07 | 5086.0254 | 0.0019042
121540047 | B | LC | ETL.1710.POLE.WDPS | 44512090 | MOSSLNDG | CENTRAL COAST | 2021-06-15 | 2021-06-17 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Other | Customer Issue | [Customer Refusal, Completed] |  | Tier 3 | Within Both | COMP | 44510834 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0009951 | 31.6948
121547318 | F | LC | ETL.7212.POLE.STPS | 44286987 | METCALF | SAN JOSE | 2021-06-16 | 2021-07-14 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44286985 | 2015-06-25 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.14469 | 696.7528
121550577 | E | LC | ETL.5980.TOWR | 40753903 | PISMOBCH | LOS PADRES | 2021-06-16 |  | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40753903 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-11-17 | Glass Silicone Coated | Suspension |  |  |  |  | 1.696e-06 | 948.955 | 0.0016094
121551889 | E | LC | ETL.6110.INSL | 40680659 | METCALF | SAN JOSE | 2021-06-16 |  | ETL.6110 | TESLA-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40651766 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 4.4235e-07 | 2631.3333 | 0.001164
121557892 | B | LC | ETL.6480.POLE.NWOD | 44695457 | SACTO | SIERRA | 2021-06-10 | 2021-08-16 | ETL.6480 | COLGATE-CHALLENGE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44695457 | 2018-12-10 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-12-10 | Polymer | Dead End |  |  |  |  | 0.0016666 | 428.1771
121561140 | F | LC | ETL.6750.POLE.WDPS | 44232845 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44232844 | 2012-09-17 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.000475 | 221.5655
121563736 | E | LC | ETL.5290.INSL | 40781630 | PISMOBCH | LOS PADRES | 2021-06-16 |  | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40753063 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.2551e-05 | 214.1697 | 0.0026881
121573104 | E | LC | ETL.7550.POLE.WOOD | 40585241 | LAKEVLLE | HUMBOLDT | 2021-06-18 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40585241 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00137 | 15.8807 | 0.021756
121595994 | F | LC | ETL.6110.TOWR | 40644588 | METCALF | MISSION | 2021-06-18 |  | ETL.6110 | TESLA-METCALF | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40644588 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-10-14 | Glass Silicone Coated | Suspension |  |  |  |  | 1.4186e-07 | 0.20433
121596574 | F | LC | ETL.3770.TOWR | 40662391 | CONCORD | DIABLO | 2021-06-22 | 2021-09-29 | ETL.3770 | SOBRANTE-R #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40662391 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1923-01-01 | Ceramic | Suspension |  |  |  |  | 2.1426e-05 | 221.5946
121601959 | F | LC | ETL.4040.POLE.STPS | 44783293 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44783242 | 2019-07-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00024164 | 2600.6631
121603849 | B | LC | ETL.6770.POLE.WOOD | 40700279 | SACTO | SIERRA | 2021-06-22 | 2021-09-13 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.02869 | 1344.8513
121604379 | E | LC | ETL.5960.TOWR | 40863601 | PISMOBCH | LOS PADRES | 2021-06-24 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40863601 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 3.4963e-05 | 460.378 | 0.016096
121608259 | B | LC | ETL.6040.TOWR | 40651852 | MOSSLNDG | CENTRAL COAST | 2021-06-24 | 2021-07-22 | ETL.6040 | MOSS LANDING-LOS BANOS | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40651852 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2010-11-14 | Ceramic | Suspension |  |  |  |  | 2.1657e-06 | 1457.0034
121628433 | E | LC | ETL.2390.POLE.WDPS | 44391016 | VICTOR | STOCKTON | 2021-06-15 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44391013 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 5.7132e-05 | 4273.2705 | 0.24414
121637381 | F | LC | ETL.8365.POLE.WOOD | 40861083 | EUREKA | HUMBOLDT | 2021-06-22 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40861083 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.036768 | 809.8629
121653363 | E | LC | ETL.6650.POLE.WDPS | 44386939 | TABLEMTN | NORTH VALLEY | 2021-07-02 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44386937 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.2678 | 3328.8765 | 891.4814
121662804 | E | LC | ETL.6470.POLE.WDPS | 44291240 | SACTO | SACRAMENTO | 2021-07-01 |  | ETL.6470 | COLGATE-ALLEGHANY | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44291238 | 2015-10-21 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0026323 | 680.261 | 1.7907
121667181 | F | LC | ETL.4316.POLE.NWOD | 45102881 | TABLEMTN | NORTH VALLEY | 2021-07-06 | 2021-07-28 | ETL.4316 | PARADISE-TABLE MTN | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 45102881 | 2021-04-30 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2021-04-30 | Glass | Suspension |  |  |  |  | 3.449e-05 | 1982.3486
121667769 | E | LC | ETL.6650.POLE.WDPS | 44386905 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44386904 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [8 empty] | 3328.8765
121671134 | F | LC | ETL.6110.TOWR | 40681913 | METCALF | STOCKTON | 2021-07-06 |  | ETL.6110 | TESLA-METCALF | Guy Wire Mark /Indic-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40681913 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-11-05 | Glass Silicone Coated | Suspension |  |  |  |  | 7.2375e-09
121675548 | E | LC | ETL.9240.TOWR | 43249534 | PISMOBCH | LOS PADRES | 2021-07-07 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier3 | Tier 3 | Within Both | PEND | 43249534 |  | LATTICE STEEL TOWER | [9 empty] | 253.3087
121682936 | E | LC | ETL.9240.TOWR | 43249721 | PISMOBCH | LOS PADRES | 2021-07-08 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249721 |  | LATTICE STEEL TOWER | [9 empty] | 288.0655
121684456 | F | LC | ETL.1810.POLE.STPS | 45128064 | EUREKA | HUMBOLDT | 2021-07-03 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 45128014 | 2020-10-20 | 2-Pole Non Wood | 2PS - 2 Pole SUSP
121726974 | B | LC | ETL.1820.INSL.CERA | 40741282 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-04 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553923 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.086843
121726974 | B | LC | ETL.1820.INSL.CERA | 40741282 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-04 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553923 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Suspension |  |  |  |  | 0.086843
121741741 | E | LC | ETL.1710.INSL.NCER | 40901341 | MOSSLNDG | CENTRAL COAST | 2021-07-14 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40876836 | 1972-01-01 | Single Wood Pole | 3P DDE - 3 Pole Double Dead End | 1972-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 0.00034185 | 31.6948 | 0.010835
121745268 | E | LC | ETL.4223.POLE.WOOD | 42567892 | TABLEMTN | NORTH VALLEY | 2021-07-14 |  | ETL.4223 | KANAKA TAP | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42567892 | 2013-01-01 | Single Wood Pole | 3P DV - 3 Pole Double Vertical |  | Ceramic | [5 empty] | 0.00049075 | 490.687 | 0.24081
121760133 | B | LC | ETL.1440.INSL | 40636121 | SACTO | SIERRA | 2021-07-19 | 2021-09-14 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40603748 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.013989
121760133 | B | LC | ETL.1440.INSL | 40636121 | SACTO | SIERRA | 2021-07-19 | 2021-09-14 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40603748 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.013989
121769935 | E | LC | ETL.6280.POLE.WOOD | 40769500 | TABLEMTN | NORTH VALLEY | 2021-07-21 |  | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40769500 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 5.6991e-06 | 6616.2266 | 0.037707
121781031 | F | LC | ETL.2540.POLE.WDPS | 44551366 | MOSSLNDG | CENTRAL COAST | 2021-07-21 | 2021-08-16 | ETL.2540 | METCALF-GREEN VALLEY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44550897 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0090247 | 823.3626
121781356 | E | LC | ETL.9240.TOWR | 43249685 | PISMOBCH | LOS PADRES | 2021-07-22 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249685 |  | LATTICE STEEL TOWER | [9 empty] | 158.4262
121783480 | E | LC | ETL.6220.POLE.WDPS | 44402606 | EUREKA | HUMBOLDT | 2021-07-20 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44402604 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.064991 | 2499.4965 | 162.4456
121803005 | E | LC | ETL.6020.TOWR | 40868972 | TABLEMTN | NORTH VALLEY | 2021-07-26 |  | ETL.6020 | MALIN-ROUND MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40868972 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 9.7097e-07 | 237.3869 | 0.0002305
121807349 | F | LC | ETL.2790.TOWR | 40822492 | CONCORD | EAST BAY | 2021-07-26 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40822492 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 0.00012942 | 0.065147 | 8.4313e-06
121814391 | E | LC | ETL.7130.POLE.WOOD | 40751081 | EUREKA | HUMBOLDT | 2021-07-29 |  | ETL.7130 | HUMBOLDT-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40751081 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.043663 | 94.9585 | 4.1462
121814391 | E | LC | ETL.7130.POLE.WOOD | 40751081 | EUREKA | HUMBOLDT | 2021-07-29 |  | ETL.7130 | HUMBOLDT-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40751081 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Polymer | Dead End |  |  |  |  | 0.043663 | 94.9585 | 4.1462
121824922 | B | LC | ETL.6070.INSL | 40796989 | TABLEMTN | NORTH VALLEY | 2021-07-31 | 2021-10-06 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121860343 | B | LC | ETL.6300.POLE.WOOD | 44191051 | TABLEMTN | NORTH VALLEY | 2021-08-07 | 2021-08-25 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.00070422 | 15.8815
121979152 | E | LC | ETL.2060.POLE.WOOD | 40772268 | LAKEVLLE | SONOMA | 2021-08-31 |  | ETL.2060 | FORT BRAGG-ELK | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40772268 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 2021-08-20 | Glass | Dead End |  |  |  |  | 0.27575 | 15.8807 | 4.3792
122121177 | E | LC | ETL.8405.POLE.WOOD | 42569705 | SACTO | SACRAMENTO | 2021-09-29 |  | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42569705 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.43441 | 2531.4304 | 1099.6708
122331551 | E | LC | ETL.6870.POLE.WOOD | 40664826 | SACTO | SACRAMENTO | 2021-11-06 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40664826 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.067014 | 94.9894 | 6.3656
118437891 | A | LC | ETL.7490.POLE.WDPS | 44743796 | EUREKA | HUMBOLDT | 2020-01-16 | 2020-06-08 | ETL.7490 | MAPLE CREEK-HOOPA | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP | [12 empty] | 0.065148
118442075 | A | LC | ETL.6222.POLE.WOOD | 40825299 | EUREKA | HUMBOLDT | 2020-01-17 | 2020-10-15 | ETL.6222 | FORT SEWARD TAP | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40825299 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0013193
118447053 | E | LC | ETL.5440.POLE.WDPS | 44558409 | TABLEMTN |  | 2020-01-18 | 2020-05-18 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118491682 | F | LC | ETL.4590.TOWR | 40910111 | TABLEMTN | NORTH VALLEY | 2020-02-03 | 2020-02-12 | ETL.4590 | CRESTA-RIO OSO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40910111 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 5.2668e-05 | 414.5687
118575961 | E | LC | ETL.4340.INSL | 40611761 | CONCORD |  | 2020-02-25 | 2021-07-13 | ETL.4340 | BAHIA-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587014 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 0.0005073 | 1395.4297
118575961 | E | LC | ETL.4340.INSL | 40611761 | CONCORD |  | 2020-02-25 | 2021-07-13 | ETL.4340 | BAHIA-MORAGA | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587014 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-02 | Glass Silicone Coated | Suspension |  |  |  |  | 0.0005073 | 1395.4297
118654448 | E | LC | ETL.5240.INSL | 40884965 | METCALF | SAN JOSE | 2020-03-09 |  | ETL.5240 | MONTA VISTA-SARATOGA | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40862831 | 1957-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1957-01-01 | Ceramic | Suspension |  |  |  |  | 0.012564 | 158.2135 | 1.9877
118654448 | E | LC | ETL.5240.INSL | 40884965 | METCALF | SAN JOSE | 2020-03-09 |  | ETL.5240 | MONTA VISTA-SARATOGA | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40862831 | 1957-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-09-25 | Glass | Suspension |  |  |  |  | 0.012564 | 158.2135 | 1.9877
118782391 | E | LC | ETL.8990.TOWR | 40607049 | FRESNO | FRESNO | 2020-04-07 | 2020-11-12 | ETL.8990 | MERCED FALLS-EXCHEQUER | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40607049 | 1929-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-11-08 | Glass | Suspension |  |  |  |  | 2.7745e-08 | 1996.226
118791787 | E | LC | ETL.2760.INSL | 40671361 | CONCORD | EAST BAY | 2020-04-07 | 2021-04-12 | ETL.2760 | MORAGA-OAKLAND J | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118950776 | E | LC | ETL.1430.INSL.CERA | 40633062 | SACTO | SACRAMENTO | 2020-04-27 | 2020-06-03 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118957072 | E | LC | ETL.8650.TOWR | 40660802 | FRESNO | YOSEMITE | 2020-04-23 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40660802 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-12-17 | Glass | Suspension |  |  |  |  | 0.015321 | 18.2586
118976175 | F | LC | ETL.2060.POLE.WOOD | 40875135 | LAKEVLLE | HUMBOLDT | 2020-04-30 |  | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40875135 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 2014-11-12 | Ceramic | Suspension |  |  |  |  | 0.19232 | 0.066432
118999813 | E | LC | ETL.7510.POLE.WOOD | 40667053 | LAKEVLLE | SONOMA | 2020-05-08 | 2020-06-01 | ETL.7510 | MENDOCINO-HARTLEY | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40667053 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 8.5909e-06 | 5098.6011
119004907 | E | LC | ETL.8650.TOWR | 40872816 | FRESNO | YOSEMITE | 2020-05-04 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40872816 | 1929-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2019-11-18 | Glass | Suspension |  |  |  |  | 0.0097588 | 7011.6025
119018159 | E | LC | ETL.8650.TOWR | 40806454 | FRESNO | YOSEMITE | 2020-05-05 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119036739 | E | LC | ETL.6440.POLE.WOOD | 40760020 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-07-21 | ETL.6440 | COLEMAN-RED BLUFF | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760020 |  | Single Wood Pole | T2N | 2020-06-29 | Polymer | Post |  |  |  |  | 0.0073252 | 4421.1396
119041880 | E | LC | ETL.6810.POLE.WOOD | 40658082 | EUREKA | HUMBOLDT | 2020-05-07 |  | ETL.6810 | ESSEX JCT-ORICK | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Zone 1 | HFRA Removal | PEND | 40658082 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.016099
119066641 | E | LC | ETL.7550.POLE.WOOD | 40861258 | LAKEVLLE | HUMBOLDT | 2020-05-22 | 2021-01-15 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
119075471 | E | LC | ETL.4040.POLE.WDPS | 44553626 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2020-07-13 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119086657 | E | LC | ETL.6720.POLE.WOOD | 42578834 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2021-03-03 | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119116571 | F | LC | ETL.1330.TOWR | 40819842 | LAKEVLLE | HUMBOLDT | 2020-05-27 | 2020-12-30 | ETL.1330 | CORTINA-MENDOCINO #1 | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40819842 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension | [5 empty] | 6459.0942
119116571 | F | LC | ETL.1330.TOWR | 40819842 | LAKEVLLE | HUMBOLDT | 2020-05-27 | 2020-12-30 | ETL.1330 | CORTINA-MENDOCINO #1 | Vegetation-Tower | Overgrown | [Cage Clearing, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40819842 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-29 | Porcelain | Suspension | [5 empty] | 6459.0942
119117385 | F | LC | ETL.1400.POLE.NWOD | 44384141 | VICTOR | YOSEMITE | 2020-05-27 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44384141 | 2017-08-17 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2017-08-17 | Ceramic | Suspension |  |  |  |  | 4.7361e-05 | 965.199
119118054 | E | LC | ETL.7140.POLE.WOOD | 41111795 | LAKEVLLE | NORTH BAY | 2020-05-29 | 2021-06-02 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111795 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.023234
119118054 | E | LC | ETL.7140.POLE.WOOD | 41111795 | LAKEVLLE | NORTH BAY | 2020-05-29 | 2021-06-02 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111795 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.023234
119118054 | E | LC | ETL.7140.POLE.WOOD | 41111795 | LAKEVLLE | NORTH BAY | 2020-05-29 | 2021-06-02 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41111795 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.023234
119118872 | F | LC | ETL.6330.POLE.WOOD | 40598388 | TABLEMTN | NORTH VALLEY | 2020-05-28 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40598388 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00049577 | 1502.9633
119119184 | E | LC | ETL.8290.POLE.WOOD | 40667432 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-22 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40667432 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.0039265 | 3057.9141
119119548 | F | LC | ETL.7300.POLE.WOOD | 40752154 | TABLEMTN |  | 2020-06-03 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40752154 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0036087 | 554.6501
119125661 | E | LC | ETL.7300.POLE.WOOD | 40656965 | TABLEMTN |  | 2020-06-03 | 2021-02-22 | ETL.7300 | KILARC-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119152846 | B | LC | ETL.1810.INSL.CERA | 40720033 | EUREKA | HUMBOLDT | 2020-06-11 | 2020-09-17 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322437 |  | 2-Pole Wood | 2P DDE-A - 2 Pole Double Dead End Angle |  | Porcelain | Suspension |  |  |  |  | 0.0056486
119152846 | B | LC | ETL.1810.INSL.CERA | 40720033 | EUREKA | HUMBOLDT | 2020-06-11 | 2020-09-17 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322437 |  | 2-Pole Wood | 2P DDE-A - 2 Pole Double Dead End Angle |  | Porcelain | Suspension |  |  |  |  | 0.0056486
119163037 | F | LC | ETL.2420.POLE.STPS | 44923921 | LAKEVLLE | HUMBOLDT | 2020-06-13 |  | ETL.2420 | MENDOCINO-UKIAH | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 44923818 | 2020-04-25 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.1721e-06 | 254.2747 | 0.00029802
119181124 | E | LC | ETL.7300.POLE.WOOD | 40676515 | TABLEMTN |  | 2020-06-16 | 2021-01-21 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119183109 | F | LC | ETL.5090.TOWR | 40581171 | MOSSLNDG | DE ANZA | 2020-06-16 | 2021-01-11 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581171 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.16282 | 363.9585
119185896 | F | LC | ETL.1810.TOWR | 44321407 | EUREKA | HUMBOLDT | 2020-06-18 | 2021-01-19 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44321407 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 1.6549e-05
119188144 | E | LC | ETL.5780.TOWR | 40821587 | VICTOR | STOCKTON | 2020-06-18 | 2021-06-01 | ETL.5780 | TIGER CREEK-ELECTRA | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40821587 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.9811e-06 | 237.591
119188478 | E | LC | ETL.1430.INSL.NCER | 44934901 | SACTO | SIERRA | 2020-06-19 | 2021-03-05 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40596159 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2019-09-06 | Glass | Dead End |  |  |  |  | 0.00034231 | 5272.9805
119188478 | E | LC | ETL.1430.INSL.NCER | 44934901 | SACTO | SIERRA | 2020-06-19 | 2021-03-05 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40596159 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-04-25 | Glass | Dead End |  |  |  |  | 0.00034231 | 5272.9805
119194432 | E | LC | ETL.6470.POLE.WOOD | 40767328 | SACTO | SIERRA | 2020-06-22 | 2021-07-19 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.042855 | 95.0148
119195364 | F | LC | ETL.6470.POLE.WOOD | 40593293 | SACTO | SIERRA | 2020-06-22 | 2021-07-26 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593293 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.034596 | 727.8687
119195545 | F | LC | ETL.6470.POLE.WOOD | 40658320 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40658320 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.41914 | 174.1689
119198009 | F | LC | ETL.6470.POLE.WOOD | 40766598 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40766598 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.0043254 | 680.261
119204723 | E | LC | ETL.6470.POLE.WOOD | 40664626 | SACTO | SIERRA | 2020-06-23 | 2021-08-04 | ETL.6470 | COLGATE-ALLEGHANY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40664626 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.029358 | 291.1891
119208045 | F | LC | ETL.6890.POLE.WOOD | 40584860 | LAKEVLLE | SONOMA | 2020-06-24 | 2021-02-11 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 2 | Within Both | DLFL | 40584860 | 1948-01-01 | Single Wood Pole | DV - Double Vertical | 2021-03-08 | Glass | Dead End |  |  |  |  | 0.00048663 | 745.8444
119222956 | E | LC | ETL.4590.TOWR | 41083097 | TABLEMTN | NORTH VALLEY | 2020-06-24 | 2021-05-27 | ETL.4590 | CRESTA-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41083097 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.7712e-07 | 2916.0366
119231118 | B | LC | ETL.7360.POLE.WOOD | 40877737 | LAKEVLLE | SONOMA | 2020-06-25 | 2020-08-12 | ETL.7360 | LAKEVILLE #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119231578 | E | LC | ETL.1240.POLE.STPS | 44843351 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2020-08-04 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44843321 | 2019-08-28 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.4562e-09 | 2391.1674
119232543 | E | LC | ETL.4050.POLE.WOOD | 40750653 | LAKEVLLE | SONOMA | 2020-06-29 | 2021-01-13 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750653 | 1970-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-04-14 | Glass | Dead End |  |  |  |  | 0.0010647 | 5287.5088
119236584 | F | LC | ETL.7270.POLE.WOOD | 40908533 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908533 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0059018 | 4367.7598
119311177 | E | LC | ETL.1450.POLE.WDPS | 44552263 | SACTO | SACRAMENTO | 2020-07-01 | 2021-09-30 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 3 | Within Both | COMP | 44551549 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00043839 | 3069.2839 | 1.3455
119313857 | E | LC | ETL.1110.POLE.WDPS | 44423876 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423875 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00041536 | 6664.6621
119315619 | E | LC | ETL.8170.POLE.WOOD | 40906237 | EUREKA | HUMBOLDT | 2020-07-06 | 2021-09-13 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906237 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.064987 | 269.0298
119325741 | F | LC | ETL.6650.POLE.WDPS | 44386833 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-06-16 | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44386831 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0095839 | 491.2338
119341387 | F | LC | ETL.1110.TOWR | 40760091 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-21 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760091 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 2.8092e-05 | 6521.0264
119341754 | B | LC | ETL.6280.POLE.WOOD | 40768774 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2020-10-27 | ETL.6280 | CARIBOU #2 | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40768774 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 3.0662e-05 | 490.3705
119357529 | F | LC | ETL.6280.POLE.WOOD | 40600685 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600685 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 5.0512e-05 | 4065.6267
119363551 | E | LC | ETL.6300.POLE.WOOD | 40824693 | TABLEMTN |  | 2020-07-13 | 2021-08-17 | ETL.6300 | CARIBOU-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824693 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Pin |  |  |  |  | 1.2925e-05 | 2024.5519
119365521 | E | LC | ETL.1820.POLE.NWOD | 44926549 | EUREKA | HUMBOLDT | 2020-06-19 | 2021-04-05 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44926549 | 2020-06-11 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-11 | Glass | Dead End |  |  |  |  | 0.019298 | 79.1467
119468022 | E | LC | ETL.8060.POLE.WOOD | 40586102 | SACTO | SACRAMENTO | 2020-07-17 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586102 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.05494 | 31.7066
119468260 | E | LC | ETL.6880.POLE.WOOD | 40667686 | LAKEVLLE | SONOMA | 2020-07-17 | 2021-08-24 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Rotten | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40667686 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00042554 | 775.2442
119468366 | E | LC | ETL.5970.INSL | 40886019 | PISMOBCH | LOS PADRES | 2020-07-17 | 2020-07-20 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119469887 | F | LC | ETL.1430.TOWR | 40746589 | SACTO | SACRAMENTO | 2020-07-17 | 2021-02-22 | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40746589 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical |  | Ceramic | Post |  |  |  |  | 0.035415 | 158.3103
119474362 | F | LC | ETL.7160.POLE.WOOD | 44871185 | LAKEVLLE | NORTH BAY | 2020-07-20 |  | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871185 | 2019-09-19 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2019-09-19 | Glass | Dead End |  |  |  |  | 0.23317 | 174.0409
119477146 | E | LC | ETL.2060.POLE.WOOD | 40876283 | LAKEVLLE | SONOMA | 2020-07-20 | 2021-08-12 | ETL.2060 | FORT BRAGG-ELK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876283 | 1961-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2021-08-05 | Glass | Suspension |  |  |  |  | 0.20501 | 151.8946
119479634 | F | LC | ETL.8960.POLE.STPS | 44236991 | FRESNO | FRESNO | 2020-07-21 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44236989 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.581e-07
119499513 | F | LC | ETL.6280.POLE.WOOD | 40815744 | TABLEMTN | NORTH VALLEY | 2020-07-24 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40815744 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0001326 | 6607.0406
119556652 | F | LC | ETL.7590.POLE.WOOD | 40665307 | MOSSLNDG | DE ANZA | 2020-08-04 | 2020-09-14 | ETL.7590 | MONTA VISTA-BURNS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 |  |  | COMP
119560947 | F | LC | ETL.7180.POLE.WOOD | 40657346 | LAKEVLLE | NORTH BAY | 2020-08-04 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40657346 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 3.3225e-06 | 117.5681
119577354 | F | LC | ETL.8210.POLE.WOOD | 40907079 | VICTOR | STOCKTON | 2020-08-07 | 2021-09-02 | ETL.8210 | VALLEY SPRINGS #1 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40907079 | 1985-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0087093 | 4654.7056
119603561 | E | LC | ETL.7930.POLE.WOOD | 40825944 | MOSSLNDG | CENTRAL COAST | 2020-08-12 | 2021-01-07 | ETL.7930 | SALINAS-LAURELES | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40825944 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0042496 | 0.065147
119608836 | B | LC | ETL.8650.TOWR | 40646342 | FRESNO | FRESNO | 2020-08-13 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Customer Refusal, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40646342 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1929-01-01 | Porcelain | Suspension |  |  |  |  | 0.0032518 | 50.078
119609167 | F | LC | ETL.5463.TOWR | 40819144 | CONCORD | DIABLO | 2020-08-13 | 2021-04-12 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40819144 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 1.2705e-09 | 616.8689
119613401 | E | LC | ETL.8365.POLE.WOOD | 40906612 | EUREKA | HUMBOLDT | 2020-08-13 | 2021-04-26 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40906612 | 2010-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.035759
119636545 | E | LC | ETL.6310.POLE.WOOD | 40759468 | TABLEMTN | NORTH VALLEY | 2020-08-19 | 2021-08-23 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759468 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.7085e-05 | 3041.8088
119641255 | E | LC | ETL.6310.POLE.WOOD | 40650236 | TABLEMTN | NORTH VALLEY | 2020-08-20 | 2021-08-12 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650236 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 6.4951e-06 | 5214.5394
119643322 | B | LC | ETL.8650.POLE.NWOD | 44420155 | FRESNO | FRESNO | 2020-08-20 | 2020-12-09 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44420155 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0041302 | 207.8215
119647858 | E | LC | ETL.8480.POLE.WOOD | 40679170 | PISMOBCH | LOS PADRES | 2020-08-19 | 2021-04-20 | ETL.8480 | ATASCADERO-CAYUCOS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40679170 | 1954-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1954-01-01 | Polymer | Dead End |  |  |  |  | 0.00034145 | 102.8729
119652818 | F | LC | ETL.4770.TOWR | 40681664 | LAKEVLLE | SONOMA | 2020-08-21 |  | ETL.4770 | GEYSERS #17-FULTON | GO95 / Anti Climb | Clearance | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40681664 | 1982-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 2.3763e-06 | 1472.3439
119669575 | F | LC | ETL.7180.POLE.STPS | 44360974 | LAKEVLLE | NORTH BAY | 2020-08-25 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Tier 2 | Within Both | PEND | 44360973 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.4013e-06 | 242.9024
119684352 | E | LC | ETL.6520.POLE.WOOD | 42562758 | SACTO | SIERRA | 2020-08-20 | 2021-02-18 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119687943 | F | LC | ETL.3800.TOWR | 40681869 | CONCORD | EAST BAY | 2020-08-26 | 2021-04-19 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40681869 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-05-05 | Glass | Double Dead End |  |  |  |  | 5.9031e-08 | 1427.5685
119687943 | F | LC | ETL.3800.TOWR | 40681869 | CONCORD | EAST BAY | 2020-08-26 | 2021-04-19 | ETL.3800 | SOBRANTE-STANDARD OIL SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40681869 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.9031e-08 | 1427.5685
119688147 | F | LC | ETL.9210.POLE.WOOD | 40822442 | MIDWAY | KERN | 2020-08-27 |  | ETL.9210 | TAFT-CUYAMA #2 | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40822442 | 1946-01-01 | Single Wood Pole | T-1 - Tri Post | 1946-01-01 | Polymer | Post |  |  |  |  | 0.045162
119692411 | A | LC | ETL.7590.POLE.NWOD | 44908672 | MOSSLNDG | CENTRAL COAST | 2020-08-30 | 2020-09-24 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44908672 | 2020-05-11 | Light Duty Steel Pole | T1DE - Tri Post Dead End 115 | 2020-09-17 | Polymer | Dead End |  |  |  |  | 0.18334 | 63.351
119719007 | F | LC | ETL.9210.POLE.WOOD | 40583865 | MIDWAY | KERN | 2020-09-03 | 2021-02-25 | ETL.9210 | TAFT-CUYAMA #2 | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40583865 | 1946-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-11-15 | Polymer | Dead End |  |  |  |  | 0.095653
119720039 | F | LC | ETL.6760.POLE.NWOD | 44997686 | SACTO | SIERRA | 2020-08-07 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44997686 | 2020-11-06 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-11-06 | Glass | Double Dead End |  |  |  |  | 0.026374 | 142.5076
119722842 | E | LC | ETL.1710.POLE.WDPS | 44513698 | MOSSLNDG | CENTRAL COAST | 2020-08-06 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44512275 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0038027 | 16.6744 | 0.063407
119727587 | B | LC | ETL.6480.POLE.WOOD | 44695489 | SACTO | SIERRA | 2020-09-04 | 2020-11-17 | ETL.6480 | COLGATE-CHALLENGE | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44695489 | 2018-12-10 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-12-10 | Polymer | Dead End |  |  |  |  | 0.073313 | 664.4426
119752344 | E | LC | ETL.7270.INSL.CERA | 40720532 | TABLEMTN |  | 2020-08-13 |  | ETL.7270 | KESWICK-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40674320 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.044288 | 3233.4868 | 143.2038
119754567 | E | LC | ETL.1110.POLE.NWOD | 42603423 | TABLEMTN | NORTH VALLEY | 2020-08-14 | 2021-07-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42603423 |  | Lattice Steel Pole | DDE - Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.00034681 | 221.5655
119763182 | F | LC | ETL.8240.POLE.WOOD | 40758491 | VICTOR | STOCKTON | 2020-09-14 | 2021-02-09 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40758491 | 1969-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0014308 | 2804.8376
119765579 | E | LC | ETL.6310.POLE.WOOD | 40592306 | TABLEMTN | NORTH VALLEY | 2020-09-08 | 2021-08-17 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592306 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 1.1109e-05 | 1537.4215
119770757 | E | LC | ETL.8650.INSL.CERA | 40833012 | FRESNO | FRESNO | 2020-08-14 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44420143 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0040859 | 6552.5298
119784956 | F | LC | ETL.6490.POLE.WOOD | 40599485 | SACTO | SIERRA | 2020-09-10 |  | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40599485 |  | Single Wood Pole | DV - Double Vertical |  | Ceramic | Other |  |  |  |  | 0.046986 | 3211.3491
119786351 | E | LC | ETL.6230.POLE.WOOD | 44993927 | MOSSLNDG | CENTRAL COAST | 2020-09-18 | 2021-09-01 | ETL.6230 | BURNS-LONE STAR #1 | Damper-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44993927 | 2020-09-03 | Light Duty Steel Pole | T2N | 2020-09-03 | Polymer | Post |  |  |  |  | 0.10886 | 31.7081
119787066 | F | LC | ETL.6690.POLE.NWOD | 44919742 | SACTO | SIERRA | 2020-09-16 | 2021-07-06 | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44919742 | 2020-05-02 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-02 | Glass | Dead End |  |  |  |  | 0.01219 | 63.3607
119800671 | E | LC | ETL.7130.POLE.WOOD | 40577299 | EUREKA | HUMBOLDT | 2020-09-21 |  | ETL.7130 | HUMBOLDT-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40577299 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Ceramic | [5 empty] | 0.44441 | 71.3456 | 31.707
119804054 | E | LC | ETL.1450.INSL.NCER | 40780307 | SACTO | SACRAMENTO | 2020-09-22 | 2021-05-04 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119805971 | F | LC | ETL.1073.POLE.WDPS | 44962141 | VICTOR | STOCKTON | 2020-09-23 | 2021-03-22 | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803739 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00014147 | 19.0429
119817054 | F | LC | ETL.8240.POLE.WOOD | 40654691 | VICTOR | STOCKTON | 2020-09-12 |  | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40654691 | 1995-01-01 | Single Wood Pole | TP - Tri Pin |  | Non Ceramic | Pin |  |  |  |  | 0.0039031 | 3815.678
120013257 | E | LC | ETL.8580.TOWR | 40652834 | PISMOBCH | CENTRAL COAST | 2020-11-10 | 2021-03-10 | ETL.8580 | COALINGA #1-SAN MIGUEL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40652834 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-12-13 | Glass | Suspension |  |  |  |  | 1.3679e-06
120018071 | F | LC | ETL.5934.TOWR | 40818496 | PISMOBCH | FRESNO | 2020-11-10 | 2021-01-11 | ETL.5934 | TEMPLETON-GATES | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40818496 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.00013158
120018071 | F | LC | ETL.5934.TOWR | 40818496 | PISMOBCH | FRESNO | 2020-11-10 | 2021-01-11 | ETL.5934 | TEMPLETON-GATES | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40818496 | 1954-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.00013158
120042180 | E | LC | ETL.1890.INSL.CERA | 40724990 | FRESNO | FRESNO | 2020-11-10 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40682157 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1986-01-01 | Porcelain | Suspension |  |  |  |  | 5.6541e-07
120110085 | F | LC | ETL.3180.TOWR | 43249381 | CONCORD | EAST BAY | 2020-11-16 |  | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 43249381 | 1921-01-01 | LATTICE STEEL TOWER | Unknown |  | Ceramic | Unknown |  |  |  |  | 3.7903e-07 | 128.3416
120120786 | E | LC | ETL.1440.POLE.WOOD | 42572626 | SACTO | SIERRA | 2020-11-30 | 2021-06-16 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 7.1092e-05 | 237.4101
120126718 | F | LC | ETL.7780.POLE.WOOD | 40871811 | LAKEVLLE | HUMBOLDT | 2020-10-07 | 2021-09-28 | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40871811 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 9.8935e-06 | 411.3464
120427377 | B | LC | ETL.7930.SWIT | 40744049 | MOSSLNDG | CENTRAL COAST | 2021-01-13 | 2021-01-14 | ETL.7930 | SALINAS-LAURELES | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 |  |  | COMP | [9 empty] | HIGH VELOCITY INTERRUPTER | Manual
120444850 | A | LC | ETL.1650.POLE.STPS | 44298350 | LAKEVLLE | SONOMA | 2021-01-19 | 2021-01-25 | ETL.1650 | GEYSERS #3-CLOVERDALE | Emergency-Steel | Other | [Replace, Completed] |  | Tier 3 | Within Both | COMP | 44298348 | 2018-05-16 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 8.372e-08 | 3610.0372
120457984 | A | LC | ETL.5220.TOWR | 40593386 | METCALF | SAN JOSE | 2021-01-22 | 2021-01-25 | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593386 | 1963-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2021-03-04 | Glass | Double Dead End |  |  |  |  | 0.047453 | 506.3516
120457984 | A | LC | ETL.5220.TOWR | 40593386 | METCALF | SAN JOSE | 2021-01-22 | 2021-01-25 | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Emergency | Storm Related | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593386 | 1963-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1963-01-01 | Ceramic | Dead End |  |  |  |  | 0.047453 | 506.3516
120526615 | E | LC | ETL.1450.POLE.WDPS | 44558975 | SACTO | SACRAMENTO | 2020-08-24 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 44558463 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0019214 | 1260.556 | 2.422
120612185 | B | LC | ETL.2390.POLE.WDPS | 44391168 | VICTOR | STOCKTON | 2021-03-08 | 2021-06-01 | ETL.2390 | MELONES-CURTIS | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
120663007 | F | LC | ETL.4680.TOWR | 40658939 | LAKEVLLE | SONOMA | 2021-03-19 |  | ETL.4680 | FULTON-IGNACIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40658939 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 8.511e-07 | 697.5563 | 0.00059369
120668315 | F | LC | ETL.4222.POLE.NWOD | 44922950 | TABLEMTN | NORTH VALLEY | 2021-03-20 |  | ETL.4222 | FORBESTOWN TAP | Guy Wire Mark /Indic-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44922950 | 2020-05-09 | Light Duty Steel Pole | 1VP - 1 Vertical | 2020-05-09 | Glass | Dead End | [5 empty] | 537.9951
120679037 | E | LC | ETL.5630.TOWR | 40815731 | TABLEMTN | NORTH VALLEY | 2021-03-23 |  | ETL.5630 | ROCK CREEK-POE | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40815731 | 1950-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-09-18 | Ceramic | Suspension |  |  |  |  | 3.7713e-05 | 3544.0063 | 0.13366
120690084 | F | LC | ETL.6720.POLE.WDPS | 44926546 | TABLEMTN | NORTH VALLEY | 2021-03-25 | 2021-06-18 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 42578821 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 6.5736e-05 | 949.264
120692025 | F | LC | ETL.3830.POLE.NWOD | 45099294 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45099294 | 2015-11-02 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2015-11-02 | Ceramic | Suspension |  |  |  |  | 1.3835e-08 | 554.9735
120699958 | E | LC | ETL.6979.POLE.WDPS | 44312232 | LAKEVLLE | SONOMA | 2021-03-26 |  | ETL.6979 | MONTE RIO-FORT ROSS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44312230 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00045326 | 1867.9512 | 0.84667
120700981 | E | LC | ETL.4040.INSL.CERA | 44784185 | TABLEMTN | NORTH VALLEY | 2021-03-27 | 2021-10-06 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44784116 | 2019-07-14 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | 2019-07-14 | Ceramic | Suspension |  |  |  |  | 5.5143e-05
120700981 | E | LC | ETL.4040.INSL.CERA | 44784185 | TABLEMTN | NORTH VALLEY | 2021-03-27 | 2021-10-06 | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44784116 | 2019-07-14 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | 2019-07-14 | Ceramic | Suspension |  |  |  |  | 5.5143e-05
120708073 | E | LC | ETL.7140.POLE.WOOD | 41111777 | LAKEVLLE | SONOMA | 2021-03-29 | 2021-06-25 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
120713307 | E | LC | ETL.3840.INSL.CERA | 40619704 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40579642 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 7.7919e-05 | 377.268 | 0.029396
120725739 | F | LC | ETL.5140.POLE.NWOD | 44410252 | SACTO | SACRAMENTO | 2021-04-01 | 2021-11-08 | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44410252 | 2015-11-02 | Light Duty Steel Pole | 3P SV - 3 Pole Single Vertical | 2015-11-02 | Ceramic | Suspension |  |  |  |  | 6.1948e-05 | 585.5076
120734121 | F | LC | ETL.6890.POLE.WOOD | 40750150 | LAKEVLLE | SONOMA | 2021-04-02 | 2021-09-23 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40750150 | 1932-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.00066727 | 1851.1217
120736829 | E | LC | ETL.1650.POLE.NWOD | 45033434 | LAKEVLLE | SONOMA | 2021-04-02 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45033434 | 2021-01-23 | Light Duty Steel Pole | T2N | 2021-01-23 | Polymer | Post |  |  |  |  | 3.3843e-09 | 951.7994 | 3.2212e-06
120742469 | F | LC | ETL.1890.TOWR | 40646709 | FRESNO | FRESNO | 2021-03-29 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40646709 | 1982-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2015-12-01 | Ceramic | Suspension |  |  |  |  | 1.0654e-06 | 5667.228 | 0.0060379
120742756 | F | LC | ETL.1350.POLE.STPS | 44282809 | TABLEMTN | NORTH VALLEY | 2021-04-05 |  | ETL.1350 | CRAG VIEW-CASCADE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44282808 | 2015-11-25 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.1836e-05 | 269.0551
120754769 | E | LC | ETL.4440.INSL.CERA | 44283306 | TABLEMTN | NORTH VALLEY | 2021-04-01 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40761877 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-12-22 | Ceramic | Suspension |  |  |  |  | 7.9598e-08 | 365.2195 | 2.9071e-05
120756966 | E | LC | ETL.1730.POLE.WOOD | 40878202 | MOSSLNDG | CENTRAL COAST | 2021-03-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40878202 | 1972-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1972-01-01 | Polymer | Double Dead End |  |  |  |  | 0.0001222 | 0.066432 | 8.1181e-06
120758612 | E | LC | ETL.1350.POLE.STPS | 44273550 | TABLEMTN | NORTH VALLEY | 2021-04-07 | 2021-07-06 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44273547 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 6.234e-05 | 15.8866
120770320 | E | LC | ETL.6370.POLE.WOOD | 40599510 | CONCORD | DIABLO | 2021-04-09 |  | ETL.6370 | CHRISTIE-WILLOW PASS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40599510 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.12047 | 79.1846 | 9.5391
120787009 | E | LC | ETL.8250.POLE.WOOD | 44673342 | VICTOR | STOCKTON | 2021-04-10 | 2021-07-26 | ETL.8250 | CLAY-MARTEL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44673342 | 2018-11-08 | Single Wood Pole | T-1 - Tri Post | 2018-11-08 | Polymer | Post |  |  |  |  | 2.1344e-05 | 2235.5154
120801583 | F | LC | ETL.5300.TOWR | 40587298 | PISMOBCH | LOS PADRES | 2021-04-12 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587298 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-09-17 | Glass | Suspension |  |  |  |  | 0.18843 | 411.8201 | 77.6007
120810865 | F | LC | ETL.9100.POLE.WOOD | 44191282 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-30 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191282 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 3.462e-06 | 2154.311
120813231 | F | LC | ETL.4750.TOWR | 40756494 | LAKEVLLE | SONOMA | 2021-04-14 |  | ETL.4750 | GEYSERS #12-FULTON | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40756494 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Porcelain | Suspension |  |  |  |  | 4.7038e-05 | 2773.1933
120813231 | F | LC | ETL.4750.TOWR | 40756494 | LAKEVLLE | SONOMA | 2021-04-14 |  | ETL.4750 | GEYSERS #12-FULTON | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40756494 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2017-03-07 | Porcelain | Suspension |  |  |  |  | 4.7038e-05 | 2773.1933
120830142 | F | LC | ETL.9250.POLE.WOOD | 40749434 | MIDWAY | KERN | 2021-04-16 | 2021-07-12 | ETL.9250 | TEJON-LEBEC | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40749434 | 1967-01-01 | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | Pin |  |  |  |  | 0.019731 | 9424.9238
120840029 | F | LC | ETL.1070.POLE.WOOD | 40762951 | VICTOR | STOCKTON | 2021-04-12 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40762951 | 1998-01-01 | Single Wood Pole | DDE - Double Dead End | 1957-01-01 | Polymer | Dead End |  |  |  |  | 5.9976e-06 | 2978.6118
120861618 | F | LC | ETL.5790.TOWR | 40664035 | VICTOR | STOCKTON | 2021-04-21 |  | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40664035 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 5.6459e-06 | 1202.2845 | 0.006788
120892049 | E | LC | ETL.6890.POLE.WOOD | 40601401 | LAKEVLLE | SONOMA | 2021-04-27 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40601401 | 1932-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0017532 | 1996.5448 | 3.5004
120899152 | E | LC | ETL.7220.POLE.WOOD | 40767172 | METCALF | SAN JOSE | 2021-04-29 |  | ETL.7220 | JEFFERSON-STANFORD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40767172 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00029735 | 520.3731 | 0.15473
120903610 | E | LC | ETL.3960.TOWR | 40862004 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40862004 | 1941-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 1.1349e-08 | 4702.6406 | 5.337e-05
120903610 | E | LC | ETL.3960.TOWR | 40862004 | PISMOBCH | LOS PADRES | 2021-04-29 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40862004 | 1941-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1951-01-01 | Polymer | Suspension |  |  |  |  | 1.1349e-08 | 4702.6406 | 5.337e-05
120912748 | F | LC | ETL.7100.POLE.WOOD | 40648530 | EUREKA | HUMBOLDT | 2021-05-01 |  | ETL.7100 | HUMBOLDT BAY-RIO DELL JCT | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40648530 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Porcelain | [5 empty] | 0.29336 | 285.2721 | 83.6876
120920663 | E | LC | ETL.6470.POLE.WDPS | 44385193 | SACTO | SACRAMENTO | 2021-05-03 |  | ETL.6470 | COLGATE-ALLEGHANY | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44385190 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.048026 | 680.261 | 32.6703
120921878 | E | LC | ETL.3960.INSL.CERA | 40779708 | PISMOBCH | LOS PADRES | 2021-04-30 | 2021-05-20 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40751483 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 8.2235e-07 | 4005.4612
120923266 | E | LC | ETL.3960.INSL.CERA | 40620288 | PISMOBCH | LOS PADRES | 2021-05-03 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40580089 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 2.343e-09 | 4085.4031 | 9.5722e-06
120948304 | E | LC | ETL.6760.INSL.NCER | 40849898 | SACTO | SACRAMENTO | 2021-05-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40822674 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0030207 | 31.7022 | 0.095763
120949648 | E | LC | ETL.5310.INSL | 40885404 | PISMOBCH | LOS PADRES | 2021-04-19 | 2021-10-13 | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40863079 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 1.182e-05 | 1871.3141 | 0.022118
121322379 | E | LC | ETL.7490.INSL | 40713632 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.7490 | MAPLE CREEK-HOOPA | Conductor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40662168 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Ceramic | Suspension - Post |  |  |  |  | 0.098736 | 0.065148 | 0.0064324
121329011 | E | LC | ETL.1401.POLE.WDPS | 44390918 | VICTOR | STOCKTON | 2021-05-13 |  | ETL.1401 | BEARDSLEY TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44390916 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.002703 | 31.7334 | 0.085775
121329464 | F | LC | ETL.5330.TOWR | 40594154 | MOSSLNDG | CENTRAL COAST | 2021-04-22 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40594154 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 8.384e-07 | 47.5602 | 3.9874e-05
121329464 | F | LC | ETL.5330.TOWR | 40594154 | MOSSLNDG | CENTRAL COAST | 2021-04-22 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40594154 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 8.384e-07 | 47.5602 | 3.9874e-05
121332015 | F | LC | ETL.6770.POLE.WOOD | 40810145 | SACTO | SIERRA | 2021-05-13 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40810145 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.22231 | 237.4101
121361014 | F | LC | ETL.5660.TOWR | 40681921 | CONCORD | MISSION | 2021-04-29 |  | ETL.5660 | SAN RAMON-MORAGA | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40681921 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-03-22 | Glass | Dead End |  |  |  |  | 9.9409e-07 | 763.1666
121361014 | F | LC | ETL.5660.TOWR | 40681921 | CONCORD | MISSION | 2021-04-29 |  | ETL.5660 | SAN RAMON-MORAGA | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40681921 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 9.9409e-07 | 763.1666
121361173 | E | LC | ETL.5660.TOWR | 40857928 | CONCORD | MISSION | 2021-04-29 | 2021-08-30 | ETL.5660 | SAN RAMON-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857928 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 1.8856e-08 | 1397.5155
121361173 | E | LC | ETL.5660.TOWR | 40857928 | CONCORD | MISSION | 2021-04-29 | 2021-08-30 | ETL.5660 | SAN RAMON-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40857928 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Dead End |  |  |  |  | 1.8856e-08 | 1397.5155
121362688 | B | LC | ETL.6720.POLE.NWOD | 44871639 | TABLEMTN | NORTH VALLEY | 2021-05-19 | 2021-06-03 | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44871639 | 2019-08-25 | Light Duty Steel Pole | T1-1A | 2019-08-25 | Polymer | Post |  |  |  |  | 5.6866e-09 | 253.3114
121370641 | E | LC | ETL.5070.TOWR | 40873307 | FRESNO | YOSEMITE | 2021-05-04 |  | ETL.5070 | QUINTO SW STA-WESTLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40873307 | 1947-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1947-01-01 | Ceramic | Suspension |  |  |  |  | 2.2788e-06 | 767.5238 | 0.001749
121379084 | F | LC | ETL.5280.TOWR | 40740430 | PISMOBCH | LOS PADRES | 2021-05-04 |  | ETL.5280 | MORRO BAY-CALIFORNIA FLATS SW STA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40740430 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1955-01-01 | Ceramic | Suspension |  |  |  |  | 9.268e-08 | 5161.2417
121383489 | E | LC | ETL.6890.POLE.NWOD | 44628930 | LAKEVLLE | SONOMA | 2021-05-13 |  | ETL.6890 | FULTON-HOPLAND | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44628930 | 2018-06-13 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-06-13 | Polymer | Suspension - Post |  |  |  |  | 5.9137e-05 | 1094.799 | 0.064743
121383512 | F | LC | ETL.8000.POLE.NWOD | 44179464 | SACTO | SIERRA | 2021-05-11 |  | ETL.8000 | SMARTVILLE-NICOLAUS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44179464 | 2013-08-20 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2013-08-20 | Polymer | Post |  |  |  |  | 0.00029372 | 4324.2319
121385437 | F | LC | ETL.6690.POLE.WOOD | 40664853 | SACTO | SIERRA | 2021-05-14 | 2021-06-25 | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40664853 |  | Single Wood Pole | T-1 - Tri Post | 2015-08-10 | Polymer | Post |  |  |  |  | 0.079981 | 142.4769
121395445 | F | LC | ETL.6660.POLE.NWOD | 44358502 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44358502 | 2016-10-23 | Light Duty Steel Pole | T2N | 2021-03-04 | Polymer | Post |  |  |  |  | 5.1778e-11 | 2996.0371
121398173 | F | LC | ETL.4050.POLE.WOOD | 40584968 | LAKEVLLE | SONOMA | 2021-05-19 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40584968 | 1988-01-01 | Single Wood Pole | SUSP - Suspension (TWR) | 1970-01-01 | Ceramic | Post |  |  |  |  | 0.0017628 | 5287.5088
121401402 | E | LC | ETL.8365.INSL.NCER | 45095057 | EUREKA | HUMBOLDT | 2021-05-26 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 45095009 | 2021-04-21 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-04-21 | Glass | Dead End |  |  |  |  | 0.0054564
121408917 | E | LC | ETL.3840.INSL.NCER | 40779084 | VICTOR | STOCKTON | 2021-05-21 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40750281 | 1927-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 7.2778e-07 | 2131.6895 | 0.0015514
121409331 | F | LC | ETL.7040.POLE.WOOD | 40815259 | TABLEMTN | NORTH VALLEY | 2021-05-24 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40815259 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.06354 | 206.0313
121412436 | E | LC | ETL.1450.POLE.WDPS | 44553676 | SACTO | SACRAMENTO | 2021-05-27 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553168 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00041097 | 0.065152 | 2.6775e-05
121417817 | E | LC | ETL.7490.POLE.NWOD | 44960389 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.7490 | MAPLE CREEK-HOOPA | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44960389 | 2020-07-13 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-07-13 | Glass | Dead End |  |  |  |  | 0.019178 | 189.8608 | 3.6411
121418412 | E | LC | ETL.1401.POLE.WDPS | 44390890 | VICTOR | STOCKTON | 2021-05-25 |  | ETL.1401 | BEARDSLEY TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44390889 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0057521 | 2246.7366 | 12.9235
121419811 | E | LC | ETL.7212.INSL.NCER | 44799077 | METCALF | PENINSULA | 2021-05-27 | 2021-08-30 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44799075 | 2019-07-01 | Single Wood Pole | T-1 - Tri Post | 2019-07-01 | Polymer | Post |  |  |  |  | 0.17472 | 1060.9368
121423049 | F | LC | ETL.6230.POLE.WOOD | 40826873 | MOSSLNDG | CENTRAL COAST | 2021-05-27 | 2021-06-28 | ETL.6230 | BURNS-LONE STAR #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40826873 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.14152 | 15.8866
121428451 | E | LC | ETL.1400.POLE.STPS | 44379639 | VICTOR | YOSEMITE | 2021-05-25 |  | ETL.1400 | DONNELLS-MI-WUK | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44379638 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.9197e-05 | 2626.426 | 0.18174
121472548 | E | LC | ETL.8170.POLE.WOOD | 40602091 | EUREKA | HUMBOLDT | 2021-06-02 |  | ETL.8170 | TRINITY-MAPLE CREEK | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40602091 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-04-21 | Polymer | Dead End |  |  |  |  | 0.019222 | 15.8815 | 0.30527
121475266 | F | LC | ETL.7550.POLE.WOOD | 40600413 | LAKEVLLE | HUMBOLDT | 2021-05-29 | 2021-06-24 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40600413 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 1.028e-05 | 5427.1299
121475473 | F | LC | ETL.7390.POLE.WOOD | 40808769 | LAKEVLLE | HUMBOLDT | 2021-05-28 | 2021-06-24 | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
121489430 | E | LC | ETL.1450.POLE.WDPS | 44553573 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553099 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00091983 | 541.3708 | 0.49797
121491789 | B | LC | ETL.8060.INSL.NCER | 40836944 | SACTO | SACRAMENTO | 2021-06-08 | 2021-08-31 | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810153 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0091795 | 2547.2131
121493780 | F | LC | ETL.5630.TOWR | 40590837 | TABLEMTN | NORTH VALLEY | 2021-06-01 |  | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40590837 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 9.2846e-05 | 6047.0801 | 0.56145
121494677 | B | LC | ETL.8650.INSL.CERA | 40691572 | FRESNO | FRESNO | 2021-06-07 | 2021-08-16 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44420148 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0067397 | 6995.4082
121497070 | B | LC | ETL.4392.INSL.CERA | 41129238 | LAKEVLLE | SONOMA | 2021-06-08 | 2021-08-20 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41129346 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.00096873 | 2219.7998
121497070 | B | LC | ETL.4392.INSL.CERA | 41129238 | LAKEVLLE | SONOMA | 2021-06-08 | 2021-08-20 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41129346 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.00096873 | 2219.7998
121499786 | E | LC | ETL.6220.POLE.WOOD | 40752646 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40752646 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.025019 | 633.9066 | 15.8594
121511142 | E | LC | ETL.5140.POLE.WDPS | 44761223 | SACTO | SACRAMENTO | 2021-06-04 | 2021-07-08 | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40873592 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.023742 | 2531.4304
121512721 | F | LC | ETL.6760.POLE.WOOD | 40596067 | SACTO | SIERRA | 2021-06-05 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40596067 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.11131 | 126.6688
121516220 | E | LC | ETL.6500.INSL.CERA | 43690670 | SACTO | NORTH VALLEY | 2021-06-09 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 43690666 | 2015-08-20 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2015-08-20 | Porcelain | Dead End |  |  |  |  | 0.01652 | 4948.6592 | 81.7511
121516632 | F | LC | ETL.6979.POLE.WOOD | 40587327 | LAKEVLLE | SONOMA | 2021-06-03 |  | ETL.6979 | MONTE RIO-FORT ROSS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40587327 | 1953-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.018624 | 1867.9512 | 34.7893
121518394 | E | LC | ETL.1650.POLE.WOOD | 40587970 | LAKEVLLE | SONOMA | 2021-06-05 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40587970 | 1966-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 1966-01-01 | Porcelain | Suspension |  |  |  |  | 0.00023838 | 4151.2271 | 0.98957
121523651 | E | LC | ETL.1450.POLE.WDPS | 44553499 | SACTO | SACRAMENTO | 2021-06-09 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553151 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00087411 | 1131.3246 | 0.9889
121525695 | E | LC | ETL.1350.POLE.NWOD | 44552244 | TABLEMTN |  | 2021-06-08 | 2021-07-12 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [12 empty] | 1.6473
121536109 | E | LC | ETL.1600.INSL.CERA | 40706289 | LAKEVLLE | SONOMA | 2021-06-09 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40648157 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Porcelain | Suspension |  |  |  |  | 1.7065e-08 | 712.2047 | 1.2154e-05
121536461 | B | LC | ETL.1330.INSL.NCER | 44645416 | LAKEVLLE | HUMBOLDT | 2021-06-14 | 2021-07-29 | ETL.1330 | CORTINA-MENDOCINO #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44645378 | 2018-08-05 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2018-08-05 | Polymer | Dead End - Suspension |  |  |  |  | 0.0006195 | 5715.6968
121536608 | E | LC | ETL.4440.INSL.CERA | 40616982 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591404 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 0.0010761 | 4336.8823 | 4.6668
121540575 | E | LC | ETL.4316.POLE.STPS | 45086484 | TABLEMTN | NORTH VALLEY | 2021-06-09 | 2021-07-01 | ETL.4316 | PARADISE-TABLE MTN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45086347 | 2021-04-30 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 9.2383e-05 | 1123.6886
121544875 | E | LC | ETL.5420.POLE.WDPS | 44562904 | TABLEMTN | NORTH VALLEY | 2021-06-14 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562414 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.012154 | 1028.4974 | 12.4999
121545966 | E | LC | ETL.6861.POLE.WOOD | 40585196 | LAKEVLLE | SONOMA | 2021-06-16 | 2021-09-09 | ETL.6861 | KONOCTI-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40585196 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-11-06 | Polymer | Dead End |  |  |  |  | 2.3516e-05 | 4196.1401
121546100 | E | LC | ETL.6060.TOWR | 40601310 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.6060 | ROUND MTN-TABLE MTN #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40601310 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Non Ceramic | Suspension |  |  |  |  | 9.6191e-06 | 1800.2244 | 0.017316
121546100 | E | LC | ETL.6060.TOWR | 40601310 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.6060 | ROUND MTN-TABLE MTN #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40601310 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 9.6191e-06 | 1800.2244 | 0.017316
121548614 | E | LC | ETL.6720.INSL.CERA | 42579529 | TABLEMTN | NORTH VALLEY | 2021-06-15 | 2021-11-17 | ETL.6720 | DESABLA-CENTERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121555021 | E | LC | ETL.6110.TOWR | 40587592 | METCALF | SAN JOSE | 2021-06-17 | 2021-09-29 | ETL.6110 | TESLA-METCALF | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587592 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 8.0755e-09 | 2901.3721
121560586 | E | LC | ETL.1820.POLE.WDPS | 44562818 | EUREKA | HUMBOLDT | 2021-06-08 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562460 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.94292 | 395.7131 | 373.124
121561515 | E | LC | ETL.6750.POLE.WDPS | 44374928 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44374927 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00026446 | 221.5655 | 0.058595
121568323 | F | LC | ETL.5790.TOWR | 40645135 | VICTOR | STOCKTON | 2021-06-14 |  | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40645135 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 3.2819e-06 | 110.8074 | 0.00036366
121577829 | E | LC | ETL.6110.INSL | 40791498 | METCALF | SAN JOSE | 2021-06-16 |  | ETL.6110 | TESLA-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40761192 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.1048e-08 | 4627.0366 | 5.1118e-05
121580870 | F | LC | ETL.7550.POLE.WOOD | 40750980 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40750980 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.00091359 | 15.8807
121608690 | F | LC | ETL.7550.POLE.WOOD | 40698029 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40698029 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Porcelain | [5 empty] | 9.6298e-05 | 31.7022 | 0.0030528
121622232 | E | LC | ETL.6050.TOWR | 40765362 | MOSSLNDG | CENTRAL COAST | 2021-06-25 |  | ETL.6050 | MOSS LANDING-METCALF | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40765362 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.9679e-05 | 3053.9343 | 0.090639
121623675 | E | LC | ETL.1481.INSL.NCER | 40884545 | LAKEVLLE |  | 2021-06-15 |  | ETL.1481 | LOWER LAKE-HOMESTAKE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40861310 | 1985-01-01 | Single Wood Pole | T1DE - Tri Post Dead End 115 | 1985-01-01 | Polymer | Dead End |  |  |  |  | 0.00047809 | 6824.1045 | 3.2626
121639441 | B | LC | ETL.6070.INSL | 40619354 | TABLEMTN | NORTH VALLEY | 2021-06-30 | 2021-07-27 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40593560 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 8.8171e-05 | 462.5264
121641447 | E | LC | ETL.5490.TOWR | 40746311 | CONCORD | DIABLO | 2021-06-25 |  | ETL.5490 | PITTSBURG-SAN RAMON | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40746311 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.00040638 | 3561.409 | 1.4473
121653518 | E | LC | ETL.6500.POLE.STPS | 44206525 | SACTO | SACRAMENTO | 2021-06-22 |  | ETL.6500 | COLGATE-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44206523 | 2014-07-13 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 7.923e-05 | 79.1957 | 0.0062747
121653596 | E | LC | ETL.1400.POLE.WDPS | 45077522 | VICTOR | YOSEMITE | 2021-07-02 |  | ETL.1400 | DONNELLS-MI-WUK | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40744852 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.009221 | 31.7334 | 0.29261
121669333 | E | LC | ETL.6650.POLE.WDPS | 44386924 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44386922 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0071287 | 2632.3416 | 18.7653
121676035 | E | LC | ETL.7030.POLE.WOOD | 40667978 | TABLEMTN | NORTH VALLEY | 2021-07-07 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40667978 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.016191 | 0.06515 | 0.0010548
121676757 | E | LC | ETL.5960.TOWR | 40658790 | PISMOBCH | LOS PADRES | 2021-07-06 | 2021-10-21 | ETL.5960 | DIABLO-GATES #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40658790 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 1.4497e-05 | 1550.6904 | 0.022481
121679156 | E | LC | ETL.1400.INSL.NCER | 40620400 | VICTOR | YOSEMITE | 2021-07-02 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40580180 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0026421
121679156 | E | LC | ETL.1400.INSL.NCER | 40620400 | VICTOR | YOSEMITE | 2021-07-02 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40580180 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0026421
121685443 | F | LC | ETL.7550.POLE.WOOD | 40876373 | LAKEVLLE | HUMBOLDT | 2021-07-05 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40876373 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 6.8943e-05 | 110.7947 | 0.0076385
121705989 | E | LC | ETL.6020.TOWR | 40817693 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.6020 | MALIN-ROUND MTN #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40817693 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 7.5616e-08 | 759.742 | 5.7449e-05
121720821 | F | LC | ETL.8350.POLE.NWOD | 45096599 | VICTOR | STOCKTON | 2021-07-12 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45096599 | 2021-03-26 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-03-26 | Glass | Dead End |  |  |  |  | 0.00044073 | 175.6506
121737137 | F | LC | ETL.8290.POLE.WOOD | 40592130 | TABLEMTN | NORTH VALLEY | 2021-07-15 | 2021-10-27 | ETL.8290 | VOLTA-DESCHUTES | Road | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592130 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0001324 | 920.9262
121738022 | F | LC | ETL.4221.POLE.NWOD | 44820159 | TABLEMTN | NORTH VALLEY | 2021-07-14 |  | ETL.4221 | SLY CREEK TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44820159 | 2019-05-24 | Light Duty Steel Pole | DDE - Double Dead End | 2020-10-01 | Glass | Double Dead End |  |  |  |  | 2.0305e-05 | 348.1806
121741223 | E | LC | ETL.6020.INSL | 40635016 | TABLEMTN | NORTH VALLEY | 2021-07-14 |  | ETL.6020 | MALIN-ROUND MTN #2 | Conductor-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40601181 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.8066e-05 | 158.2797 | 0.0044423
121743860 | E | LC | ETL.1820.POLE.WDPS | 44560618 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560158 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.84689 | 253.1639 | 214.4023
121746985 | E | LC | ETL.7390.POLE.WOOD | 40666667 | LAKEVLLE | HUMBOLDT | 2021-07-14 | 2021-10-21 | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40666667 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.074153
121785859 | E | LC | ETL.1710.POLE.WDPS | 45074075 | MOSSLNDG | CENTRAL COAST | 2021-07-21 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 42567487 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical | [7 empty] | 0.00029056 | 47.5096 | 0.013804
121792267 | E | LC | ETL.9240.TOWR | 43249599 | PISMOBCH | LOS PADRES | 2021-07-23 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249599 |  | LATTICE STEEL TOWER | [9 empty] | 1871.2655
121797596 | F | LC | ETL.6690.POLE.NWOD | 44916819 | SACTO | SIERRA | 2021-07-26 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44916819 | 2020-05-04 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-04 | Glass | Dead End |  |  |  |  | 0.014604 | 63.3607
121810023 | E | LC | ETL.6950.INSL.NCER | 40640080 | SACTO | SACRAMENTO | 2021-07-28 |  | ETL.6950 | GOLD HILL #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40613768 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.002784 | 617.0629 | 1.7179
121812837 | B | LC | ETL.6070.TOWR | 40760720 | TABLEMTN | NORTH VALLEY | 2021-07-28 | 2021-09-14 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40760720 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 0.0076551 | 190.8412
121816591 | E | LC | ETL.5442.POLE.NWOD | 45120523 | TABLEMTN | NORTH VALLEY | 2021-07-28 |  | ETL.5442 | PIT #7 TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 45120523 | 2021-06-24 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2021-06-24 | Glass | Suspension | [5 empty] | 665.1749
121822187 | F | LC | ETL.6760.POLE.WOOD | 44178366 | SACTO | SIERRA | 2021-07-29 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44178366 | 2015-03-25 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2015-03-25 | Porcelain | Dead End |  |  |  |  | 0.033774 | 1.647
121825042 | F | LC | ETL.6880.POLE.NWOD | 45076257 | LAKEVLLE | NORTH BAY | 2021-07-30 |  | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45076257 | 2020-03-05 | Tubular Steel Pole | DCPOST - Double Circuit Post | 2020-03-05 | Polymer | Post |  |  |  |  | 9.2638e-09 | 15.8859
121890719 | F | LC | ETL.6650.POLE.STPS | 44386873 | TABLEMTN | NORTH VALLEY | 2021-07-13 | 2021-09-30 | ETL.6650 | COTTONWOOD-BENTON #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44386871 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00087994 | 696.4862
121908404 | B | LC | ETL.6280.POLE.WOOD | 40754023 | TABLEMTN | NORTH VALLEY | 2021-08-16 | 2021-09-07 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace, Completed] | Tier2 |  |  | DLFL | [11 empty] | 1.5033e-05 | 31.7104
122020582 | E | LC | ETL.4440.POLE.NWOD | 44190875 | TABLEMTN | NORTH VALLEY | 2021-09-02 |  | ETL.4440 | CARIBOU-TABLE MTN | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44190875 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 0.00042126 | 6034.1842 | 2.542
122057944 | E | LC | ETL.4780.INSL.NCER | 45128987 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129350 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.00034598 | 1332.3551 | 0.46097
122057944 | E | LC | ETL.4780.INSL.NCER | 45128987 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129350 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.00034598 | 1332.3551 | 0.46097
122058471 | E | LC | ETL.4780.INSL.NCER | 45129026 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129370 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 0.0023384 | 240.1402 | 0.56155
122058471 | E | LC | ETL.4780.INSL.NCER | 45129026 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129370 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.0023384 | 240.1402 | 0.56155
122088530 | E | LC | ETL.6470.POLE.WOOD | 40760711 | SACTO | SACRAMENTO | 2021-09-23 |  | ETL.6470 | COLGATE-ALLEGHANY | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40760711 |  | Single Wood Pole | T2N | 2021-07-19 | Polymer | Post |  |  |  |  | 0.0042022 | 205.7058 | 0.86443
122392814 | E | LC | ETL.9040.POLE.WOOD | 40647961 | MIDWAY | FRESNO | 2021-11-06 |  | ETL.9040 | TULE-SPRINGVILLE | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40647961 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.5989e-05 | 3421.446 | 0.054704
118529561 | E | LC | ETL.4750.INSL.CERA | 40786520 | LAKEVLLE |  | 2020-02-13 | 2020-04-21 | ETL.4750 | GEYSERS #12-FULTON | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118543518 | E | LC | ETL.1330.TOWR | 40870938 | LAKEVLLE | SONOMA | 2020-02-17 | 2021-04-12 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870938 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 9.1021e-05 | 2028.8955
118771371 | B | LC | ETL.5090.TOWR | 40660512 | MOSSLNDG | DE ANZA | 2020-04-01 | 2021-07-12 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Hardware-Tower | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40660512 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0071317 | 79.1724
119026160 | F | LC | ETL.6950.POLE.NWOD | 40598499 | SACTO | SIERRA | 2020-05-12 |  | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40598499 |  | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 5.024e-05 | 5239.9517
119088691 | E | LC | ETL.5300.TOWR | 40870323 | PISMOBCH | LOS PADRES | 2020-05-15 | 2020-12-18 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40870323 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 2.6041e-07 | 3768.8535
119101282 | F | LC | ETL.7560.POLE.WOOD | 40766774 | SACTO | SIERRA | 2020-05-20 |  | ETL.7560 | WEIMAR #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
119111313 | F | LC | ETL.5290.TOWR | 40863186 | PISMOBCH | LOS PADRES | 2020-05-26 | 2021-01-19 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863186 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-23 | Glass | Suspension |  |  |  |  | 1.2167e-09 | 1981.7017
119111313 | F | LC | ETL.5290.TOWR | 40863186 | PISMOBCH | LOS PADRES | 2020-05-26 | 2021-01-19 | ETL.5290 | MORRO BAY-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863186 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-01-26 | Ceramic | Suspension |  |  |  |  | 1.2167e-09 | 1981.7017
119116223 | E | LC | ETL.7380.POLE.WOOD | 40617443 | MOSSLNDG | CENTRAL COAST | 2020-05-29 | 2021-08-19 | ETL.7380 | LAURELES-OTTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40617443 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.76728 | 142.4119
119119190 | F | LC | ETL.7290.POLE.WOOD | 40592397 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40592397 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0032722 | 334.5242
119142499 | F | LC | ETL.6330.POLE.WOOD | 40816798 | TABLEMTN | NORTH VALLEY | 2020-06-02 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40816798 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0054806 | 142.736
119150581 | F | LC | ETL.8170.POLE.WOOD | 40906426 | EUREKA | HUMBOLDT | 2020-06-03 | 2021-06-25 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906426 |  | Single Wood Pole | DDE - Double Dead End |  | Porcelain | [5 empty] | 0.0095369 | 31.7207
119155622 | F | LC | ETL.7300.POLE.WOOD | 40825984 | TABLEMTN | NORTH VALLEY | 2020-06-04 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40825984 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00011486 | 5047.3159
119187518 | F | LC | ETL.6280.POLE.WOOD | 40675432 | TABLEMTN | NORTH VALLEY | 2020-06-19 | 2021-09-14 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40675432 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 4.9817e-06 | 411.289
119193856 | E | LC | ETL.3720.TOWR | 40804930 | CONCORD | EAST BAY | 2020-06-18 | 2021-04-12 | ETL.3720 | SOBRANTE-G #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40804930 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 3.1386e-06 | 300.5749
119200319 | F | LC | ETL.6470.POLE.WOOD | 40766632 | SACTO | SIERRA | 2020-06-23 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40766632 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.25214 | 47.5273
119203419 | F | LC | ETL.6480.POLE.NWOD | 45108090 | SACTO | SIERRA | 2020-06-22 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45108090 | 2020-11-14 | Light Duty Steel Pole | T-1 - Tri Post | 2020-11-14 | Polymer | Post | [5 empty] | 1139.0737
119220991 | E | LC | ETL.7520.POLE.WOOD | 40667085 | LAKEVLLE | SONOMA | 2020-06-26 |  | ETL.7520 | MENDOCINO-PHILO JCT-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40667085 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 2.5315e-05 | 2045.5366 | 0.051783
119233756 | F | LC | ETL.9330.TOWR | 40597310 | FRESNO | FRESNO | 2020-06-29 | 2021-04-07 | ETL.9330 | WISHON-COPPERMINE | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40597310 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 6.962e-05
119238612 | F | LC | ETL.6980.POLE.WOOD | 40616631 | LAKEVLLE | SONOMA | 2020-06-30 |  | ETL.6980 | FORT ROSS-GUALALA | Raptor Guard-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40616631 | 1985-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 1953-01-01 | Polymer | Suspension |  |  |  |  | 0.36932 | 174.1901 | 64.332
119295024 | F | LC | ETL.7270.POLE.WOOD | 40906497 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40906497 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0031954 | 996.8419
119295860 | F | LC | ETL.1400.POLE.WDPS | 44776435 | VICTOR | STOCKTON | 2020-07-01 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40643191 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.0049883 | 3654.8457
119300100 | F | LC | ETL.1400.POLE.STPS | 44379627 | VICTOR | YOSEMITE | 2020-07-01 | 2021-03-24 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44379624 | 2017-08-17 | 3-Pole Non Wood | DV-DE - Double Vertical Dead End | [7 empty] | 0.00033822 | 79.1977
119301529 | F | LC | ETL.6900.POLE.WOOD | 41119970 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 41119970 |  | Single Wood Pole | TH - TriAngle Post 70 | [7 empty] | 8.9495e-06 | 285.7849
119315315 | F | LC | ETL.1110.POLE.WDPS | 44424027 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-02-10 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44424026 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00084417 | 4088.4016
119317062 | E | LC | ETL.7300.POLE.WOOD | 40617697 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-03-10 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40617697 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00040889 | 3833.8523
119325121 | E | LC | ETL.6760.POLE.WOOD | 40693327 | SACTO | SACRAMENTO | 2020-07-07 | 2021-03-15 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119329266 | E | LC | ETL.1450.POLE.WDPS | 44549921 | SACTO | SACRAMENTO | 2020-07-01 | 2020-07-10 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 3 | Within Both | DLFL | 44549462 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014358 | 47.5526
119329266 | E | LC | ETL.1450.POLE.WDPS | 44549921 | SACTO | SACRAMENTO | 2020-07-01 | 2020-07-10 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 3 | Within Both | DLFL | 44549462 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0014358 | 47.5526
119332356 | B | LC | ETL.3960.TOWR | 40803639 | PISMOBCH | LOS PADRES | 2020-07-08 | 2020-12-15 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40803639 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 1.7899e-05 | 47.5141
119332838 | B | LC | ETL.6280.POLE.WOOD | 40824590 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2020-10-27 | ETL.6280 | CARIBOU #2 | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40824590 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 8.6636e-06 | 6616.2266
119334755 | E | LC | ETL.1110.POLE.WDPS | 44515803 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-04-12 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44515183 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0047891 | 5350.7036
119338291 | F | LC | ETL.6280.POLE.WOOD | 40876608 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
119339685 | E | LC | ETL.6620.TOWR | 40910972 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-04-12 | ETL.6620 | COTTONWOOD #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40910972 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-10-12 | Glass | Suspension |  |  |  |  | 0.00022706 | 4310.3522
119339685 | E | LC | ETL.6620.TOWR | 40910972 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-04-12 | ETL.6620 | COTTONWOOD #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40910972 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | Unknown |  |  |  |  | 0.00022706 | 4310.3522
119340514 | F | LC | ETL.7300.POLE.WOOD | 40827912 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-02-11 | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40827912 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00022295 | 5356.6348
119350911 | F | LC | ETL.6280.POLE.WOOD | 40600652 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600652 |  | Single Wood Pole | T2N | 2021-08-12 | Polymer | Post |  |  |  |  | 3.8528e-05 | 5520.0938
119353973 | E | LC | ETL.6760.POLE.NWOD | 45072113 | SACTO | SIERRA | 2020-07-10 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Damper-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45072113 | 2020-05-27 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-27 | Glass | Dead End |  |  |  |  | 0.034076 | 205.7564 | 7.0114
119354099 | E | LC | ETL.7212.POLE.WDPS | 44384399 | METCALF | PENINSULA | 2020-07-07 | 2021-05-03 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44384397 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.15292 | 1519.1747
119354542 | E | LC | ETL.8480.POLE.WOOD | 40597525 | PISMOBCH | LOS PADRES | 2020-07-10 | 2021-04-05 | ETL.8480 | ATASCADERO-CAYUCOS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40597525 | 1954-01-01 | Single Wood Pole | T-1 - Tri Post | 2019-07-14 | Polymer | Post |  |  |  |  | 7.8558e-05 | 3039.8909
119356323 | F | LC | ETL.1810.POLE.WDPS | 44322362 | EUREKA | HUMBOLDT | 2020-07-10 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44322360 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0048898
119359661 | F | LC | ETL.7270.POLE.WOOD | 40701693 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2020-11-09 | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40701693 |  | Single Wood Pole | T-1 - Tri Post | 2019-09-10 | Polymer | Post |  |  |  |  | 0.046975 | 1550.618
119379159 | F | LC | ETL.7030.POLE.WOOD | 40759027 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40759027 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.006126 | 15.8837
119379487 | B | LC | ETL.6220.POLE.WOOD | 40810947 | EUREKA | HUMBOLDT | 2020-07-15 | 2020-09-28 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40810947 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Post |  |  |  |  | 0.18542 | 5040.4707
119379487 | B | LC | ETL.6220.POLE.WOOD | 40810947 | EUREKA | HUMBOLDT | 2020-07-15 | 2020-09-28 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40810947 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.18542 | 5040.4707
119469582 | E | LC | ETL.1370.POLE.WOOD | 40598169 | PISMOBCH | LOS PADRES | 2020-07-16 | 2021-08-19 | ETL.1370 | DIVIDE-CABRILLO #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40598169 | 1960-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 1988-01-01 | Porcelain | Suspension |  |  |  |  | 0.019568 | 1272.3468
119470121 | E | LC | ETL.3190.TOWR | 40858895 | TABLEMTN | NORTH VALLEY | 2020-07-17 |  | ETL.3190 | CARIBOU-PALERMO | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40858895 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 0.035082 | 6046.7764 | 212.1353
119471389 | E | LC | ETL.6220.POLE.WOOD | 40769364 | EUREKA | HUMBOLDT | 2020-07-18 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40769364 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.18588 | 1772.7183 | 329.521
119472973 | B | LC | ETL.7030.INSL | 40630428 | TABLEMTN |  | 2020-07-16 | 2020-09-30 | ETL.7030 | HAT CREEK #1-WESTWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40589877 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.011585
119479118 | E | LC | ETL.1450.TOWR | 40602591 | SACTO | SIERRA | 2020-07-20 | 2021-04-19 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602591 | 1955-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | 1955-01-01 | Ceramic | Dead End |  |  |  |  | 4.3035e-06 | 348.1462
119479292 | E | LC | ETL.8960.POLE.STPS | 44236986 | FRESNO | FRESNO | 2020-07-21 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44236985 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.8436e-07
119479314 | E | LC | ETL.9200.POLE.WOOD | 40764574 | MIDWAY | KERN | 2020-07-20 |  | ETL.9200 | TAFT-CUYAMA #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40764574 | 1962-01-01 | Single Wood Pole | TPSRD - Tramp Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.019817
119480904 | E | LC | ETL.6810.POLE.WOOD | 40585287 | EUREKA | HUMBOLDT | 2020-07-21 |  | ETL.6810 | ESSEX JCT-ORICK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Zone 1 | HFRA Removal | PEND | 40585287 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.015714
119491097 | E | LC | ETL.9200.POLE.WOOD | 40586190 | MIDWAY | KERN | 2020-07-22 |  | ETL.9200 | TAFT-CUYAMA #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40586190 | 1962-01-01 | Single Wood Pole | DDE - Double Dead End | 1962-01-01 | Ceramic | Dead End |  |  |  |  | 0.021342
119553804 | E | LC | ETL.5650.INSL | 40840954 | TABLEMTN | NORTH VALLEY | 2020-08-03 | 2021-02-26 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119555077 | B | LC | ETL.5440.POLE.WDPS | 44558392 | TABLEMTN |  | 2020-07-20 | 2020-09-02 | ETL.5440 | PIT #6 JCT-ROUND MTN | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119561081 | F | LC | ETL.8410.POLE.NWOD | 44148106 | LAKEVLLE | HUMBOLDT | 2020-08-05 |  | ETL.8410 | ELK-GUALALA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44148106 | 2014-07-31 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2014-07-31 | Polymer | Post |  |  |  |  | 0.017838 | 713.1954
119563353 | E | LC | ETL.4393.POLE.WDPS | 44199669 | SACTO | SACRAMENTO | 2020-08-05 | 2021-04-14 | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119575422 | E | LC | ETL.5650.TOWR | 40864681 | TABLEMTN | NORTH VALLEY | 2020-08-07 | 2021-03-29 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40864681 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.448e-06 | 1285.8232
119592546 | F | LC | ETL.6330.POLE.NWOD | 40585933 | TABLEMTN | NORTH VALLEY | 2020-08-10 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40585933 | 1998-01-01 | Tubular Steel Pole | TH - TriAngle Post 70 |  | Non Ceramic | Pin |  |  |  |  | 4.758e-06 | 4497.1958
119600880 | F | LC | ETL.7930.POLE.WOOD | 40666662 | MOSSLNDG | CENTRAL COAST | 2020-08-11 |  | ETL.7930 | SALINAS-LAURELES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40666662 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0027599 | 63.3245
119619345 | E | LC | ETL.7560.POLE.NWOD | 44923842 | SACTO | SACRAMENTO | 2020-08-14 | 2020-08-19 | ETL.7560 | WEIMAR #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44923842 | 2019-08-12 | Light Duty Steel Pole | T2N | 2019-08-12 | Polymer | Post |  |  |  |  | 0.01152 | 617.1262
119622036 | E | LC | ETL.6480.POLE.WOOD | 40598490 | SACTO | SACRAMENTO | 2020-08-15 | 2021-06-29 | ETL.6480 | COLGATE-CHALLENGE | Conductor-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40598490 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Polymer | Suspension |  |  |  |  | 0.063158 | 113.9584
119628659 | F | LC | ETL.6870.POLE.NWOD | 40822860 | SACTO | SIERRA | 2020-08-17 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40822860 |  | Light Duty Steel Pole | T-1 - Tri Post | 2013-01-01 | Polymer | Post |  |  |  |  | 0.020963 | 0.065152
119629194 | F | LC | ETL.6870.POLE.WOOD | 40862121 | SACTO | SIERRA | 2020-08-17 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40862121 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.067014 | 94.9894
119632294 | B | LC | ETL.4050.POLE.WDPS | 44558420 | LAKEVLLE |  | 2020-08-13 | 2020-11-10 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119636105 | E | LC | ETL.3500.TOWR | 40579984 | VICTOR | STOCKTON | 2020-08-19 | 2021-11-29 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40579984 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 4.3853e-05 | 806.947 | 0.035387
119643741 | F | LC | ETL.7490.POLE.WOOD | 40827965 | EUREKA | HUMBOLDT | 2020-08-20 | 2021-08-18 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40827965 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-09-29 | Ceramic | Dead End |  |  |  |  | 0.026057 | 94.963
119658721 | E | LC | ETL.4781.TOWR | 40819423 | LAKEVLLE | SONOMA | 2020-08-22 |  | ETL.4781 | GEYSERS #13 TAP | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40819423 | 1979-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 3.6808e-05 | 175.4736 | 0.0064588
119675958 | E | LC | ETL.7560.POLE.WOOD | 40869854 | SACTO | SACRAMENTO | 2020-08-26 | 2021-04-08 | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119696373 | E | LC | ETL.6300.INSL | 40855113 | TABLEMTN |  | 2020-08-29 | 2021-08-19 | ETL.6300 | CARIBOU-WESTWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826509 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper |  | Ceramic | Pin |  |  |  |  | 5.3047e-06 | 31.6978
119719914 | F | LC | ETL.5452.TOWR | 40804947 | CONCORD | DIABLO | 2020-06-22 | 2021-01-20 | ETL.5452 | CONTRA COSTA-MORAGA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40804947 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2013-01-01 | Ceramic | Suspension |  |  |  |  | 2.076e-07 | 31.7066
119721478 | F | LC | ETL.6440.POLE.WOOD | 41144161 | TABLEMTN | NORTH VALLEY | 2020-07-30 |  | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41144161 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0094413 | 4927.5908
119722725 | E | LC | ETL.6440.POLE.NWOD | 44928283 | TABLEMTN | NORTH VALLEY | 2020-08-04 | 2020-09-14 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Non-HFTD | Non-HFRA | DLFL | 44928283 | 2020-06-20 | Light Duty Steel Pole | T-1 - Tri Post | 2020-06-20 | Polymer | Post |  |  |  |  | 0.0004834
119723023 | F | LC | ETL.7260.POLE.WOOD | 40867989 | TABLEMTN | NORTH VALLEY | 2020-08-11 |  | ETL.7260 | KESWICK-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40867989 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 1.243e-05 | 648.9557
119723356 | F | LC | ETL.1350.POLE.STPS | 44994608 | TABLEMTN | NORTH VALLEY | 2020-08-07 | 2021-07-06 | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44993924 | 2020-06-16 | 3-Pole Non Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 5.1506e-05 | 411.4229
119726279 | E | LC | ETL.7490.POLE.NWOD | 44735711 | EUREKA | HUMBOLDT | 2020-08-12 |  | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44735711 | 2019-03-19 | Light Duty Steel Pole | 3P DV - 3 Pole Double Vertical | 2019-03-19 | Polymer | Post |  |  |  |  | 0.00020948 | 47.5141 | 0.0099535
119743253 | E | LC | ETL.1600.TOWR | 40650792 | LAKEVLLE | SONOMA | 2020-09-10 | 2021-03-29 | ETL.1600 | FULTON-PUEBLO | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650792 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Polymer | Suspension |  |  |  |  | 2.3264e-06 | 0.065159
119751605 | E | LC | ETL.4220.POLE.WDPS | 44942608 | TABLEMTN | NORTH VALLEY | 2020-08-04 |  | ETL.4220 | WOODLEAF-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | PEND | 42568045 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.010746 | 1328.9435 | 14.2807
119754627 | F | LC | ETL.7780.POLE.WOOD | 40605857 | LAKEVLLE | HUMBOLDT | 2020-09-11 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40605857 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 1.0086e-05 | 174.0688
119769765 | B | LC | ETL.8170.POLE.WOOD | 40588786 | EUREKA | HUMBOLDT | 2020-09-14 | 2020-11-02 | ETL.8170 | TRINITY-MAPLE CREEK | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40588786 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Ceramic | [5 empty] | 0.21046 | 79.1467
119772868 | F | LC | ETL.6440.POLE.NWOD | 44744774 | TABLEMTN | NORTH VALLEY | 2020-08-25 |  | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44744774 | 2019-04-03 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2019-04-03 | Polymer | Post |  |  |  |  | 0.00015987 | 4800.9653
119775155 | F | LC | ETL.6760.POLE.WOOD | 40757035 | SACTO | SIERRA | 2020-09-08 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40757035 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Unknown |  |  |  |  | 0.2259 | 632.8055
119811211 | F | LC | ETL.3530.TOWR | 40651033 | PISMOBCH | LOS PADRES | 2020-08-14 | 2021-01-28 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40651033 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1952-01-01 | Porcelain | Suspension |  |  |  |  | 5.8354e-07 | 2266.824
119816221 | F | LC | ETL.1421.POLE.NWOD | 44814409 | SACTO | SIERRA | 2020-08-29 | 2021-05-23 | ETL.1421 | DUTCH FLAT #2 TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44814409 | 2019-06-04 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-06-04 | Glass | Suspension |  |  |  |  | 1.077e-05 | 664.5352
119839967 | F | LC | ETL.6760.POLE.WOOD | 40813447 | SACTO | SIERRA | 2020-09-08 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40813447 |  | Single Wood Pole | TAP - Tri Arm Post | 2020-05-22 | Polymer | Post |  |  |  |  | 0.01795 | 94.9894
119850359 | F | LC | ETL.8365.POLE.WOOD | 40906587 | EUREKA | HUMBOLDT | 2020-09-16 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40906587 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0060746
119876247 | A | LC | ETL.6880.POLE.WOOD | 40912459 | LAKEVLLE | SONOMA | 2020-10-06 | 2020-10-09 | ETL.6880 | FULTON-CALISTOGA | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40912459 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2020-03-03 | Glass | Suspension |  |  |  |  | 0.0076165 | 1709.667
119887621 | E | LC | ETL.1430.INSL | 40684689 | SACTO | SACRAMENTO | 2020-10-05 | 2021-03-29 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119892266 | A | LC | ETL.6480.POLE.WOOD | 40598507 | SACTO | SACRAMENTO | 2020-10-12 | 2020-10-21 | ETL.6480 | COLGATE-CHALLENGE | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40598507 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.20573 | 2072.3279
119967816 | E | LC | ETL.5390.INSL.CERA | 40788834 | TABLEMTN | NORTH VALLEY | 2020-08-28 | 2021-01-11 | ETL.5390 | PIT #1-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119983714 | F | LC | ETL.6220.POLE.WOOD | 40661911 | EUREKA | HUMBOLDT | 2020-11-02 | 2021-02-04 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40661911 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.21191
119995716 | F | LC | ETL.7030.POLE.WOOD | 40676171 | TABLEMTN | NORTH VALLEY | 2020-10-05 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40676171 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Pin |  |  |  |  | 0.011163 | 4401.856
120088937 | E | LC | ETL.8060.POLE.WOOD | 40770670 | SACTO | SIERRA | 2020-11-23 | 2021-05-23 | ETL.8060 | SPAULDING-SUMMIT | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40770670 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | [5 empty] | 0.072811 | 0.065152
120131266 | F | LC | ETL.1820.POLE.WOOD | 44559958 | EUREKA | HUMBOLDT | 2020-12-04 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
120164729 | F | LC | ETL.6280.POLE.NWOD | 40824580 | TABLEMTN | NORTH VALLEY | 2020-12-07 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40824580 |  | Light Duty Steel Pole | T2N | 2021-09-14 | Polymer | Post |  |  |  |  | 1.3698e-05 | 5142.6284
120238335 | F | LC | ETL.6280.POLE.NWOD | 44259038 | TABLEMTN | NORTH VALLEY | 2020-12-02 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44259038 | 2020-07-16 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2020-07-16 | Polymer | Post |  |  |  |  | 7.8849e-08 | 158.2282
120255824 | E | LC | ETL.6240.POLE.NWOD | 40652088 | MOSSLNDG | CENTRAL COAST | 2021-01-04 | 2021-08-17 | ETL.6240 | BURNS-LONE STAR #2 | Switch-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40652088 |  | Light Duty Steel Pole | FSS - Field Switch Structure | [7 empty] | 0.034278 | 1123.7659
120452175 | E | LC | ETL.5140.INSL | 40689270 | SACTO | SACRAMENTO | 2021-01-21 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40659056 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Dead End |  |  |  |  | 5.8958e-11 | 1582.1367 | 9.328e-08
120472031 | A | LC | ETL.7640.POLE.WOOD | 44564172 | TABLEMTN | NORTH VALLEY | 2021-01-27 | 2021-02-01 | ETL.7640 | MTN GATE JCT-CASCADE | Emergency | Storm Related | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564172 | 2019-07-18 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-07-18 | Glass | Double Dead End | [5 empty] | 47.5422
120558950 | E | LC | ETL.1450.POLE.WOOD | 44212217 | SACTO | SIERRA | 2020-10-06 | 2021-11-18 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0069198 | 0.065152 | 0.00045083
120670231 | E | LC | ETL.6521.POLE.WOOD | 40767543 | SACTO | SACRAMENTO | 2021-03-19 |  | ETL.6521 | NARROWS #2 TAP | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40767543 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 4.853e-05 | 2836.0979 | 0.13764
120676072 | F | LC | ETL.1710.TOWR | 40816121 | MOSSLNDG | CENTRAL COAST | 2021-03-22 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40816121 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-04-23 | Glass | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147 | 4.5491e-09
120676072 | F | LC | ETL.1710.TOWR | 40816121 | MOSSLNDG | CENTRAL COAST | 2021-03-22 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40816121 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147 | 4.5491e-09
120714510 | B | LC | ETL.5630.TOWR | 40758304 | TABLEMTN | NORTH VALLEY | 2021-03-30 | 2021-04-15 | ETL.5630 | ROCK CREEK-POE | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758304 | 1958-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1958-01-01 | Ceramic | Other |  |  |  |  | 1.1336e-05 | 5382.2134
120719350 | E | LC | ETL.6760.POLE.WOOD | 40674395 | SACTO | SACRAMENTO | 2021-03-31 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40674395 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0075465 | 221.5243 | 1.6717
120725101 | E | LC | ETL.6040.TOWR | 40863545 | MOSSLNDG | CENTRAL COAST | 2021-04-01 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Structure-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40863545 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.6079e-07 | 1287.725 | 0.00020706
120726758 | B | LC | ETL.3840.INSL.CERA | 40877453 | VICTOR | STOCKTON | 2021-03-25 | 2021-05-24 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40856513 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 1.7446e-07 | 5336.0039
120755737 | F | LC | ETL.1530.POLE.NWOD | 40809718 | SACTO | SIERRA | 2021-03-25 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40809718 | 1980-01-01 | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 4.384e-07 | 142.4317 | 6.2442e-05
120757545 | F | LC | ETL.5650.TOWR | 40819298 | TABLEMTN | NORTH VALLEY | 2021-04-07 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40819298 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-07-06 | Glass | Suspension |  |  |  |  | 1.2697e-05 | 2426.0139 | 0.030802
120769542 | E | LC | ETL.8350.POLE.NWOD | 44918783 | VICTOR | STOCKTON | 2021-04-08 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44918783 | 2020-03-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-03-03 | Polymer | Dead End |  |  |  |  | 2.1343e-05 | 931.735 | 0.019886
120772670 | F | LC | ETL.3820.TOWR | 40642808 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40642808 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.071e-07 | 5398.1479
120773344 | E | LC | ETL.6030.TOWR | 40655329 | MIDWAY | KERN | 2021-04-09 | 2021-05-18 | ETL.6030 | MIDWAY-WHIRLWIND | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40655329 | 1973-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-12-09 | Glass Silicone Coated | Suspension |  |  |  |  | 3.4984e-06 | 7017.4551
120785595 | E | LC | ETL.8365.POLE.NWOD | 44974327 | EUREKA | HUMBOLDT | 2021-04-09 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44974327 | 2020-08-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-08-01 | Glass | Dead End |  |  |  |  | 0.00018494 | 1139.0485 | 0.21065
120785706 | E | LC | ETL.5510.TOWR | 40650652 | CONCORD | DIABLO | 2021-04-10 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40650652 | 1961-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1953-01-01 | Ceramic | Dead End |  |  |  |  | 4.6165e-09 | 4234.8496 | 1.955e-05
120803554 | E | LC | ETL.3830.TOWR | 40579570 | VICTOR | STOCKTON | 2021-04-12 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40579570 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 6.2531e-06 | 5451.7767 | 0.034091
120812392 | E | LC | ETL.4040.POLE.STPS | 44647095 | TABLEMTN | NORTH VALLEY | 2021-04-14 | 2021-09-14 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44646894 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0049403 | 3420.8389
120814048 | E | LC | ETL.4316.TOWR | 40815553 | TABLEMTN | NORTH VALLEY | 2021-04-14 |  | ETL.4316 | PARADISE-TABLE MTN | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier2 | Tier 2 | Within Both | PEND | 40815553 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Suspension |  |  |  |  | 0.044083 | 4386.7925 | 193.3817
120815744 | E | LC | ETL.5300.INSL.NCER | 44660806 | PISMOBCH | LOS PADRES | 2021-04-08 | 2021-10-13 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40689432 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-09-17 | Glass | Suspension |  |  |  |  | 1.1861e-05 | 4765.5547 | 0.056523
120819620 | F | LC | ETL.1530.TOWR | 40581059 | SACTO | SIERRA | 2021-04-14 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40581059 | 1923-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 7.5402e-06 | 3701.6848
120820572 | F | LC | ETL.2740.TOWR | 40644201 | CONCORD | DIABLO | 2021-04-14 |  | ETL.2740 | MORAGA-OAKLAND #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40644201 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 0.028775 | 0.065152 | 0.0018747
120828273 | E | LC | ETL.3750.TOWR | 40580981 | CONCORD | DIABLO | 2021-04-16 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40580981 | 1922-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.3602e-07 | 23.8277
120842451 | F | LC | ETL.4870.TOWR | 40746663 | FRESNO | FRESNO | 2021-04-19 |  | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40746663 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 4.5038e-08 | 6632.0591 | 0.00029869
120852037 | E | LC | ETL.1073.POLE.STPS | 44385270 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.1073 | MI-WUK-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44385269 | 2017-08-17 | 3-Pole Non Wood | DV-DE - Double Vertical Dead End | [7 empty] | 8.8031e-06 | 15.88 | 0.00013979
120868696 | E | LC | ETL.1860.POLE.WOOD | 40811023 | LAKEVLLE | SONOMA | 2021-04-22 |  | ETL.1860 | IGNACIO-LAS GALLINAS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | HFRA Removal | PEND | 40811023 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 2.1213e-06 | 15.8851 | 3.3697e-05
120873894 | B | LC | ETL.4880.INSL | 40726377 | FRESNO | FRESNO | 2021-04-21 | 2021-06-24 | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40684265 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.6528e-07 | 5556.3848
120879452 | E | LC | ETL.4040.POLE.STPS | 44647075 | TABLEMTN | NORTH VALLEY | 2021-04-24 | 2021-08-05 | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44646838 | 2018-08-17 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.00066038 | 206.9966
120897043 | E | LC | ETL.5390.TOWR | 41107619 | TABLEMTN | NORTH VALLEY | 2021-04-28 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41107619 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.9093e-05 | 458.8391 | 0.0087608
120899929 | E | LC | ETL.6640.POLE.WOOD | 40667500 | TABLEMTN | NORTH VALLEY | 2021-04-29 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40667500 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.0065058 | 933.8852 | 6.0757
120913193 | E | LC | ETL.1450.POLE.NWOD | 45095745 | SACTO | SIERRA | 2021-05-01 |  | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45095745 |  | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 1.3749e-06 | 47.5273 | 6.5347e-05
120935602 | E | LC | ETL.3960.INSL.CERA | 40779708 | PISMOBCH | LOS PADRES | 2021-04-15 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40751483 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 8.2235e-07 | 4005.4612 | 0.0032939
120949837 | E | LC | ETL.6470.POLE.NWOD | 44398579 | SACTO | SIERRA | 2021-05-07 |  | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44398579 | 2017-05-18 | Light Duty Steel Pole | T2N | 2017-05-18 | Polymer | Dead End |  |  |  |  | 0.018991 | 1408.1655 | 26.7425
121187752 | F | LC | ETL.1810.POLE.WDPS | 44322738 | EUREKA | HUMBOLDT | 2021-05-10 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44322737 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.9654e-05 | 0.065148
121187798 | E | LC | ETL.7630.POLE.WOOD | 40770566 | LAKEVLLE | SONOMA | 2021-05-11 |  | ETL.7630 | MONTE RIO-FULTON | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40770566 | 1952-01-01 | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.021613 | 85.493 | 1.8478
121322920 | F | LC | ETL.3500.TOWR | 40803566 | VICTOR | STOCKTON | 2021-04-21 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40803566 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 0.00029931 | 6855.1987 | 2.0518
121336717 | E | LC | ETL.6890.POLE.WOOD | 40587771 | LAKEVLLE | SONOMA | 2021-04-24 |  | ETL.6890 | FULTON-HOPLAND | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40587771 | 1948-01-01 | Single Wood Pole | DV - Double Vertical | 2021-03-12 | Glass | Double Dead End |  |  |  |  | 0.00057675 | 745.8444 | 0.43017
121340493 | E | LC | ETL.6470.POLE.WOOD | 40664738 | SACTO | SACRAMENTO | 2021-05-15 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40664738 |  | Single Wood Pole | T2N | 2021-07-16 | Polymer | Post |  |  |  |  | 0.11199 | 126.6309 | 14.1815
121342838 | E | LC | ETL.7490.POLE.WOOD | 40752761 | EUREKA | HUMBOLDT | 2021-05-15 |  | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40752761 |  | Single Wood Pole | T2N | 2021-08-01 | Polymer | Post |  |  |  |  | 0.033915 | 0.065148 | 0.0022095
121351713 | E | LC | ETL.8480.INSL.NCER | 40691449 | PISMOBCH | LOS PADRES | 2021-05-18 |  | ETL.8480 | ATASCADERO-CAYUCOS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40660688 | 2007-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2007-01-01 | Polymer | Post |  |  |  |  | 0.00012515 | 2751.8838 | 0.34439
121362585 | E | LC | ETL.6130.TOWR | 40664504 | VICTOR | STOCKTON | 2021-05-19 |  | ETL.6130 | TRACY-LOS BANOS | Structure-Tower | Anti-Climbing Guard | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40664504 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Glass | Suspension |  |  |  |  | 2.9797e-09 | 1777.1232
121363274 | F | LC | ETL.3500.TOWR | 40579965 | VICTOR | STOCKTON | 2021-04-22 | 2021-10-14 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40579965 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 6.9774e-05 | 6601.4917 | 0.46061
121368326 | E | LC | ETL.9340.POLE.NWOD | 44844646 | FRESNO | YOSEMITE | 2021-05-03 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44844646 | 2019-09-29 | Light Duty Steel Pole | T-1 - Tri Post | 2019-09-29 | Porcelain | Post |  |  |  |  | 0.0023187 | 5284.1674 | 12.2526
121374597 | E | LC | ETL.4580.TOWR | 40816767 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40816767 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Porcelain | Suspension |  |  |  |  | 1.0682e-07 | 3559.869 | 0.00038026
121374597 | E | LC | ETL.4580.TOWR | 40816767 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40816767 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.0682e-07 | 3559.869 | 0.00038026
121378959 | F | LC | ETL.1070.POLE.WOOD | 40644824 | VICTOR | YOSEMITE | 2021-05-05 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40644824 | 1957-01-01 | Single Wood Pole | T-1 - Tri Post | 1957-01-01 | Polymer | Suspension |  |  |  |  | 4.0646e-05 | 1809.5526
121381200 | F | LC | ETL.8350.POLE.NWOD | 44920073 | VICTOR | STOCKTON | 2021-05-08 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44920073 | 2020-01-15 | Light Duty Steel Pole | T-1 - Tri Post | 2020-01-15 | Polymer | Post |  |  |  |  | 2.9002e-07 | 95.3431
121382867 | F | LC | ETL.8000.POLE.NWOD | 44180742 | SACTO | SIERRA | 2021-05-11 |  | ETL.8000 | SMARTVILLE-NICOLAUS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44180742 | 2013-08-20 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2013-08-20 | Polymer | Post |  |  |  |  | 0.00016483 | 4118.7144
121383295 | E | LC | ETL.6470.POLE.WOOD | 44398861 | SACTO | SIERRA | 2021-05-10 |  | ETL.6470 | COLGATE-ALLEGHANY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44398861 | 2017-04-26 | Single Wood Pole | T-1 - Tri Post | 2017-04-26 | Polymer | Post |  |  |  |  | 0.043291 | 664.4426 | 28.7647
121383972 | F | LC | ETL.1820.POLE.WDPS | 44562301 | EUREKA | HUMBOLDT | 2021-05-22 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40581876 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.022822 | 63.351 | 1.4458
121385593 | F | LC | ETL.1650.POLE.WOOD | 40659189 | LAKEVLLE | SONOMA | 2021-05-14 | 2021-07-08 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40659189 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 5.3451e-05 | 3938.675
121399752 | E | LC | ETL.1710.POLE.WDPS | 44513711 | MOSSLNDG | CENTRAL COAST | 2021-05-25 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Crossarm-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44512232 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.005666 | 31.6948 | 0.17958
121403433 | F | LC | ETL.6870.POLE.WOOD | 40751812 | SACTO | SIERRA | 2021-05-19 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40751812 |  | Light Duty Steel Pole | T-1 - Tri Post | 1966-01-01 | Ceramic | Post |  |  |  |  | 0.0028691 | 0.065152
121405315 | F | LC | ETL.7290.POLE.WOOD | 40809929 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40809929 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.023009 | 189.9176
121405322 | E | LC | ETL.8290.POLE.NWOD | 44949894 | TABLEMTN | NORTH VALLEY | 2021-05-20 | 2021-06-11 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44949894 | 2019-06-10 | Light Duty Steel Pole | T2N | 2019-06-10 | Polymer | Post |  |  |  |  | 4.7149e-07 | 3010.644
121405590 | E | LC | ETL.6640.POLE.WOOD | 40809873 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40809873 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.015466 | 0.066431 | 0.0010274
121405620 | F | LC | ETL.7000.POLE.WOOD | 40809576 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.7000 | HAMILTON BRANCH-CHESTER | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40809576 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00019949 | 980.6759
121428832 | E | LC | ETL.1710.INSL.CERA | 42567477 | MOSSLNDG | CENTRAL COAST | 2021-05-26 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42567475 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical |  | Ceramic | Double Dead End |  |  |  |  | 0.00013371
121428832 | E | LC | ETL.1710.INSL.CERA | 42567477 | MOSSLNDG | CENTRAL COAST | 2021-05-26 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42567475 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical |  | Ceramic | Double Dead End |  |  |  |  | 0.00013371
121428832 | E | LC | ETL.1710.INSL.CERA | 42567477 | MOSSLNDG | CENTRAL COAST | 2021-05-26 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42567475 |  | 3-Pole Wood | 3P SV - 3 Pole Single Vertical |  | Ceramic | Double Dead End |  |  |  |  | 0.00013371
121436203 | E | LC | ETL.6220.POLE.WOOD | 40586727 | EUREKA | HUMBOLDT | 2021-05-27 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40586727 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.1339 | 332.2581 | 44.4897
121447470 | B | LC | ETL.5980.INSL | 40894129 | PISMOBCH | LOS PADRES | 2021-06-02 | 2021-06-28 | ETL.5980 | DIABLO-MIDWAY #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870391 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.1268e-10 | 885.721
121452554 | F | LC | ETL.1400.POLE.STPS | 44382145 | VICTOR | YOSEMITE | 2021-05-25 | 2021-09-02 | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44382144 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.9991e-05 | 79.1977
121472543 | F | LC | ETL.1710.TOWR | 40605354 | MOSSLNDG | CENTRAL COAST | 2021-06-03 | 2021-06-23 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40605354 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-06 | Glass | Dead End |  |  |  |  | 6.9828e-08 | 0.065147
121472543 | F | LC | ETL.1710.TOWR | 40605354 | MOSSLNDG | CENTRAL COAST | 2021-06-03 | 2021-06-23 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40605354 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147
121489168 | B | LC | ETL.4880.INSL | 40740870 | FRESNO | FRESNO | 2021-06-07 | 2021-07-26 | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Zone 1 | HFRA Removal | COMP | 40740038 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle |  | Ceramic | Double Dead End |  |  |  |  | 1.3535e-05
121490005 | E | LC | ETL.1400.POLE.WDPS | 44776448 | VICTOR | STOCKTON | 2021-06-01 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40643737 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.0013675 | 31.7334 | 0.043394
121491153 | F | LC | ETL.8060.POLE.WOOD | 40771531 | SACTO | SIERRA | 2021-06-08 | 2021-06-17 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [11 empty] | 0.0068914 | 443.0452
121497508 | B | LC | ETL.4440.INSL | 40614501 | TABLEMTN | NORTH VALLEY | 2021-06-08 | 2021-08-23 | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40589255 | 1968-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Ceramic | Suspension |  |  |  |  | 6.2805e-05 | 5825.6519
121499584 | E | LC | ETL.6880.POLE.NWOD | 44915837 | LAKEVLLE | NORTH BAY | 2021-06-04 |  | ETL.6880 | FULTON-CALISTOGA | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44915837 | 2020-03-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-03-03 | Glass | Dead End |  |  |  |  | 0.00065069 | 938.7179 | 0.61081
121513664 | E | LC | ETL.1420.INSL.NCER | 40845823 | SACTO | SACRAMENTO | 2021-06-05 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Steel | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | PEND | 40819127 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm |  | Polymer | [5 empty] | 5.7259e-05 | 3797.0496 | 0.21742
121516180 | E | LC | ETL.1450.POLE.WDPS | 44553705 | SACTO | SACRAMENTO | 2021-06-10 | 2021-09-09 | ETL.1450 | DRUM-SUMMIT #2 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 |  |  | CNCL | [12 empty] | 3274.9534
121519239 | F | LC | ETL.4393.POLE.STPS | 45070815 | SACTO | SIERRA | 2021-06-04 |  | ETL.4393 | DRUM-HIGGINS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45070789 | 2021-03-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.8281e-05 | 94.9894
121520245 | E | LC | ETL.8060.POLE.WOOD | 40862184 | SACTO | SIERRA | 2021-06-08 |  | ETL.8060 | SPAULDING-SUMMIT | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40862184 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Polymer | [5 empty] | 0.30024 | 1123.6396 | 337.3581
121537929 | E | LC | ETL.6880.POLE.WOOD | 40585438 | LAKEVLLE | NORTH BAY | 2021-06-14 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40585438 |  | Single Wood Pole | DV-DE - Double Vertical Dead End | 2021-07-24 | Glass | Dead End |  |  |  |  | 2.6742e-05 | 775.2442 | 0.020732
121538962 | E | LC | ETL.5390.TOWR | 40592468 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5390 | PIT #1-COTTONWOOD | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40592468 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.2534e-06 | 4041.2002 | 0.0050651
121544949 | F | LC | ETL.5420.POLE.STPS | 44399984 | TABLEMTN | NORTH VALLEY | 2021-06-13 | 2021-07-29 | ETL.5420 | PIT #5-ROUND MTN #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44399983 | 2017-11-30 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 2.4704e-05 | 632.9359
121545377 | E | LC | ETL.1440.POLE.WOOD | 40870568 | SACTO | SIERRA | 2021-06-12 | 2021-07-19 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [11 empty] | 0.00067083 | 63.348
121547451 | E | LC | ETL.7640.POLE.WDPS | 44565554 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564298 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 6.3368e-05 | 3880.9729 | 0.24593
121550027 | B | LC | ETL.1660.POLE.WDPS | 44298611 | LAKEVLLE |  | 2021-06-15 | 2021-08-10 | ETL.1660 | GEYSERS #3-EAGLE ROCK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
121553275 | A | LC | ETL.6050.INSL | 40783423 | MOSSLNDG | CENTRAL COAST | 2021-06-17 | 2021-06-24 | ETL.6050 | MOSS LANDING-METCALF | Emergency-Steel | Other | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40753796 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 0.00016593 | 1250.099
121557235 | F | LC | ETL.1820.POLE.NWOD | 45009268 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45009268 | 2020-06-03 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-03 | Glass | Double Dead End |  |  |  |  | 0.0014959 | 0.065148
121561209 | F | LC | ETL.6750.POLE.WDPS | 44232846 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44232844 | 2012-09-17 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.000475 | 221.5655
121561702 | E | LC | ETL.7640.POLE.WDPS | 44565417 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.7640 | MTN GATE JCT-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44564195 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0021043 | 79.1851 | 0.16663
121592686 | B | LC | ETL.7000.POLE.WOOD | 44225094 | TABLEMTN | NORTH VALLEY | 2021-06-23 | 2021-06-30 | ETL.7000 | HAMILTON BRANCH-CHESTER | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44225094 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.091877 | 47.5141
121592686 | B | LC | ETL.7000.POLE.WOOD | 44225094 | TABLEMTN | NORTH VALLEY | 2021-06-23 | 2021-06-30 | ETL.7000 | HAMILTON BRANCH-CHESTER | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44225094 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.091877 | 47.5141
121605221 | F | LC | ETL.6660.POLE.NWOD | 45087058 | TABLEMTN | NORTH VALLEY | 2021-06-23 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45087058 | 2021-03-04 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-04 | Polymer | Post |  |  |  |  | 1.7018e-08 | 1253.0741
121624452 | B | LC | ETL.6300.INSL.CERA | 42624396 | TABLEMTN | NORTH VALLEY | 2021-06-27 | 2021-07-20 | ETL.6300 | CARIBOU-WESTWOOD | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42624181 | 2013-01-01 | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 1.4397e-06 | 0.065148
121636052 | B | LC | ETL.6070.INSL | 40894623 | TABLEMTN | NORTH VALLEY | 2021-06-27 | 2021-07-16 | ETL.6070 | ROUND MTN-TABLE MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40870739 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 3.9345e-06 | 1079.2146
121638597 | E | LC | ETL.7180.POLE.WDPS | 44360908 | LAKEVLLE | NORTH BAY | 2021-06-23 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44360907 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0045311 | 146.3688 | 0.66322
121647989 | B | LC | ETL.1350.POLE.STPS | 44993139 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-08-06 | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993110 | 2019-10-19 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0019468 | 174.1138
121657272 | E | LC | ETL.1730.POLE.WDPS | 44413339 | MOSSLNDG | CENTRAL COAST | 2021-06-30 | 2021-08-02 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Jumper-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44413338 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 2.7454e-05 | 0.065147
121662075 | E | LC | ETL.1730.POLE.WDPS | 44561135 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44515870 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.001161 | 257.9785 | 0.29951
121675207 | E | LC | ETL.1730.INSL.NCER | 42674843 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44413434 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 4.9788e-05
121675207 | E | LC | ETL.1730.INSL.NCER | 42674843 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44413434 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 4.9788e-05
121675207 | E | LC | ETL.1730.INSL.NCER | 42674843 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44413434 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 4.9788e-05
121675657 | E | LC | ETL.1372.POLE.WDPS | 44283686 | PISMOBCH | LOS PADRES | 2021-07-06 |  | ETL.1372 | MANVILLE TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44283684 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00019582 | 1442.1754 | 0.28241
121694846 | A | LC | ETL.7930.POLE.WOOD | 40600170 | MOSSLNDG | CENTRAL COAST | 2021-07-09 | 2021-07-21 | ETL.7930 | SALINAS-LAURELES | Emergency-Wood | Other | [Replace, Completed] | Tier2 |  |  | COMP
121717377 | E | LC | ETL.6890.POLE.WOOD | 40825344 | LAKEVLLE | SONOMA | 2021-07-08 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40825344 | 1994-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0030769 | 395.8061 | 1.2179
121721913 | E | LC | ETL.4393.POLE.WOOD | 40593233 | SACTO | SIERRA | 2021-06-12 |  | ETL.4393 | DRUM-HIGGINS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40593233 |  | Single Wood Pole | DE - Dead End |  | Polymer | [5 empty] | 0.0016387 | 822.7424 | 1.3482
121722502 | E | LC | ETL.6520.POLE.WOOD | 40669371 | SACTO | SIERRA | 2021-07-08 |  | ETL.6520 | COLGATE-SMARTVILLE #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40669371 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 0.02101 | 428.1771 | 8.996
121735330 | E | LC | ETL.6710.POLE.WOOD | 40768285 | MOSSLNDG | CENTRAL COAST | 2021-07-15 |  | ETL.6710 | DEL MONTE-VIEJO | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40768285 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2021-07-11 | Glass | Suspension |  |  |  |  | 0.98019 | 0.066432 | 0.065116
121735744 | F | LC | ETL.1820.POLE.STPS | 44395273 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44395272 | 2020-03-03 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00039887 | 348.0238
121747163 | E | LC | ETL.1820.POLE.WDPS | 44562277 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591243 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.87148 | 395.7131 | 344.8554
121749526 | B | LC | ETL.6020.INSL | 40610987 | TABLEMTN | NORTH VALLEY | 2021-07-17 | 2021-08-31 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586427 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 4.8963e-07 | 791.1378
121749526 | B | LC | ETL.6020.INSL | 40610987 | TABLEMTN | NORTH VALLEY | 2021-07-17 | 2021-08-31 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586427 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 4.8963e-07 | 791.1378
121749693 | F | LC | ETL.1820.POLE.WDPS | 44565330 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564305 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.2634 | 5399.9375
121754951 | A | LC | ETL.7590.SWIT | 40743953 | MOSSLNDG | CENTRAL COAST | 2021-07-19 | 2021-07-21 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Storm Related | [Repair, Completed, Completed] | Tier3 |  |  | COMP | [7 empty] | 2015-06-11 | SEECO | VACUUM INTERRUPTER (3 GAP) | SCADA Only
121770128 | E | LC | ETL.2390.POLE.WDPS | 44195279 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44195278 | 2013-09-19 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.1786e-05 | 2751.947 | 0.032434
121781595 | E | LC | ETL.4040.POLE.WDPS | 45100475 | TABLEMTN | NORTH VALLEY | 2021-07-21 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42622415 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0071618 | 4067.0386 | 29.1272
121790221 | E | LC | ETL.9240.TOWR | 43249490 | PISMOBCH | LOS PADRES | 2021-07-24 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 43249490 |  | LATTICE STEEL TOWER | [9 empty] | 4846.4956
121792981 | E | LC | ETL.4960.INSL | 40891951 | CONCORD |  | 2021-07-23 |  | ETL.4960 | LAKEVILLE-SOBRANTE #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40868831 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.028202 | 650.6212 | 18.3487
121795442 | E | LC | ETL.9240.TOWR | 43249733 | PISMOBCH | LOS PADRES | 2021-07-26 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 43249733 |  | LATTICE STEEL TOWER | [9 empty] | 4846.4956
121803555 | F | LC | ETL.8365.POLE.NWOD | 40906673 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40906673 | 2011-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0028245
121808205 | E | LC | ETL.1400.POLE.WDPS | 45051010 | VICTOR | YOSEMITE | 2021-07-26 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40661820 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0047609 | 221.5655 | 1.0549
121813879 | E | LC | ETL.5960.INSL | 40741130 | PISMOBCH | LOS PADRES | 2021-07-27 |  | ETL.5960 | DIABLO-GATES #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40740277 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 1.0213e-07 | 838.9597 | 8.5685e-05
122136723 | E | LC | ETL.6280.POLE.WOOD | 40666874 | TABLEMTN | NORTH VALLEY | 2021-10-01 |  | ETL.6280 | CARIBOU #2 | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40666874 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Other |  |  |  |  | 0.0003519 | 490.3705 | 0.17256
118519915 | E | LC | ETL.3830.TOWR | 40642821 | VICTOR | STOCKTON | 2020-02-10 | 2021-02-28 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40642821 | 1989-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 5.7587e-07 | 5966.103
118779326 | E | LC | ETL.4050.POLE.WOOD | 40861269 | LAKEVLLE | SONOMA | 2020-04-06 | 2020-05-11 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861269 | 1970-01-01 | Single Wood Pole | T-1 - Tri Post | 1970-01-01 | Ceramic | Post |  |  |  |  | 0.00010187 | 3134.4199
118940804 | F | LC | ETL.4750.POLE.NWOD | 44469284 | LAKEVLLE | SONOMA | 2020-04-22 | 2021-02-10 | ETL.4750 | GEYSERS #12-FULTON | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44469284 | 2018-01-31 | Tubular Steel Pole | SVDE - Single Vertical Dead End | 2018-01-31 | Ceramic | Post |  |  |  |  | 0.00057081 | 1188.9327
118961303 | E | LC | ETL.6220.POLE.WOOD | 40666733 | EUREKA | HUMBOLDT | 2020-04-29 | 2020-12-08 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Idle | [Remove] | Tier3 |  |  | DLFL
118975983 | F | LC | ETL.1330.TOWR | 40593956 | LAKEVLLE | HUMBOLDT | 2020-04-23 | 2021-04-13 | ETL.1330 | CORTINA-MENDOCINO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40593956 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 0.00045167 | 6093.8936
118991426 | E | LC | ETL.1651.POLE.WOOD | 40588002 | LAKEVLLE | SONOMA | 2020-05-06 | 2021-07-15 | ETL.1651 | MISSION POWER TAP | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118999616 | E | LC | ETL.2740.INSL.NCER | 40828528 | CONCORD | EAST BAY | 2020-05-01 | 2021-06-10 | ETL.2740 | MORAGA-OAKLAND #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119014291 | F | LC | ETL.1890.TOWR | 40806740 | FRESNO | FRESNO | 2020-05-11 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Structure-Steel | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40806740 | 1986-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1986-01-01 | Porcelain | Suspension |  |  |  |  | 5.0626e-07 | 5983.5244
119049741 | E | LC | ETL.1240.POLE.WDPS | 44386162 | TABLEMTN | NORTH VALLEY | 2020-05-13 | 2020-06-10 | ETL.1240 | CASCADE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44386161 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.9993e-05 | 2441.9417
119096830 | E | LC | ETL.6852.POLE.WOOD | 40584516 | LAKEVLLE | SONOMA | 2020-06-02 | 2021-06-03 | ETL.6852 | CLEAR LAKE-KONOCTI | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119101707 | F | LC | ETL.5140.POLE.WOOD | 42569834 | SACTO | SIERRA | 2020-05-20 | 2020-10-22 | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
119112920 | F | LC | ETL.5140.POLE.WOOD | 42569860 | SACTO | SIERRA | 2020-05-27 | 2020-07-31 | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL | [12 empty] | 63.3518
119116007 | E | LC | ETL.1470.POLE.WOOD | 41176294 | LAKEVLLE | HUMBOLDT | 2020-05-21 | 2020-11-10 | ETL.1470 | EAGLE ROCK-CORTINA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 41176294 | 1978-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1978-01-01 | Glass | Dead End |  |  |  |  | 0.0026987 | 4353.3184
119117091 | F | LC | ETL.6720.POLE.WOOD | 40815777 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2021-09-03 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119125651 | F | LC | ETL.6490.POLE.WOOD | 40869595 | SACTO | SIERRA | 2020-06-03 | 2020-06-26 | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL
119151605 | F | LC | ETL.6320.POLE.WOOD | 40867501 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2020-09-28 | ETL.6320 | CENTERVILLE-TABLE MTN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40867501 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00058484 | 1333.3591
119157651 | F | LC | ETL.7260.POLE.WOOD | 40759171 | TABLEMTN | NORTH VALLEY | 2020-06-09 |  | ETL.7260 | KESWICK-CASCADE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40759171 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 1.7843e-05 | 2535.75
119158000 | B | LC | ETL.1430.INSL.NCER | 44305007 | SACTO | SACRAMENTO | 2020-06-11 | 2020-08-05 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119162631 | E | LC | ETL.1810.POLE.WDPS | 44322335 | EUREKA | HUMBOLDT | 2020-06-11 | 2021-05-03 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322334 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0022299
119163479 | E | LC | ETL.7780.INSL.NCER | 40800769 | LAKEVLLE | HUMBOLDT | 2020-06-13 |  | ETL.7780 | PHILO JCT-ELK | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40769204 |  | Single Wood Pole | TPSR - Tri Post & Susp Light |  | Non Ceramic | [5 empty] | 0.0013954 | 126.5897 | 0.17664
119169330 | F | LC | ETL.6480.POLE.WOOD | 40757254 | SACTO | SIERRA | 2020-06-15 |  | ETL.6480 | COLGATE-CHALLENGE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40757254 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.14828 | 3859.7815
119176859 | E | LC | ETL.6220.POLE.WDPS | 44402619 | EUREKA | HUMBOLDT | 2020-06-12 | 2021-02-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44402616 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.21191
119197980 | F | LC | ETL.6470.POLE.WOOD | 40590447 | SACTO | SIERRA | 2020-06-22 | 2021-07-08 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.060001 | 110.8355
119207436 | B | LC | ETL.2060.POLE.WOOD | 40697798 | LAKEVLLE | SONOMA | 2020-06-22 | 2021-07-06 | ETL.2060 | FORT BRAGG-ELK | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40697798 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.14155 | 94.9585
119229231 | E | LC | ETL.7180.POLE.WOOD | 40585481 | LAKEVLLE | SONOMA | 2020-06-29 | 2021-02-08 | ETL.7180 | IGNACIO-BOLINAS #2 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier2 | Tier 2 | Within Both | CNCL | 40585481 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 5.5052e-06 | 71.6461
119290377 | B | LC | ETL.6950.POLE.WOOD | 40756914 | SACTO | SACRAMENTO | 2020-07-01 | 2020-09-17 | ETL.6950 | GOLD HILL #1 | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40756914 |  | Single Wood Pole | T-1 - Tri Post |  | Porcelain | [5 empty] | 0.0006456 | 1504.152
119296065 | E | LC | ETL.6890.POLE.WOOD | 40877294 | LAKEVLLE | SONOMA | 2020-06-30 | 2021-03-10 | ETL.6890 | FULTON-HOPLAND | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 40877294 | 1948-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Other |  |  |  |  | 0.00057397 | 126.6897
119301216 | F | LC | ETL.6760.POLE.WOOD | 45072082 | SACTO | SIERRA | 2020-07-02 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45072082 | 2019-08-05 | Single Wood Pole | T2N | 2019-08-05 | Polymer | Post |  |  |  |  | 0.063475 | 49.1321
119308123 | B | LC | ETL.7140.POLE.STPS | 44928847 | LAKEVLLE | NORTH BAY | 2020-07-03 | 2020-11-09 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] |  | Tier 3 | Within Both | COMP | 44928271 | 2020-06-13 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0020446 | 4211.6216
119317389 | F | LC | ETL.7030.POLE.NWOD | 44311024 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-06-14 | ETL.7030 | HAT CREEK #1-WESTWOOD | Hardware-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44311024 | 2014-07-24 | Fiberglass | T2N | 2014-07-24 | Polymer | Post |  |  |  |  | 0.0066681 | 15.8837
119317830 | E | LC | ETL.8170.POLE.WDPS | 44769586 | EUREKA | HUMBOLDT | 2020-07-01 | 2021-06-08 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119324458 | F | LC | ETL.7270.POLE.WOOD | 40909517 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-08-12 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40909517 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.022524 | 4936.5352
119325308 | E | LC | ETL.7180.POLE.WDPS | 44360912 | LAKEVLLE | NORTH BAY | 2020-07-06 | 2021-04-06 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44360910 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 4.7751e-06 | 269.3192
119325861 | E | LC | ETL.1430.TOWR | 40590518 | SACTO | SACRAMENTO | 2020-07-07 | 2021-03-08 | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40590518 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.0011591 | 316.4733
119326253 | F | LC | ETL.6300.POLE.WOOD | 44191092 | TABLEMTN | NORTH VALLEY | 2020-07-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND
119327168 | F | LC | ETL.1110.POLE.STPS | 44424632 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-07-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424629 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 9.452e-06 | 3453.0132
119327839 | F | LC | ETL.6300.POLE.WOOD | 40599570 | TABLEMTN |  | 2020-07-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40599570 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 3.6221e-06 | 15.8815
119341475 | F | LC | ETL.6280.POLE.WOOD | 40675381 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40675381 |  | Single Wood Pole | TP - Tri Pin |  | Non Ceramic | Pin |  |  |  |  | 0.00033767 | 4683.9302
119355821 | E | LC | ETL.8170.POLE.WOOD | 40906382 | EUREKA | HUMBOLDT | 2020-07-10 | 2021-06-03 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906382 |  | Single Wood Pole | T1DE - Tri Post Dead End 115 |  | Porcelain | Post |  |  |  |  | 0.017793 | 15.8866
119356147 | E | LC | ETL.5980.TOWR | 40869950 | PISMOBCH | LOS PADRES | 2020-07-10 | 2021-05-20 | ETL.5980 | DIABLO-MIDWAY #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40869950 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-05-05 | Glass Silicone Coated | Suspension |  |  |  |  | 6.4197e-09 | 5049.7915
119359511 | F | LC | ETL.7030.POLE.WOOD | 40769950 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-02-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40769950 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.013974 | 95.1533
119359571 | F | LC | ETL.7030.POLE.WOOD | 40676331 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40676331 |  | Single Wood Pole | TPA - Tri Pin Arm | [7 empty] | 0.0023768 | 5620.1401
119362705 | E | LC | ETL.6290.POLE.WOOD | 44168170 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-09-02 | ETL.6290 | CARIBOU-PLUMAS JCT | Vegetation | Overgrown | [Trim] | Tier2 | Tier 2 | Within Both | DLFL | 44168170 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.031033 | 0.066432
119367250 | E | LC | ETL.6880.POLE.WOOD | 44677462 | LAKEVLLE | SONOMA | 2020-07-14 | 2021-08-09 | ETL.6880 | FULTON-CALISTOGA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44677462 | 2017-10-21 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2017-10-21 | Ceramic | Suspension |  |  |  |  | 0.0032849 | 1250.5789
119374914 | E | LC | ETL.1440.POLE.WDPS | 40876967 | SACTO | SIERRA | 2020-07-13 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876967 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00058908
119374914 | E | LC | ETL.1440.POLE.WDPS | 40876967 | SACTO | SIERRA | 2020-07-13 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876967 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00058908
119461633 | E | LC | ETL.7030.POLE.WOOD | 40589874 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-06-29 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40589874 |  | Single Wood Pole | T2N | 2017-09-27 | Polymer | Post |  |  |  |  | 0.010043 | 0.06515
119490015 | F | LC | ETL.2060.POLE.WOOD | 40824335 | LAKEVLLE | SONOMA | 2020-07-22 | 2020-08-10 | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40824335 | 1961-01-01 | Single Wood Pole | FIG4W - Wood X Arm | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.36168 | 23.8261
119497626 | E | LC | ETL.8060.INSL.CERA | 40610597 | SACTO | SACRAMENTO | 2020-07-23 | 2021-05-04 | ETL.8060 | SPAULDING-SUMMIT | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119503529 | F | LC | ETL.6760.POLE.WOOD | 45072082 | SACTO | SIERRA | 2020-07-23 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45072082 | 2019-08-05 | Single Wood Pole | T2N | 2019-08-05 | Polymer | Post |  |  |  |  | 0.063475 | 49.1321
119511695 | F | LC | ETL.4393.TOWR | 40594566 | SACTO | SACRAMENTO | 2020-07-27 |  | ETL.4393 | DRUM-HIGGINS | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40594566 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | [5 empty] | 4.3492e-05 | 139.349
119554792 | F | LC | ETL.8365.POLE.WOOD | 40912655 | EUREKA | HUMBOLDT | 2020-08-03 | 2021-05-11 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912655 | 2010-01-01 | Light Duty Steel Pole | T2N | 2021-04-30 | Polymer | Post |  |  |  |  | 0.0067889
119555799 | E | LC | ETL.7490.POLE.WOOD | 40877970 | EUREKA | HUMBOLDT | 2020-08-04 | 2021-08-19 | ETL.7490 | MAPLE CREEK-HOOPA | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40877970 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 0.0028939 | 221.4934
119558259 | E | LC | ETL.7490.POLE.NWOD | 40810442 | EUREKA | HUMBOLDT | 2020-08-04 | 2021-08-17 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40810442 | 2011-01-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Ceramic | [5 empty] | 0.00018867 | 118.7001
119558775 | E | LC | ETL.6490.POLE.WOOD | 40768370 | SACTO | SACRAMENTO | 2020-08-04 | 2021-03-08 | ETL.6490 | COLGATE-GRASS VALLEY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40768370 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.004348 | 2230.4749
119603808 | E | LC | ETL.7930.INSL | 40632229 | MOSSLNDG | CENTRAL COAST | 2020-08-11 | 2021-01-07 | ETL.7930 | SALINAS-LAURELES | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40594167 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0013091 | 0.076662
119618180 | B | LC | ETL.8650.POLE.NWOD | 44420175 | FRESNO | FRESNO | 2020-08-14 | 2020-12-11 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420175 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0021672 | 3305.365
119640146 | E | LC | ETL.9200.POLE.WDPS | 44976204 | MIDWAY | KERN | 2020-08-19 | 2021-08-18 | ETL.9200 | TAFT-CUYAMA #1 | Vegetation | Overgrown | [Remove, Completed] |  | Non-HFTD | HFRA Addition | COMP | 42696685 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.014778
119643870 | F | LC | ETL.6480.POLE.WOOD | 42549795 | SACTO | SACRAMENTO | 2020-08-20 | 2021-07-06 | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42549795 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.069116 | 316.448
119666521 | A | LC | ETL.6230.POLE.WOOD | 40770678 | MOSSLNDG | CENTRAL COAST | 2020-08-25 | 2020-09-19 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119682836 | E | LC | ETL.3500.TOWR | 40820781 | VICTOR | STOCKTON | 2020-08-27 | 2021-04-26 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40820781 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 0.00010807 | 142.4769
119698791 | E | LC | ETL.4100.TOWR | 40755557 | SACTO | SACRAMENTO | 2020-09-01 | 2021-03-01 | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40755557 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-05-29 | Glass Silicone Coated | Suspension |  |  |  |  | 2.8464e-06 | 6000.2266
119723039 | F | LC | ETL.3190.TOWR | 40910266 | TABLEMTN | NORTH VALLEY | 2020-07-28 | 2021-04-04 | ETL.3190 | CARIBOU-PALERMO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40910266 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Other |  |  |  |  | 0.00046147 | 0.065148
119728567 | E | LC | ETL.1110.POLE.WDPS | 44423994 | TABLEMTN | HUMBOLDT | 2020-09-08 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44423993 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00082551 | 6712.0757
119780772 | F | LC | ETL.8240.POLE.NWOD | 44918448 | VICTOR | STOCKTON | 2020-09-12 |  | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44918448 | 2020-06-02 | Light Duty Steel Pole | T-1 - Tri Post | 2020-06-02 | Polymer | Post |  |  |  |  | 0.00026382 | 2360.2708
119784674 | E | LC | ETL.7180.POLE.WOOD | 40577322 | LAKEVLLE | NORTH BAY | 2020-09-14 | 2021-04-06 | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40577322 |  | Single Wood Pole | T-1 - Tri Post | 2021-04-03 | Polymer | Post |  |  |  |  | 2.3218e-05 | 412.5442
119806434 | F | LC | ETL.6760.POLE.WOOD | 40767237 | SACTO | SIERRA | 2020-08-11 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40767237 |  | Single Wood Pole | DDE - Double Dead End | 2020-04-23 | Glass | Dead End |  |  |  |  | 0.24222 | 1503.0458
119809959 | F | LC | ETL.8170.POLE.WDPS | 44420591 | EUREKA | HUMBOLDT | 2020-08-18 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44420590 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.025759 | 4417.1171
119810341 | F | LC | ETL.1440.POLE.STPS | 44782930 | SACTO | SACRAMENTO | 2020-08-13 | 2021-05-05 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44782926 | 2019-06-10 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.6049e-06 | 1819.4475
119818415 | F | LC | ETL.7270.POLE.WOOD | 40909531 | TABLEMTN | NORTH VALLEY | 2020-08-29 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40909531 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0015495 | 5300.8838
119830050 | B | LC | ETL.6880.POLE.WOOD | 40751174 | LAKEVLLE | NORTH BAY | 2020-09-29 | 2020-11-05 | ETL.6880 | FULTON-CALISTOGA | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119835092 | F | LC | ETL.5463.TOWR | 40805055 | CONCORD | DIABLO | 2020-09-02 | 2021-04-06 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805055 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2001-01-01 | Non Ceramic | Dead End |  |  |  |  | 2.8582e-05 | 5213.9293
119845071 | E | LC | ETL.8060.POLE.WOOD | 40826204 | SACTO | SIERRA | 2020-10-01 | 2021-01-26 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
119872109 | E | LC | ETL.6020.TOWR | 40821490 | TABLEMTN | NORTH VALLEY | 2020-10-08 | 2020-11-04 | ETL.6020 | MALIN-ROUND MTN #2 | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40821490 | 1993-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 2.9175e-07 | 1112.6673
119918001 | F | LC | ETL.4040.POLE.STPS | 44647157 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-07-19 | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 3 | Within Both | DLFL | 44646917 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00050018 | 190.5046
119960044 | F | LC | ETL.6240.POLE.WOOD | 40593140 | MOSSLNDG | CENTRAL COAST | 2020-10-28 | 2021-04-07 | ETL.6240 | BURNS-LONE STAR #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40593140 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.55457 | 110.8153
120097350 | E | LC | ETL.2270.INSL.CERA | 44737534 | CONCORD | EAST BAY | 2020-11-16 | 2021-06-09 | ETL.2270 | MARTINEZ-SOBRANTE | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40581522 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.7997e-05 | 24.3147
120097350 | E | LC | ETL.2270.INSL.CERA | 44737534 | CONCORD | EAST BAY | 2020-11-16 | 2021-06-09 | ETL.2270 | MARTINEZ-SOBRANTE | Conductor-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40581522 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-03-27 | Glass Silicone Coated | Suspension |  |  |  |  | 1.7997e-05 | 24.3147
120120668 | F | LC | ETL.6720.POLE.STPS | 44949090 | TABLEMTN | NORTH VALLEY | 2020-11-30 | 2021-02-01 | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44860100 | 2019-12-06 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 6.04e-07 | 15.8851
120133775 | F | LC | ETL.8060.POLE.WOOD | 44349563 | SACTO | SIERRA | 2020-10-19 | 2021-07-21 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44349563 | 2018-09-06 | Single Wood Pole | T2N | 2018-09-06 | Polymer | Post |  |  |  |  | 0.0044488 | 238.958
120228017 | E | LC | ETL.7490.POLE.WOOD | 40662163 | EUREKA | HUMBOLDT | 2020-12-22 | 2021-08-17 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40662163 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2021-08-06 | Polymer | Dead End |  |  |  |  | 0.8777 | 0.065148
120232357 | F | LC | ETL.7180.POLE.WOOD | 40742824 | LAKEVLLE | NORTH BAY | 2020-11-23 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40742824 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.0002795 | 31.7201
120233237 | E | LC | ETL.9340.POLE.NWOD | 44180722 | FRESNO | YOSEMITE | 2020-12-23 | 2021-06-29 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 44180722 | 2015-06-18 | Light Duty Steel Pole | T-1 - Tri Post | 2015-06-18 | Non Ceramic | Post |  |  |  |  | 0.00082105 | 5445.5674
120447988 | E | LC | ETL.7590.POLE.WOOD | 40657783 | MOSSLNDG | CENTRAL COAST | 2021-01-19 | 2021-01-20 | ETL.7590 | MONTA VISTA-BURNS | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier3 |  |  | COMP
120584982 | E | LC | ETL.7640.INSL.CERA | 40634807 | TABLEMTN | NORTH VALLEY | 2021-02-25 |  | ETL.7640 | MTN GATE JCT-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564306 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00042102
120584982 | E | LC | ETL.7640.INSL.CERA | 40634807 | TABLEMTN | NORTH VALLEY | 2021-02-25 |  | ETL.7640 | MTN GATE JCT-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564306 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.00042102
120609381 | A | LC | ETL.2390.POLE.WDPS | 44391058 | VICTOR | STOCKTON | 2021-03-06 | 2021-03-10 | ETL.2390 | MELONES-CURTIS | Emergency | Storm Related | [Replace, Completed, Completed] | Tier2 |  |  | COMP
120699193 | E | LC | ETL.2170.TOWR | 40579947 | SACTO | SACRAMENTO | 2021-03-26 |  | ETL.2170 | MADISON-VACA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40579947 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-04-30 | Glass | Suspension |  |  |  |  | 8.1473e-07 | 9772.6035 | 0.007962
120701732 | E | LC | ETL.1710.POLE.WDPS | 44510528 | MOSSLNDG | CENTRAL COAST | 2021-03-27 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Rotten | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44509653 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0022363 | 15.88 | 0.035512
120705762 | E | LC | ETL.3840.INSL.NCER | 40603110 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40579597 | 1956-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2017-01-02 | Polymer | Dead End - Suspension |  |  |  |  | 6.7457e-07 | 5967.0518 | 0.0040252
120705762 | E | LC | ETL.3840.INSL.NCER | 40603110 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40579597 | 1956-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1999-01-01 | Polymer | Dead End - Suspension |  |  |  |  | 6.7457e-07 | 5967.0518 | 0.0040252
120706381 | F | LC | ETL.5330.TOWR | 40810592 | MOSSLNDG | CENTRAL COAST | 2021-03-29 |  | ETL.5330 | MOSS LANDING-COBURN | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40810592 | 1949-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1949-01-01 | Ceramic | Suspension |  |  |  |  | 3.2997e-06 | 427.0656 | 0.0014092
120707722 | E | LC | ETL.1350.POLE.STPS | 44409304 | TABLEMTN | NORTH VALLEY | 2021-03-29 | 2021-06-23 | ETL.1350 | CRAG VIEW-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44409303 | 2017-10-27 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0001304 | 221.5655
120711311 | B | LC | ETL.1900.INSL.CERA | 40851360 | FRESNO | FRESNO | 2021-03-29 | 2021-05-03 | ETL.1900 | KERCKHOFF-CLOVIS-SANGER #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40822376 | 1940-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 8.2375e-07 | 5129.5869
120712462 | E | LC | ETL.3700.INSL.CERA | 40789343 | PISMOBCH | LOS PADRES | 2021-03-25 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40759939 | 1989-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 1989-01-01 | Porcelain | Unknown |  |  |  |  | 0.00067688 | 4133.0879 | 2.7976
120720927 | E | LC | ETL.5140.POLE.STPS | 45112050 | SACTO | SIERRA | 2021-03-31 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45111953 | 2019-10-21 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [8 empty] | 142.4895
120759762 | E | LC | ETL.3830.TOWR | 40870677 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40870677 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 8.3704e-06 | 4067.2603 | 0.034044
120765043 | B | LC | ETL.5090.INSL | 40622801 | MOSSLNDG | CENTRAL COAST | 2021-04-08 | 2021-05-13 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40582103 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1970-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.0071317 | 79.1724
120765761 | F | LC | ETL.4440.TOWR | 40870654 | TABLEMTN | NORTH VALLEY | 2021-04-01 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40870654 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 6.7431e-08 | 1632.2432 | 0.00011006
120773232 | E | LC | ETL.6870.POLE.WOOD | 40649995 | SACTO | SACRAMENTO | 2021-04-09 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40649995 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.10309 | 63.386 | 6.5346
120796094 | E | LC | ETL.4040.POLE.STPS | 44648005 | TABLEMTN | NORTH VALLEY | 2021-04-12 | 2021-10-05 | ETL.4040 | TRINITY-COTTONWOOD | Hardware-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44647967 | 2018-06-30 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 1.9532e-06 | 2708.5825 | 0.0052905
120796342 | E | LC | ETL.8250.INSL.NCER | 40918602 | VICTOR | STOCKTON | 2021-04-12 | 2021-06-08 | ETL.8250 | CLAY-MARTEL | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40908883 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.00023503 | 2614.054
120799954 | E | LC | ETL.4100.TOWR | 40589119 | LAKEVLLE | SACRAMENTO | 2021-04-12 |  | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40589119 | 1913-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2018-05-28 | Glass | Suspension |  |  |  |  | 3.1851e-05 | 5716.2656 | 0.18207
120809209 | F | LC | ETL.3500.TOWR | 40803572 | VICTOR | STOCKTON | 2021-04-13 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40803572 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 1.9703e-06 | 110.8102 | 0.00021833
120811798 | B | LC | ETL.2720.TOWR | 40857639 | CONCORD | DIABLO | 2021-04-14 | 2021-04-26 | ETL.2720 | MORAGA-OAKLAND #1 | Structure-Tower | Anti-Climbing Guard | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40857639 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1931-01-01 | Non Ceramic | Dead End |  |  |  |  | 7.7847e-06 | 0.065147
120811798 | B | LC | ETL.2720.TOWR | 40857639 | CONCORD | DIABLO | 2021-04-14 | 2021-04-26 | ETL.2720 | MORAGA-OAKLAND #1 | Structure-Tower | Anti-Climbing Guard | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40857639 | 1931-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1931-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 7.7847e-06 | 0.065147
120817547 | E | LC | ETL.5850.TOWR | 40603696 | LAKEVLLE | SACRAMENTO | 2021-04-14 | 2021-10-12 | ETL.5850 | VACA-PARKWAY | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40603696 | 1946-01-01 | LATTICE STEEL TOWER | Unknown | 1946-01-01 | Ceramic | Dead End |  |  |  |  | 8.7672e-10 | 3163.8147 | 2.7738e-06
120819419 | B | LC | ETL.4680.TOWR | 40604941 | LAKEVLLE | SONOMA | 2021-04-15 | 2021-05-04 | ETL.4680 | FULTON-IGNACIO #1 | Other | Customer Issue | [Access Issue] | Tier3 | Tier 3 | Within Both | COMP | 40604941 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 3.8667e-05 | 142.516
120835969 | E | LC | ETL.3500.INSL | 40879084 | VICTOR | STOCKTON | 2021-04-17 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40856676 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1930-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 5.9081e-05 | 1740.3693 | 0.10282
120845852 | E | LC | ETL.6760.POLE.WOOD | 40767233 | SACTO | SACRAMENTO | 2021-04-19 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40767233 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.1526 | 47.5526 | 7.2566
120863234 | E | LC | ETL.3720.INSL.CERA | 40879000 | CONCORD | DIABLO | 2021-04-21 |  | ETL.3720 | SOBRANTE-G #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857820 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 6.2927e-06 | 316.3912 | 0.001991
120863234 | E | LC | ETL.3720.INSL.CERA | 40879000 | CONCORD | DIABLO | 2021-04-21 |  | ETL.3720 | SOBRANTE-G #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857820 | 1968-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 6.2927e-06 | 316.3912 | 0.001991
120867267 | F | LC | ETL.6480.POLE.WOOD | 40611067 | SACTO | SACRAMENTO | 2021-04-22 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40611067 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.069468 | 284.7983
120868341 | E | LC | ETL.3960.INSL.CERA | 44366463 | PISMOBCH | LOS PADRES | 2021-04-21 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40607920 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 6.9827e-08 | 5098.0332 | 0.00035598
120868341 | E | LC | ETL.3960.INSL.CERA | 44366463 | PISMOBCH | LOS PADRES | 2021-04-21 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40607920 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 6.9827e-08 | 5098.0332 | 0.00035598
120878999 | E | LC | ETL.6470.POLE.WOOD | 40869632 | SACTO | SACRAMENTO | 2021-04-24 | 2021-08-30 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40869632 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.048687 | 5650.8154
120882407 | B | LC | ETL.1530.INSL.CERA | 43704881 | SACTO | SACRAMENTO | 2021-04-19 | 2021-07-08 | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40650095 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-11-10 | Ceramic | Dead End |  |  |  |  | 1.6992e-05 | 1344.6511
120889860 | E | LC | ETL.5510.TOWR | 40650648 | CONCORD | DIABLO | 2021-04-27 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40650648 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Suspension |  |  |  |  | 3.1801e-08 | 4955.9199 | 0.0001576
120896381 | E | LC | ETL.3960.INSL.CERA | 40779704 | PISMOBCH | LOS PADRES | 2021-04-28 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40751479 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 6.121e-06 | 3389.209 | 0.020745
120898197 | E | LC | ETL.1401.POLE.WDPS | 44390917 | VICTOR | STOCKTON | 2021-04-28 |  | ETL.1401 | BEARDSLEY TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44390916 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.002703 | 31.7334 | 0.085775
120899176 | F | LC | ETL.4410.TOWR | 40752448 | CONCORD | DIABLO | 2021-04-27 | 2021-07-26 | ETL.4410 | BRENTWOOD-KELSO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40752448 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-09-16 | Glass | Suspension |  |  |  |  | 4.6579e-07 | 5177.3608
120899176 | F | LC | ETL.4410.TOWR | 40752448 | CONCORD | DIABLO | 2021-04-27 | 2021-07-26 | ETL.4410 | BRENTWOOD-KELSO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40752448 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 4.6579e-07 | 5177.3608
120909945 | E | LC | ETL.6020.TOWR | 40868386 | TABLEMTN | NORTH VALLEY | 2021-04-30 |  | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40868386 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Dead End |  |  |  |  | 9.1248e-10 | 1347.8633 | 1.2299e-06
120924477 | E | LC | ETL.6890.POLE.WOOD | 40664510 | LAKEVLLE | SONOMA | 2021-05-03 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40664510 | 1948-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Other |  |  |  |  | 0.012028 | 538.1696 | 6.4731
120927376 | F | LC | ETL.5300.TOWR | 40753265 | PISMOBCH | LOS PADRES | 2021-04-13 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40753265 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 6.2352e-06 | 984.3804 | 0.0061379
120928409 | F | LC | ETL.6890.POLE.NWOD | 44712984 | LAKEVLLE | SONOMA | 2021-05-04 |  | ETL.6890 | FULTON-HOPLAND | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44712984 | 2019-02-16 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-02-16 | Ceramic | Suspension |  |  |  |  | 9.2319e-08 | 3884.5432 | 0.00035862
120932279 | F | LC | ETL.4440.TOWR | 40819011 | TABLEMTN | NORTH VALLEY | 2021-04-15 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40819011 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 5.3654e-07 | 1234.3652 | 0.00066229
120952993 | E | LC | ETL.7610.POLE.WOOD | 40874220 | METCALF | SAN JOSE | 2021-05-08 |  | ETL.7610 | MONTA VISTA-LOS GATOS | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | HFRA Removal | PEND | 40874220 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00013658 | 0.065147 | 8.8976e-06
121319683 | F | LC | ETL.6110.TOWR | 40869059 | METCALF | SAN JOSE | 2021-05-12 |  | ETL.6110 | TESLA-METCALF | Guy Wire Mark /Indic-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40869059 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.1048e-08 | 3091.4861
121338359 | E | LC | ETL.6220.POLE.WOOD | 40824514 | EUREKA | HUMBOLDT | 2021-05-13 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40824514 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.15349 | 1537.8777 | 236.0463
121338968 | F | LC | ETL.1890.TOWR | 40761988 | FRESNO | FRESNO | 2021-04-16 |  | ETL.1890 | KERCKHOFF-CLOVIS-SANGER #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40761988 | 1982-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2015-12-01 | Ceramic | Dead End |  |  |  |  | 8.7908e-08 | 5935.9028 | 0.00052181
121347620 | E | LC | ETL.1820.POLE.WDPS | 44557587 | EUREKA | HUMBOLDT | 2021-05-17 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44553968 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.026804 | 63.351 | 1.6981
121351478 | E | LC | ETL.2760.INSL | 40604516 | CONCORD | EAST BAY | 2021-04-24 |  | ETL.2760 | MORAGA-OAKLAND J | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40580821 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 2.8573e-08 | 332.4702 | 9.4997e-06
121358085 | E | LC | ETL.7780.POLE.WOOD | 40876342 | LAKEVLLE | SONOMA | 2021-05-19 |  | ETL.7780 | PHILO JCT-ELK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40876342 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 5.7237e-05 | 4717.9409 | 0.27004
121359223 | E | LC | ETL.5930.INSL | 40726170 | LAKEVLLE |  | 2021-04-29 | 2021-11-29 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40683919 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 2.1821e-08 | 158.2408 | 3.453e-06
121359223 | E | LC | ETL.5930.INSL | 40726170 | LAKEVLLE |  | 2021-04-29 | 2021-11-29 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40683919 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.1821e-08 | 158.2408 | 3.453e-06
121359541 | F | LC | ETL.8490.POLE.NWOD | 42700023 | PISMOBCH | LOS PADRES | 2021-04-23 |  | ETL.8490 | ATASCADERO-SAN LUIS OBISPO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 42700023 | 2013-03-11 | Light Duty Steel Pole | T-1 - Tri Post | 2013-03-11 | Non Ceramic | Post |  |  |  |  | 1.5935e-06 | 967.313
121372985 | E | LC | ETL.6660.POLE.WOOD | 44358503 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Fence / Gate | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44358503 | 2016-10-23 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2021-03-04 | Glass | Dead End |  |  |  |  | 3.0314e-06 | 1253.0741
121380569 | E | LC | ETL.6040.TOWR | 40762402 | MOSSLNDG | CENTRAL COAST | 2021-05-21 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40762402 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 2.2865e-05 | 192.7658 | 0.0044076
121381599 | F | LC | ETL.8250.POLE.WOOD | 40908855 | VICTOR | STOCKTON | 2021-05-10 | 2021-06-24 | ETL.8250 | CLAY-MARTEL | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40908855 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00069237 | 2773.2007
121381695 | F | LC | ETL.6500.POLE.WOOD | 40873544 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40873544 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0018399 | 647.846
121391921 | F | LC | ETL.4750.TOWR | 40651666 | LAKEVLLE | HUMBOLDT | 2021-05-15 | 2021-10-11 | ETL.4750 | GEYSERS #12-FULTON | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40651666 | 1971-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Porcelain | Suspension |  |  |  |  | 0.00086367 | 4974.6279
121393851 | E | LC | ETL.8060.POLE.WOOD | 40819457 | SACTO | SIERRA | 2021-05-18 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40819457 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.051465 | 63.348 | 3.2602
121428064 | F | LC | ETL.5630.POLE.STPS | 44727544 | TABLEMTN | NORTH VALLEY | 2021-05-26 |  | ETL.5630 | ROCK CREEK-POE | Road | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40656124 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.1291e-09 | 63.3704
121428102 | F | LC | ETL.7560.POLE.WDPS | 44414826 | SACTO | SIERRA | 2021-05-26 |  | ETL.7560 | WEIMAR #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44414823 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.41962 | 79.1577 | 33.2161
121431034 | E | LC | ETL.7380.POLE.WDPS | 44562752 | MOSSLNDG | CENTRAL COAST | 2021-05-26 |  | ETL.7380 | LAURELES-OTTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44562363 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.22902 | 1693.2699 | 387.7989
121466211 | F | LC | ETL.1350.TOWR | 40810512 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40810512 | 1944-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.00064043 | 174.1138
121466211 | F | LC | ETL.1350.TOWR | 40810512 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40810512 | 1944-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-12-15 | Glass | Dead End |  |  |  |  | 0.00064043 | 174.1138
121474731 | E | LC | ETL.4393.POLE.WDPS | 44172131 | SACTO | SACRAMENTO | 2021-06-04 |  | ETL.4393 | DRUM-HIGGINS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44172129 | 2015-03-27 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0010029 | 269.0937 | 0.26987
121484563 | E | LC | ETL.1710.POLE.WDPS | 44510570 | MOSSLNDG | CENTRAL COAST | 2021-05-26 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44509647 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0024739 | 47.5096 | 0.11754
121485970 | F | LC | ETL.4316.POLE.NWOD | 45102885 | TABLEMTN | NORTH VALLEY | 2021-05-29 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45102885 | 2021-04-26 | Light Duty Steel Pole | SVDE - Single Vertical Dead End | 2021-04-26 | Glass | Dead End |  |  |  |  | 0.00025416 | 506.6335
121494678 | F | LC | ETL.8650.POLE.NWOD | 44420148 | FRESNO | YOSEMITE | 2021-06-07 | 2021-08-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44420148 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.0067397 | 6995.4082
121496057 | E | LC | ETL.1400.POLE.WDPS | 44770792 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40744847 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0096467 | 965.199 | 9.311
121500611 | E | LC | ETL.4040.INSL.CERA | 44646972 | TABLEMTN | NORTH VALLEY | 2021-06-04 |  | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44646865 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2018-08-17 | Ceramic | Suspension |  |  |  |  | 7.931e-05
121500611 | E | LC | ETL.4040.INSL.CERA | 44646972 | TABLEMTN | NORTH VALLEY | 2021-06-04 |  | ETL.4040 | TRINITY-COTTONWOOD | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44646865 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2018-08-17 | Ceramic | Suspension |  |  |  |  | 7.931e-05
121516624 | F | LC | ETL.4221.POLE.WDPS | 44561281 | TABLEMTN |  | 2021-06-04 |  | ETL.4221 | SLY CREEK TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44559139 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00044292 | 110.7793 | 0.049066
121516969 | E | LC | ETL.6240.POLE.WOOD | 40767349 | MOSSLNDG | CENTRAL COAST | 2021-06-07 |  | ETL.6240 | BURNS-LONE STAR #2 | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40767349 |  | Single Wood Pole | T2N | 2020-09-13 | Polymer | Post |  |  |  |  | 0.24202 | 20.633 | 4.9936
121520015 | E | LC | ETL.1440.POLE.WDPS | 44768919 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40590114 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017838 | 95.0021 | 0.16946
121523106 | F | LC | ETL.6760.POLE.WOOD | 40758331 | SACTO | SIERRA | 2021-06-09 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758331 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0093065 | 253.1613
121530738 | E | LC | ETL.5390.TOWR | 40660514 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5390 | PIT #1-COTTONWOOD | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40660514 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 4.2415e-07 | 1158.6814 | 0.00049146
121536135 | F | LC | ETL.6880.POLE.WOOD | 44860475 | LAKEVLLE | NORTH BAY | 2021-06-10 |  | ETL.6880 | FULTON-CALISTOGA | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44860475 | 2019-12-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-12-16 | Glass | Dead End - Post |  |  |  |  | 3.8604e-05 | 4321.8276
121536551 | E | LC | ETL.4440.INSL.CERA | 40849208 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.4440 | CARIBOU-TABLE MTN | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40820433 | 1968-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1968-01-01 | Porcelain | Dead End |  |  |  |  | 3.3434e-05 | 5461.7759 | 0.18261
121536742 | E | LC | ETL.7550.INSL.CERA | 40882996 | LAKEVLLE |  | 2021-06-10 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40861242 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 9.5993e-05 | 110.7947 | 0.010635
121541572 | E | LC | ETL.1450.POLE.WDPS | 44549915 | SACTO | SACRAMENTO | 2021-06-15 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44549505 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0024785 | 2056.7583 | 5.0976
121542590 | F | LC | ETL.6500.POLE.WOOD | 40866208 | SACTO | SIERRA | 2021-06-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40866208 |  | Single Wood Pole | T2N | 2018-06-29 | Polymer | Post |  |  |  |  | 0.00079978 | 95.0648
121543488 | F | LC | ETL.6470.POLE.WOOD | 40693523 | SACTO | SIERRA | 2021-06-09 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40693523 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.015338 | 1598.1093
121543839 | F | LC | ETL.5390.TOWR | 40868863 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5390 | PIT #1-COTTONWOOD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40868863 | 1938-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 4.6959e-05 | 601.1985
121546079 | E | LC | ETL.4440.INSL.CERA | 44449018 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.4440 | CARIBOU-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40815790 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 2017-11-14 | Porcelain | Dead End |  |  |  |  | 1.0116e-06 | 2380.4187 | 0.002408
121550849 | F | LC | ETL.7990.POLE.WOOD | 40908942 | SACTO | SIERRA | 2021-06-12 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40908942 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | [5 empty] | 0.00015157 | 4253.1412
121551627 | E | LC | ETL.6720.POLE.WDPS | 44974727 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-11-17 | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 42578845 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.01641 | 47.5251 | 0.77991
121595316 | E | LC | ETL.8365.POLE.STPS | 45130598 | EUREKA | HUMBOLDT | 2021-06-24 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Steel | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 45130514 | 2021-04-28 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End
121599498 | E | LC | ETL.1450.POLE.WDPS | 44557578 | SACTO | SACRAMENTO | 2021-06-25 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44554038 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.060122 | 31.7066 | 1.9063
121603728 | B | LC | ETL.6050.INSL | 40624047 | MOSSLNDG | CENTRAL COAST | 2021-06-25 | 2021-07-08 | ETL.6050 | MOSS LANDING-METCALF | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40597456 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Dead End |  |  |  |  | 1.9406e-07 | 4260.0718
121608684 | B | LC | ETL.5960.INSL | 40839521 | PISMOBCH | LOS PADRES | 2021-06-26 | 2021-07-28 | ETL.5960 | DIABLO-GATES #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40812106 | 1973-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 5.3332e-07 | 618.0835
121609008 | F | LC | ETL.4040.POLE.STPS | 44634848 | TABLEMTN |  | 2021-06-23 |  | ETL.4040 | TRINITY-COTTONWOOD | Hardware-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44632188 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00013764 | 206.9966 | 0.02849
121641784 | E | LC | ETL.2700.INSL | 40878710 | CONCORD | EAST BAY | 2021-06-22 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857616 | 1944-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 1.1831e-06 | 1370.5471 | 0.0016215
121641784 | E | LC | ETL.2700.INSL | 40878710 | CONCORD | EAST BAY | 2021-06-22 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40857616 | 1944-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-03-30 | Glass | Suspension |  |  |  |  | 1.1831e-06 | 1370.5471 | 0.0016215
121644291 | E | LC | ETL.6880.INSL.NCER | 45100539 | LAKEVLLE | NORTH BAY | 2021-06-25 |  | ETL.6880 | FULTON-CALISTOGA | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45100487 | 2020-10-03 | Single Wood Pole | T-1 - Tri Post | 2020-10-03 | Polymer | Post |  |  |  |  | 0.00020368 | 522.1488 | 0.10635
121648475 | E | LC | ETL.1252.INSL.NCER | 40626182 | FRESNO | FRESNO | 2021-06-26 |  | ETL.1252 | OAKHURST TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40585019 | 2005-01-01 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2005-01-01 | Polymer | Dead End |  |  |  |  | 4.6676e-06 | 47.5096 | 0.00022176
121653734 | F | LC | ETL.1450.POLE.NWOD | 44967731 | SACTO | SIERRA | 2021-06-27 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44967731 | 2020-09-01 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2020-09-01 | Glass | Suspension |  |  |  |  | 3.0261e-06 | 1819.4475
121664282 | E | LC | ETL.1660.POLE.WOOD | 44298570 | LAKEVLLE | SONOMA | 2021-06-26 |  | ETL.1660 | GEYSERS #3-EAGLE ROCK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44298570 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees |  | Polymer | [5 empty] | 0.00022381 | 5144.023 | 1.1513
121667062 | B | LC | ETL.6020.INSL | 40775081 | TABLEMTN | NORTH VALLEY | 2021-07-06 | 2021-07-13 | ETL.6020 | MALIN-ROUND MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40746593 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 7.5753e-09 | 221.6034
121719529 | B | LC | ETL.1820.INSL.NCER | 45036778 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 45036776 | 2020-06-10 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-06-10 | Glass | Dead End |  |  |  |  | 0.18813 | 284.7712
121733473 | E | LC | ETL.1820.INSL.CERA | 44559953 | EUREKA | HUMBOLDT | 2021-06-27 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44559943 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.019333 | 15.8866 | 0.30714
121735024 | B | LC | ETL.5420.POLE.WOOD | 44562859 | TABLEMTN | NORTH VALLEY | 2021-07-09 | 2021-09-29 | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 696.9175
121741600 | E | LC | ETL.1710.INSL.NCER | 42567501 | MOSSLNDG | CENTRAL COAST | 2021-07-14 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 42567498 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Non Ceramic | Double Dead End |  |  |  |  | 0.00070883 | 31.6948 | 0.022466
121791113 | F | LC | ETL.6300.POLE.WDPS | 45015259 | TABLEMTN | NORTH VALLEY | 2021-07-20 | 2021-08-03 | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL | [12 empty] | 0.065148
121803595 | F | LC | ETL.7550.POLE.WOOD | 40600356 | LAKEVLLE | HUMBOLDT | 2021-07-26 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40600356 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2018-11-26 | Polymer | Dead End |  |  |  |  | 0.00012741 | 110.7947 | 0.014116
121815900 | E | LC | ETL.7390.POLE.WDPS | 44412039 | LAKEVLLE |  | 2021-07-26 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44412036 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.12177
121890033 | E | LC | ETL.5140.POLE.WDPS | 44557460 | SACTO | SACRAMENTO | 2021-05-26 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44553973 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00044898 | 63.3721 | 0.028453
121940474 | B | LC | ETL.6300.POLE.WDPS | 45015259 | TABLEMTN | NORTH VALLEY | 2021-08-23 | 2021-09-23 | ETL.6300 | CARIBOU-WESTWOOD | Emergency | Fire | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [12 empty] | 0.065148
122125579 | E | LC | ETL.7270.INSL.NCER | 40919283 | TABLEMTN | NORTH VALLEY | 2021-09-30 |  | ETL.7270 | KESWICK-TRINITY | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40909544 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0016009 | 933.5561 | 1.4945
122405115 | E | LC | ETL.6470.POLE.WOOD | 40912101 | SACTO | SACRAMENTO | 2021-11-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40912101 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.075701 | 79.2067 | 5.996
118735114 | F | LC | ETL.8170.POLE.WOOD | 40906445 | EUREKA | HUMBOLDT | 2020-03-23 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40906445 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.024786 | 94.9939
118751402 | E | LC | ETL.4316.POLE.STPS | 44674924 | TABLEMTN | NORTH VALLEY | 2020-03-27 |  | ETL.4316 | PARADISE-TABLE MTN | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 3 | Within Both | PEND | 44674843 | 2018-11-18 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.0016309 | 158.2903 | 0.25816
118948274 | E | LC | ETL.6220.POLE.NWOD | 44813261 | EUREKA | HUMBOLDT | 2020-04-24 | 2021-07-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44813261 | 2019-06-29 | Light Duty Steel Pole | T2N | 2019-06-29 | Polymer | Post |  |  |  |  | 0.011906 | 332.2834
118948289 | F | LC | ETL.6880.POLE.NWOD | 40616539 | LAKEVLLE | SONOMA | 2020-04-22 | 2020-11-10 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 |  |  | DLFL
118950981 | E | LC | ETL.5440.INSL.CERA | 44150297 | TABLEMTN | NORTH VALLEY | 2020-04-27 | 2020-06-15 | ETL.5440 | PIT #6 JCT-ROUND MTN | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
118957081 | F | LC | ETL.4392.TOWR | 41129323 | LAKEVLLE | SONOMA | 2020-04-28 | 2021-02-11 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41129323 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 0.00016787 | 2470.457
118957081 | F | LC | ETL.4392.TOWR | 41129323 | LAKEVLLE | SONOMA | 2020-04-28 | 2021-02-11 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 41129323 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.00016787 | 2470.457
118959206 | E | LC | ETL.6980.POLE.WOOD | 40587351 | LAKEVLLE | SONOMA | 2020-04-27 | 2021-08-03 | ETL.6980 | FORT ROSS-GUALALA | Vegetation | Overgrown | [Trim, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587351 | 1953-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 1953-01-01 | Polymer | Suspension |  |  |  |  | 0.51534 | 174.1901
118960544 | E | LC | ETL.7510.POLE.WOOD | 40862982 | LAKEVLLE | SONOMA | 2020-04-29 | 2020-07-09 | ETL.7510 | MENDOCINO-HARTLEY | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
118988474 | E | LC | ETL.1402.POLE.WDPS | 44550764 | VICTOR | STOCKTON | 2020-05-01 | 2021-02-11 | ETL.1402 | SPRING GAP TAP | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44550067 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.001497 | 854.4362
119026678 | E | LC | ETL.8650.POLE.NWOD | 44420135 | FRESNO | YOSEMITE | 2020-05-08 | 2020-12-17 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44420135 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.010175 | 2977.8208
119026750 | E | LC | ETL.8350.POLE.WDPS | 44405872 | VICTOR | STOCKTON | 2020-05-11 | 2020-05-15 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 3 | Within Both | DLFL | 44405871 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.1034e-05 | 1075.7365
119054538 | E | LC | ETL.7212.POLE.WDPS | 44384390 | METCALF | SAN JOSE | 2020-05-21 | 2021-05-09 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119062249 | F | LC | ETL.6440.POLE.WOOD | 40875739 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2021-01-04 | ETL.6440 | COLEMAN-RED BLUFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40875739 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0011282 | 4056.3687
119070717 | E | LC | ETL.1420.TOWR | 40820314 | SACTO | SIERRA | 2020-05-19 | 2021-01-27 | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40820314 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm |  | Porcelain | Post |  |  |  |  | 1.2714e-05 | 269.0173
119072905 | F | LC | ETL.8300.POLE.WOOD | 40601124 | TABLEMTN | NORTH VALLEY | 2020-05-28 | 2021-07-19 | ETL.8300 | VOLTA-SOUTH | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40601124 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.016699 | 4102.6147
119073589 | E | LC | ETL.6440.INSL.NCER | 40734323 | TABLEMTN |  | 2020-05-26 | 2020-09-02 | ETL.6440 | COLEMAN-RED BLUFF | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119081519 | F | LC | ETL.4220.POLE.WOOD | 40591080 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2020-08-25 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP
119096752 | E | LC | ETL.7211.POLE.NWOD | 42836736 | METCALF | SAN JOSE | 2020-06-02 |  | ETL.7211 | CRYSTAL SPRINGS TAP | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | HFRA Removal | PEND | 42836736 |  | Tubular Steel Pole | DDE - Double Dead End |  | Non Ceramic | Dead End |  |  |  |  | 1.4197e-08 | 0.065147 | 9.249e-10
119108966 | F | LC | ETL.1210.TOWR | 40585571 | PISMOBCH | LOS PADRES | 2020-05-21 |  | ETL.1210 | CALLENDER SW STA-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40585571 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-12-13 | Glass | Double Dead End |  |  |  |  | 0.00051128 | 969.1475 | 0.49551
119108966 | F | LC | ETL.1210.TOWR | 40585571 | PISMOBCH | LOS PADRES | 2020-05-21 |  | ETL.1210 | CALLENDER SW STA-MESA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40585571 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-02-19 | Glass | Double Dead End - Suspension |  |  |  |  | 0.00051128 | 969.1475 | 0.49551
119111158 | B | LC | ETL.3190.INSL | 40787781 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2020-08-21 | ETL.3190 | CARIBOU-PALERMO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758459 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0012165 | 3642.2964
119116278 | F | LC | ETL.6690.POLE.NWOD | 44221777 | SACTO | SIERRA | 2020-05-29 |  | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44221777 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.04947 | 870.2045
119116484 | E | LC | ETL.7490.POLE.STPS | 45016524 | EUREKA | HUMBOLDT | 2020-06-01 | 2021-08-12 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44735735 | 2019-03-29 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.059634 | 142.4498
119116553 | F | LC | ETL.6690.POLE | 40598794 | SACTO | SIERRA | 2020-05-29 |  | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40598794 |  | Single Wood Pole | T-1 - Tri Post | 2019-06-27 | Polymer | Post |  |  |  |  | 0.081037 | 870.2045
119117447 | E | LC | ETL.8240.POLE.WOOD | 40876069 | VICTOR | STOCKTON | 2020-06-01 | 2021-03-30 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876069 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0077304 | 4937.2936
119119126 | E | LC | ETL.4620.INSL | 40835757 | PISMOBCH | LOS PADRES | 2020-06-03 | 2021-06-23 | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119119273 | E | LC | ETL.6520.POLE.WOOD | 40771343 | SACTO | SIERRA | 2020-06-03 | 2020-11-12 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119122059 | F | LC | ETL.7290.POLE.WOOD | 40677172 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-03-02 | ETL.7290 | KILARC-CEDAR CREEK | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40677172 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.011241 | 126.6376
119126521 | E | LC | ETL.1470.POLE.WOOD | 41176311 | LAKEVLLE | SONOMA | 2020-06-08 | 2020-06-11 | ETL.1470 | EAGLE ROCK-CORTINA | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41176311 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Porcelain | Post |  |  |  |  | 0.0072137 | 0.065149
119131439 | E | LC | ETL.2060.INSL | 40899589 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-09-09 | ETL.2060 | FORT BRAGG-ELK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
119142605 | F | LC | ETL.6220.POLE.WOOD | 40810943 | EUREKA | HUMBOLDT | 2020-06-05 | 2021-01-27 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40810943 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.084481
119162973 | F | LC | ETL.6280.POLE.WOOD | 40826440 | TABLEMTN | NORTH VALLEY | 2020-06-13 | 2021-11-23 | ETL.6280 | CARIBOU #2 | Structure-Steel | Paint/Coating | [Other] | Tier2 |  |  | DLFL
119163833 | F | LC | ETL.6440.POLE.WOOD | 40760292 | TABLEMTN | NORTH VALLEY | 2020-06-09 | 2020-08-27 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760292 |  | Single Wood Pole | T-1 - Tri Post | 2013-01-18 | Polymer | Post |  |  |  |  | 0.00042375 | 2108.0396
119172461 | E | LC | ETL.6220.POLE.WOOD | 40752680 | EUREKA | HUMBOLDT | 2020-06-16 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40752680 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.056405 | 2151.1467 | 121.3349
119177288 | E | LC | ETL.7590.POLE.WOOD | 41124291 | MOSSLNDG | DE ANZA | 2020-04-15 | 2020-09-14 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41124291 |  | Single Wood Pole | DV - Double Vertical |  | Non Ceramic | [5 empty] | 0.64746 | 1405.7223
119178562 | E | LC | ETL.9340.POLE.WOOD | 40763117 | FRESNO | FRESNO | 2020-06-17 | 2020-08-11 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Vegetation | Overgrown | [Remove, Completed] | Tier3 |  |  | COMP
119182519 | E | LC | ETL.6310.POLE.WOOD | 40600653 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-08-19 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600653 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 1.1335e-06 | 4206.9112
119185227 | F | LC | ETL.6280.POLE.WOOD | 40816774 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-08-02 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40816774 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.0024683 | 1739.9091
119196150 | B | LC | ETL.6470.INSL.CERA | 40789964 | SACTO | SACRAMENTO | 2020-06-22 | 2020-07-20 | ETL.6470 | COLGATE-ALLEGHANY | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119200329 | F | LC | ETL.7321.POLE.WOOD | 44212730 | MOSSLNDG | CENTRAL COAST | 2020-06-22 |  | ETL.7321 | JOLON TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44212730 | 2014-12-16 | Fiberglass | SV2 - Angle 30-80 Degrees | 2014-12-16 | Non Ceramic | Suspension |  |  |  |  | 0.00022301 | 365.3837
119205238 | F | LC | ETL.9340.POLE.NWOD | 43680874 | FRESNO | FRESNO | 2020-06-24 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 43680874 | 2015-06-15 | Light Duty Steel Pole | T-1 - Tri Post | 2016-06-15 | Polymer | Post |  |  |  |  | 0.0020335 | 5506.9414
119210637 | B | LC | ETL.4220.POLE.STPS | 44558404 | TABLEMTN | NORTH VALLEY | 2020-06-24 | 2020-10-16 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue, Completed] |  | Tier 3 | Within Both | CNCL | 44557885 | 2019-07-27 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0011981 | 174.0849
119221585 | F | LC | ETL.7180.POLE.WOOD | 40658520 | LAKEVLLE | NORTH BAY | 2020-06-24 | 2021-04-08 | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40658520 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper |  | Glass | [5 empty] | 7.3513e-06 | 1632.0029
119227911 | B | LC | ETL.8060.POLE.WOOD | 40770710 | SACTO | SACRAMENTO | 2020-06-27 | 2020-06-30 | ETL.8060 | SPAULDING-SUMMIT | Switch | Out of Adjustment | [Repair, Completed] |  | Zone 1 | HFRA Removal | COMP | 40770710 |  | Single Wood Pole | FSS - Field Switch Structure | [7 empty] | 0.013322 | 1212.3663
119233062 | F | LC | ETL.7640.POLE.WOOD | 44825336 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2021-07-02 | ETL.7640 | MTN GATE JCT-CASCADE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44825336 | 2019-07-18 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-07-18 | Glass | Double Dead End |  |  |  |  | 0.00016926 | 47.5422
119238259 | F | LC | ETL.8060.POLE.WOOD | 40659230 | SACTO | SIERRA | 2020-06-29 | 2021-05-10 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40659230 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.011349 | 63.348
119304011 | E | LC | ETL.7300.POLE.WOOD | 40759292 | TABLEMTN | NORTH VALLEY | 2020-07-02 | 2021-03-19 | ETL.7300 | KILARC-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759292 |  | Single Wood Pole | T2N | 2021-03-04 | Polymer | Post |  |  |  |  | 0.0011554 | 300.6448
119304621 | F | LC | ETL.1400.POLE.STPS | 44382673 | VICTOR | YOSEMITE | 2020-06-30 | 2021-04-14 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44382672 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.3945e-05 | 31.7334
119311147 | F | LC | ETL.8060.POLE.WOOD | 40602298 | SACTO | SIERRA | 2020-07-02 | 2020-11-12 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40602298 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.059897 | 1117.8371
119314248 | F | LC | ETL.8060.POLE.WOOD | 40761367 | SACTO | SIERRA | 2020-07-02 | 2021-05-10 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761367 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.01731 | 743.7906
119316227 | F | LC | ETL.7180.POLE.WOOD | 40876301 | LAKEVLLE | SONOMA | 2020-07-06 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40876301 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 7.3678e-06 | 427.6578
119316619 | E | LC | ETL.7270.POLE.WOOD | 40906096 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40906096 |  | Single Wood Pole | T2N | 2021-08-14 | Polymer | Post |  |  |  |  | 0.0013189 | 996.9431 | 1.3149
119324524 | F | LC | ETL.6710.POLE.WOOD | 40613864 | MOSSLNDG | CENTRAL COAST | 2020-07-07 | 2020-08-03 | ETL.6710 | DEL MONTE-VIEJO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40613864 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | [5 empty] | 0.06204 | 0.066432
119328209 | E | LC | ETL.8060.INSL.CERA | 40610641 | SACTO | SACRAMENTO | 2020-07-07 | 2021-04-29 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586116 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0061906 | 348.1462
119328812 | F | LC | ETL.2395.POLE.WDPS | 44550829 | TABLEMTN |  | 2020-07-06 | 2021-07-19 | ETL.2395 | GRIZZLY TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119334282 | E | LC | ETL.6890.POLE.NWOD | 44878704 | LAKEVLLE | SONOMA | 2020-07-08 | 2021-04-22 | ETL.6890 | FULTON-HOPLAND | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44878704 | 2019-07-20 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-07-20 | Polymer | Post |  |  |  |  | 1.3572e-06 | 2375.323
119337248 | E | LC | ETL.6710.INSL | 40712095 | MOSSLNDG | CENTRAL COAST | 2020-07-09 |  | ETL.6710 | DEL MONTE-VIEJO | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40659352 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.50226 | 0.065148 | 0.032721
119353369 | E | LC | ETL.7180.POLE.WDPS | 44360924 | LAKEVLLE | NORTH BAY | 2020-07-07 | 2021-04-12 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44360921 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.4263e-05 | 2155.5891
119360114 | F | LC | ETL.1440.POLE.WOOD | 40590113 | SACTO | SIERRA | 2020-07-13 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.0012487
119361537 | E | LC | ETL.7780.POLE.WOOD | 40820707 | LAKEVLLE | SONOMA | 2020-07-13 | 2021-07-08 | ETL.7780 | PHILO JCT-ELK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40820707 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Other |  |  |  |  | 5.99e-08 | 2423.4854
119372731 | B | LC | ETL.6870.POLE.WOOD | 40766792 | SACTO | SACRAMENTO | 2020-07-14 | 2021-05-26 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40766792 | 1966-01-01 | Single Wood Pole | T2N | 2021-05-17 | Polymer | Post |  |  |  |  | 0.052179 | 332.3381
119377664 | E | LC | ETL.2060.POLE.WOOD | 40655894 | LAKEVLLE | SONOMA | 2020-07-15 | 2021-08-09 | ETL.2060 | FORT BRAGG-ELK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40655894 | 1961-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2021-08-05 | Glass | Suspension |  |  |  |  | 0.16999 | 63.3274
119471151 | F | LC | ETL.7030.POLE.WOOD | 40701361 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40701361 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.023367 | 189.9505
119487051 | E | LC | ETL.6240.POLE.WOOD | 40768008 | MOSSLNDG | CENTRAL COAST | 2020-07-22 | 2020-09-24 | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119488013 | F | LC | ETL.8170.POLE.WOOD | 40810479 | EUREKA | HUMBOLDT | 2020-07-21 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40810479 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.010764 | 5065.561
119496202 | F | LC | ETL.1110.POLE.STPS | 44424638 | EUREKA | HUMBOLDT | 2020-07-22 | 2021-01-27 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424637 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.6692e-06 | 657.3666
119502444 | F | LC | ETL.8060.POLE.WOOD | 40771558 | SACTO | SIERRA | 2020-07-22 | 2021-09-13 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771558 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Polymer | [5 empty] | 0.073691 | 221.5552
119516827 | E | LC | ETL.6861.POLE.WOOD | 40808796 | LAKEVLLE | HUMBOLDT | 2020-07-28 | 2021-08-17 | ETL.6861 | KONOCTI-EAGLE ROCK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808796 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 5.4048e-05 | 4430.5728
119523706 | E | LC | ETL.4392.TOWR | 40740504 | LAKEVLLE | SONOMA | 2020-07-29 | 2021-05-11 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40740504 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 1.1932e-07 | 5607.6411
119523706 | E | LC | ETL.4392.TOWR | 40740504 | LAKEVLLE | SONOMA | 2020-07-29 | 2021-05-11 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Jumper-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40740504 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-02-05 | Porcelain | Dead End |  |  |  |  | 1.1932e-07 | 5607.6411
119527044 | F | LC | ETL.7490.POLE.NWOD | 40586862 | EUREKA | HUMBOLDT | 2020-07-30 | 2020-11-10 | ETL.7490 | MAPLE CREEK-HOOPA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40586862 | 2011-01-01 | Light Duty Steel Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 3.028e-05 | 113.9438
119534333 | E | LC | ETL.6520.POLE.WOOD | 40772189 | SACTO | SIERRA | 2020-07-23 | 2021-06-09 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119547182 | E | LC | ETL.5650.INSL | 40789059 | TABLEMTN | NORTH VALLEY | 2020-07-31 | 2021-03-03 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119549834 | B | LC | ETL.7490.INSL.NCER | 44145899 | EUREKA | HUMBOLDT | 2020-08-03 | 2020-09-23 | ETL.7490 | MAPLE CREEK-HOOPA | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44145877 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.031617 | 94.9756
119568599 | E | LC | ETL.5420.POLE.WDPS | 44559047 | TABLEMTN | NORTH VALLEY | 2020-08-06 | 2020-11-10 | ETL.5420 | PIT #5-ROUND MTN #1 | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP | [12 empty] | 952.427
119577557 | E | LC | ETL.8365.POLE.WOOD | 40912647 | EUREKA | HUMBOLDT | 2020-08-07 | 2021-05-03 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912647 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.08477
119604532 | F | LC | ETL.6520.POLE.WOOD | 40666771 | SACTO | SACRAMENTO | 2020-08-12 | 2021-06-15 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 |  |  | COMP
119610810 | F | LC | ETL.1112.POLE.NWOD | 44420223 | FRESNO | FRESNO | 2020-08-13 |  | ETL.1112 | INDIAN FLAT-YOSEMITE | Road | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44420223 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Glass | Suspension |  |  |  |  | 0.0007353 | 6664.3394
119611848 | E | LC | ETL.6490.POLE.WOOD | 40599624 | SACTO | SACRAMENTO | 2020-08-13 | 2021-05-27 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP
119664658 | E | LC | ETL.6520.POLE.STPS | 44967707 | SACTO | SIERRA | 2020-08-24 | 2021-06-23 | ETL.6520 | COLGATE-SMARTVILLE #2 | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44963397 | 2020-08-11 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [8 empty] | 269.2076
119686517 | F | LC | ETL.1110.POLE.STPS | 44424646 | EUREKA | HUMBOLDT | 2020-08-26 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44424645 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00038436 | 126.5956
119710020 | E | LC | ETL.7640.POLE.WOOD | 44825336 | TABLEMTN | NORTH VALLEY | 2020-08-31 |  | ETL.7640 | MTN GATE JCT-CASCADE | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44825336 | 2019-07-18 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-07-18 | Glass | Double Dead End |  |  |  |  | 0.00016926 | 47.5422 | 0.0080471
119718950 | F | LC | ETL.4440.TOWR | 40758291 | TABLEMTN | NORTH VALLEY | 2020-08-27 | 2021-03-29 | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40758291 | 1958-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 1.2353e-06 | 285.0905
119720075 | B | LC | ETL.1330.TOWR | 40870933 | LAKEVLLE | HUMBOLDT | 2020-07-28 | 2020-10-14 | ETL.1330 | CORTINA-MENDOCINO #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870933 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.0275e-05 | 4549.376
119720075 | B | LC | ETL.1330.TOWR | 40870933 | LAKEVLLE | HUMBOLDT | 2020-07-28 | 2020-10-14 | ETL.1330 | CORTINA-MENDOCINO #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870933 | 1951-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1951-01-01 | Ceramic | Dead End |  |  |  |  | 1.0275e-05 | 4549.376
119720754 | E | LC | ETL.3190.TOWR | 40755509 | TABLEMTN | NORTH VALLEY | 2020-07-27 |  | ETL.3190 | CARIBOU-PALERMO | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40755509 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0008843 | 3621.0801 | 3.2021
119721861 | B | LC | ETL.8310.POLE.WOOD | 40771447 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-12-07 | ETL.8310 | WATSONVILLE-SALINAS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119753426 | E | LC | ETL.5960.TOWR | 40582836 | FRESNO | FRESNO | 2020-09-11 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40582836 | 1973-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 2021-07-28 | Glass Silicone Coated | Double Dead End |  |  |  |  | 0.027988
119771624 | E | LC | ETL.6690.POLE.WOOD | 40590222 | SACTO | SACRAMENTO | 2020-09-16 | 2021-03-22 | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119817755 | F | LC | ETL.8060.POLE.WOOD | 40862152 | SACTO | SIERRA | 2020-09-11 | 2021-07-06 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | DLFL | 40862152 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.011388 | 63.3733
119829245 | B | LC | ETL.6470.POLE.WOOD | 40822719 | SACTO | SIERRA | 2020-09-29 | 2020-10-02 | ETL.6470 | COLGATE-ALLEGHANY | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40822719 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0092617 | 870.1591
119829760 | E | LC | ETL.8580.TOWR | 40582580 | FRESNO | FRESNO | 2020-09-28 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40582580 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-07-07 | Porcelain | Suspension |  |  |  |  | 0.00010625
119898259 | E | LC | ETL.6890.POLE.WOOD | 40692955 | LAKEVLLE | SONOMA | 2020-10-06 | 2021-07-26 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40692955 | 1991-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Dead End |  |  |  |  | 0.010409 | 427.4466
119900272 | E | LC | ETL.7950.POLE.WOOD | 42560675 | METCALF | PENINSULA | 2020-10-07 | 2021-04-19 | ETL.7950 | SAN MATEO-HILLSDALE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 42560675 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0086461
119900272 | E | LC | ETL.7950.POLE.WOOD | 42560675 | METCALF | PENINSULA | 2020-10-07 | 2021-04-19 | ETL.7950 | SAN MATEO-HILLSDALE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 42560675 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0086461
119900272 | E | LC | ETL.7950.POLE.WOOD | 42560675 | METCALF | PENINSULA | 2020-10-07 | 2021-04-19 | ETL.7950 | SAN MATEO-HILLSDALE JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 42560675 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0086461
119930828 | B | LC | ETL.5980.TOWR | 40872384 | PISMOBCH | LOS PADRES | 2020-10-21 | 2020-11-23 | ETL.5980 | DIABLO-MIDWAY #3 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40872384 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-11-18 | Glass Silicone Coated | Suspension |  |  |  |  | 2.7616e-10 | 2390.3567
119951921 | B | LC | ETL.2911.INSL.NCER | 43192767 | MOSSLNDG | CENTRAL COAST | 2020-10-27 | 2020-11-13 | ETL.2911 | LLAGAS-HOLLISTER | Splice-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 44414523 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | [5 empty] | 1.7215e-08
119951921 | B | LC | ETL.2911.INSL.NCER | 43192767 | MOSSLNDG | CENTRAL COAST | 2020-10-27 | 2020-11-13 | ETL.2911 | LLAGAS-HOLLISTER | Splice-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 44414523 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Non Ceramic | Suspension |  |  |  |  | 1.7215e-08
119951921 | B | LC | ETL.2911.INSL.NCER | 43192767 | MOSSLNDG | CENTRAL COAST | 2020-10-27 | 2020-11-13 | ETL.2911 | LLAGAS-HOLLISTER | Splice-Steel | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 44414523 |  | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Polymer | [5 empty] | 1.7215e-08
119964965 | F | LC | ETL.8960.POLE.WDPS | 44236931 | FRESNO | FRESNO | 2020-10-27 |  | ETL.8960 | LOS BANOS-PACHECO | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44236929 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 8.1722e-06
119966874 | F | LC | ETL.4316.TOWR | 40816520 | TABLEMTN | NORTH VALLEY | 2020-10-28 | 2021-07-06 | ETL.4316 | PARADISE-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816520 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Suspension |  |  |  |  | 0.00037262 | 2501.2377
119978372 | F | LC | ETL.8580.TOWR | 40609736 | PISMOBCH | CENTRAL COAST | 2020-10-29 | 2021-09-01 | ETL.8580 | COALINGA #1-SAN MIGUEL | Structure-Steel | Paint/Coating | [Other, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40609736 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-05-22 | Glass | Suspension |  |  |  |  | 2.0663e-08
119989288 | E | LC | ETL.7150.POLE.WOOD | 40663619 | LAKEVLLE | NORTH BAY | 2020-11-03 |  | ETL.7150 | IGNACIO-ALTO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40663619 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.03185 | 0.066431 | 0.0021158
119989635 | E | LC | ETL.8960.INSL.CERA | 40692550 | FRESNO | FRESNO | 2020-11-03 | 2021-05-21 | ETL.8960 | LOS BANOS-PACHECO | Insulator-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40661760 |  | Single Wood Pole | DDE - Double Dead End | 1979-01-01 | Glass | Post |  |  |  |  | 0.0031607
120129222 | F | LC | ETL.8480.POLE.WOOD | 40760579 | PISMOBCH | LOS PADRES | 2020-08-19 |  | ETL.8480 | ATASCADERO-CAYUCOS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40760579 | 1954-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1954-01-01 | Polymer | Suspension |  |  |  |  | 0.0021432 | 3266.1378
120144381 | F | LC | ETL.1110.POLE.WDPS | 44561159 | TABLEMTN | HUMBOLDT | 2020-12-08 |  | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44515844 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00099143 | 5129.4224
120244164 | F | LC | ETL.4590.POLE.NWOD | 44859708 | TABLEMTN | NORTH VALLEY | 2020-12-11 |  | ETL.4590 | CRESTA-RIO OSO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44859708 | 2019-10-30 | Tubular Steel Pole | DV-PJ - Double Vertical Post Jumper | 2019-10-30 | Ceramic | Dead End |  |  |  |  | 6.9436e-08 | 3986.9912
120654560 | E | LC | ETL.7300.POLE.WOOD | 40602053 | TABLEMTN | NORTH VALLEY | 2021-03-17 |  | ETL.7300 | KILARC-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40602053 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.04399 | 1439.4246 | 63.3203
120680013 | F | LC | ETL.1530.POLE.WOOD | 40658456 | SACTO | SACRAMENTO | 2021-03-23 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40658456 | 1980-01-01 | Single Wood Pole | Unknown | 1980-01-01 | Ceramic | Post |  |  |  |  | 0.00023699 | 17.4655
120689692 | F | LC | ETL.5330.TOWR | 40662597 | MOSSLNDG | CENTRAL COAST | 2021-03-24 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40662597 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 2.8091e-07 | 31.6948 | 8.9032e-06
120689692 | F | LC | ETL.5330.TOWR | 40662597 | MOSSLNDG | CENTRAL COAST | 2021-03-24 |  | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40662597 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 2.8091e-07 | 31.6948 | 8.9032e-06
120705007 | F | LC | ETL.3830.TOWR | 40803335 | VICTOR | STOCKTON | 2021-03-26 | 2021-09-30 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Steel | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803335 | 1989-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 4.5605e-06 | 3089.6807
120705468 | E | LC | ETL.3840.INSL.NCER | 40772477 | VICTOR | STOCKTON | 2021-03-24 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40744474 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Polymer | Suspension |  |  |  |  | 1.8381e-06 | 2646.5061 | 0.0048645
120705468 | E | LC | ETL.3840.INSL.NCER | 40772477 | VICTOR | STOCKTON | 2021-03-24 |  | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40744474 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Polymer | Post |  |  |  |  | 1.8381e-06 | 2646.5061 | 0.0048645
120715507 | E | LC | ETL.3700.POLE.WOOD | 40818030 | PISMOBCH | LOS PADRES | 2021-03-30 | 2021-11-09 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40818030 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Porcelain | Post |  |  |  |  | 2.0768e-05 | 5477.0957 | 0.11375
120718889 | F | LC | ETL.6880.POLE.NWOD | 44958688 | LAKEVLLE | SONOMA | 2021-03-31 |  | ETL.6880 | FULTON-CALISTOGA | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44958688 | 2020-01-15 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-01-15 | Glass | Dead End |  |  |  |  | 2.6045e-05 | 6032.0103
120740630 | E | LC | ETL.1720.POLE.WDPS | 44513716 | MOSSLNDG | CENTRAL COAST | 2021-04-03 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44512226 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0025775 | 1234.1384 | 3.1809
120770875 | E | LC | ETL.1720.POLE.WDPS | 44400961 | MOSSLNDG | CENTRAL COAST | 2021-04-08 | 2021-10-04 | ETL.1720 | GREEN VALLEY-LLAGAS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44400960 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00017066 | 4161.2969 | 0.71018
120806961 | E | LC | ETL.4316.INSL.NCER | 41089364 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44383211 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle |  | Polymer | Suspension |  |  |  |  | 0.004223
120806961 | E | LC | ETL.4316.INSL.NCER | 41089364 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44383211 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle |  | Polymer | Suspension |  |  |  |  | 0.004223
120806961 | E | LC | ETL.4316.INSL.NCER | 41089364 | TABLEMTN | NORTH VALLEY | 2021-04-13 |  | ETL.4316 | PARADISE-TABLE MTN | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44383211 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle |  | Polymer | Suspension |  |  |  |  | 0.004223
120812422 | F | LC | ETL.8060.POLE.WOOD | 40751843 | SACTO | SACRAMENTO | 2021-04-14 |  | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40751843 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.017816 | 791.3312
120833556 | E | LC | ETL.4000.INSL.NCER | 40922569 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.4000 | TESLA-SALADO-MANTECA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40912760 | 1925-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1925-01-01 | Polymer | [5 empty] | 0.0095044 | 1935.4041 | 18.3948
120843386 | E | LC | ETL.6640.POLE.WOOD | 40769497 | TABLEMTN | NORTH VALLEY | 2021-04-19 | 2021-08-30 | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [12 empty] | 5514.3303
120846019 | E | LC | ETL.5970.TOWR | 40762408 | PISMOBCH | LOS PADRES | 2021-04-19 |  | ETL.5970 | DIABLO-MIDWAY #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762408 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 5.536e-09 | 2598.1006 | 1.4383e-05
120849669 | F | LC | ETL.6470.POLE.WOOD | 40611354 | SACTO | SACRAMENTO | 2021-04-20 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40611354 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.0036383 | 205.7058
120857397 | E | LC | ETL.3500.TOWR | 40643023 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40643023 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 0.00016433 | 553.8282 | 0.091013
120859552 | F | LC | ETL.6480.POLE.NWOD | 45120502 | SACTO | NORTH VALLEY | 2021-04-21 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45120502 | 2021-06-11 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-06-11 | Glass | Dead End | [5 empty] | 680.261
120861316 | F | LC | ETL.8423.POLE.NWOD | 40652674 | MOSSLNDG | CENTRAL COAST | 2021-04-21 |  | ETL.8423 | SALINAS-FORT ORD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40652674 |  | Lattice Steel Pole | DCPOST - Double Circuit Post |  | Porcelain | [5 empty] | 4.9839e-06 | 0.065148 | 3.2469e-07
120873896 | E | LC | ETL.4870.INSL | 40726375 | FRESNO | FRESNO | 2021-04-21 |  | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40684265 | 1985-01-01 | LATTICE STEEL TOWER | 3P DDE-A - 3 Pole Double Dead End Angle | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.6528e-07 | 5556.3848 | 0.00091838
120878226 | E | LC | ETL.7590.POLE.WOOD | 40767268 | MOSSLNDG | CENTRAL COAST | 2021-04-23 |  | ETL.7590 | MONTA VISTA-BURNS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40767268 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | Double Dead End |  |  |  |  | 0.15498 | 63.351 | 9.8179
120885894 | E | LC | ETL.1250.POLE.NWOD | 40859551 | FRESNO | YOSEMITE | 2021-04-22 | 2021-10-15 | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40859551 |  | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 7.4196e-07 | 4323.0181
120887451 | F | LC | ETL.1820.POLE.WDPS | 44560486 | EUREKA | HUMBOLDT | 2021-04-26 | 2021-07-06 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44560072 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.047525 | 0.065148
120911439 | E | LC | ETL.5930.TOWR | 40684414 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40684414 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-03 | Glass | Suspension |  |  |  |  | 1.2233e-07 | 650.6212 | 7.9589e-05
120911439 | E | LC | ETL.5930.TOWR | 40684414 | LAKEVLLE | DIABLO | 2021-04-30 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40684414 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.2233e-07 | 650.6212 | 7.9589e-05
120914664 | E | LC | ETL.5930.TOWR | 40762530 | LAKEVLLE | DIABLO | 2021-05-01 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40762530 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.8096e-09 | 822.7153 | 2.3115e-06
121189193 | E | LC | ETL.8250.INSL.CERA | 40918572 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40908853 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.018395 | 754.7912 | 13.8842
121189251 | E | LC | ETL.7630.POLE.WOOD | 40765903 | LAKEVLLE | SONOMA | 2021-05-11 |  | ETL.7630 | MONTE RIO-FULTON | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40765903 | 1952-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Suspension |  |  |  |  | 0.021613 | 257.9308 | 5.5748
121321874 | E | LC | ETL.1810.POLE.WDPS | 44557614 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44554035 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.011922
121322353 | E | LC | ETL.1820.POLE.WDPS | 44395481 | EUREKA | HUMBOLDT | 2021-05-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395480 | 2020-03-12 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.026025 | 4209.2925 | 109.5483
121323409 | B | LC | ETL.7140.POLE.WOOD | 40762994 | LAKEVLLE | NORTH BAY | 2021-05-12 | 2021-06-23 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762994 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.11267 | 348.1174
121328668 | F | LC | ETL.4870.TOWR | 40576615 | FRESNO | FRESNO | 2021-04-21 | 2021-07-12 | ETL.4870 | HELMS-GREGG #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40576615 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 3.4639e-06 | 2957.7136
121329811 | F | LC | ETL.2900.TOWR | 40607876 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40607876 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0051057 | 6677.1885 | 34.0916
121338688 | E | LC | ETL.1420.INSL.CERA | 40633067 | SACTO | SACRAMENTO | 2021-04-28 |  | ETL.1420 | DRUM-RIO OSO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40596168 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.00096281 | 4276.3892 | 4.1173
121339199 | F | LC | ETL.3500.TOWR | 40580456 | VICTOR | STOCKTON | 2021-04-26 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40580456 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-01-29 | Ceramic | Suspension |  |  |  |  | 1.3351e-05 | 95.0148 | 0.0012685
121341063 | E | LC | ETL.5510.TOWR | 40682748 | CONCORD | DIABLO | 2021-04-26 |  | ETL.5510 | PITTSBURG-TESLA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40682748 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Dead End |  |  |  |  | 3.1022e-07 | 4386.4697 | 0.0013608
121355091 | B | LC | ETL.6220.INSL.CERA | 40640372 | EUREKA | HUMBOLDT | 2021-05-18 | 2021-10-20 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Tie Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40614596 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.1089 | 332.2581 | 36.184
121381195 | E | LC | ETL.6760.POLE.WOOD | 40824406 | SACTO | SIERRA | 2021-05-05 | 2021-06-07 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40824406 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.043911 | 110.7947
121382042 | E | LC | ETL.8250.POLE.WOOD | 44194065 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44194065 | 2014-05-08 | Single Wood Pole | TH - TriAngle Post 70 | 2014-05-08 | Polymer | Post |  |  |  |  | 0.00048293 | 3214.9548 | 1.5526
121383542 | E | LC | ETL.8250.POLE.WOOD | 40908859 | VICTOR | STOCKTON | 2021-05-11 |  | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40908859 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0049637 | 2773.2007 | 13.7654
121384895 | F | LC | ETL.6500.POLE.NWOD | 42564759 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 42564759 |  | Tubular Steel Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 1.0744e-06 | 2361.856
121403461 | E | LC | ETL.2700.INSL.CERA | 42581973 | CONCORD | EAST BAY | 2021-05-19 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44188763 | 2008-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.687e-06 | 445.731 | 0.0016434
121419816 | E | LC | ETL.7212.INSL.NCER | 44862029 | METCALF | PENINSULA | 2021-05-27 | 2021-08-12 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44862012 | 2019-10-25 | Single Wood Pole | T-1 - Tri Post | 2019-10-25 | Polymer | Post |  |  |  |  | 0.13644 | 114.309
121421269 | F | LC | ETL.1440.POLE.WOOD | 42572711 | SACTO | SIERRA | 2021-05-28 |  | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 42572711 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 0.00024037 | 0.065152 | 1.5661e-05
121427600 | E | LC | ETL.6220.POLE.WOOD | 40876490 | EUREKA | HUMBOLDT | 2021-05-28 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40876490 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.14538 | 554.6226 | 80.6312
121430879 | F | LC | ETL.7630.POLE.WOOD | 40827326 | LAKEVLLE | SONOMA | 2021-05-27 |  | ETL.7630 | MONTE RIO-FULTON | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40827326 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.021613 | 79.1651 | 1.711
121469863 | E | LC | ETL.7780.POLE.WOOD | 40871811 | LAKEVLLE | HUMBOLDT | 2021-05-29 |  | ETL.7780 | PHILO JCT-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40871811 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 9.8935e-06 | 411.3464 | 0.0040697
121488585 | E | LC | ETL.6110.TOWR | 40607990 | METCALF | MISSION | 2021-05-29 |  | ETL.6110 | TESLA-METCALF | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40607990 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-10-06 | Glass | Suspension |  |  |  |  | 3.2245e-10 | 2505.4932 | 8.079e-07
121493536 | F | LC | ETL.6890.POLE.NWOD | 42646232 | LAKEVLLE | HUMBOLDT | 2021-06-02 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 42646232 |  | Light Duty Steel Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 5.9032e-06 | 3880.4331
121499556 | E | LC | ETL.1601.INSL.CERA | 40609150 | LAKEVLLE |  | 2021-06-03 |  | ETL.1601 | RINCON #1 TAP | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40584855 | 1969-01-01 | Tubular Steel Pole | DC-DDE - Double Circuit Double Dead End | 1969-01-01 | Porcelain | Dead End |  |  |  |  | 2.7986e-05 | 286.1265 | 0.0080077
121512294 | B | LC | ETL.1401.INSL.NCER | 45095096 | VICTOR | YOSEMITE | 2021-06-09 | 2021-06-28 | ETL.1401 | BEARDSLEY TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44390882 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2021-04-29 | Glass | Dead End |  |  |  |  | 0.00064647
121512294 | B | LC | ETL.1401.INSL.NCER | 45095096 | VICTOR | YOSEMITE | 2021-06-09 | 2021-06-28 | ETL.1401 | BEARDSLEY TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44390882 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2021-04-29 | Glass | Dead End |  |  |  |  | 0.00064647
121512294 | B | LC | ETL.1401.INSL.NCER | 45095096 | VICTOR | YOSEMITE | 2021-06-09 | 2021-06-28 | ETL.1401 | BEARDSLEY TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44390882 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2021-04-29 | Glass | Dead End |  |  |  |  | 0.00064647
121516205 | B | LC | ETL.1820.INSL.NCER | 44395691 | EUREKA | HUMBOLDT | 2021-06-10 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44395477 | 2020-03-12 | 2-Pole Wood |  | 2020-03-12 | Glass | Dead End |  |  |  |  | 0.025138
121516205 | B | LC | ETL.1820.INSL.NCER | 44395691 | EUREKA | HUMBOLDT | 2021-06-10 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44395477 | 2020-03-12 | 2-Pole Wood |  | 2020-03-12 | Glass | Dead End |  |  |  |  | 0.025138
121516888 | E | LC | ETL.4580.TOWR | 40822896 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Structure-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40822896 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 8.2562e-08 | 3597.8909 | 0.00029705
121516888 | E | LC | ETL.4580.TOWR | 40822896 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.4580 | COTTONWOOD-DELEVAN #2 | Structure-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40822896 | 1924-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1924-01-01 | Porcelain | Suspension |  |  |  |  | 8.2562e-08 | 3597.8909 | 0.00029705
121517053 | F | LC | ETL.5650.TOWR | 40810666 | TABLEMTN | NORTH VALLEY | 2021-06-07 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40810666 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 9.9562e-05 | 889.7038 | 0.088581
121519331 | E | LC | ETL.8310.POLE.WDPS | 44564917 | MOSSLNDG | CENTRAL COAST | 2021-06-11 | 2021-10-28 | ETL.8310 | WATSONVILLE-SALINAS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564326 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.018079 | 3291.4099 | 59.5064
121521980 | E | LC | ETL.7550.POLE.WOOD | 40826143 | LAKEVLLE | HUMBOLDT | 2021-06-10 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40826143 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 1.1597e-05 | 854.1058 | 0.0099054
121524661 | E | LC | ETL.1440.POLE.WDPS | 44762532 | SACTO | SACRAMENTO | 2021-06-12 | 2021-08-26 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121524931 | E | LC | ETL.1820.POLE.WDPS | 44562869 | EUREKA | HUMBOLDT | 2021-06-09 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44562438 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.022029 | 47.5295 | 1.047
121527141 | F | LC | ETL.8060.POLE.WOOD | 40826216 | SACTO | SIERRA | 2021-06-08 | 2021-11-29 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40826216 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.028681 | 15.8859
121533398 | F | LC | ETL.1480.TOWR | 40682405 | LAKEVLLE | SONOMA | 2021-06-14 |  | ETL.1480 | EAGLE ROCK-REDBUD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40682405 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-11-04 | Glass | Suspension |  |  |  |  | 0.00013397 | 2597.3052
121533398 | F | LC | ETL.1480.TOWR | 40682405 | LAKEVLLE | SONOMA | 2021-06-14 |  | ETL.1480 | EAGLE ROCK-REDBUD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40682405 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 0.00013397 | 2597.3052
121543480 | F | LC | ETL.1440.POLE.WDPS | 44338226 | SACTO | SIERRA | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44338225 | 2018-09-06 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.5674e-05 | 95.0021
121547497 | E | LC | ETL.6222.POLE.WDPS | 44741479 | EUREKA | HUMBOLDT | 2021-06-14 |  | ETL.6222 | FORT SEWARD TAP | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40770377 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00019902 | 714.1774 | 0.14214
121562329 | B | LC | ETL.4870.INSL | 40578889 | FRESNO | FRESNO | 2021-06-16 | 2021-07-27 | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121568314 | F | LC | ETL.8290.POLE.NWOD | 45078161 | TABLEMTN | NORTH VALLEY | 2021-06-15 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45078161 | 2021-04-19 | Light Duty Steel Pole | T2N | 2021-04-19 | Polymer | Post |  |  |  |  | 0.000108 | 3057.9141
121600190 | E | LC | ETL.1440.POLE.WDPS | 45096560 | SACTO | SACRAMENTO | 2021-06-25 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40603748 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.013989 | 3243.312 | 45.3699
121604188 | E | LC | ETL.7180.POLE.WOOD | 40767550 | LAKEVLLE | NORTH BAY | 2021-06-18 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40767550 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2016-04-29 | Ceramic | Suspension |  |  |  |  | 0.002686 | 412.6046 | 1.1082
121634788 | F | LC | ETL.6220.POLE.NWOD | 44855784 | EUREKA | HUMBOLDT | 2021-06-24 | 2021-09-30 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | DLFL | 44855784 | 2019-09-17 | Light Duty Steel Pole | T2N | 2019-09-17 | Polymer | Post |  |  |  |  | 0.0027498 | 832.1305
121639813 | B | LC | ETL.9040.POLE.WOOD | 40765682 | MIDWAY | KERN | 2021-06-30 | 2021-09-22 | ETL.9040 | TULE-SPRINGVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.00010983 | 96.1814
121645195 | E | LC | ETL.5520.INSL.CERA | 44313401 | CONCORD | DIABLO | 2021-07-01 |  | ETL.5520 | PITTSBURG-TESLA #2 | Insulator | Contaminated | [Ground Wash] | Tier2 | Tier 2 | Within Both | PEND | 40819252 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Dead End |  |  |  |  | 5.7411e-08 | 4101.8267 | 0.00023549
121648548 | E | LC | ETL.6220.INSL.CERA | 40611404 | EUREKA | HUMBOLDT | 2021-06-26 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40586721 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.050761 | 633.9066 | 32.1777
121662801 | E | LC | ETL.4440.POLE.STPS | 45112504 | TABLEMTN | NORTH VALLEY | 2021-07-01 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44190865 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 3.4309e-05 | 5874.6039 | 0.20155
121685474 | E | LC | ETL.6060.INSL | 40618323 | TABLEMTN | NORTH VALLEY | 2021-06-30 |  | ETL.6060 | ROUND MTN-TABLE MTN #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40592687 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.0010149 | 462.5264 | 0.46944
121705542 | B | LC | ETL.1810.TOWR | 40598282 | EUREKA | HUMBOLDT | 2021-07-09 | 2021-10-11 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40598282 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Polymer | Suspension |  |  |  |  | 0.0045066
121714175 | E | LC | ETL.8340.POLE.WOOD | 45114388 | SACTO | SIERRA | 2021-07-12 |  | ETL.8340 | WEIMAR-HALSEY | Guy Wire-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45114388 | 2021-06-28 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-06-28 | Glass | Dead End | [5 empty] | 1439.5874
121719521 | F | LC | ETL.8350.POLE.NWOD | 44331432 | VICTOR | STOCKTON | 2021-07-12 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44331432 | 2016-12-23 | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 4.0858e-05 | 300.6168
121721239 | E | LC | ETL.7140.INSL.CERA | 45096554 | LAKEVLLE | NORTH BAY | 2021-07-13 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41111803 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.28751
121721239 | E | LC | ETL.7140.INSL.CERA | 45096554 | LAKEVLLE | NORTH BAY | 2021-07-13 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41111803 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.28751
121721239 | E | LC | ETL.7140.INSL.CERA | 45096554 | LAKEVLLE | NORTH BAY | 2021-07-13 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41111803 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.28751
121731295 | E | LC | ETL.5430.POLE.WDPS | 44562997 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562424 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0037193 | 759.4948 | 2.8248
121732104 | E | LC | ETL.1480.POLE.WDPS | 44298228 | LAKEVLLE |  | 2021-07-09 |  | ETL.1480 | EAGLE ROCK-REDBUD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44298225 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0023078 | 6142.7134 | 14.1764
121732111 | F | LC | ETL.4440.POLE.NWOD | 40819098 | TABLEMTN | NORTH VALLEY | 2021-07-12 |  | ETL.4440 | CARIBOU-TABLE MTN | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40819098 |  | Lattice Steel Pole | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 1.5634e-07 | 490.3705
121733746 | E | LC | ETL.1820.POLE.WDPS | 44562690 | EUREKA | HUMBOLDT | 2021-07-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44562401 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.5151
121744783 | E | LC | ETL.1820.INSL.NCER | 45105756 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 45105741 |  | Single Wood Pole | 3P SV - 3 Pole Single Vertical |  | Non Ceramic | Suspension | [5 empty] | 4084.9047
121746268 | B | LC | ETL.2395.INSL.CERA | 40889122 | TABLEMTN | NORTH VALLEY | 2021-07-15 | 2021-10-07 | ETL.2395 | GRIZZLY TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44550085 |  | Single Wood Pole | SVDE - Single Vertical Dead End |  | Ceramic | Suspension |  |  |  |  | 0.010078 | 1763.6081 | 17.7741
121747176 | F | LC | ETL.1720.POLE.WOOD | 42567608 | MOSSLNDG | SAN JOSE | 2021-07-14 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 42567608 |  | Single Wood Pole | DV-PJ - Double Vertical Post Jumper |  | Ceramic | Double Dead End - Post |  |  |  |  | 5.3586e-05 | 2375.2947
121753729 | A | LC | ETL.6040.INSL | 40879876 | MOSSLNDG | CENTRAL COAST | 2021-07-19 | 2021-07-22 | ETL.6040 | MOSS LANDING-LOS BANOS | Emergency-Steel | Other | [Replace, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40858421 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 0.0088012
121780469 | F | LC | ETL.6810.POLE.WOOD | 40770309 | EUREKA | HUMBOLDT | 2021-07-19 |  | ETL.6810 | ESSEX JCT-ORICK | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Zone 1 | HFRA Removal | PEND | 40770309 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.055167
121813322 | F | LC | ETL.7780.POLE.WOOD | 44947088 | LAKEVLLE | HUMBOLDT | 2021-07-28 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44947088 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Non Ceramic | Suspension |  |  |  |  | 0.00018829 | 0.065148
121815902 | E | LC | ETL.1810.POLE.WDPS | 44322501 | EUREKA | HUMBOLDT | 2021-07-26 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44322500 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.013663
121816523 | E | LC | ETL.6760.POLE.WOOD | 40674403 | SACTO | SIERRA | 2021-07-29 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40674403 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.097983 | 442.9834 | 43.4051
121818319 | F | LC | ETL.6020.TOWR | 41162685 | TABLEMTN | NORTH VALLEY | 2021-07-29 |  | ETL.6020 | MALIN-ROUND MTN #2 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41162685 | 1965-01-01 | LATTICE STEEL TOWER | Unknown | [7 empty] | 2.8504e-06 | 427.3329
121822893 | E | LC | ETL.4920.TOWR | 40594302 | LAKEVLLE | EAST BAY | 2021-07-30 |  | ETL.4920 | IGNACIO-SOBRANTE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40594302 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 8.6275e-05 | 930.4564 | 0.080275
121843140 | E | LC | ETL.4316.INSL.CERA | 40656285 | TABLEMTN | NORTH VALLEY | 2021-08-04 |  | ETL.4316 | PARADISE-TABLE MTN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 41101721 | 1921-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1986-01-01 | Porcelain | Suspension |  |  |  |  | 9.8075e-05 | 1362.5446 | 0.13363
121893881 | E | LC | ETL.1180.POLE.WDPS | 44399495 | TABLEMTN | NORTH VALLEY | 2021-08-12 |  | ETL.1180 | BUTTE VALLEY-CARIBOU | Emergency | Fire | [Replace] |  | Tier 2 | Within Both | PEND | 44399492 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0040828 | 5538.7192 | 22.6132
121977218 | E | LC | ETL.6750.POLE.WDPS | 44232855 | TABLEMTN | NORTH VALLEY | 2021-08-30 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44232853 | 2012-09-17 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00036396 | 31.7081 | 0.01154
122054614 | E | LC | ETL.4780.INSL.NCER | 45129007 | LAKEVLLE | SONOMA | 2021-09-15 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129319 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 4.657e-05 | 2200.2283 | 0.10247
122054614 | E | LC | ETL.4780.INSL.NCER | 45129007 | LAKEVLLE | SONOMA | 2021-09-15 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129319 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-22 | Glass | Suspension |  |  |  |  | 4.657e-05 | 2200.2283 | 0.10247
118442248 | A | LC | ETL.7490.POLE.WOOD | 40810419 | EUREKA | HUMBOLDT | 2020-01-17 | 2020-02-19 | ETL.7490 | MAPLE CREEK-HOOPA | Crossarm-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
118499059 | F | LC | ETL.7970.POLE.WOOD | 40766877 | SACTO | SIERRA | 2020-02-05 |  | ETL.7970 | SMARTVILLE-CAMP FAR WEST | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40766877 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 8.9745e-06 | 2552.4258
118747424 | E | LC | ETL.6280.POLE.WOOD | 42559992 | TABLEMTN | NORTH VALLEY | 2020-03-26 | 2020-06-17 | ETL.6280 | CARIBOU #2 | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42559992 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00022377 | 1898.3378
118796208 | F | LC | ETL.4392.POLE.NWOD | 44191132 | LAKEVLLE | SONOMA | 2020-04-08 | 2021-07-15 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44191132 |  | Tubular Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | [5 empty] | 0.0013354 | 886.3674
118912316 | E | LC | ETL.4590.TOWR | 40910174 | TABLEMTN | NORTH VALLEY | 2020-04-11 | 2020-09-30 | ETL.4590 | CRESTA-RIO OSO | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910174 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-11-03 | Glass | Suspension |  |  |  |  | 1.0865e-05 | 2531.262
118927253 | F | LC | ETL.7212.POLE.NWOD | 44865993 | METCALF | SAN JOSE | 2020-04-13 | 2020-07-29 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44865993 | 2019-01-23 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-01-23 | Glass | Dead End |  |  |  |  | 0.14922 | 94.9668
118940477 | E | LC | ETL.4750.POLE.NWOD | 44386967 | LAKEVLLE | SONOMA | 2020-04-22 | 2020-04-28 | ETL.4750 | GEYSERS #12-FULTON | Structure-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44386967 | 2020-07-05 | Tubular Steel Pole | DV-DE - Double Vertical Dead End | 2020-07-05 | Ceramic | Dead End |  |  |  |  | 7.2016e-07 | 190.1994
118944790 | E | LC | ETL.4750.TOWR | 41129184 | LAKEVLLE | SONOMA | 2020-04-23 | 2020-06-01 | ETL.4750 | GEYSERS #12-FULTON | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129184 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2021-04-22 | Glass | Dead End |  |  |  |  | 0.0022144 | 1646.4998
118944790 | E | LC | ETL.4750.TOWR | 41129184 | LAKEVLLE | SONOMA | 2020-04-23 | 2020-06-01 | ETL.4750 | GEYSERS #12-FULTON | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129184 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 2020-02-07 | Glass | Dead End |  |  |  |  | 0.0022144 | 1646.4998
118951220 | E | LC | ETL.1650.POLE.WOOD | 40750642 | LAKEVLLE | SONOMA | 2020-04-23 | 2021-02-04 | ETL.1650 | GEYSERS #3-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750642 | 1987-01-01 | Single Wood Pole | WB - Wishbone | 1966-01-01 | Porcelain | Dead End |  |  |  |  | 4.7038e-05 | 951.7994
118957082 | E | LC | ETL.4392.TOWR | 41129326 | LAKEVLLE | SONOMA | 2020-04-28 | 2021-03-03 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129326 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-06-01 | Glass | Dead End |  |  |  |  | 0.00023592 | 3246.7576
118957082 | E | LC | ETL.4392.TOWR | 41129326 | LAKEVLLE | SONOMA | 2020-04-28 | 2021-03-03 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129326 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2019-11-22 | Glass | Dead End |  |  |  |  | 0.00023592 | 3246.7576
118958220 | E | LC | ETL.6980.POLE.WOOD | 40596034 | LAKEVLLE | SONOMA | 2020-04-27 | 2021-07-06 | ETL.6980 | FORT ROSS-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40596034 | 1985-01-01 | Single Wood Pole | TPSRD - Tri Post & Susp Dead End | 2021-06-18 | Glass | Dead End |  |  |  |  | 0.32286 | 433.7946
118961268 | E | LC | ETL.6220.POLE.WOOD | 40614602 | EUREKA | HUMBOLDT | 2020-04-29 | 2021-04-21 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40614602 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.3017 | 728.9435
118972041 | B | LC | ETL.6980.POLE.WOOD | 40648491 | LAKEVLLE | HUMBOLDT | 2020-04-30 | 2020-05-19 | ETL.6980 | FORT ROSS-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648491 | 1986-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2010-01-01 | Polymer | Suspension |  |  |  |  | 0.073493 | 921.4786
118993843 | E | LC | ETL.9090.POLE.WOOD | 40589825 | PISMOBCH | LOS PADRES | 2020-05-05 | 2021-08-17 | ETL.9090 | SAN LUIS OBISPO-CAYUCOS | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40589825 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-08-03 | Glass | Double Dead End |  |  |  |  | 0.0013109 | 1885.8511
119059388 | E | LC | ETL.1240.POLE.STPS | 44765249 | LAKEVLLE | NORTH VALLEY | 2020-04-29 | 2020-05-24 | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44741987 | 2019-03-29 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.5614e-07 | 2632.3416
119083825 | E | LC | ETL.7780.POLE.WOOD | 40826126 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-04-12 | ETL.7780 | PHILO JCT-ELK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826126 |  | Single Wood Pole | DDE-A - Double Dead End Angle | 2013-07-11 | Ceramic | Double Dead End - Post |  |  |  |  | 1.3765e-05 | 1029.736
119088678 | E | LC | ETL.6470.POLE.WOOD | 40817333 | SACTO | SIERRA | 2020-06-01 | 2021-08-05 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119096320 | E | LC | ETL.6470.POLE.WOOD | 40760425 | SACTO | SIERRA | 2020-06-01 | 2020-07-06 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP | [12 empty] | 1439.967
119096825 | E | LC | ETL.7150.INSL.CERA | 40714584 | LAKEVLLE | NORTH BAY | 2020-05-18 |  | ETL.7150 | IGNACIO-ALTO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40663518 | 1961-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.00096542 | 94.985 | 0.0917
119096825 | E | LC | ETL.7150.INSL.CERA | 40714584 | LAKEVLLE | NORTH BAY | 2020-05-18 |  | ETL.7150 | IGNACIO-ALTO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40663518 | 1961-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | [5 empty] | 0.00096542 | 94.985 | 0.0917
119096898 | E | LC | ETL.8290.POLE.WOOD | 40759232 | TABLEMTN | NORTH VALLEY | 2020-06-01 | 2021-04-26 | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119097266 | F | LC | ETL.1430.TOWR | 40672397 | SACTO | SIERRA | 2020-05-19 | 2021-03-01 | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40672397 | 1913-01-01 | LATTICE STEEL TOWER | Unknown | 2016-11-14 | Non Ceramic | Post |  |  |  |  | 0.002243 | 1977.4294
119103144 | E | LC | ETL.6520.POLE.WOOD | 40864694 | SACTO | SIERRA | 2020-06-02 | 2021-06-08 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119103974 | F | LC | ETL.7300.POLE.WOOD | 40771252 | TABLEMTN |  | 2020-06-03 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40771252 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.00088461 | 3200.7368
119105264 | F | LC | ETL.1450.POLE.WDPS | 44549915 | SACTO | SACRAMENTO | 2020-05-19 | 2021-07-08 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549505 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0024785 | 2056.7583
119108957 | F | LC | ETL.6240.POLE.WDPS | 44413788 | MOSSLNDG | CENTRAL COAST | 2020-05-21 | 2021-01-12 | ETL.6240 | BURNS-LONE STAR #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119112773 | E | LC | ETL.9340.POLE.NWOD | 44844647 | FRESNO | YOSEMITE | 2020-06-02 | 2021-10-27 | ETL.9340 | WISHON-SAN JOAQUIN #3 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44844647 | 2019-09-28 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2019-09-28 | Glass | Suspension |  |  |  |  | 0.00056391 | 7011.6025 | 3.9539
119113140 | E | LC | ETL.5140.TOWR | 40815981 | SACTO | SIERRA | 2020-06-01 | 2021-04-29 | ETL.5140 | MIDDLE FORK-GOLD HILL | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40815981 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Dead End |  |  |  |  | 3.4327e-09 | 6902.4902
119118297 | E | LC | ETL.7290.POLE.WOOD | 40868039 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-03-01 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40868039 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0022652 | 747.6403
119118687 | F | LC | ETL.6470.POLE.WOOD | 40598545 | SACTO | SIERRA | 2020-06-01 | 2021-02-10 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40598545 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.016063 | 1439.967
119118695 | E | LC | ETL.1050.TOWR | 40816899 | FRESNO | FRESNO | 2020-05-26 | 2020-11-17 | ETL.1050 | BALCH-SANGER | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816899 | 1923-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1923-01-01 | Porcelain | Suspension |  |  |  |  | 0.0012174 | 6854.0659
119118777 | E | LC | ETL.8560.POLE.WOOD | 40871956 | PISMOBCH | LOS PADRES | 2020-06-03 | 2021-03-17 | ETL.8560 | CAYUCOS-CAMBRIA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871956 |  | Single Wood Pole | FIG4W - Wood X Arm | 2019-09-13 | Glass | Suspension |  |  |  |  | 0.0074353 | 490.9069
119122094 | F | LC | ETL.6490.POLE.WOOD | 40613018 | SACTO | SIERRA | 2020-06-02 | 2021-02-18 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40613018 |  | Single Wood Pole | T2N | 2021-02-15 | Polymer | Post |  |  |  |  | 0.012818 | 3639.9543
119130111 | F | LC | ETL.7300.POLE.WOOD | 40865090 | TABLEMTN |  | 2020-06-04 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40865090 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0001659 | 5290.9702
119130259 | F | LC | ETL.7300.POLE.NWOD | 44809980 | TABLEMTN | NORTH VALLEY | 2020-06-04 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44809980 | 2019-06-05 | Light Duty Steel Pole | T-1 - Tri Post | 2019-06-05 | Polymer | Post |  |  |  |  | 1.9145e-05 | 554.6501
119145936 | F | LC | ETL.9100.POLE.WOOD | 44191387 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-26 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove, Completed] | Tier3 |  |  | COMP | [11 empty] | 1.3988e-05 | 1250.3605
119163561 | E | LC | ETL.7140.POLE.WOOD | 40750706 | LAKEVLLE | NORTH BAY | 2020-06-11 | 2021-09-01 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750706 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | [5 empty] | 0.28672 | 79.2129
119171154 | B | LC | ETL.7850.POLE.WDPS | 44403580 | EUREKA | HUMBOLDT | 2020-06-15 | 2020-09-09 | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44403578 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 9.1656e-06 | 641.5788
119171721 | B | LC | ETL.9100.POLE.WOOD | 44191934 | PISMOBCH | LOS PADRES | 2020-06-16 | 2020-08-10 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 |  |  | CNCL | [11 empty] | 2.6003e-06 | 2732.2681
119196420 | F | LC | ETL.6470.POLE.WOOD | 40767222 | SACTO | SIERRA | 2020-06-22 | 2021-07-13 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767222 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.16852 | 79.2067
119199063 | F | LC | ETL.6470.POLE.WOOD | 40767224 | SACTO | SIERRA | 2020-06-23 | 2021-07-08 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767224 |  | Single Wood Pole | T2N | 2021-07-16 | Polymer | Post |  |  |  |  | 0.087167 | 126.6309
119200422 | B | LC | ETL.4220.POLE.WOOD | 40864031 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-10-26 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue, Completed] | Tier2 |  |  | COMP
119238567 | E | LC | ETL.7270.POLE.WOOD | 40906491 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2021-10-25 | ETL.7270 | KESWICK-TRINITY | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906491 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.0024671 | 996.9431 | 2.4595
119295334 | E | LC | ETL.8170.POLE.WDPS | 44565320 | EUREKA | HUMBOLDT | 2020-07-01 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564177 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.028619 | 553.6737 | 15.8455
119311179 | E | LC | ETL.1450.POLE.WDPS | 44552475 | SACTO | SACRAMENTO | 2020-07-01 | 2021-09-29 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 3 | Within Both | COMP | 44551549 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00043839 | 3069.2839 | 1.3455
119311261 | E | LC | ETL.7180.POLE.WOOD | 40750715 | LAKEVLLE | SONOMA | 2020-07-03 | 2020-07-23 | ETL.7180 | IGNACIO-BOLINAS #2 | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40750715 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 2019-08-27 | Polymer | Post |  |  |  |  | 4.2762e-06 | 412.6046
119313019 | E | LC | ETL.8170.POLE.WOOD | 40906455 | EUREKA | HUMBOLDT | 2020-07-03 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40906455 |  | Single Wood Pole | TPAF - Flat Pin Arm |  | Ceramic | [5 empty] | 0.02388 | 57.0224 | 1.3617
119324067 | E | LC | ETL.5431.TOWR | 40586415 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-07-08 | ETL.5431 | BLACK TAP | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586415 | 1964-01-01 | LATTICE STEEL TOWER | Unknown | [7 empty] | 2.7807e-08 | 269.0425
119325439 | E | LC | ETL.6720.POLE.STPS | 44893476 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2021-03-03 | ETL.6720 | DESABLA-CENTERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44893445 | 2019-12-06 | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 1.1513e-05 | 0.065151
119325503 | F | LC | ETL.6710.POLE.WOOD | 40768285 | MOSSLNDG | CENTRAL COAST | 2020-07-07 | 2021-07-02 | ETL.6710 | DEL MONTE-VIEJO | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40768285 |  | Single Wood Pole | SV2 - Angle 30-80 Degrees | 2021-07-11 | Glass | Suspension |  |  |  |  | 0.98019 | 0.066432
119327301 | E | LC | ETL.7300.POLE.WOOD | 44825403 | TABLEMTN | NORTH VALLEY | 2020-07-07 | 2021-03-04 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44825403 | 2019-03-02 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-03-02 | Polymer | Post |  |  |  |  | 0.00013965 | 2806.333
119335112 | E | LC | ETL.7030.POLE.WOOD | 40591884 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-06-21 | ETL.7030 | HAT CREEK #1-WESTWOOD | Anchor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591884 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.010627 | 31.7022
119339295 | E | LC | ETL.7300.POLE.WOOD | 40588852 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-02-08 | ETL.7300 | KILARC-DESCHUTES | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
119341238 | F | LC | ETL.6290.POLE.WOOD | 43250177 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 43250177 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.032963 | 0.065148
119362294 | F | LC | ETL.6280.POLE.WOOD | 40585997 | TABLEMTN | NORTH VALLEY | 2020-07-13 | 2021-09-14 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40585997 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Other |  |  |  |  | 0.00015238 | 126.5956
119367310 | F | LC | ETL.1440.POLE.WDPS | 44162401 | SACTO | SACRAMENTO | 2020-07-13 | 2021-06-08 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44162400 | 2013-09-10 | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00017859 | 79.1687
119375419 | F | LC | ETL.7030.POLE.WOOD | 40759224 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-07-07 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier2 |  |  | COMP
119375449 | F | LC | ETL.7030.POLE.WOOD | 40676331 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40676331 |  | Single Wood Pole | TPA - Tri Pin Arm | [7 empty] | 0.0023768 | 5620.1401
119376128 | B | LC | ETL.7130.POLE.WOOD | 40751086 | EUREKA | HUMBOLDT | 2020-07-15 | 2020-08-18 | ETL.7130 | HUMBOLDT-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40751086 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | [5 empty] | 0.28702
119377236 | E | LC | ETL.7630.POLE.WOOD | 40584630 | LAKEVLLE | SONOMA | 2020-07-15 | 2021-07-02 | ETL.7630 | MONTE RIO-FULTON | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119464531 | F | LC | ETL.1820.POLE.STPS | 44395196 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44395195 | 2017-09-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017267
119474445 | E | LC | ETL.6280.POLE.NWOD | 44259036 | TABLEMTN | NORTH VALLEY | 2020-07-20 | 2020-11-06 | ETL.6280 | CARIBOU #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44259036 | 2020-07-16 | Light Duty Steel Pole | T2N | 2020-07-16 | Polymer | Post |  |  |  |  | 5.6365e-08 | 158.2282
119524253 | E | LC | ETL.7380.POLE.WDPS | 44562702 | MOSSLNDG | CENTRAL COAST | 2020-07-29 | 2021-04-19 | ETL.7380 | LAURELES-OTTER | Anchor-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 3 | Within Both | DLFL | 44562359 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.57242 | 0.065148
119529836 | E | LC | ETL.6220.POLE.WOOD | 40810905 | EUREKA | HUMBOLDT | 2020-07-30 | 2021-02-24 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40810905 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Polymer | [5 empty] | 0.0051198 | 499.5363
119530020 | F | LC | ETL.6220.POLE.WOOD | 40876484 | EUREKA | HUMBOLDT | 2020-07-30 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40876484 | 2020-08-18 | Light Duty Steel Pole | T-1 - Tri Post | 2020-08-18 | Polymer | Post |  |  |  |  | 0.033461 | 2372.7383
119553802 | E | LC | ETL.5650.TOWR | 40762206 | TABLEMTN | NORTH VALLEY | 2020-08-03 | 2021-04-14 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762206 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 1.0904e-06 | 809.5917
119577760 | E | LC | ETL.6220.POLE.WOOD | 40591138 | EUREKA | HUMBOLDT | 2020-08-06 | 2020-10-05 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40591138 |  | Light Duty Steel Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.066693
119580647 | E | LC | ETL.7490.POLE.WOOD | 40591315 | EUREKA | HUMBOLDT | 2020-08-08 | 2021-08-17 | ETL.7490 | MAPLE CREEK-HOOPA | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40591315 |  | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Ceramic | Suspension |  |  |  |  | 0.087285 | 0.065148
119591062 | E | LC | ETL.8210.POLE.WOOD | 40908269 | VICTOR | STOCKTON | 2020-08-06 | 2021-07-13 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908269 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0018677 | 1221.7842
119602606 | E | LC | ETL.1450.POLE.WDPS | 44552314 | SACTO | SACRAMENTO | 2020-08-11 | 2021-07-06 | ETL.1450 | DRUM-SUMMIT #2 | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44551583 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0023913 | 411.4417
119608891 | B | LC | ETL.5934.TOWR | 40858178 | FRESNO | FRESNO | 2020-08-12 | 2020-10-21 | ETL.5934 | TEMPLETON-GATES | Hardware-Tower | Missing | [Install, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40858178 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 0.00015184
119610128 | F | LC | ETL.1401.POLE.WDPS | 44390914 | VICTOR | STOCKTON | 2020-08-13 | 2021-03-17 | ETL.1401 | BEARDSLEY TAP | Marker (i.e. signs)-Wood | Missing | [Install, Completed] |  | Tier 3 | Within Both | COMP | 44390913 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0021273 | 253.2337
119625308 | E | LC | ETL.1450.POLE.WOOD | 42572836 | SACTO | SACRAMENTO | 2020-08-17 | 2021-12-02 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42572836 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | [5 empty] | 0.00050531 | 0.065152 | 3.2922e-05
119629195 | F | LC | ETL.6900.POLE.NWOD | 44944251 | LAKEVLLE | SONOMA | 2020-08-14 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44944251 | 2020-07-22 | Light Duty Steel Pole | T-1 - Tri Post | 2020-07-22 | Polymer | Post |  |  |  |  | 3.1734e-11 | 1979.5121
119632830 | E | LC | ETL.6911.POLE.WOOD | 41101268 | LAKEVLLE | SONOMA | 2020-08-18 |  | ETL.6911 | WASHOE TAP | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 41101268 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 3.6723e-05 | 1141.3943 | 0.041915
119637963 | E | LC | ETL.7170.INSL.CERA | 40802523 | LAKEVLLE | SONOMA | 2020-08-19 |  | ETL.7170 | IGNACIO-ALTO-SAUSALITO #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40770977 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | [5 empty] | 0.011047 | 15.8851 | 0.17549
119637963 | E | LC | ETL.7170.INSL.CERA | 40802523 | LAKEVLLE | SONOMA | 2020-08-19 |  | ETL.7170 | IGNACIO-ALTO-SAUSALITO #2 | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40770977 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | [5 empty] | 0.011047 | 15.8851 | 0.17549
119639822 | E | LC | ETL.1430.TOWR | 40608843 | SACTO | SACRAMENTO | 2020-08-19 | 2021-09-15 | ETL.1430 | DRUM-RIO OSO #2 | Vegetation | Overgrown | [Trim] | Tier3 | Tier 3 | Within Both | DLFL | 40608843 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-03-08 | Glass | Suspension |  |  |  |  | 0.014735 | 316.4733
119643287 | B | LC | ETL.8650.TOWR | 40873716 | FRESNO | FRESNO | 2020-08-20 | 2020-12-14 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40873716 | 1929-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0035639 | 5678.02
119702232 | F | LC | ETL.7780.POLE.WOOD | 40819537 | LAKEVLLE | HUMBOLDT | 2020-08-25 |  | ETL.7780 | PHILO JCT-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40819537 |  | Single Wood Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.0004399 | 543.4383
119719682 | B | LC | ETL.1401.INSL.NCER | 40835073 | VICTOR | STOCKTON | 2020-08-18 | 2020-10-22 | ETL.1401 | BEARDSLEY TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
119721891 | A | LC | ETL.7590.POLE.WOOD | 40694963 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-10-21 | ETL.7590 | MONTA VISTA-BURNS | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119722865 | F | LC | ETL.1650.POLE.WDPS | 44512126 | LAKEVLLE |  | 2020-08-06 | 2021-02-14 | ETL.1650 | GEYSERS #3-CLOVERDALE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44510876 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.3534e-05 | 4860.2104
119723179 | E | LC | ETL.1400.POLE.WOOD | 40656086 | VICTOR | YOSEMITE | 2020-08-05 | 2021-05-10 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40656086 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00075983
119723179 | E | LC | ETL.1400.POLE.WOOD | 40656086 | VICTOR | YOSEMITE | 2020-08-05 | 2021-05-10 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40656086 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00075983
119743161 | B | LC | ETL.6490.INSL | 40618998 | SACTO | SACRAMENTO | 2020-09-10 | 2020-09-23 | ETL.6490 | COLGATE-GRASS VALLEY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119743206 | F | LC | ETL.6490.POLE.WOOD | 40593248 | SACTO | SIERRA | 2020-09-10 | 2021-02-12 | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40593248 |  | Single Wood Pole | T2N | 2020-09-20 | Polymer | Post |  |  |  |  | 0.022514 | 71.3642
119756339 | E | LC | ETL.7270.POLE.WOOD | 40815295 | TABLEMTN | NORTH VALLEY | 2020-08-14 | 2020-12-04 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40815295 |  | Single Wood Pole | SVDE - Single Vertical Dead End |  | Polymer | [5 empty] | 0.0034947 | 2409.1135
119764304 | B | LC | ETL.8170.POLE.NWOD | 44964304 | EUREKA | HUMBOLDT | 2020-09-14 | 2020-11-24 | ETL.8170 | TRINITY-MAPLE CREEK | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44964304 | 2020-05-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-05-18 | Glass | Dead End |  |  |  |  | 2.15e-05 | 94.963
119777268 | E | LC | ETL.7300.INSL.NCER | 44837973 | TABLEMTN | NORTH VALLEY | 2020-09-10 | 2021-03-17 | ETL.7300 | KILARC-DESCHUTES | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40868564 |  | Single Wood Pole | T-1 - Tri Post | 2019-09-27 | Polymer | Post |  |  |  |  | 0.0042071 | 0.33085
119779999 | E | LC | ETL.1112.POLE.NWOD | 44420234 | FRESNO | YOSEMITE | 2020-09-10 |  | ETL.1112 | INDIAN FLAT-YOSEMITE | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44420234 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Glass | Suspension |  |  |  |  | 0.00072896 | 2803.7676 | 2.0438
119790309 | F | LC | ETL.8410.POLE.WOOD | 44946531 | LAKEVLLE | HUMBOLDT | 2020-07-30 |  | ETL.8410 | ELK-GUALALA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44946531 | 2020-06-25 | Single Wood Pole | T-1 - Tri Post | 2020-06-25 | Polymer | Post |  |  |  |  | 0.049121 | 0.065148
119805095 | F | LC | ETL.1400.POLE.STPS | 44384133 | VICTOR | YOSEMITE | 2020-08-07 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | PEND | 44384132 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.7304e-05 | 31.7081
119808893 | F | LC | ETL.1400.POLE.STPS | 44384130 | VICTOR | YOSEMITE | 2020-08-13 |  | ETL.1400 | DONNELLS-MI-WUK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 3 | Within Both | PEND | 44384129 | 2017-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.7248e-05 | 1297.5381
119818724 | F | LC | ETL.8060.POLE.WOOD | 40702018 | SACTO | SIERRA | 2020-08-28 | 2021-05-20 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40702018 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0039872 | 0.065152
119824259 | F | LC | ETL.9340.POLE.STPS | 45086292 | FRESNO | YOSEMITE | 2020-09-28 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Structure-Steel | Paint/Coating | [Other] | Tier3 | Tier 3 | Within Both | PEND | 40859495 |  | 2-Pole Non Wood | TPAF - Flat Pin Arm | [7 empty] | 0.0014965 | 7011.5898 | 10.4927
119827027 | B | LC | ETL.6880.POLE.WOOD | 44761203 | LAKEVLLE | NORTH BAY | 2020-09-28 | 2020-10-15 | ETL.6880 | FULTON-CALISTOGA | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119829929 | E | LC | ETL.8580.TOWR | 40609728 | FRESNO | FRESNO | 2020-09-28 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | PEND | 40609728 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | [5 empty] | 1.0141e-06
119844624 | A | LC | ETL.1110.INSL.NCER | 44772147 | TABLEMTN | HUMBOLDT | 2020-10-02 | 2020-10-21 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Emergency | Storm Related | [Repair, Completed, Completed] | Tier2 |  |  | COMP
119892264 | E | LC | ETL.6650.POLE.NWOD | 44917357 | TABLEMTN | NORTH VALLEY | 2020-10-12 | 2021-05-11 | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44917357 | 2020-04-08 | Light Duty Steel Pole | TPSRD - Tramp Double Dead End | 2020-04-08 | Glass | Dead End |  |  |  |  | 0.00016494 | 363.0611
119894846 | E | LC | ETL.1073.POLE.WDPS | 44948164 | VICTOR | STOCKTON | 2020-10-13 | 2021-01-25 | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40872955 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00070476 | 31.7081
119917437 | F | LC | ETL.8290.POLE.NWOD | 44614851 | TABLEMTN | NORTH VALLEY | 2020-09-22 |  | ETL.8290 | VOLTA-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44614851 | 2018-05-17 | Light Duty Steel Pole | DV-PJ - Double Vertical Post Jumper |  | Polymer | Post |  |  |  |  | 5.092e-07 | 2351.9229
120015319 | E | LC | ETL.2911.INSL.CERA | 40835266 | MOSSLNDG | CENTRAL COAST | 2020-11-10 |  | ETL.2911 | LLAGAS-HOLLISTER | Insulator-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40810380 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0002907
120076226 | E | LC | ETL.6500.POLE.WOOD | 40692851 | TABLEMTN | NORTH VALLEY | 2020-06-30 | 2020-11-20 | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40692851 |  | Single Wood Pole | TP - Tri Pin |  | Porcelain | Pin |  |  |  |  | 0.024312 | 4456.2533
120088495 | E | LC | ETL.2270.INSL.CERA | 44737533 | CONCORD | EAST BAY | 2020-11-19 |  | ETL.2270 | MARTINEZ-SOBRANTE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40857608 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 6.8512e-05 | 16.3243 | 0.0011184
120088495 | E | LC | ETL.2270.INSL.CERA | 44737533 | CONCORD | EAST BAY | 2020-11-19 |  | ETL.2270 | MARTINEZ-SOBRANTE | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40857608 | 1941-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-03-25 | Glass Silicone Coated | Suspension |  |  |  |  | 6.8512e-05 | 16.3243 | 0.0011184
120126138 | F | LC | ETL.8350.POLE.WOOD | 40824060 | VICTOR | STOCKTON | 2020-10-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40824060 | 1994-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Ceramic | [5 empty] | 1.8728e-05 | 110.82
120204595 | B | LC | ETL.3840.INSL.NCER | 44951567 | VICTOR | STOCKTON | 2020-12-14 | 2021-03-03 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Hardware-Tower | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41196641 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-05-13 | Glass | Suspension |  |  |  |  | 1.1065e-07 | 809.4304
120232358 | F | LC | ETL.2700.TOWR | 40745866 | CONCORD | EAST BAY | 2020-11-24 | 2021-03-04 | ETL.2700 | MORAGA-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40745866 | 1944-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1944-01-01 | Ceramic | Suspension |  |  |  |  | 2.1543e-05 | 0.065158
120460793 | B | LC | ETL.9200.POLE.WOOD | 40583961 | MIDWAY | KERN | 2021-01-25 | 2021-04-30 | ETL.9200 | TAFT-CUYAMA #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40583961 | 1962-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-04-19 | Glass | Dead End |  |  |  |  | 0.019016
120663641 | E | LC | ETL.8290.POLE.WOOD | 40702894 | TABLEMTN | NORTH VALLEY | 2021-03-19 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40702894 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 6.5786e-05 | 3010.644 | 0.19806
120678742 | E | LC | ETL.3700.INSL.CERA | 40701138 | PISMOBCH | LOS PADRES | 2021-03-23 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40669541 | 1989-01-01 | Single Wood Pole | SV2 - Angle 30-80 Degrees | 1989-01-01 | Porcelain | Suspension |  |  |  |  | 1.4642e-05 | 2048.0973 | 0.029987
120683970 | B | LC | ETL.1810.POLE.WDPS | 44322335 | EUREKA | HUMBOLDT | 2021-03-17 | 2021-06-07 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44322334 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0022299
120686563 | F | LC | ETL.5463.TOWR | 40805085 | CONCORD | MISSION | 2021-03-23 | 2021-04-19 | ETL.5463 | PITTSBURG-SAN MATEO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40805085 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Non Ceramic | Suspension |  |  |  |  | 3.8028e-10 | 1468.4569
120688944 | E | LC | ETL.4870.TOWR | 40746661 | FRESNO | FRESNO | 2021-03-24 |  | ETL.4870 | HELMS-GREGG #1 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40746661 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.803e-06 | 6789.9419 | 0.032612
120689379 | F | LC | ETL.1680.POLE.WDPS | 44298668 | LAKEVLLE | SONOMA | 2021-03-25 | 2021-06-24 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44298666 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0018828 | 2708.3875
120696573 | B | LC | ETL.3840.INSL.NCER | 40836426 | VICTOR | STOCKTON | 2021-03-25 | 2021-05-24 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809680 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Polymer | Post |  |  |  |  | 1.9115e-07 | 5336.0039
120696573 | B | LC | ETL.3840.INSL.NCER | 40836426 | VICTOR | STOCKTON | 2021-03-25 | 2021-05-24 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Hardware-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809680 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Polymer | Suspension |  |  |  |  | 1.9115e-07 | 5336.0039
120701731 | B | LC | ETL.1710.POLE.STPS | 44879503 | MOSSLNDG | CENTRAL COAST | 2021-03-27 | 2021-05-25 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44879476 | 2019-07-27 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.3144e-07 | 15.88
120711331 | B | LC | ETL.2170.TOWR | 40643367 | SACTO | SACRAMENTO | 2021-03-29 | 2021-04-06 | ETL.2170 | MADISON-VACA | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40643367 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-04-30 | Glass | Suspension |  |  |  |  | 1.4688e-08 | 9772.6035
120714250 | E | LC | ETL.8560.INSL.CERA | 44652092 | PISMOBCH | LOS PADRES | 2021-03-30 | 2021-08-05 | ETL.8560 | CAYUCOS-CAMBRIA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
120719974 | E | LC | ETL.6060.TOWR | 40820727 | TABLEMTN | NORTH VALLEY | 2021-03-31 |  | ETL.6060 | ROUND MTN-TABLE MTN #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40820727 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.2846e-05 | 174.1355 | 0.0022369
120721180 | F | LC | ETL.1650.POLE.STPS | 44565654 | LAKEVLLE | SONOMA | 2021-03-31 | 2021-06-18 | ETL.1650 | GEYSERS #3-CLOVERDALE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44564996 |  | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 4.3468e-06 | 4036.5188
120725720 | E | LC | ETL.7390.POLE.WOOD | 40750459 | LAKEVLLE | SONOMA | 2021-04-01 |  | ETL.7390 | LAYTONVILLE-COVELO | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40750459 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.073467
120762426 | F | LC | ETL.1350.POLE.WDPS | 44552360 | TABLEMTN | NORTH VALLEY | 2021-04-08 |  | ETL.1350 | CRAG VIEW-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44551559 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.030972 | 72.8438
120771030 | F | LC | ETL.7140.POLE.WOOD | 40827632 | LAKEVLLE | SONOMA | 2021-04-09 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40827632 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 0.050693 | 490.9328 | 24.887
120794593 | E | LC | ETL.5970.TOWR | 40863558 | PISMOBCH | LOS PADRES | 2021-04-12 |  | ETL.5970 | DIABLO-MIDWAY #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40863558 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-04-22 | Glass | Suspension |  |  |  |  | 3.2415e-07 | 1629.5242 | 0.0005282
120795697 | E | LC | ETL.3830.INSL | 40878810 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40856448 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 8.1565e-06 | 5666.2915 | 0.046217
120798590 | E | LC | ETL.3820.INSL.CERA | 40835154 | VICTOR | STOCKTON | 2021-04-09 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Splice-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40808612 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | [5 empty] | 7e-05 | 4067.2603 | 0.28471
120806697 | F | LC | ETL.1710.POLE.NWOD | 40689909 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40689909 | 1971-01-01 | Lattice Steel Pole | DDE - Double Dead End | 1971-01-01 | Ceramic | Dead End |  |  |  |  | 2.6654e-07 | 0.066431
120806697 | F | LC | ETL.1710.POLE.NWOD | 40689909 | MOSSLNDG | CENTRAL COAST | 2021-04-07 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40689909 | 1971-01-01 | Lattice Steel Pole | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.6654e-07 | 0.066431
120822854 | F | LC | ETL.5330.TOWR | 40587149 | MOSSLNDG | CENTRAL COAST | 2021-04-15 | 2021-05-23 | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40587149 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 3.5267e-06 | 3069.9011
120822854 | F | LC | ETL.5330.TOWR | 40587149 | MOSSLNDG | CENTRAL COAST | 2021-04-15 | 2021-05-23 | ETL.5330 | MOSS LANDING-COBURN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40587149 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 3.5267e-06 | 3069.9011
120841530 | E | LC | ETL.1610.INSL.NCER | 40879865 | LAKEVLLE | SONOMA | 2021-04-12 |  | ETL.1610 | SILVERADO-FULTON JCT | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40858410 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Polymer | Suspension |  |  |  |  | 1.3332e-06 | 269.18 | 0.00035886
120854492 | E | LC | ETL.3500.TOWR | 40856664 | VICTOR | STOCKTON | 2021-04-20 |  | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40856664 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-07-07 | Glass | Double Dead End |  |  |  |  | 0.0012913 | 6665.3057 | 8.6072
120868792 | F | LC | ETL.2700.TOWR | 44188762 | CONCORD | DIABLO | 2021-04-22 |  | ETL.2700 | MORAGA-CLAREMONT #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44188762 | 2008-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | [7 empty] | 3.687e-06 | 445.731
120872365 | E | LC | ETL.5330.INSL | 40714168 | MOSSLNDG | CENTRAL COAST | 2021-04-23 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40662982 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 5.6946e-08 | 0.077799 | 4.4304e-09
120872365 | E | LC | ETL.5330.INSL | 40714168 | MOSSLNDG | CENTRAL COAST | 2021-04-23 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 40662982 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 5.6946e-08 | 0.077799 | 4.4304e-09
120878286 | E | LC | ETL.1250.INSL.NCER | 44189607 | FRESNO | FRESNO | 2021-04-22 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44191793 |  | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 6.9097e-05 | 5983.6006 | 0.41345
120880829 | E | LC | ETL.3500.INSL.NCER | 44461334 | VICTOR | STOCKTON | 2021-04-24 | 2021-07-06 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40820783 | 1930-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2018-01-30 | Glass | Dead End |  |  |  |  | 3.2415e-06 | 95.0148
120912077 | E | LC | ETL.6470.POLE.WOOD | 40693184 | SACTO | SACRAMENTO | 2021-04-30 | 2021-08-09 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693184 |  | Single Wood Pole | T-1 - Tri Post | 2015-10-19 | Polymer | Post |  |  |  |  | 0.014958 | 1439.967
120920363 | E | LC | ETL.7212.POLE.NWOD | 44865989 | METCALF | SAN JOSE | 2021-05-03 | 2021-08-09 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44865989 | 2019-11-01 | Light Duty Steel Pole | T-1 - Tri Post | 2019-11-01 | Polymer | Post |  |  |  |  | 0.6496 | 1430.604
120939121 | E | LC | ETL.8580.TOWR | 40690778 | FRESNO | FRESNO | 2021-05-05 |  | ETL.8580 | COALINGA #1-SAN MIGUEL | Structure-Tower | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40690778 | 1930-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle |  | Porcelain | [5 empty] | 8.9161e-05
120948587 | E | LC | ETL.5300.TOWR | 40762344 | PISMOBCH | LOS PADRES | 2021-04-14 | 2021-11-12 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40762344 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-09-17 | Glass | Suspension |  |  |  |  | 5.9589e-06 | 3926.4705 | 0.023397
121099251 | F | LC | ETL.5300.TOWR | 40821532 | PISMOBCH | LOS PADRES | 2021-04-19 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40821532 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 1.1733e-06 | 3135.615 | 0.003679
121188777 | E | LC | ETL.8250.POLE.WOOD | 40912845 | VICTOR | STOCKTON | 2021-05-11 | 2021-05-13 | ETL.8250 | CLAY-MARTEL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40912845 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 7.3989e-05 | 2471.1772
121322515 | F | LC | ETL.4850.TOWR | 40581322 | FRESNO | FRESNO | 2021-04-21 |  | ETL.4850 | HAAS-MCCALL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40581322 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1957-01-01 | Ceramic | Double Dead End |  |  |  |  | 7.0557e-06 | 6837.5508 | 0.048244
121345327 | B | LC | ETL.6980.INSL.NCER | 40699250 | LAKEVLLE | HUMBOLDT | 2021-05-17 | 2021-05-25 | ETL.6980 | FORT ROSS-GUALALA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40667852 | 2003-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 2003-01-01 | Polymer | Dead End |  |  |  |  | 0.052646 | 1030.7567
121351843 | F | LC | ETL.4100.TOWR | 40862956 | LAKEVLLE | SACRAMENTO | 2021-04-28 |  | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40862956 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-05-28 | Glass | Suspension |  |  |  |  | 2.9416e-05 | 5399.8154 | 0.15884
121357034 | F | LC | ETL.1422.TOWR | 40872251 | SACTO | SIERRA | 2021-04-22 |  | ETL.1422 | BRUNSWICK #1 TAP | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40872251 | 1975-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1975-01-01 | Ceramic | Dead End |  |  |  |  | 5.967e-06 | 506.2574 | 0.0030208
121359293 | F | LC | ETL.4590.TOWR | 40910151 | TABLEMTN | NORTH VALLEY | 2021-04-23 |  | ETL.4590 | CRESTA-RIO OSO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40910151 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-03-15 | Ceramic | Suspension |  |  |  |  | 1.14e-05 | 601.2244
121367076 | B | LC | ETL.1350.INSL | 40845402 | TABLEMTN |  | 2021-05-18 | 2021-05-27 | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40817457 | 1993-01-01 | Single Wood Pole | DV - Double Vertical | 1993-01-01 | Ceramic | Suspension |  |  |  |  | 0.016586 | 3785.6211
121370642 | E | LC | ETL.5070.TOWR | 40873307 | FRESNO | YOSEMITE | 2021-05-04 |  | ETL.5070 | QUINTO SW STA-WESTLEY | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40873307 | 1947-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1947-01-01 | Ceramic | Suspension |  |  |  |  | 2.2788e-06 | 767.5238 | 0.001749
121370685 | F | LC | ETL.6880.POLE.WOOD | 40700650 | LAKEVLLE | NORTH BAY | 2021-05-01 | 2021-06-04 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 |  |  | DLFL
121370884 | E | LC | ETL.5140.POLE.NWOD | 45146240 | SACTO | SIERRA | 2021-05-01 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45146240 | 2020-10-08 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2020-10-08 | Glass | Dead End
121378583 | E | LC | ETL.3700.POLE.WOOD | 40828911 | PISMOBCH | LOS PADRES | 2021-05-06 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40828911 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Porcelain | Post |  |  |  |  | 0.00067688 | 4133.0879 | 2.7976
121379180 | E | LC | ETL.8350.POLE.NWOD | 44762534 | VICTOR | STOCKTON | 2021-05-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44762534 | 2019-05-13 | Light Duty Steel Pole | T-1 - Tri Post | 2019-05-13 | Polymer | Post |  |  |  |  | 1.8681e-06 | 4494.9391 | 0.0083971
121379589 | E | LC | ETL.3830.TOWR | 40604155 | VICTOR | STOCKTON | 2021-05-21 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40604155 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 2.2414e-06 | 809.4304 | 0.0018143
121381977 | F | LC | ETL.6500.POLE.WOOD | 40824164 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40824164 |  | Single Wood Pole | T2N | 2018-06-29 | Polymer | Post |  |  |  |  | 0.014036 | 95.0648
121382283 | F | LC | ETL.6760.POLE.WOOD | 40603085 | SACTO | SIERRA | 2021-05-05 | 2021-10-04 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40603085 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.026999 | 901.7202
121384461 | E | LC | ETL.7380.POLE.WOOD | 40827811 | MOSSLNDG | CENTRAL COAST | 2021-05-12 | 2021-06-11 | ETL.7380 | LAURELES-OTTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40827811 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.25369 | 221.4934
121384463 | F | LC | ETL.6500.POLE.WOOD | 40766507 | SACTO | SIERRA | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40766507 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00052562 | 2214.9285
121403713 | E | LC | ETL.6290.POLE.WOOD | 40809566 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40809566 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.071201 | 5282.8242 | 376.1429
121403991 | E | LC | ETL.8410.POLE.WOOD | 40820744 | LAKEVLLE | SONOMA | 2021-05-26 |  | ETL.8410 | ELK-GUALALA | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40820744 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 2020-12-08 | Glass | Suspension |  |  |  |  | 0.22742 | 795.2655 | 180.8566
121405619 | E | LC | ETL.6040.TOWR | 40587672 | MOSSLNDG | CENTRAL COAST | 2021-05-21 |  | ETL.6040 | MOSS LANDING-LOS BANOS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40587672 | 1966-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 1.0462e-07 | 113.7675 | 1.1902e-05
121417444 | E | LC | ETL.6720.POLE.WOOD | 40649885 | TABLEMTN | NORTH VALLEY | 2021-05-19 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40649885 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Pin |  |  |  |  | 0.0006003 | 221.5575 | 0.133
121418441 | E | LC | ETL.1402.POLE.WDPS | 44550063 | VICTOR | YOSEMITE | 2021-05-25 | 2021-07-12 | ETL.1402 | SPRING GAP TAP | Crossarm-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44550063 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0092432
121418441 | E | LC | ETL.1402.POLE.WDPS | 44550063 | VICTOR | YOSEMITE | 2021-05-25 | 2021-07-12 | ETL.1402 | SPRING GAP TAP | Crossarm-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44550063 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Ceramic | Suspension |  |  |  |  | 0.0092432
121420291 | E | LC | ETL.1400.POLE.STPS | 44381770 | VICTOR | YOSEMITE | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44381769 | 2017-08-17 | 2-Pole Non Wood | DE - Dead End | [7 empty] | 0.00011602 | 158.2923 | 0.018365
121420340 | E | LC | ETL.7290.POLE.WOOD | 40660764 | TABLEMTN | NORTH VALLEY | 2021-05-27 | 2021-07-12 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
121422105 | E | LC | ETL.6640.POLE.WOOD | 40825162 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40825162 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0066689 | 886.3928 | 5.9113
121436455 | F | LC | ETL.5640.TOWR | 40756113 | TABLEMTN | NORTH VALLEY | 2021-06-01 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40756113 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 3.9107e-06 | 4421.1143 | 0.017289
121470104 | B | LC | ETL.2790.INSL | 40792395 | CONCORD | EAST BAY | 2021-06-04 | 2021-07-29 | ETL.2790 | MORAGA-SAN LEANDRO #3 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40761845 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 4.2616e-06 | 0.065147
121475219 | E | LC | ETL.8365.POLE.WOOD | 40698328 | EUREKA | HUMBOLDT | 2021-05-28 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40698328 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.011982 | 1014.259 | 12.1527
121475847 | E | LC | ETL.7212.POLE.WOOD | 40656247 | METCALF | PENINSULA | 2021-05-27 | 2021-08-17 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40656247 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 0.17404 | 648.7263
121493486 | E | LC | ETL.5640.TOWR | 40858196 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5640 | ROUND MTN-COTTONWOOD #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40858196 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1954-01-01 | Ceramic | Suspension |  |  |  |  | 1.8533e-07 | 2615.6379 | 0.00048476
121495161 | E | LC | ETL.4880.TOWR | 40740035 | FRESNO | FRESNO | 2021-06-07 |  | ETL.4880 | HELMS-GREGG #2 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] |  | Zone 1 | HFRA Removal | PEND | 40740035 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 9.3078e-06
121496593 | E | LC | ETL.1600.INSL.NCER | 40781106 | LAKEVLLE | SONOMA | 2021-06-01 |  | ETL.1600 | FULTON-PUEBLO | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40752686 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1946-01-01 | Polymer | Suspension |  |  |  |  | 2.0113e-06 | 0.06643 | 1.3361e-07
121499793 | E | LC | ETL.1350.POLE.WDPS | 44549951 | TABLEMTN |  | 2021-06-04 |  | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44549436 |  | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.012073 | 411.4229 | 4.9672
121500489 | F | LC | ETL.1450.POLE.WDPS | 44155567 | SACTO | SACRAMENTO | 2021-06-04 | 2021-07-12 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44155566 | 2013-11-06 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0038709 | 3069.2839
121512428 | B | LC | ETL.1350.POLE.WDPS | 44552551 | TABLEMTN |  | 2021-06-09 | 2021-08-02 | ETL.1350 | CRAG VIEW-CASCADE | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44551562 |  | 2-Pole Wood | DDE - Double Dead End | [7 empty] | 0.055855 | 1422.5072
121517041 | E | LC | ETL.2760.INSL | 40629434 | CONCORD | EAST BAY | 2021-06-03 |  | ETL.2760 | MORAGA-OAKLAND J | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40587933 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.4185e-05 | 0.065147 | 2.8785e-06
121517041 | E | LC | ETL.2760.INSL | 40629434 | CONCORD | EAST BAY | 2021-06-03 |  | ETL.2760 | MORAGA-OAKLAND J | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40587933 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 4.4185e-05 | 0.065147 | 2.8785e-06
121523815 | E | LC | ETL.4440.TOWR | 40591401 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.4440 | CARIBOU-TABLE MTN | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40591401 | 1958-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 3.9365e-05 | 6758.8389 | 0.26606
121524952 | E | LC | ETL.1440.POLE.WDPS | 44765652 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40865987 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0018212 | 648.7145 | 1.1815
121525468 | F | LC | ETL.6500.POLE.NWOD | 44424341 | SACTO | NORTH VALLEY | 2021-06-09 | 2021-07-06 | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44424341 | 2018-02-17 | Tubular Steel Pole | FSS - Field Switch Structure | [7 empty] | 6.1539e-06 | 3374.0149
121526789 | E | LC | ETL.7990.POLE.WOOD | 40909013 | SACTO | SIERRA | 2021-06-09 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40909013 |  | Single Wood Pole | TCP - Twin Circuit Pin |  | Porcelain | Unknown |  |  |  |  | 0.00022753 | 2125.1653 | 0.48355
121527046 | B | LC | ETL.1610.INSL | 40611458 | LAKEVLLE | SONOMA | 2021-06-12 | 2021-09-09 | ETL.1610 | SILVERADO-FULTON JCT | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40586773 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 4.6457e-05 | 2438.3081
121539819 | E | LC | ETL.1820.POLE.WDPS | 44557657 | EUREKA | HUMBOLDT | 2021-06-10 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44553920 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.081849 | 5273.0366 | 431.5945
121542241 | E | LC | ETL.5720.TOWR | 40869514 | CONCORD | MISSION | 2021-06-11 | 2021-10-27 | ETL.5720 | TESLA-NEWARK #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40869514 | 1971-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1972-01-01 | Ceramic | Suspension |  |  |  |  | 8.2214e-08 | 3469.124 | 0.00028521
121542912 | F | LC | ETL.1820.POLE.NWOD | 45009232 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45009232 | 2020-06-08 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-08 | Glass | Double Dead End |  |  |  |  | 0.0013564 | 63.3274
121546318 | E | LC | ETL.7020.POLE.WDPS | 44417289 | TABLEMTN | NORTH VALLEY | 2021-06-16 |  | ETL.7020 | HAT CREEK #1-PIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44417286 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.88937 | 1969.1527 | 1751.3039
121549309 | F | LC | ETL.1820.POLE.NWOD | 44947380 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44947380 | 2020-03-03 | Light Duty Steel Pole | DDE - Double Dead End | 2020-03-03 | Glass | Dead End |  |  |  |  | 6.8763e-05 | 2704.6782
121550168 | F | LC | ETL.1350.POLE.WOOD | 44993915 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.1350 | CRAG VIEW-CASCADE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44993915 | 2020-06-16 | Light Duty Steel Pole | DDE - Double Dead End | 2020-06-16 | Glass | Dead End |  |  |  |  | 5.9411e-05 | 142.6993
121557095 | E | LC | ETL.6750.POLE.WDPS | 44561500 | TABLEMTN |  | 2021-06-17 |  | ETL.6750 | DELTA-MTN GATE JCT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44560769 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00050883 | 94.9939 | 0.048336
121573570 | E | LC | ETL.7390.POLE.WOOD | 40648608 | LAKEVLLE | HUMBOLDT | 2021-06-18 | 2021-10-21 | ETL.7390 | LAYTONVILLE-COVELO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648608 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.040782 | 696.1808 | 28.3913
121586949 | B | LC | ETL.1470.INSL.CERA | 40778578 | LAKEVLLE | HUMBOLDT | 2021-06-14 | 2021-07-26 | ETL.1470 | EAGLE ROCK-CORTINA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40750571 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 3.5556e-06 | 6459.0942
121587237 | F | LC | ETL.4040.POLE.STPS | 44647042 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44646866 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00034786 | 919.3794
121588389 | B | LC | ETL.7060.POLE.WDPS | 45099514 | METCALF | PENINSULA | 2021-06-23 | 2021-07-08 | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Other | Vegetation Overgrown | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42564724 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0023905 | 412.0099
121603725 | B | LC | ETL.7851.POLE.WDPS | 44752426 | EUREKA | HUMBOLDT | 2021-06-24 | 2021-08-18 | ETL.7851 | RIO DELL TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587603 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.42117 | 221.4831
121604304 | E | LC | ETL.6020.TOWR | 40753301 | TABLEMTN | NORTH VALLEY | 2021-06-24 |  | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40753301 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 9.9361e-05 | 569.8778 | 0.056624
121605417 | E | LC | ETL.6760.POLE.WOOD | 40758335 | SACTO | SIERRA | 2021-06-23 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40758335 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0041316 | 15.8837 | 0.065626
121624921 | E | LC | ETL.1710.POLE.WDPS | 44510537 | MOSSLNDG | CENTRAL COAST | 2021-06-28 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44509646 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0011403 | 0.065147 | 7.4286e-05
121653915 | B | LC | ETL.3700.INSL.NCER | 44619251 | PISMOBCH | LOS PADRES | 2021-06-30 | 2021-07-19 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44390255 | 2018-04-08 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-04-08 | Polymer | Dead End |  |  |  |  | 0.00022939
121653915 | B | LC | ETL.3700.INSL.NCER | 44619251 | PISMOBCH | LOS PADRES | 2021-06-30 | 2021-07-19 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44390255 | 2018-04-08 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-04-08 | Polymer | Dead End |  |  |  |  | 0.00022939
121653915 | B | LC | ETL.3700.INSL.NCER | 44619251 | PISMOBCH | LOS PADRES | 2021-06-30 | 2021-07-19 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44390255 | 2018-04-08 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | 2018-04-08 | Polymer | Dead End |  |  |  |  | 0.00022939
121660212 | E | LC | ETL.4610.POLE.NWOD | 45026139 | PISMOBCH | LOS PADRES | 2021-06-26 | 2021-09-15 | ETL.4610 | DIABLO PP STANDBY SUPPLY | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 45026139 | 2020-10-28 | Tubular Steel Pole | DE - Dead End | 2020-10-28 | Glass Silicone Coated | Dead End |  |  |  |  | 1.0088e-06 | 1061
121669029 | E | LC | ETL.6650.POLE.WDPS | 44386746 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44386745 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.016048 | 519.4674 | 8.3365
121670344 | E | LC | ETL.1710.POLE.WDPS | 44512100 | MOSSLNDG | CENTRAL COAST | 2021-07-06 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44510838 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.005844 | 3.2281 | 0.018865
121704636 | E | LC | ETL.6020.TOWR | 40819384 | TABLEMTN | NORTH VALLEY | 2021-07-09 | 2021-08-05 | ETL.6020 | MALIN-ROUND MTN #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40819384 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 3.9302e-07 | 174.1517
121706527 | E | LC | ETL.6770.INSL.NCER | 45081644 | SACTO | SIERRA | 2021-07-09 |  | ETL.6770 | DRUM-SPAULDING | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45081631 | 2021-04-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-04-16 | Glass | Dead End |  |  |  |  | 0.0082103 | 47.5526 | 0.39042
121707279 | E | LC | ETL.7640.POLE.WDPS | 44565575 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44564245 |  | 2-Pole Wood | TH - TriAngle Post 70 | [7 empty] | 6.7495e-05 | 3880.9729 | 0.26195
121731972 | F | LC | ETL.1440.POLE.NWOD | 44338091 | SACTO | SIERRA | 2021-07-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44338091 |  | Light Duty Steel Pole | 3P DV - 3 Pole Double Vertical | 2018-09-06 | Ceramic | Dead End |  |  |  |  | 2.3808e-05 | 2056.7583
121741591 | F | LC | ETL.6660.POLE.NWOD | 45084740 | TABLEMTN | NORTH VALLEY | 2021-07-09 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45084740 | 2021-03-04 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-03-04 | Glass | Dead End |  |  |  |  | 4.2644e-11 | 4215.1406
121743988 | F | LC | ETL.1660.POLE.NWOD | 44650022 | LAKEVLLE | SONOMA | 2021-07-15 |  | ETL.1660 | GEYSERS #3-EAGLE ROCK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44650022 | 2018-09-08 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2018-09-08 | Polymer | Suspension |  |  |  |  | 1.8626e-07 | 5274.8779
121747165 | E | LC | ETL.1820.POLE.WDPS | 44562177 | EUREKA | HUMBOLDT | 2021-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591243 | 1949-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.87148 | 395.7131 | 344.8554
121749940 | E | LC | ETL.4040.POLE.STPS | 45100485 | TABLEMTN | NORTH VALLEY | 2021-07-14 |  | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | PEND | 42622397 |  | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00090329 | 142.4582 | 0.12868
121753134 | F | LC | ETL.8365.POLE.NWOD | 45021957 | EUREKA | HUMBOLDT | 2021-07-19 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 45021957 | 2020-12-21 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-12-21 | Polymer | Post |  |  |  |  | 0.00057876
121755505 | F | LC | ETL.1440.POLE.NWOD | 45109892 | SACTO | SIERRA | 2021-07-19 | 2021-07-29 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 45109892 | 2020-08-10 | Light Duty Steel Pole | DDE - Double Dead End | 2020-08-10 | Glass | Dead End | [5 empty] | 0.065152
121803873 | B | LC | ETL.5970.INSL | 40729647 | PISMOBCH | LOS PADRES | 2021-07-26 | 2021-09-15 | ETL.5970 | DIABLO-MIDWAY #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40690279 | 1973-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 2.76e-06 | 838.9597
121810304 | B | LC | ETL.2420.POLE.WDPS | 44226602 | LAKEVLLE |  | 2021-07-27 | 2021-08-16 | ETL.2420 | MENDOCINO-UKIAH | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44226600 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 5.9346e-05 | 2309.5676
121816818 | F | LC | ETL.8405.POLE.WOOD | 40611426 | SACTO | SIERRA | 2021-07-28 | 2021-10-04 | ETL.8405 | MIDDLE FORK #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40611426 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0017884 | 6807.7681
121820954 | E | LC | ETL.8630.POLE.WDPS | 44565491 | PISMOBCH | LOS PADRES | 2021-07-28 |  | ETL.8630 | DIVIDE-VANDENBERG #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44564299 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00032026 | 3009.1343 | 0.96371
121960127 | F | LC | ETL.9250.POLE.NWOD | 40820577 | MIDWAY | KERN | 2021-08-26 |  | ETL.9250 | TEJON-LEBEC | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40820577 |  | Tubular Steel Pole | T-1 - Tri Post |  | Non Ceramic | [5 empty] | 0.00067402 | 4976.3872
121983996 | E | LC | ETL.6300.POLE.WOOD | 40656481 | TABLEMTN | NORTH VALLEY | 2021-09-01 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40656481 |  | Single Wood Pole | TCDE - Tap Construction Dead End | 2014-11-07 | Non Ceramic | Dead End |  |  |  |  | 0.00020901 | 5538.7192 | 1.1576
122256498 | B | LC | ETL.7140.POLE.STPS | 41178108 | LAKEVLLE | SONOMA | 2021-10-25 | 2021-11-02 | ETL.7140 | IGNACIO-BOLINAS #1 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41178108 |  | 2-Pole Non Wood | DE - Dead End | 2021-02-28 | Glass Silicone Coated | Dead End |  |  |  |  | 0.00050138
122256498 | B | LC | ETL.7140.POLE.STPS | 41178108 | LAKEVLLE | SONOMA | 2021-10-25 | 2021-11-02 | ETL.7140 | IGNACIO-BOLINAS #1 | Non-Routine Patrol | Investigate | [Ground Patrol, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41178108 |  | 2-Pole Non Wood | DE - Dead End | 2021-02-28 | Glass Silicone Coated | Dead End |  |  |  |  | 0.00050138
118454001 | E | LC | ETL.6760.POLE.WOOD | 40693456 | SACTO | SACRAMENTO | 2020-01-23 | 2020-06-04 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40693456 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.037736 | 632.8055
118575999 | E | LC | ETL.4340.INSL | 40884843 | CONCORD |  | 2020-02-25 | 2020-06-08 | ETL.4340 | BAHIA-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862755 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-26 | Glass Silicone Coated | Suspension |  |  |  |  | 1.3065e-08 | 556.4825
118575999 | E | LC | ETL.4340.INSL | 40884843 | CONCORD |  | 2020-02-25 | 2020-06-08 | ETL.4340 | BAHIA-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40862755 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 1.3065e-08 | 556.4825
118576047 | B | LC | ETL.4340.INSL.NCER | 44812804 | CONCORD |  | 2020-02-25 | 2020-04-08 | ETL.4340 | BAHIA-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600039 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-06-01 | Glass | Suspension |  |  |  |  | 7.4285e-09 | 619.7224
118576047 | B | LC | ETL.4340.INSL.NCER | 44812804 | CONCORD |  | 2020-02-25 | 2020-04-08 | ETL.4340 | BAHIA-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600039 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 7.4285e-09 | 619.7224
118786144 | B | LC | ETL.5463.TOWR | 40819690 | CONCORD | MISSION | 2020-04-06 | 2020-07-06 | ETL.5463 | PITTSBURG-SAN MATEO | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40819690 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 7.2762e-08 | 2709.8901
118796932 | E | LC | ETL.3960.TOWR | 40861661 | PISMOBCH | LOS PADRES | 2020-04-08 | 2020-05-20 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861661 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 1.3355e-05 | 1568.4982
118796932 | E | LC | ETL.3960.TOWR | 40861661 | PISMOBCH | LOS PADRES | 2020-04-08 | 2020-05-20 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40861661 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 1.3355e-05 | 1568.4982
118922445 | E | LC | ETL.7590.INSL.CERA | 40731937 | MOSSLNDG | CENTRAL COAST | 2020-04-15 | 2020-09-14 | ETL.7590 | MONTA VISTA-BURNS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40694921 |  | Single Wood Pole | 3P TRP D - 3 Pole Tramp Double Dead End |  | Ceramic | Pin |  |  |  |  | 0.35607 | 95.0065
118936194 | F | LC | ETL.8210.POLE.WOOD | 40905584 | VICTOR | STOCKTON | 2020-04-20 | 2021-01-25 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | DLFL | 40905584 | 1959-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.044866 | 47.6172
118940447 | E | LC | ETL.4780.INSL.CERA | 40629533 | LAKEVLLE | SONOMA | 2020-04-22 | 2021-05-20 | ETL.4780 | GEYSERS #9-LAKEVILLE | Damper-Steel | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129179 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1979-01-01 | Porcelain | Dead End |  |  |  |  | 0.0054538 | 1378.0675
118940447 | E | LC | ETL.4780.INSL.CERA | 40629533 | LAKEVLLE | SONOMA | 2020-04-22 | 2021-05-20 | ETL.4780 | GEYSERS #9-LAKEVILLE | Damper-Steel | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129179 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1979-01-01 | Ceramic | Dead End |  |  |  |  | 0.0054538 | 1378.0675
118940447 | E | LC | ETL.4780.INSL.CERA | 40629533 | LAKEVLLE | SONOMA | 2020-04-22 | 2021-05-20 | ETL.4780 | GEYSERS #9-LAKEVILLE | Damper-Steel | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 41129179 | 1973-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle |  | Porcelain | [5 empty] | 0.0054538 | 1378.0675
118966652 | E | LC | ETL.8351.POLE.WOOD | 40864228 | VICTOR | STOCKTON | 2020-04-30 | 2021-06-28 | ETL.8351 | PINE GROVE TAP | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40864228 | 1977-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Glass | [5 empty] | 0.00045307 | 17.4655
119000113 | E | LC | ETL.7510.POLE.WOOD | 40876798 | LAKEVLLE | SONOMA | 2020-05-08 | 2020-06-08 | ETL.7510 | MENDOCINO-HARTLEY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876798 |  | Single Wood Pole | TAP - Tri Arm Post | 2020-05-26 | Glass | Dead End |  |  |  |  | 8.69e-06 | 5288.4775
119081164 | E | LC | ETL.6710.INSL.NCER | 44925319 | MOSSLNDG | CENTRAL COAST | 2020-05-29 |  | ETL.6710 | DEL MONTE-VIEJO | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40809840 |  | Single Wood Pole | T1-1A | 2020-05-18 | Polymer | Post |  |  |  |  | 0.21591 | 0.065148 | 0.014066
119083615 | E | LC | ETL.6950.POLE.WOOD | 40693035 | SACTO | SIERRA | 2020-05-28 | 2021-08-02 | ETL.6950 | GOLD HILL #1 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40693035 | 2014-08-18 | Single Wood Pole | T-1 - Tri Post | 2021-07-27 | Polymer | Post |  |  |  |  | 0.0012546 | 1044.1373
119099307 | F | LC | ETL.6760.POLE.WOOD | 40767296 | SACTO | SIERRA | 2020-05-27 | 2021-05-08 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40767296 |  | Single Wood Pole | T1DE - Tri Post Dead End 115 | 2020-05-28 | Polymer | Dead End - Post |  |  |  |  | 0.038486 | 205.7564
119114728 | F | LC | ETL.7290.POLE.WOOD | 40592406 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40592406 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.061912 | 2361.8477
119114902 | E | LC | ETL.3750.TOWR | 44188758 | CONCORD | DIABLO | 2020-05-21 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44188758 | 2008-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | [7 empty] | 2.1728e-06 | 445.731 | 0.00096846
119116275 | E | LC | ETL.4221.POLE.WOOD | 40658758 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-04-19 | ETL.4221 | SLY CREEK TAP | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40658758 | 1982-01-01 | Single Wood Pole | SV1 - Angle 0-30 Degrees | 2019-05-21 | Glass | Suspension |  |  |  |  | 0.00040476 | 94.963
119116320 | F | LC | ETL.7290.POLE.WOOD | 40759581 | TABLEMTN | NORTH VALLEY | 2020-05-29 | 2021-08-30 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40759581 |  | Single Wood Pole | T2N | 2021-02-23 | Polymer | Post |  |  |  |  | 0.003959 | 666.5034
119118610 | F | LC | ETL.8290.POLE.WOOD | 40592115 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40592115 |  | Single Wood Pole | T2N | 2016-09-30 | Polymer | Post |  |  |  |  | 0.001388 | 5257.5366
119118686 | F | LC | ETL.6330.POLE.NWOD | 40867565 | TABLEMTN | NORTH VALLEY | 2020-06-02 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40867565 | 1998-01-01 | Tubular Steel Pole | T-1 - Tri Post | 2016-06-02 | Polymer | Post |  |  |  |  | 4.758e-06 | 4985.4875
119119124 | E | LC | ETL.7300.POLE.WOOD | 40602051 | TABLEMTN |  | 2020-06-03 | 2021-08-17 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40602051 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.0066472 | 285.7737
119119378 | F | LC | ETL.6490.POLE.WOOD | 40807974 | SACTO | SIERRA | 2020-06-02 |  | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40807974 |  | Single Wood Pole | T-1 - Tri Post | 2017-03-16 | Polymer | Post |  |  |  |  | 0.013743 | 2369.7044
119126190 | E | LC | ETL.7300.POLE.WOOD | 41118628 | TABLEMTN |  | 2020-06-04 | 2021-09-01 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41118628 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.00016875 | 4468.0879
119126194 | E | LC | ETL.7300.POLE.WOOD | 40600376 | TABLEMTN |  | 2020-06-04 | 2021-08-17 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40600376 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.00083771 | 731.3142
119129577 | F | LC | ETL.7300.POLE.WOOD | 40876556 | TABLEMTN |  | 2020-06-04 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40876556 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.0070659 | 285.7737
119163602 | E | LC | ETL.7550.INSL.NCER | 40833341 | LAKEVLLE |  | 2020-06-13 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40808804 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 7.3718e-06 | 3342.5151 | 0.02464
119168101 | F | LC | ETL.6280.POLE.WOOD | 40769592 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40769592 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Other |  |  |  |  | 1.1844e-05 | 1202.1041
119175133 | F | LC | ETL.6480.POLE.NWOD | 45122791 | SACTO | NORTH VALLEY | 2020-06-15 |  | ETL.6480 | COLGATE-CHALLENGE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45122791 | 2021-06-20 | Light Duty Steel Pole | T-1 - Tri Post | 2021-06-20 | Polymer | Post | [5 empty] | 253.3131
119180325 | F | LC | ETL.1073.POLE.WDPS | 44971839 | VICTOR | YOSEMITE | 2020-06-16 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40803419 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00014147 | 15.88
119184266 | F | LC | ETL.6440.POLE.WOOD | 40590361 | TABLEMTN | NORTH VALLEY | 2020-06-18 | 2020-07-14 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40590361 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0025397 | 3534.6604
119185224 | F | LC | ETL.6280.POLE.WOOD | 40769492 | TABLEMTN | NORTH VALLEY | 2020-06-17 | 2021-01-20 | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40769492 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 5.6472e-06 | 6570.3479
119196465 | F | LC | ETL.1350.POLE.STPS | 44996564 | TABLEMTN | NORTH VALLEY | 2020-06-22 |  | ETL.1350 | CRAG VIEW-CASCADE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44996546 | 2020-06-15 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.8841e-05 | 318.0763
119197083 | F | LC | ETL.6470.POLE.WOOD | 40824276 | SACTO | SIERRA | 2020-06-22 | 2021-07-08 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40824276 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.099748 | 142.4516
119201097 | F | LC | ETL.9340.POLE.NWOD | 44844654 | FRESNO | FRESNO | 2020-06-23 |  | ETL.9340 | WISHON-SAN JOAQUIN #3 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44844654 | 2019-09-28 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-09-28 | Glass | Dead End |  |  |  |  | 0.00021064 | 6998.9342
119202531 | B | LC | ETL.4220.POLE.STPS | 44762694 | TABLEMTN | NORTH VALLEY | 2020-06-23 | 2020-07-15 | ETL.4220 | WOODLEAF-PALERMO | Other | Customer Issue | [Access Issue] |  | Tier 2 | Within Both | DLFL | 44762533 | 2019-05-01 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 3.2164e-05 | 174.0849
119205702 | F | LC | ETL.7180.POLE.WOOD | 40770133 | LAKEVLLE | NORTH BAY | 2020-06-24 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40770133 |  | Single Wood Pole | DV-DE - Double Vertical Dead End |  | Glass | [5 empty] | 7.3513e-06 | 2361.1138
119291072 | F | LC | ETL.7270.POLE.WOOD | 40650319 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.7270 | KESWICK-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40650319 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.019903 | 205.7693
119304538 | E | LC | ETL.2060.POLE.WOOD | 40824307 | LAKEVLLE | SONOMA | 2020-07-02 | 2021-06-01 | ETL.2060 | FORT BRAGG-ELK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40824307 | 1961-01-01 | Single Wood Pole | SVDE - Single Vertical Dead End | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.16824 | 553.6479
119308400 | E | LC | ETL.1450.TOWR | 40671557 | SACTO | SIERRA | 2020-07-01 | 2020-10-06 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40671557 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Dead End |  |  |  |  | 0.00059742 | 1123.6396
119310639 | F | LC | ETL.4441.POLE.NWOD | 43198033 | TABLEMTN | NORTH VALLEY | 2020-07-02 |  | ETL.4441 | BELDEN TAP | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 43198033 |  | Lattice Steel Pole | SVDE - Single Vertical Dead End | 2021-03-31 | Glass Silicone Coated | Dead End |  |  |  |  | 1.4053e-07 | 1486.7976
119316618 | E | LC | ETL.7270.POLE.WOOD | 40827893 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2020-11-09 | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40827893 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Unknown |  |  |  |  | 0.045727 | 1076.101
119326091 | E | LC | ETL.1470.POLE.WOOD | 41176300 | LAKEVLLE | SONOMA | 2020-07-07 | 2021-06-21 | ETL.1470 | EAGLE ROCK-CORTINA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41176300 | 1978-01-01 | Single Wood Pole | T-1 - Tri Post | 1978-01-01 | Porcelain | Post |  |  |  |  | 0.0026271 | 4099.8861
119330807 | E | LC | ETL.8580.INSL.CERA | 40796346 | PISMOBCH | FRESNO | 2020-07-08 | 2021-06-30 | ETL.8580 | COALINGA #1-SAN MIGUEL | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40765605 | 1930-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.00013326 | 1157.0782
119338537 | F | LC | ETL.7030.POLE.WOOD | 40825595 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-02-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40825595 |  | Single Wood Pole | T2N | 2018-11-30 | Polymer | Post |  |  |  |  | 0.0065348 | 0.06515
119350133 | E | LC | ETL.6300.POLE.WOOD | 40656501 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-07-01 | ETL.6300 | CARIBOU-WESTWOOD | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40656501 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0035876 | 31.6984
119355076 | A | LC | ETL.1440.INSL | 40784574 | SACTO | SIERRA | 2020-07-09 | 2020-08-03 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40755595 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.02801
119355076 | A | LC | ETL.1440.INSL | 40784574 | SACTO | SIERRA | 2020-07-09 | 2020-08-03 | ETL.1440 | DRUM-SUMMIT #1 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40755595 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.02801
119360470 | F | LC | ETL.7030.POLE.WOOD | 40769937 | TABLEMTN | NORTH VALLEY | 2020-07-13 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40769937 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.012546 | 3468.7698
119371045 | F | LC | ETL.6290.POLE.WOOD | 40614947 | TABLEMTN | NORTH VALLEY | 2020-07-14 | 2021-02-11 | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40614947 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.057889 | 4824.2021
119379804 | B | LC | ETL.6222.POLE.WOOD | 40861033 | EUREKA | HUMBOLDT | 2020-07-15 | 2020-08-31 | ETL.6222 | FORT SEWARD TAP | Tie Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40861033 | 1952-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0083883
119473696 | F | LC | ETL.1820.POLE.STPS | 44395134 | EUREKA | HUMBOLDT | 2020-07-15 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44395133 | 2020-03-09 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0035163 | 189.9226
119489023 | F | LC | ETL.2060.POLE.WOOD | 40824285 | LAKEVLLE | SONOMA | 2020-07-22 |  | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40824285 | 1961-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1961-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.17591 | 0.065148
119489413 | F | LC | ETL.8170.POLE.WOOD | 40906339 | EUREKA | HUMBOLDT | 2020-07-21 |  | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40906339 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.018083 | 4462.79
119511949 | F | LC | ETL.5300.TOWR | 40689432 | PISMOBCH | LOS PADRES | 2020-07-27 | 2021-01-11 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40689432 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-09-17 | Glass | Suspension |  |  |  |  | 1.1861e-05 | 4765.5547
119535344 | E | LC | ETL.6220.POLE.WOOD | 40698372 | EUREKA | HUMBOLDT | 2020-07-31 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40698372 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.014134 | 618.2028 | 8.7378
119549736 | F | LC | ETL.6380.POLE.WOOD | 40698971 | LAKEVLLE | HUMBOLDT | 2020-08-03 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40698971 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Other |  |  |  |  | 0.00023175 | 4766.3267
119551732 | F | LC | ETL.6770.POLE | 40660061 | SACTO | SIERRA | 2020-08-03 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40660061 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.013971 | 2183.324
119559714 | F | LC | ETL.7291.POLE.WOOD | 42712147 | TABLEMTN | NORTH VALLEY | 2020-08-04 | 2021-01-20 | ETL.7291 | CLOVER CREEK TAP | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 42712147 |  | 2-Pole Wood | FSS - Field Switch Structure | [7 empty] | 0.014825
119559714 | F | LC | ETL.7291.POLE.WOOD | 42712147 | TABLEMTN | NORTH VALLEY | 2020-08-04 | 2021-01-20 | ETL.7291 | CLOVER CREEK TAP | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 42712147 |  | 2-Pole Wood | FSS - Field Switch Structure | [7 empty] | 0.014825
119573924 | E | LC | ETL.6980.POLE.WOOD | 40656415 | LAKEVLLE | HUMBOLDT | 2020-08-06 | 2021-01-14 | ETL.6980 | FORT ROSS-GUALALA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
119574600 | E | LC | ETL.8365.POLE.WOOD | 40861087 | EUREKA | HUMBOLDT | 2020-08-07 | 2021-05-11 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40861087 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0030809 | 1164.6096
119596167 | F | LC | ETL.1050.TOWR | 40585027 | FRESNO | FRESNO | 2020-08-10 |  | ETL.1050 | BALCH-SANGER | Road | Brush Fuel | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40585027 | 1923-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1923-01-01 | Glass | Dead End |  |  |  |  | 0.0034581 | 6585.0371
119608834 | B | LC | ETL.8650.TOWR | 40872816 | FRESNO | FRESNO | 2020-08-13 | 2020-12-08 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40872816 | 1929-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2019-11-18 | Glass | Suspension |  |  |  |  | 0.0097588 | 7011.6025
119608835 | B | LC | ETL.8650.TOWR | 40688822 | FRESNO | FRESNO | 2020-08-13 | 2020-12-08 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40688822 | 1929-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-11-18 | Glass | Suspension |  |  |  |  | 0.0088421 | 7011.6025
119632147 | F | LC | ETL.1450.POLE.WDPS | 44150218 | SACTO | SACRAMENTO | 2020-08-18 | 2020-09-28 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44150216 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00026051 | 31.7066
119637432 | E | LC | ETL.6310.POLE.WOOD | 40759474 | TABLEMTN | NORTH VALLEY | 2020-08-19 | 2021-08-16 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759474 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0002549 | 5196.2129
119645780 | E | LC | ETL.8365.POLE.WOOD | 42600438 | EUREKA | HUMBOLDT | 2020-08-19 | 2021-04-29 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 42600438 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0043788
119671731 | A | LC | ETL.6230.POLE.WOOD | 40874665 | MOSSLNDG | CENTRAL COAST | 2020-08-25 | 2020-09-19 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119693863 | E | LC | ETL.8060.POLE.WOOD | 40770663 | SACTO | SIERRA | 2020-08-28 | 2021-05-24 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770663 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.011137 | 427.2245
119696714 | F | LC | ETL.6770.POLE.WOOD | 40809636 | SACTO | SIERRA | 2020-08-29 | 2021-05-08 | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40809636 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.0047275 | 1344.8513
119710772 | F | LC | ETL.1110.TOWR | 40762548 | EUREKA | HUMBOLDT | 2020-08-29 | 2021-08-09 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40762548 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 0.0018611 | 0.065152
119720549 | A | LC | ETL.6240.POLE.WOOD | 40587847 | MOSSLNDG | CENTRAL COAST | 2020-09-05 | 2020-10-13 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40587847 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Polymer | [5 empty] | 0.36063 | 1028.9148
119722536 | F | LC | ETL.1730.POLE.WDPS | 44413420 | MOSSLNDG | CENTRAL COAST | 2020-08-03 | 2021-06-14 | ETL.1730 | GREEN VALLEY-PAUL SWEET | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44413419 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00021613 | 47.5096
119723206 | E | LC | ETL.6762.POLE.WOOD | 40693428 | SACTO | SIERRA | 2020-08-10 | 2021-05-23 | ETL.6762 | ROLLINS TAP | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40693428 |  | Single Wood Pole | LB - Line and Buck |  | Ceramic | [5 empty] | 0.00010392 | 854.4165
119766571 | F | LC | ETL.1110.POLE.WDPS | 44424526 | TABLEMTN | HUMBOLDT | 2020-09-08 | 2021-01-29 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44424525 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012548 | 9423.3379
119790929 | F | LC | ETL.6440.POLE.WOOD | 41144122 | TABLEMTN | NORTH VALLEY | 2020-07-30 |  | ETL.6440 | COLEMAN-RED BLUFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 41144122 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0010732 | 3748.465
119808912 | F | LC | ETL.6280.POLE.WOOD | 40862053 | TABLEMTN | NORTH VALLEY | 2020-08-13 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40862053 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | Pin |  |  |  |  | 9.4549e-06 | 506.1868
119848581 | F | LC | ETL.6760.POLE.WOOD | 40598639 | SACTO | SIERRA | 2020-09-08 | 2021-06-08 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40598639 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-05-30 | Glass | Dead End |  |  |  |  | 0.083233 | 2056.7583
119894295 | B | LC | ETL.3530.TOWR | 40662521 | PISMOBCH | LOS PADRES | 2020-10-12 | 2020-11-04 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662521 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-06-16 | Glass | Suspension |  |  |  |  | 1.5151e-06 | 1489.9122
119894295 | B | LC | ETL.3530.TOWR | 40662521 | PISMOBCH | LOS PADRES | 2020-10-12 | 2020-11-04 | ETL.3530 | SAN LUIS OBISPO-OCEANO | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662521 | 1952-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.5151e-06 | 1489.9122
119898293 | E | LC | ETL.6760.POLE.WOOD | 40813445 | SACTO | SIERRA | 2020-10-06 | 2021-03-24 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40813445 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.049446 | 142.5076
119917416 | F | LC | ETL.8365.POLE.NWOD | 40906668 | EUREKA | HUMBOLDT | 2020-09-17 | 2021-02-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40906668 | 2011-01-01 | Light Duty Steel Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.002636
119954952 | E | LC | ETL.8650.TOWR | 40871684 | FRESNO | YOSEMITE | 2020-10-23 | 2020-12-08 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871684 | 1929-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2019-11-18 | Glass | Dead End |  |  |  |  | 0.023248 | 0.065147
119965070 | F | LC | ETL.8960.POLE.WOOD | 40687127 | FRESNO | YOSEMITE | 2020-10-27 |  | ETL.8960 | LOS BANOS-PACHECO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 40687127 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 8.1721e-06
120074228 | F | LC | ETL.7260.POLE.WDPS | 44957515 | TABLEMTN | NORTH VALLEY | 2020-11-18 |  | ETL.7260 | KESWICK-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | PEND | 44651525 | 2018-08-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 4.1531e-05 | 2437.969 | 0.10125
120125692 | E | LC | ETL.6500.POLE.WOOD | 44153667 | SACTO | SIERRA | 2020-12-03 | 2021-08-17 | ETL.6500 | COLGATE-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44153667 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0019961 | 1317.8851
120129101 | F | LC | ETL.6380.POLE.WOOD | 40876750 | LAKEVLLE | HUMBOLDT | 2020-07-31 |  | ETL.6380 | KONOCTI-MIDDLETOWN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40876750 |  | Single Wood Pole | T2N | 2018-10-31 | Polymer | Post |  |  |  |  | 2.4013e-06 | 5876.6411
120137103 | E | LC | ETL.6480.POLE.WOOD | 40873617 | SACTO | SACRAMENTO | 2020-12-07 | 2021-01-19 | ETL.6480 | COLGATE-CHALLENGE | Vegetation | Overgrown | [Remove, No Action Taken] | Tier3 | Tier 3 | Within Both | CNCL | 40873617 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.21442 | 268.9798
120162434 | F | LC | ETL.6280.POLE.WOOD | 40815848 | TABLEMTN | NORTH VALLEY | 2020-12-09 | 2021-02-10 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40815848 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Other |  |  |  |  | 3.7749e-05 | 4808.4111
120164782 | F | LC | ETL.8365.POLE.NWOD | 43597919 | EUREKA | HUMBOLDT | 2020-12-04 | 2021-04-14 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 43597919 |  | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2016-10-27 | Ceramic | Dead End
120243221 | E | LC | ETL.1450.POLE.WDPS | 44561213 | SACTO | SACRAMENTO | 2020-12-31 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44559162 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00045731 | 79.1687 | 0.036205
120255772 | F | LC | ETL.6280.POLE.WOOD | 40826497 | TABLEMTN | NORTH VALLEY | 2020-12-18 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40826497 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | Other |  |  |  |  | 1.8431e-05 | 3115.8767
120582893 | E | LC | ETL.7300.POLE.WOOD | 40701767 | TABLEMTN | NORTH VALLEY | 2021-02-26 |  | ETL.7300 | KILARC-DESCHUTES | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40701767 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.00070105 | 2329.3726 | 1.633
120590300 | E | LC | ETL.7640.POLE.WOOD | 40770565 | TABLEMTN | NORTH VALLEY | 2021-03-02 |  | ETL.7640 | MTN GATE JCT-CASCADE | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40770565 |  | Single Wood Pole | TH - TriAngle Post 70 | 2015-05-05 | Polymer | [5 empty] | 1.125e-05 | 3564.7319 | 0.040103
120646697 | F | LC | ETL.2500.TOWR | 40866950 | METCALF | SAN JOSE | 2021-03-12 |  | ETL.2500 | METCALF-EL PATIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40866950 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-08-08 | Glass | Dead End |  |  |  |  | 0.002216 | 1988.1186 | 4.4058
120646697 | F | LC | ETL.2500.TOWR | 40866950 | METCALF | SAN JOSE | 2021-03-12 |  | ETL.2500 | METCALF-EL PATIO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40866950 | 1957-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2003-01-01 | Non Ceramic | Double Dead End |  |  |  |  | 0.002216 | 1988.1186 | 4.4058
120673292 | F | LC | ETL.4920.TOWR | 40760554 | LAKEVLLE | SONOMA | 2021-03-22 |  | ETL.4920 | IGNACIO-SOBRANTE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40760554 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 0.00054464 | 540.818 | 0.29455
120689124 | F | LC | ETL.5790.TOWR | 40863677 | VICTOR | STOCKTON | 2021-03-24 | 2021-10-07 | ETL.5790 | TIGER CREEK-VALLEY SPRINGS | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40863677 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1931-01-01 | Porcelain | Suspension |  |  |  |  | 7.8084e-06 | 33.284
120691850 | B | LC | ETL.1450.POLE.NWOD | 44967729 | SACTO | SACRAMENTO | 2021-03-25 | 2021-04-06 | ETL.1450 | DRUM-SUMMIT #2 | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44967729 | 2020-08-27 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2020-08-27 | Glass | Dead End |  |  |  |  | 1.839e-06 | 363.9416
120705994 | F | LC | ETL.7140.POLE.NWOD | 44878254 | LAKEVLLE | SONOMA | 2021-03-29 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44878254 | 2019-10-18 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-10-18 | Polymer | Dead End |  |  |  |  | 0.0031237 | 553.9316 | 1.7303
120711858 | E | LC | ETL.3830.INSL.NCER | 40623436 | VICTOR | STOCKTON | 2021-03-26 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40597003 | 1927-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1999-01-01 | Polymer | Suspension |  |  |  |  | 7.0696e-09 | 3814.4824 | 2.6967e-05
120726182 | F | LC | ETL.6760.POLE.NWOD | 40822678 | SACTO | SACRAMENTO | 2021-04-01 | 2021-10-13 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40822678 | 2010-01-01 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction |  | Polymer | Dead End |  |  |  |  | 0.0016165 | 672.3518
120727705 | F | LC | ETL.1710.TOWR | 40597281 | MOSSLNDG | CENTRAL COAST | 2021-04-01 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40597281 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-05 | Glass | Dead End |  |  |  |  | 0.0059255 | 31.6948 | 0.18781
120727705 | F | LC | ETL.1710.TOWR | 40597281 | MOSSLNDG | CENTRAL COAST | 2021-04-01 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40597281 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Dead End |  |  |  |  | 0.0059255 | 31.6948 | 0.18781
120737555 | F | LC | ETL.4392.TOWR | 41129342 | LAKEVLLE | SONOMA | 2021-04-02 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41129342 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1984-01-01 | Porcelain | Dead End |  |  |  |  | 1.3862e-05 | 3057.0283 | 0.042376
120737555 | F | LC | ETL.4392.TOWR | 41129342 | LAKEVLLE | SONOMA | 2021-04-02 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 41129342 | 1984-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-04-22 | Glass | Dead End |  |  |  |  | 1.3862e-05 | 3057.0283 | 0.042376
120742014 | F | LC | ETL.5960.TOWR | 40869988 | PISMOBCH | LOS PADRES | 2021-04-05 |  | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40869988 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1973-01-01 | Ceramic | Suspension |  |  |  |  | 1.4336e-10 | 5082.1426 | 7.2858e-07
120748944 | E | LC | ETL.8365.POLE.WOOD | 40600473 | EUREKA | HUMBOLDT | 2021-04-06 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600473 | 2010-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) |  | Polymer | [5 empty] | 0.019733 | 838.4967 | 16.5463
120762785 | E | LC | ETL.8350.POLE.WDPS | 44405868 | VICTOR | STOCKTON | 2021-04-08 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44405867 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0013535 | 398.6916 | 0.53961
120773827 | E | LC | ETL.8250.POLE.WOOD | 40607081 | VICTOR | STOCKTON | 2021-04-09 | 2021-06-04 | ETL.8250 | CLAY-MARTEL | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
120785594 | E | LC | ETL.8365.POLE.NWOD | 44859238 | EUREKA | HUMBOLDT | 2021-04-08 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44859238 | 2019-11-06 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-11-06 | Polymer | Dead End |  |  |  |  | 0.005202 | 917.5513 | 4.7731
120800419 | B | LC | ETL.3840.INSL.CERA | 40637628 | VICTOR | STOCKTON | 2021-04-12 | 2021-05-19 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40607305 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Glass | [5 empty] | 3.4517e-06 | 4353.7114
120811166 | E | LC | ETL.9040.POLE.WOOD | 40690981 | MIDWAY | KERN | 2021-04-12 |  | ETL.9040 | TULE-SPRINGVILLE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40690981 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 7.2932e-05 | 6394.647 | 0.46638
120820697 | E | LC | ETL.1540.INSL | 40780940 | SACTO | SIERRA | 2021-04-14 |  | ETL.1540 | EL DORADO-MISSOURI FLAT #2 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | PEND
120835370 | E | LC | ETL.8365.POLE.NWOD | 44356198 | EUREKA | HUMBOLDT | 2021-04-17 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Splice-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 44356198 | 2016-06-21 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End | 2016-06-21 | Polymer | Dead End |  |  |  |  | 0.080087
120835425 | E | LC | ETL.3740.TOWR | 40746110 | CONCORD | DIABLO | 2021-04-17 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40746110 | 1958-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 2021-03-16 | Glass | Dead End |  |  |  |  | 0.016333 | 0.065153 | 0.0010641
120835425 | E | LC | ETL.3740.TOWR | 40746110 | CONCORD | DIABLO | 2021-04-17 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40746110 | 1958-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1958-01-01 | Porcelain | Dead End |  |  |  |  | 0.016333 | 0.065153 | 0.0010641
120844085 | F | LC | ETL.1400.POLE.WDPS | 44771110 | VICTOR | STOCKTON | 2021-04-19 | 2021-06-11 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40684273 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | [7 empty] | 0.003691 | 2278.3794
120858321 | F | LC | ETL.6470.POLE.WOOD | 40664728 | SACTO | SACRAMENTO | 2021-04-21 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40664728 |  | Single Wood Pole | T2N | 2021-08-07 | Polymer | Post |  |  |  |  | 0.019089 | 539.4991
120863236 | E | LC | ETL.3720.TOWR | 40581005 | CONCORD | DIABLO | 2021-04-21 |  | ETL.3720 | SOBRANTE-G #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40581005 | 1968-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-23 | Glass | Suspension |  |  |  |  | 0.00010504 | 474.6866 | 0.049862
120863236 | E | LC | ETL.3720.TOWR | 40581005 | CONCORD | DIABLO | 2021-04-21 |  | ETL.3720 | SOBRANTE-G #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40581005 | 1968-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-18 | Glass | Suspension |  |  |  |  | 0.00010504 | 474.6866 | 0.049862
120875115 | E | LC | ETL.1440.POLE.WDPS | 44837696 | SACTO | SACRAMENTO | 2021-04-23 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40603734 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0031517 | 648.7145 | 2.0445
120888935 | E | LC | ETL.2750.INSL.NCER | 44696499 | CONCORD | DIABLO | 2021-04-27 |  | ETL.2750 | MORAGA-OAKLAND #4 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40764476 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Porcelain | Suspension |  |  |  |  | 6.0506e-05 | 1362.2408 | 0.082424
120888935 | E | LC | ETL.2750.INSL.NCER | 44696499 | CONCORD | DIABLO | 2021-04-27 |  | ETL.2750 | MORAGA-OAKLAND #4 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40764476 | 1931-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-01-29 | Polymer | Suspension |  |  |  |  | 6.0506e-05 | 1362.2408 | 0.082424
120891903 | F | LC | ETL.1420.TOWR | 40813504 | SACTO | SIERRA | 2021-04-26 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40813504 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.0011328 | 1491.3118 | 1.6894
120891903 | F | LC | ETL.1420.TOWR | 40813504 | SACTO | SIERRA | 2021-04-26 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40813504 | 1913-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-09-07 | Glass | Suspension |  |  |  |  | 0.0011328 | 1491.3118 | 1.6894
120906665 | E | LC | ETL.1400.POLE.WDPS | 45077523 | VICTOR | STOCKTON | 2021-04-30 |  | ETL.1400 | DONNELLS-MI-WUK | Anchor-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40744852 | 1956-01-01 | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.009221 | 31.7334 | 0.29261
120913829 | F | LC | ETL.1820.POLE.STPS | 44395402 | EUREKA | HUMBOLDT | 2021-05-01 | 2021-07-28 | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44395401 | 2020-03-04 | 2-Pole Non Wood | Unknown | [7 empty] | 0.0017758 | 19.0509
120941300 | E | LC | ETL.7060.POLE.WOOD | 40755273 | METCALF | SAN JOSE | 2021-05-05 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40755273 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Polymer | [5 empty] | 0.00024813 | 1122.9308 | 0.27863
120943227 | E | LC | ETL.6470.POLE.WOOD | 40760723 | SACTO | SACRAMENTO | 2021-05-04 |  | ETL.6470 | COLGATE-ALLEGHANY | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40760723 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.062676 | 474.9903 | 29.7707
120944056 | E | LC | ETL.1810.POLE.STPS | 45105808 | EUREKA | HUMBOLDT | 2021-05-05 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45105764 | 2020-12-03 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [8 empty] | 0.065148
121041146 | E | LC | ETL.1530.TOWR | 40604657 | SACTO | SIERRA | 2021-04-16 |  | ETL.1530 | EL DORADO-MISSOURI FLAT #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40604657 | 1923-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1980-01-01 | Ceramic | Suspension |  |  |  |  | 8.7939e-06 | 3701.6848 | 0.032552
121317971 | E | LC | ETL.3960.INSL.CERA | 40883525 | PISMOBCH | LOS PADRES | 2021-04-20 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40861661 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 1.3355e-05 | 1568.4982 | 0.020947
121317971 | E | LC | ETL.3960.INSL.CERA | 40883525 | PISMOBCH | LOS PADRES | 2021-04-20 |  | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40861661 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Ceramic | Suspension |  |  |  |  | 1.3355e-05 | 1568.4982 | 0.020947
121324621 | B | LC | ETL.3730.INSL.NCER | 44862021 | CONCORD | EAST BAY | 2021-05-12 | 2021-06-29 | ETL.3730 | SOBRANTE-G #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581005 | 1968-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-23 | Glass | Suspension |  |  |  |  | 0.00010504 | 474.6866
121324621 | B | LC | ETL.3730.INSL.NCER | 44862021 | CONCORD | EAST BAY | 2021-05-12 | 2021-06-29 | ETL.3730 | SOBRANTE-G #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40581005 | 1968-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-05-18 | Glass | Suspension |  |  |  |  | 0.00010504 | 474.6866
121332262 | E | LC | ETL.1650.INSL.NCER | 40710865 | LAKEVLLE | SONOMA | 2021-05-13 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40657192 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 0.00023871 | 4151.2271 | 0.99094
121338468 | E | LC | ETL.9250.POLE.NWOD | 42574834 | MIDWAY | KERN | 2021-04-26 | 2021-08-17 | ETL.9250 | TEJON-LEBEC | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42574834 |  | Light Duty Steel Pole | Unknown |  | Ceramic | [5 empty] | 0.0027625 | 6083.5864
121341081 | E | LC | ETL.8405.POLE.WOOD | 40602856 | SACTO | SIERRA | 2021-05-15 |  | ETL.8405 | MIDDLE FORK #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40602856 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Polymer | [5 empty] | 0.057815 | 6774.7476 | 391.6841
121341117 | E | LC | ETL.7590.INSL.NCER | 44974741 | MOSSLNDG | CENTRAL COAST | 2021-04-28 |  | ETL.7590 | MONTA VISTA-BURNS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44974734 | 2020-09-15 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2020-09-18 | Glass | Suspension |  |  |  |  | 0.092143 | 174.1011 | 16.0421
121357785 | E | LC | ETL.5980.TOWR | 40576868 | PISMOBCH | LOS PADRES | 2021-04-30 |  | ETL.5980 | DIABLO-MIDWAY #3 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40576868 | 1975-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1975-01-01 | Ceramic | Suspension |  |  |  |  | 1.3901e-07 | 1725.3241 | 0.00023984
121363834 | E | LC | ETL.1250.POLE.WOOD | 40807039 | FRESNO | YOSEMITE | 2021-05-01 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40807039 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00013352 | 5920.3032 | 0.79046
121370069 | F | LC | ETL.1820.POLE.STPS | 44918920 | EUREKA | HUMBOLDT | 2021-05-20 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44918831 | 2020-05-06 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.047546 | 6300.0015 | 299.541
121377301 | F | LC | ETL.1600.TOWR | 40808845 | LAKEVLLE | SONOMA | 2021-05-21 |  | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40808845 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 9.0814e-05 | 142.5877
121377301 | F | LC | ETL.1600.TOWR | 40808845 | LAKEVLLE | SONOMA | 2021-05-21 |  | ETL.1600 | FULTON-PUEBLO | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40808845 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 9.0814e-05 | 142.5877
121381952 | F | LC | ETL.7290.POLE.WOOD | 40771249 | TABLEMTN | NORTH VALLEY | 2021-05-07 | 2021-06-11 | ETL.7290 | KILARC-CEDAR CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40771249 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | [5 empty] | 0.064632 | 2329.9167
121383202 | F | LC | ETL.8000.POLE.NWOD | 44177582 | SACTO | SIERRA | 2021-05-11 |  | ETL.8000 | SMARTVILLE-NICOLAUS #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44177582 | 2013-08-20 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2013-08-20 | Polymer | Post |  |  |  |  | 0.00016447 | 3449.7656
121383337 | F | LC | ETL.1430.TOWR | 40660205 | SACTO | SIERRA | 2021-05-12 |  | ETL.1430 | DRUM-RIO OSO #2 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40660205 | 1913-01-01 | LATTICE STEEL TOWER | Unknown | 2016-11-14 | Non Ceramic | Post |  |  |  |  | 0.00015759 | 1977.4294 | 0.31162
121385607 | E | LC | ETL.1430.TOWR | 40866375 | SACTO | SIERRA | 2021-05-12 |  | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40866375 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1913-01-01 | Ceramic | Suspension |  |  |  |  | 0.01187 | 490.5074 | 5.8224
121396576 | F | LC | ETL.3720.POLE.NWOD | 44359229 | CONCORD | EAST BAY | 2021-05-17 | 2021-06-10 | ETL.3720 | SOBRANTE-G #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | HFRA Removal | DLFL | 44359229 |  | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 2.0306e-06 | 0.065147
121401072 | E | LC | ETL.1650.POLE.WOOD | 40750643 | LAKEVLLE | SONOMA | 2021-05-12 |  | ETL.1650 | GEYSERS #3-CLOVERDALE | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40750643 | 1966-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Polymer | Suspension |  |  |  |  | 0.0013226 | 2961.0818 | 3.9164
121404784 | E | LC | ETL.6870.POLE.WOOD | 40824463 | SACTO | SIERRA | 2021-05-20 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40824463 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.25484 | 63.386 | 16.1535
121405292 | F | LC | ETL.7290.POLE.WOOD | 40602035 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40602035 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.015134 | 126.6376
121413936 | F | LC | ETL.7040.POLE.WOOD | 40867032 | TABLEMTN | NORTH VALLEY | 2021-05-24 |  | ETL.7040 | PIT #1-HAT CREEK #2-BURNEY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40867032 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.045109 | 977.0062
121420086 | F | LC | ETL.1400.POLE.STPS | 44806662 | VICTOR | STOCKTON | 2021-05-25 | 2021-06-11 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44806614 | 2019-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.7303e-05 | 15.9119
121428287 | E | LC | ETL.1400.POLE.STPS | 44810086 | VICTOR | STOCKTON | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44810009 | 2019-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.6327e-05 | 47.5548 | 0.0026786
121491064 | E | LC | ETL.8060.POLE.WOOD | 42571845 | SACTO | SIERRA | 2021-06-07 |  | ETL.8060 | SPAULDING-SUMMIT | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 42571845 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.023234 | 95.0274 | 2.2078
121514083 | E | LC | ETL.4680.TOWR | 40651559 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.4680 | FULTON-IGNACIO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40651559 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-06-07 | Glass | Double Dead End |  |  |  |  | 0.038768 | 221.8368 | 8.6002
121514083 | E | LC | ETL.4680.TOWR | 40651559 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.4680 | FULTON-IGNACIO #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40651559 | 1966-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1966-01-01 | Ceramic | Double Dead End |  |  |  |  | 0.038768 | 221.8368 | 8.6002
121516548 | F | LC | ETL.6770.POLE.NWOD | 44396923 | SACTO | SIERRA | 2021-06-05 |  | ETL.6770 | DRUM-SPAULDING | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44396923 | 2018-09-06 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | [7 empty] | 0.00025887 | 205.7724
121516611 | F | LC | ETL.6770.POLE.WOOD | 40810149 | SACTO | SIERRA | 2021-06-05 |  | ETL.6770 | DRUM-SPAULDING | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40810149 |  | Single Wood Pole | DV - Double Vertical |  | Non Ceramic | [5 empty] | 0.0081281 | 1344.8513 | 10.931
121518613 | F | LC | ETL.5650.TOWR | 40762577 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40762577 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 3.2187e-06 | 4689.9517 | 0.015096
121518794 | E | LC | ETL.8350.INSL.NCER | 44918845 | VICTOR | STOCKTON | 2021-06-08 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44918774 | 2020-03-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-03-03 | Polymer | Dead End |  |  |  |  | 1.0549e-07 | 2328.6755 | 0.00024564
121519120 | E | LC | ETL.4550.TOWR | 40576670 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.4550 | COTTONWOOD-DELEVAN #1 | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576670 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 5.3061e-07 | 4816.6782 | 0.0025558
121520866 | B | LC | ETL.4870.INSL | 40623481 | FRESNO | FRESNO | 2021-06-10 | 2021-06-23 | ETL.4870 | HELMS-GREGG #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40582534 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 5.5123e-07 | 6015.2808
121524747 | F | LC | ETL.1440.POLE.WDPS | 44162111 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44162110 | 2013-09-22 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.6974e-05 | 31.7066
121536633 | F | LC | ETL.5390.TOWR | 40759701 | TABLEMTN | NORTH VALLEY | 2021-06-10 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40759701 | 1954-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 1.0891e-08 | 4326.1167
121536646 | E | LC | ETL.7550.POLE.WOOD | 40861435 | LAKEVLLE | HUMBOLDT | 2021-06-11 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40861435 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.00137 | 15.8807 | 0.021756
121538689 | F | LC | ETL.5140.TOWR | 40761204 | SACTO | SIERRA | 2021-06-14 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40761204 | 1965-01-01 | LATTICE STEEL TOWER | 3P DV - 3 Pole Double Vertical | 1965-01-01 | Ceramic | Dead End |  |  |  |  | 7.8804e-06 | 6774.7476
121546583 | E | LC | ETL.7140.POLE.WDPS | 44942598 | LAKEVLLE | NORTH BAY | 2021-06-15 | 2021-06-23 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 41111795 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.023234 | 1711.6168
121552939 | E | LC | ETL.7640.POLE.WDPS | 44565601 | TABLEMTN | NORTH VALLEY | 2021-06-17 |  | ETL.7640 | MTN GATE JCT-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44564208 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00042126 | 253.4679 | 0.10678
121568560 | F | LC | ETL.1400.POLE.NWOD | 44948558 | VICTOR | YOSEMITE | 2021-06-15 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44948558 | 2019-07-15 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2019-07-15 | Glass | Suspension |  |  |  |  | 2.0639e-05 | 4145.3232
121572822 | F | LC | ETL.7550.POLE.WOOD | 40600375 | LAKEVLLE | HUMBOLDT | 2021-06-17 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40600375 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 1.4772e-05 | 0.065148 | 9.6235e-07
121574219 | F | LC | ETL.8350.POLE.STPS | 45015323 | VICTOR | STOCKTON | 2021-06-15 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 45015278 | 2020-05-07 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 7.3561e-09 | 1075.7617
121595723 | E | LC | ETL.6330.POLE.WOOD | 41114370 | TABLEMTN | NORTH VALLEY | 2021-03-11 |  | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41114370 |  | Single Wood Pole | 3P DDE-A - 3 Pole Double Dead End Angle |  | Ceramic | [5 empty] | 0.0050086 | 954.4325 | 4.7804
121609304 | F | LC | ETL.6500.POLE.WOOD | 40866224 | SACTO | NORTH VALLEY | 2021-06-22 | 2021-10-25 | ETL.6500 | COLGATE-PALERMO | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40866224 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.00076687 | 2473.1323
121657836 | E | LC | ETL.5420.POLE.WDPS | 44558311 | TABLEMTN | NORTH VALLEY | 2021-06-28 |  | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44557897 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00081505 | 665.1749 | 0.54215
121661464 | E | LC | ETL.6650.POLE.WDPS | 44209042 | TABLEMTN | NORTH VALLEY | 2021-07-01 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44209041 | 2014-04-18 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.022445 | 2155.7598 | 48.385
121691002 | E | LC | ETL.5140.POLE.STPS | 45112043 | SACTO | SIERRA | 2021-06-30 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 45111975 | 2020-10-31 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [8 empty] | 126.6132
121715524 | B | LC | ETL.1820.INSL.NCER | 40886476 | EUREKA | HUMBOLDT | 2021-07-12 | 2021-08-03 | ETL.1820 | HUMBOLDT-TRINITY | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121717703 | E | LC | ETL.1400.INSL.NCER | 40772089 | VICTOR | YOSEMITE | 2021-07-07 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40744829 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | 1956-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0031051
121717703 | E | LC | ETL.1400.INSL.NCER | 40772089 | VICTOR | YOSEMITE | 2021-07-07 |  | ETL.1400 | DONNELLS-MI-WUK | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40744829 | 1956-01-01 | 2-Pole Wood | SUSP - Suspension (TWR) | 1956-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0031051
121717986 | E | LC | ETL.5430.POLE.WOOD | 44561481 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560805 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0025827 | 2061.0276 | 5.3231
121717986 | E | LC | ETL.5430.POLE.WOOD | 44561481 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44560805 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0025827 | 2061.0276 | 5.3231
121725241 | E | LC | ETL.6880.POLE.WOOD | 40588917 | LAKEVLLE | NORTH BAY | 2021-07-05 |  | ETL.6880 | FULTON-CALISTOGA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40588917 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.0014233 | 4321.8276 | 6.1511
121725901 | E | LC | ETL.2390.POLE.WDPS | 44391119 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Structure-Wood | Rotten | [Replace, Completed] | Tier2 | Tier 2 | Within Both | PEND | 44391116 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0013099 | 5127.0312 | 6.7161
121730967 | B | LC | ETL.7000.INSL.CERA | 40900622 | TABLEMTN | NORTH VALLEY | 2021-07-13 | 2021-07-27 | ETL.7000 | HAMILTON BRANCH-CHESTER | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40876161 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00022395 | 47.5141
121731569 | B | LC | ETL.3750.TOWR | 40804878 | CONCORD | EAST BAY | 2021-07-14 | 2021-07-26 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | DLFL | 40804878 | 1932-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 1.2388e-06 | 15.88
121748349 | E | LC | ETL.8365.POLE.WOOD | 40912514 | EUREKA | HUMBOLDT | 2021-07-16 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Conductor-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40912514 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.16635
121750818 | F | LC | ETL.7170.POLE.WOOD | 44871215 | LAKEVLLE | NORTH BAY | 2021-07-17 |  | ETL.7170 | IGNACIO-ALTO-SAUSALITO #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44871215 | 2019-09-19 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2019-09-19 | Glass | Dead End |  |  |  |  | 0.071744 | 237.5913
121754407 | F | LC | ETL.6660.POLE.NWOD | 45084710 | TABLEMTN | NORTH VALLEY | 2021-07-19 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45084710 | 2021-03-04 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-04 | Polymer | Post |  |  |  |  | 2.5029e-10 | 4785.126
121758663 | B | LC | ETL.6280.POLE.WOOD | 40768776 | TABLEMTN | NORTH VALLEY | 2021-07-19 | 2021-10-11 | ETL.6280 | CARIBOU #2 | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40768776 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 3.1788e-05 | 1739.9091
121763132 | E | LC | ETL.2390.POLE.WDPS | 44391295 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391293 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 5.3331e-05 | 996.4046 | 0.05314
121779532 | F | LC | ETL.6510.POLE.STPS | 44399413 | SACTO | SACRAMENTO | 2021-07-20 | 2021-10-12 | ETL.6510 | COLGATE-SMARTVILLE #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Tier 2 | Within Both | DLFL | 44399412 |  | 3-Pole Non Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 2.6861e-08 | 237.8615
121783882 | E | LC | ETL.9240.TOWR | 43249789 | PISMOBCH | LOS PADRES | 2021-07-20 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 43249789 |  | LATTICE STEEL TOWER | [9 empty] | 1523.1703
121785300 | E | LC | ETL.9240.TOWR | 43249701 | PISMOBCH | LOS PADRES | 2021-07-23 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249701 |  | LATTICE STEEL TOWER | [9 empty] | 158.4262
121789403 | E | LC | ETL.9240.TOWR | 43249609 | PISMOBCH | LOS PADRES | 2021-07-22 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249609 |  | LATTICE STEEL TOWER | [9 empty] | 397.9478
121809887 | E | LC | ETL.7390.POLE.WOOD | 40740733 | LAKEVLLE | HUMBOLDT | 2021-07-27 |  | ETL.7390 | LAYTONVILLE-COVELO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 40740733 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Ceramic | Suspension |  |  |  |  | 0.037328
121810691 | E | LC | ETL.8365.POLE.WOOD | 40698230 | EUREKA | HUMBOLDT | 2021-07-27 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Damper-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40698230 | 2010-01-01 | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | [5 empty] | 0.0050004 | 238.3615 | 1.1919
121812652 | E | LC | ETL.8365.POLE.NWOD | 40698315 | EUREKA | HUMBOLDT | 2021-07-28 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Hardware-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 40698315 | 2016-06-11 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End | 2016-06-11 | Polymer | Post |  |  |  |  | 0.00052655
121816064 | E | LC | ETL.6470.POLE.WOOD | 40679477 | SACTO | SIERRA | 2021-07-29 |  | ETL.6470 | COLGATE-ALLEGHANY | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40679477 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.25081 | 221.5931 | 55.578
121816143 | F | LC | ETL.8365.POLE.NWOD | 44694236 | EUREKA | HUMBOLDT | 2021-07-28 |  | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | PEND | 44694236 | 2018-12-20 | Light Duty Steel Pole | 3P DDE - 3 Pole Double Dead End | 2018-12-20 | Polymer | Dead End |  |  |  |  | 0.0030749
121816832 | B | LC | ETL.8405.INSL.NCER | 40639245 | SACTO | SACRAMENTO | 2021-07-28 | 2021-10-20 | ETL.8405 | MIDDLE FORK #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611426 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | [5 empty] | 0.0017884 | 6807.7681 | 12.1753
122059757 | E | LC | ETL.4780.INSL.CERA | 40632249 | LAKEVLLE | SONOMA | 2021-09-16 |  | ETL.4780 | GEYSERS #9-LAKEVILLE | Emergency | Fire | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 41129392 | 1984-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1984-01-01 | Porcelain | Suspension |  |  |  |  | 0.0011045 | 316.5972 | 0.3497
122108911 | E | LC | ETL.4410.TOWR | 40862377 | MIDWAY | FRESNO | 2021-09-27 |  | ETL.4410 | BRENTWOOD-KELSO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40862377 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-11 | Glass | Suspension |  |  |  |  | 4.454e-07 | 6919.9751 | 0.0030822
122108911 | E | LC | ETL.4410.TOWR | 40862377 | MIDWAY | FRESNO | 2021-09-27 |  | ETL.4410 | BRENTWOOD-KELSO | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40862377 | 1950-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1950-01-01 | Ceramic | Suspension |  |  |  |  | 4.454e-07 | 6919.9751 | 0.0030822
122162615 | E | LC | ETL.4392.INSL.NCER | 40629182 | LAKEVLLE | SONOMA | 2021-10-07 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Emergency | Storm Related | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40587747 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 7.4147e-08 | 174.2387 | 1.2919e-05
122316670 | F | LC | ETL.8210.POLE.NWOD | 45147580 | VICTOR | STOCKTON | 2021-11-04 |  | ETL.8210 | VALLEY SPRINGS #1 | Conductor-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 45147580 | 2021-08-13 | Light Duty Steel Pole | DV-DE - Double Vertical Dead End | 2021-08-13 | Glass | Dead End
118502098 | B | LC | ETL.7212.POLE.NWOD | 40758361 | METCALF | SAN JOSE | 2020-02-06 | 2020-02-10 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Non-Routine Patrol | Investigate | [Ground Patrol] | Tier2 | Tier 2 | Within Both | DLFL | 40758361 |  | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. | 2019-11-03 | Glass | Suspension |  |  |  |  | 0.019841 | 278.6491
118502098 | B | LC | ETL.7212.POLE.NWOD | 40758361 | METCALF | SAN JOSE | 2020-02-06 | 2020-02-10 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Non-Routine Patrol | Investigate | [Ground Patrol] | Tier2 | Tier 2 | Within Both | DLFL | 40758361 |  | Tubular Steel Pole | SS2 - Susp. Steel Double CIR. |  | Porcelain | [5 empty] | 0.019841 | 278.6491
118576734 | B | LC | ETL.5930.INSL.NCER | 44806741 | CONCORD |  | 2020-02-25 | 2020-04-02 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873496 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2019-04-30 | Glass | Suspension |  |  |  |  | 4.3582e-09 | 1692.6119
118576734 | B | LC | ETL.5930.INSL.NCER | 44806741 | CONCORD |  | 2020-02-25 | 2020-04-02 | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40873496 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1960-01-01 | Ceramic | Suspension |  |  |  |  | 4.3582e-09 | 1692.6119
118743556 | E | LC | ETL.7212.POLE.WDPS | 44384378 | METCALF | PENINSULA | 2020-03-25 | 2021-05-26 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44384376 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.30333 | 687.2475
118772978 | E | LC | ETL.8350.POLE.WOOD | 40600016 | VICTOR | STOCKTON | 2020-04-01 | 2020-07-16 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Jumper-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40600016 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2019-04-25 | Non Ceramic | Post |  |  |  |  | 0.00082374 | 1202.2845
118924281 | F | LC | ETL.2540.POLE.NWOD | 42567760 | MOSSLNDG | SAN JOSE | 2020-04-14 | 2021-01-20 | ETL.2540 | METCALF-GREEN VALLEY | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 42567760 |  | Light Duty Steel Pole | DDE-A - Double Dead End Angle | 2021-08-01 | Glass | Double Dead End |  |  |  |  | 0.00078394 | 47.5295
118927351 | E | LC | ETL.7212.POLE.WOOD | 40767325 | METCALF | SAN JOSE | 2020-04-15 | 2020-09-24 | ETL.7212 | SNEATH LANE-HALF MOON BAY | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767325 |  | Single Wood Pole | WB - Wishbone | 2019-11-12 | Porcelain | Suspension |  |  |  |  | 0.18798 | 1345.4139
118946605 | E | LC | ETL.4440.TOWR | 40588540 | TABLEMTN | NORTH VALLEY | 2020-04-24 | 2020-10-09 | ETL.4440 | CARIBOU-TABLE MTN | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40588540 | 1958-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1958-01-01 | Porcelain | Suspension |  |  |  |  | 1.971e-08 | 0.39411
118947388 | F | LC | ETL.1252.POLE.NWOD | 40859694 | FRESNO | FRESNO | 2020-04-24 | 2021-07-20 | ETL.1252 | OAKHURST TAP | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40859694 | 2005-01-01 | Light Duty Steel Pole | TPS - Tri Post & Susp (1-3) | 2005-01-01 | Polymer | Suspension |  |  |  |  | 3.2101e-06 | 47.5096
118975819 | F | LC | ETL.5140.POLE.STPS | 44690705 | SACTO | SIERRA | 2020-04-28 | 2021-04-29 | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44141452 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 9.1098e-09 | 253.4143
118976714 | E | LC | ETL.5463.TOWR | 40805087 | CONCORD | MISSION | 2020-04-20 | 2021-01-25 | ETL.5463 | PITTSBURG-SAN MATEO | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805087 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Ceramic | Dead End |  |  |  |  | 6.6954e-08 | 3154.5959
118976714 | E | LC | ETL.5463.TOWR | 40805087 | CONCORD | MISSION | 2020-04-20 | 2021-01-25 | ETL.5463 | PITTSBURG-SAN MATEO | Hardware-Tower | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805087 | 1964-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1964-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.6954e-08 | 3154.5959
118988551 | E | LC | ETL.1402.POLE.WDPS | 44550739 | VICTOR | STOCKTON | 2020-05-01 | 2021-01-19 | ETL.1402 | SPRING GAP TAP | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 3 | Within Both | COMP | 44550066 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.001497 | 221.5655
118991411 | F | LC | ETL.1650.POLE.NWOD | 44207445 | LAKEVLLE | SONOMA | 2020-04-23 | 2020-11-10 | ETL.1650 | GEYSERS #3-CLOVERDALE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44207445 |  | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Porcelain | Dead End |  |  |  |  | 4.4714e-09 | 4055.4705
119030021 | E | LC | ETL.1481.POLE.NWOD | 44917330 | LAKEVLLE | HUMBOLDT | 2020-05-14 | 2020-07-06 | ETL.1481 | LOWER LAKE-HOMESTAKE | Raptor Guard-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44917330 | 2020-05-07 | Light Duty Steel Pole | SV2 - Angle 30-80 Degrees | 2020-05-07 | Glass | Suspension |  |  |  |  | 5.9474e-09 | 4212.6665
119040271 | E | LC | ETL.2900.INSL.CERA | 40706506 | MOSSLNDG | CENTRAL COAST | 2020-05-18 | 2020-06-22 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648548 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0049527 | 570.9174
119045188 | E | LC | ETL.6880.POLE.WOOD | 40912441 | LAKEVLLE | NORTH BAY | 2020-05-18 | 2020-06-15 | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40912441 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Polymer | [5 empty] | 0.02906 | 540.3331
119050123 | F | LC | ETL.6440.POLE.WOOD | 42570178 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-07-14 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42570178 |  | Single Wood Pole | DDE - Double Dead End |  | Ceramic | [5 empty] | 0.018337 | 3502.9058
119056296 | E | LC | ETL.6440.POLE.WOOD | 41144162 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-07-08 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 41144162 |  | Single Wood Pole | T-1 - Tri Post | 2012-09-06 | Polymer | Post |  |  |  |  | 0.0032579 | 4927.5908
119059234 | F | LC | ETL.6440.POLE.NWOD | 40657881 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-07-20 | ETL.6440 | COLEMAN-RED BLUFF | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40657881 |  | Light Duty Steel Pole | T-1 - Tri Post |  | Ceramic | Unknown |  |  |  |  | 6.3443e-06 | 4421.0889
119064738 | B | LC | ETL.8350.POLE.WOOD | 40580253 | VICTOR | STOCKTON | 2020-05-22 | 2020-06-10 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119070566 | E | LC | ETL.7510.POLE.NWOD | 44958687 | LAKEVLLE | HUMBOLDT | 2020-05-27 | 2020-09-14 | ETL.7510 | MENDOCINO-HARTLEY | Road | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44958687 | 2020-04-21 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2020-04-21 | Glass | Dead End |  |  |  |  | 9.1489e-10 | 5345.3305
119084544 | E | LC | ETL.3150.TOWR | 40761781 | CONCORD | EAST BAY | 2020-05-22 | 2021-04-26 | ETL.3150 | OLEUM-G #1 | Structure-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40761781 | 1931-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-02-06 | Ceramic | Suspension |  |  |  |  | 1.207e-07 | 126.5956
119088860 | E | LC | ETL.2770.TOWR | 40861001 | CONCORD | EAST BAY | 2020-05-15 | 2021-03-11 | ETL.2770 | MORAGA-SAN LEANDRO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40861001 | 1925-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 1.3031e-05 | 0.065147
119103782 | F | LC | ETL.1330.TOWR | 40869783 | SACTO | SACRAMENTO | 2020-05-15 | 2020-06-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40869783 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Ceramic | Dead End |  |  |  |  | 1.9047e-05 | 6776.8228
119103782 | F | LC | ETL.1330.TOWR | 40869783 | SACTO | SACRAMENTO | 2020-05-15 | 2020-06-05 | ETL.1330 | CORTINA-MENDOCINO #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40869783 | 1951-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1951-01-01 | Porcelain | Dead End |  |  |  |  | 1.9047e-05 | 6776.8228
119111770 | E | LC | ETL.5290.TOWR | 40810713 | PISMOBCH | LOS PADRES | 2020-05-26 |  | ETL.5290 | MORRO BAY-MESA | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40810713 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 2.0654e-09 | 2706.5269 | 5.5901e-06
119111840 | E | LC | ETL.5140.POLE.WDPS | 44558258 | SACTO | SACRAMENTO | 2020-05-21 | 2020-06-30 | ETL.5140 | MIDDLE FORK-GOLD HILL | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 |  |  | DLFL
119113424 | F | LC | ETL.8240.POLE.WOOD | 40753644 | VICTOR | STOCKTON | 2020-06-01 | 2021-04-05 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40753644 | 1992-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.002014 | 1966.6844
119115197 | F | LC | ETL.6470.POLE.WOOD | 40818480 | SACTO | SIERRA | 2020-05-29 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40818480 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.02176 | 31.7148
119118906 | F | LC | ETL.8170.POLE.WOOD | 40803410 | EUREKA | HUMBOLDT | 2020-06-03 | 2021-06-14 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803410 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.018707 | 300.6727
119119224 | E | LC | ETL.6490.POLE.WOOD | 40760646 | SACTO | SIERRA | 2020-06-02 | 2021-02-18 | ETL.6490 | COLGATE-GRASS VALLEY | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760646 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.02019 | 3679.4845
119126985 | E | LC | ETL.1431.INSL | 40834399 | SACTO | SACRAMENTO | 2020-06-04 | 2021-03-23 | ETL.1431 | BRUNSWICK #2 TAP | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119127960 | B | LC | ETL.8365.POLE.NWOD | 40912688 | EUREKA | HUMBOLDT | 2020-06-08 | 2020-09-09 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912688 | 2010-01-01 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees |  | Polymer | [5 empty] | 0.0041006 | 4492.853
119142905 | F | LC | ETL.1810.TOWR | 44321409 | EUREKA | HUMBOLDT | 2020-06-05 | 2021-01-19 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 44321409 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Porcelain | [5 empty] | 5.3012e-07
119158799 | E | LC | ETL.8170.POLE.WOOD | 40605815 | EUREKA | HUMBOLDT | 2020-06-02 | 2021-06-14 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40605815 |  | Single Wood Pole | 3P DDE - 3 Pole Double Dead End |  | Ceramic | [5 empty] | 0.061156 | 4621.6372
119163567 | F | LC | ETL.1810.POLE.WDPS | 44322298 | EUREKA | HUMBOLDT | 2020-06-11 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44322296 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00049591
119165974 | E | LC | ETL.6690.POLE.WOOD | 40866658 | SACTO | SIERRA | 2020-06-15 | 2021-07-26 | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40866658 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Non Ceramic | [5 empty] | 0.20878 | 63.348
119176153 | E | LC | ETL.6440.POLE.WOOD | 42570176 | TABLEMTN | NORTH VALLEY | 2020-06-16 | 2020-07-08 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119176965 | F | LC | ETL.7300.POLE.NWOD | 44809989 | TABLEMTN | NORTH VALLEY | 2020-06-16 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44809989 | 2019-06-26 | Light Duty Steel Pole | T-1 - Tri Post | 2019-06-26 | Polymer | Post |  |  |  |  | 8.0469e-08 | 2900.9131
119180451 | E | LC | ETL.5300.TOWR | 40863077 | PISMOBCH | LOS PADRES | 2020-06-17 | 2021-10-04 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Damper-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863077 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-06-11 | Glass | Dead End |  |  |  |  | 2.7422e-06 | 509.5179 | 0.0013972
119180451 | E | LC | ETL.5300.TOWR | 40863077 | PISMOBCH | LOS PADRES | 2020-06-17 | 2021-10-04 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Damper-Steel | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40863077 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1962-01-01 | Ceramic | Double Dead End |  |  |  |  | 2.7422e-06 | 509.5179 | 0.0013972
119199512 | F | LC | ETL.6470.POLE.WOOD | 40822634 | SACTO | SIERRA | 2020-06-23 | 2021-07-08 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822634 |  | Single Wood Pole | T2N | 2021-07-16 | Polymer | Post |  |  |  |  | 0.082852 | 158.2723
119201523 | F | LC | ETL.7160.TOWR | 40601773 | LAKEVLLE | NORTH BAY | 2020-06-23 | 2021-01-20 | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40601773 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Non Ceramic | [5 empty] | 0.0079328 | 0.065151
119201523 | F | LC | ETL.7160.TOWR | 40601773 | LAKEVLLE | NORTH BAY | 2020-06-23 | 2021-01-20 | ETL.7160 | IGNACIO-ALTO-SAUSALITO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40601773 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | [5 empty] | 0.0079328 | 0.065151
119211576 | E | LC | ETL.7290.POLE.WOOD | 40822571 | TABLEMTN | NORTH VALLEY | 2020-06-25 | 2021-03-01 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40822571 |  | Single Wood Pole | T2N | 2021-02-24 | Polymer | Post |  |  |  |  | 0.0041788 | 1064.7484
119220467 | E | LC | ETL.6290.INSL.CERA | 42722005 | TABLEMTN | NORTH VALLEY | 2020-06-26 | 2021-11-18 | ETL.6290 | CARIBOU-PLUMAS JCT | Damper-Steel | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119235615 | F | LC | ETL.8060.POLE.WOOD | 40771542 | SACTO | SIERRA | 2020-06-29 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40771542 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.073438 | 31.7066
119236190 | F | LC | ETL.6980.POLE.WOOD | 40656433 | LAKEVLLE | SONOMA | 2020-06-30 | 2021-01-19 | ETL.6980 | FORT ROSS-GUALALA | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40656433 | 1986-01-01 | Single Wood Pole | DV-PJ - Double Vertical Post Jumper | 2010-01-01 | Polymer | Dead End |  |  |  |  | 0.17899 | 47.5118
119290149 | F | LC | ETL.7300.POLE.WOOD | 40600373 | TABLEMTN | NORTH VALLEY | 2020-07-01 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600373 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.00045637 | 2867.8467
119292465 | E | LC | ETL.1110.POLE.WDPS | 44423848 | TABLEMTN | NORTH VALLEY | 2020-07-01 | 2021-04-28 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119295303 | E | LC | ETL.1820.INSL.NCER | 40788606 | EUREKA | HUMBOLDT | 2020-07-01 | 2021-04-01 | ETL.1820 | HUMBOLDT-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | DLFL
119295721 | F | LC | ETL.6900.POLE.WOOD | 40700736 | LAKEVLLE | SONOMA | 2020-06-30 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 40700736 | 1956-01-01 | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 6.6591e-06 | 1171.3424
119300875 | E | LC | ETL.8060.POLE.WOOD | 40660186 | SACTO | SIERRA | 2020-06-29 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40660186 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.056014 | 221.5552
119307696 | F | LC | ETL.1440.TOWR | 44768872 | SACTO | SIERRA | 2020-07-01 | 2021-02-11 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44768872 |  | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-08-23 | Glass | Dead End |  |  |  |  | 0.00041292 | 1123.6396
119309986 | F | LC | ETL.8060.POLE.WOOD | 40826183 | SACTO | SIERRA | 2020-07-02 | 2021-05-11 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826183 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.023813 | 981.4936
119312481 | E | LC | ETL.6290.POLE.WOOD | 40585989 | TABLEMTN | NORTH VALLEY | 2020-07-03 | 2021-09-14 | ETL.6290 | CARIBOU-PLUMAS JCT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40585989 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 2010-01-01 | Polymer | Post |  |  |  |  | 0.058223 | 5253.1437
119312583 | F | LC | ETL.4040.POLE.STPS | 44647156 | TABLEMTN | NORTH VALLEY | 2020-07-03 | 2021-09-23 | ETL.4040 | TRINITY-COTTONWOOD | Marker (i.e. signs)-Wood | Missing | [Install, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44646911 | 2018-08-17 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00020369 | 569.688
119316162 | E | LC | ETL.6760.POLE.WOOD | 40766645 | SACTO | SACRAMENTO | 2020-07-06 | 2020-11-12 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | DLFL | 40766645 |  | Light Duty Steel Pole | T2N |  | Polymer | Post |  |  |  |  | 0.002047 | 94.9894
119316540 | F | LC | ETL.7270.POLE.WOOD | 40909519 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40909519 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0073151 | 4936.5352 | 36.1111
119317647 | F | LC | ETL.7030.POLE.WOOD | 40827515 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire Mark /Indic-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40827515 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0066447
119324002 | F | LC | ETL.7980.POLE.WOOD | 40760139 | SACTO | SIERRA | 2020-07-07 |  | ETL.7980 | SMARTVILLE-MARYSVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40760139 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.00020416 | 1807.0808
119332313 | E | LC | ETL.7270.POLE.WOOD | 40877840 | TABLEMTN | NORTH VALLEY | 2020-07-06 | 2020-11-09 | ETL.7270 | KESWICK-TRINITY | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40877840 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.076155 | 1550.618
119334659 | E | LC | ETL.7300.POLE.WOOD | 40600396 | TABLEMTN | NORTH VALLEY | 2020-07-08 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600396 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00045991 | 2630.762 | 1.2099
119341492 | E | LC | ETL.7030.POLE.WOOD | 40599854 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-23 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119354643 | E | LC | ETL.1480.TOWR | 40588084 | LAKEVLLE | SACRAMENTO | 2020-07-10 |  | ETL.1480 | EAGLE ROCK-REDBUD | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier3 | Tier 3 | Within Both | PEND | 40588084 | 1978-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1978-01-01 | Glass | Suspension |  |  |  |  | 0.0016036 | 574.263 | 0.9209
119358108 | F | LC | ETL.8170.POLE.WDPS | 44565419 | EUREKA | HUMBOLDT | 2020-07-10 | 2021-06-30 | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44564200 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.01394 | 63.351
119360524 | E | LC | ETL.7270.POLE.WOOD | 40577352 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40577352 |  | Single Wood Pole | T-1 - Tri Post | 2020-04-17 | Polymer | Post |  |  |  |  | 0.0068147 | 79.5646 | 0.54221
119364825 | F | LC | ETL.6380.POLE.WOOD | 40752528 | LAKEVLLE | SONOMA | 2020-07-13 | 2021-02-16 | ETL.6380 | KONOCTI-MIDDLETOWN | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40752528 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 2.8572e-05 | 3473.7505
119367188 | F | LC | ETL.7590.POLE.WOOD | 40694958 | MOSSLNDG | CENTRAL COAST | 2020-07-14 | 2020-07-15 | ETL.7590 | MONTA VISTA-BURNS | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL
119370744 | E | LC | ETL.8410.POLE.WOOD | 40870898 | LAKEVLLE | SONOMA | 2020-07-14 | 2021-03-24 | ETL.8410 | ELK-GUALALA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870898 | 1960-01-01 | Single Wood Pole | WB - Wishbone | 1960-01-01 | Porcelain | Dead End |  |  |  |  | 0.27554 | 1356.5956
119372694 | F | LC | ETL.4040.POLE.STPS | 44789690 | TABLEMTN |  | 2020-07-13 | 2021-04-19 | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | DLFL | 44551682 | 2019-07-26 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00010555 | 4514.9478
119377649 | F | LC | ETL.1440.POLE.WDPS | 44768916 | SACTO | SACRAMENTO | 2020-07-13 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40821387 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00089063 | 47.5273
119461572 | F | LC | ETL.6290.POLE.WOOD | 40768890 | TABLEMTN | NORTH VALLEY | 2020-07-16 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40768890 | 1962-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1962-01-01 | Porcelain | Pin |  |  |  |  | 0.038262 | 5017.1824
119464290 | F | LC | ETL.7030.POLE.WOOD | 40769979 | TABLEMTN | NORTH VALLEY | 2020-07-15 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40769979 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00025225 | 540.4122
119474925 | F | LC | ETL.8960.POLE.WDPS | 45020874 | FRESNO | YOSEMITE | 2020-07-20 |  | ETL.8960 | LOS BANOS-PACHECO | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40821711 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00044345
119482148 | E | LC | ETL.7140.POLE.WOOD | 40701396 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-08-30 | ETL.7140 | IGNACIO-BOLINAS #1 | Damper-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40701396 |  | Single Wood Pole | T-1 - Tri Post | 2020-06-21 | Polymer | Post |  |  |  |  | 0.0034809 | 2185.4529
119484917 | F | LC | ETL.6890.POLE.WOOD | 40877300 | LAKEVLLE | SONOMA | 2020-07-21 | 2021-04-19 | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40877300 | 1974-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0076385 | 2548.5022
119486597 | F | LC | ETL.6300.POLE.WDPS | 44976255 | TABLEMTN | NORTH VALLEY | 2020-07-21 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 42624198 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 1.7825e-05 | 221.7338
119495452 | F | LC | ETL.1110.POLE.STPS | 44425582 | EUREKA | HUMBOLDT | 2020-07-22 | 2021-08-17 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44425580 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 5.6078e-05 | 601.7299
119504917 | E | LC | ETL.8060.POLE.WDPS | 44420792 | SACTO | SACRAMENTO | 2020-07-23 | 2021-05-10 | ETL.8060 | SPAULDING-SUMMIT | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | DLFL
119556896 | E | LC | ETL.7490.INSL.NCER | 44645854 | EUREKA | HUMBOLDT | 2020-08-03 | 2020-11-10 | ETL.7490 | MAPLE CREEK-HOOPA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44645838 | 2018-08-10 | Single Wood Pole | T2N | 2018-08-10 | Polymer | Post |  |  |  |  | 0.0028146 | 189.8608
119568440 | F | LC | ETL.1073.POLE.WOOD | 44789680 | VICTOR | STOCKTON | 2020-08-06 |  | ETL.1073 | MI-WUK-CURTIS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44789680 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Non Ceramic | Other |  |  |  |  | 0.00042073 | 31.7081
119591975 | F | LC | ETL.9210.POLE.WOOD | 40654751 | MIDWAY | KERN | 2020-08-10 |  | ETL.9210 | TAFT-CUYAMA #2 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40654751 | 1946-01-01 | Single Wood Pole | 2PS - 2 Pole SUSP | 1946-01-01 | Ceramic | Pin |  |  |  |  | 0.0081438
119594594 | F | LC | ETL.6890.POLE.WOOD | 40601387 | LAKEVLLE | SONOMA | 2020-08-10 | 2021-01-25 | ETL.6890 | FULTON-HOPLAND | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 |  |  | DLFL
119603968 | E | LC | ETL.6222.POLE.WOOD | 40861033 | EUREKA | HUMBOLDT | 2020-08-10 | 2020-09-23 | ETL.6222 | FORT SEWARD TAP | Anchor-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40861033 | 1952-01-01 | Single Wood Pole | TPS - Tri Post & Susp (1-3) | 1952-01-01 | Ceramic | Pin |  |  |  |  | 0.0083883
119615476 | E | LC | ETL.1810.POLE.STPS | 44322649 | EUREKA | HUMBOLDT | 2020-08-14 | 2021-06-17 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Crossarm-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322649 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2021-05-14 | Glass | Suspension |  |  |  |  | 1.1044e-05
119615476 | E | LC | ETL.1810.POLE.STPS | 44322649 | EUREKA | HUMBOLDT | 2020-08-14 | 2021-06-17 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Crossarm-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44322649 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2021-05-14 | Glass | Suspension |  |  |  |  | 1.1044e-05
119619208 | B | LC | ETL.8650.POLE.NWOD | 44420180 | FRESNO | FRESNO | 2020-08-14 | 2020-12-11 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420180 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Porcelain | Suspension |  |  |  |  | 0.002777 | 6041.3433
119629810 | E | LC | ETL.6870.INSL | 40639253 | SACTO | SACRAMENTO | 2020-08-17 | 2021-06-07 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611448 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Polymer | Post |  |  |  |  | 0.031493 | 31.7319
119629810 | E | LC | ETL.6870.INSL | 40639253 | SACTO | SACRAMENTO | 2020-08-17 | 2021-06-07 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611448 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Polymer | Post |  |  |  |  | 0.031493 | 31.7319
119629810 | E | LC | ETL.6870.INSL | 40639253 | SACTO | SACRAMENTO | 2020-08-17 | 2021-06-07 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611448 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.031493 | 31.7319
119629810 | E | LC | ETL.6870.INSL | 40639253 | SACTO | SACRAMENTO | 2020-08-17 | 2021-06-07 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40611448 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.031493 | 31.7319
119638499 | E | LC | ETL.1450.POLE.WDPS | 44553672 | SACTO | SACRAMENTO | 2020-08-19 | 2021-09-30 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 44553218 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0017933 | 31.7066
119688015 | F | LC | ETL.8650.TOWR | 40582615 | FRESNO | YOSEMITE | 2020-08-27 |  | ETL.8650 | EXCHEQUER-INDIAN FLAT | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40582615 | 1966-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1966-01-01 | Glass | Suspension |  |  |  |  | 0.0085058 | 1331.6866 | 11.3271
119695289 | E | LC | ETL.7780.POLE.WOOD | 40614170 | LAKEVLLE | HUMBOLDT | 2020-08-27 | 2021-02-17 | ETL.7780 | PHILO JCT-ELK | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40614170 |  | Single Wood Pole | LB - Line and Buck |  | Ceramic | [5 empty] | 3.4829e-05 | 316.4353
119696485 | E | LC | ETL.7560.POLE.WDPS | 44414809 | SACTO | SACRAMENTO | 2020-08-25 | 2021-04-12 | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119715286 | F | LC | ETL.8180.POLE.NWOD | 44164662 | LAKEVLLE | SACRAMENTO | 2020-09-01 |  | ETL.8180 | TULUCAY-NAPA #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44164662 | 2012-07-03 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2021-06-15 | Glass | Dead End |  |  |  |  | 0.0020463 | 3705.6223
119721043 | A | LC | ETL.6230.POLE.NWOD | 44178492 | MOSSLNDG | CENTRAL COAST | 2020-09-06 | 2020-09-24 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44178492 | 2014-06-08 | Light Duty Steel Pole | T-1 - Tri Post | 2020-09-21 | Polymer | Post |  |  |  |  | 0.035571 | 427.5717
119725302 | F | LC | ETL.6290.POLE.WDPS | 44399514 | TABLEMTN | NORTH VALLEY | 2020-08-12 | 2020-09-24 | ETL.6290 | CARIBOU-PLUMAS JCT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 44399511 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.27051 | 5538.7192
119753124 | F | LC | ETL.7590.POLE.WDPS | 44944231 | MOSSLNDG | CENTRAL COAST | 2020-08-06 | 2021-01-12 | ETL.7590 | MONTA VISTA-BURNS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | DLFL
119766042 | E | LC | ETL.8961.POLE.WDPS | 44231073 | FRESNO | FRESNO | 2020-09-15 |  | ETL.8961 | DINOSAUR POINT TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44231070 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00087586 | 1870.4016 | 1.6382
119795014 | F | LC | ETL.6690.POLE.WOOD | 40654887 | SACTO | SIERRA | 2020-08-05 | 2021-07-06 | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40654887 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | [5 empty] | 0.031276 | 723.1693
119818440 | A | LC | ETL.1401.POLE.WDPS | 44805704 | VICTOR | STOCKTON | 2020-09-26 | 2020-09-30 | ETL.1401 | BEARDSLEY TAP | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44805704 | 2019-08-06 | 2-Pole Wood | 2PS - 2 Pole SUSP | 2019-08-06 | Polymer | Suspension |  |  |  |  | 0.0012514
119818440 | A | LC | ETL.1401.POLE.WDPS | 44805704 | VICTOR | STOCKTON | 2020-09-26 | 2020-09-30 | ETL.1401 | BEARDSLEY TAP | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44805704 | 2019-08-06 | 2-Pole Wood | 2PS - 2 Pole SUSP | 2019-08-06 | Polymer | Suspension |  |  |  |  | 0.0012514
119850160 | E | LC | ETL.7030.POLE.WOOD | 40760940 | TABLEMTN | NORTH VALLEY | 2020-10-02 | 2021-05-13 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40760940 |  | Single Wood Pole | T2N | 2021-05-04 | Polymer | Post |  |  |  |  | 0.0030179 | 2693.4546
119930555 | E | LC | ETL.1110.POLE.NWOD | 42603539 | TABLEMTN | HUMBOLDT | 2020-10-21 | 2021-06-30 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Damper-Steel | Missing | [Install, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42603539 |  | Lattice Steel Pole | DDE - Double Dead End | 2020-10-12 | Glass | Double Dead End |  |  |  |  | 1.0336e-05 | 205.744
119963157 | F | LC | ETL.8960.POLE.STPS | 44236987 | FRESNO | FRESNO | 2020-10-27 |  | ETL.8960 | LOS BANOS-PACHECO | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Non-HFTD | HFRA Addition | PEND | 44236985 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.8436e-07
120076417 | F | LC | ETL.6280.POLE.WOOD | 40876684 | TABLEMTN | NORTH VALLEY | 2020-11-16 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | PEND | [11 empty] | 2.9971e-05 | 15.8815
120132237 | E | LC | ETL.1450.POLE.WDPS | 44559031 | SACTO | SACRAMENTO | 2020-12-04 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44558462 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.0092565 | 110.8102 | 1.0257
120211142 | F | LC | ETL.4870.TOWR | 40582543 | FRESNO | FRESNO | 2020-11-09 | 2021-10-07 | ETL.4870 | HELMS-GREGG #1 | Marker (i.e. signs)-Steel | Missing | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40582543 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 5.2516e-06
120227424 | F | LC | ETL.6890.POLE.NWOD | 44713028 | LAKEVLLE | SONOMA | 2020-12-22 | 2021-05-10 | ETL.6890 | FULTON-HOPLAND | Road | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | DLFL | 44713028 | 2019-02-16 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-02-16 | Ceramic | Dead End |  |  |  |  | 1.5776e-09 | 1865.8288
120243320 | E | LC | ETL.1450.POLE.WDPS | 44553708 | SACTO | SACRAMENTO | 2020-12-31 | 2021-09-30 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553188 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.132 | 3274.9534
120657945 | B | LC | ETL.6890.POLE.NWOD | 44713023 | LAKEVLLE | SONOMA | 2021-03-18 | 2021-03-31 | ETL.6890 | FULTON-HOPLAND | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44713023 | 2019-02-16 | Light Duty Steel Pole | SS1 - Susp. Steel Single. CIR | 2019-02-16 | Ceramic | Suspension |  |  |  |  | 1.1263e-09 | 949.8127
120679687 | E | LC | ETL.3700.POLE.WOOD | 40751448 | PISMOBCH | LOS PADRES | 2021-03-22 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40751448 | 1989-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1989-01-01 | Porcelain | Dead End |  |  |  |  | 0.00080886 | 3563.9187 | 2.8827
120689958 | E | LC | ETL.1680.POLE.WDPS | 44298671 | LAKEVLLE | SONOMA | 2021-03-25 | 2021-03-29 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44298670 |  | 3-Pole Wood | FSS - Field Switch Structure | [7 empty] | 0.0013052 | 4639.9287
120701867 | E | LC | ETL.5630.TOWR | 40671054 | TABLEMTN | NORTH VALLEY | 2021-03-27 | 2021-08-12 | ETL.5630 | ROCK CREEK-POE | Jumper-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | DLFL | 40671054 | 1950-01-01 | LATTICE STEEL TOWER | TPSRD - Tramp Double Dead End | 1950-01-01 | Ceramic | Dead End |  |  |  |  | 3.9235e-05 | 1006.2033
120707537 | E | LC | ETL.3700.INSL.CERA | 40842801 | PISMOBCH | LOS PADRES | 2021-03-29 | 2021-10-06 | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Hardware-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816917 | 1989-01-01 | Single Wood Pole | T-1 - Tri Post | 1989-01-01 | Porcelain | Post |  |  |  |  | 4.4724e-05 | 7061.4551 | 0.31582
120737120 | E | LC | ETL.2900.TOWR | 40752788 | MOSSLNDG | CENTRAL COAST | 2021-04-02 | 2021-08-02 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752788 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.02649 | 841.4142
120737120 | E | LC | ETL.2900.TOWR | 40752788 | MOSSLNDG | CENTRAL COAST | 2021-04-02 | 2021-08-02 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40752788 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Polymer | Suspension |  |  |  |  | 0.02649 | 841.4142
120742231 | E | LC | ETL.2540.INSL.NCER | 42567762 | MOSSLNDG | SAN JOSE | 2021-04-05 | 2021-08-10 | ETL.2540 | METCALF-GREEN VALLEY | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
120770196 | F | LC | ETL.4750.TOWR | 40756565 | LAKEVLLE | SONOMA | 2021-04-09 |  | ETL.4750 | GEYSERS #12-FULTON | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40756565 | 1971-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1971-01-01 | Porcelain | Dead End |  |  |  |  | 1.9942e-09 | 1634.3027
120773496 | E | LC | ETL.6870.POLE.WOOD | 40589919 | SACTO | SACRAMENTO | 2021-04-09 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40589919 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.067014 | 126.6562 | 8.4877
120801586 | E | LC | ETL.1070.POLE.WOOD | 40580889 | VICTOR | YOSEMITE | 2021-04-12 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40580889 | 1957-01-01 | Single Wood Pole | SUSP - Suspension (TWR) | 1957-01-01 | Non Ceramic | Suspension |  |  |  |  | 9.19e-07 | 2154.8721 | 0.0019803
120811269 | F | LC | ETL.9100.POLE.WOOD | 44191304 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191304 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 8.6142e-06 | 3211.6518
120812169 | A | LC | ETL.7360.POLE.WOOD | 40585409 | LAKEVLLE | SONOMA | 2021-04-14 | 2021-04-15 | ETL.7360 | LAKEVILLE #1 | Emergency-Wood | Other | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40585409 | 1961-01-01 | Single Wood Pole | T2N | 2021-04-14 | Polymer | Post |  |  |  |  | 0.0015149 | 158.7034
120812257 | F | LC | ETL.9100.POLE.WOOD | 44191863 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191863 |  | Single Wood Pole | WB - Wishbone |  | Porcelain | [5 empty] | 4.4303e-05 | 1952.4196
120813346 | F | LC | ETL.5300.TOWR | 40765332 | PISMOBCH | LOS PADRES | 2021-04-07 |  | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40765332 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 5.5731e-07 | 2345.0251 | 0.0013069
120822386 | F | LC | ETL.1073.POLE.NWOD | 44699316 | VICTOR | STOCKTON | 2021-04-15 |  | ETL.1073 | MI-WUK-CURTIS | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44699316 | 2018-12-08 | Tubular Steel Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End - Suspension |  |  |  |  | 1.4882e-05 | 31.7081
120823122 | B | LC | ETL.1073.POLE.WDPS | 44976973 | VICTOR | STOCKTON | 2021-04-15 | 2021-07-13 | ETL.1073 | MI-WUK-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40860732 | 1956-01-01 | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00050975 | 15.8866
120839807 | E | LC | ETL.3820.TOWR | 40803363 | VICTOR | STOCKTON | 2021-04-12 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Vegetation-Tower | Overgrown | [Cage Clearing] | Tier2 | Tier 2 | Within Both | PEND | 40803363 | 1910-01-01 | LATTICE STEEL TOWER | DCPOST - Double Circuit Post | 1989-01-01 | Polymer | Suspension |  |  |  |  | 4.8264e-06 | 5476.1846 | 0.02643
120840145 | E | LC | ETL.3750.INSL.CERA | 40835557 | CONCORD | EAST BAY | 2021-04-19 |  | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Splice-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40808958 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1944-01-01 | Ceramic | Suspension |  |  |  |  | 1.2388e-06 | 1045.262 | 0.0012949
120860776 | E | LC | ETL.8240.POLE.WOOD | 40758344 | VICTOR | STOCKTON | 2021-04-21 | 2021-05-07 | ETL.8240 | VALLEY SPRINGS-MARTELL #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
120868912 | E | LC | ETL.1860.POLE.WOOD | 40811665 | LAKEVLLE | SONOMA | 2021-04-22 |  | ETL.1860 | IGNACIO-LAS GALLINAS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | HFRA Removal | PEND | 40811665 |  | Single Wood Pole | DV - Double Vertical |  | Ceramic | Other |  |  |  |  | 0.00031148 | 15.8851 | 0.004948
120872244 | E | LC | ETL.5330.INSL | 40679536 | MOSSLNDG | CENTRAL COAST | 2021-04-23 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40651054 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Suspension |  |  |  |  | 7.1608e-08 | 15.8926 | 1.138e-06
120872244 | E | LC | ETL.5330.INSL | 40679536 | MOSSLNDG | CENTRAL COAST | 2021-04-23 |  | ETL.5330 | MOSS LANDING-COBURN | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40651054 | 1969-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1969-01-01 | Ceramic | Other |  |  |  |  | 7.1608e-08 | 15.8926 | 1.138e-06
120884258 | F | LC | ETL.5400.TOWR | 40605537 | TABLEMTN | NORTH VALLEY | 2021-04-26 |  | ETL.5400 | PIT #3-PIT #1 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40605537 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 0.0062037 | 80.8927
120910679 | F | LC | ETL.7550.POLE.WOOD | 40768545 | LAKEVLLE | SONOMA | 2021-04-30 | 2021-10-28 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40768545 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0001559 | 2392.1772
120930834 | E | LC | ETL.4570.INSL | 40842691 | TABLEMTN | NORTH VALLEY | 2021-05-04 |  | ETL.4570 | COTTONWOOD-LOGAN CREEK | Conductor-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40816835 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 3.929e-07 | 5006.2686 | 0.001967
120935344 | E | LC | ETL.6890.POLE.NWOD | 44989195 | LAKEVLLE | SONOMA | 2021-05-04 |  | ETL.6890 | FULTON-HOPLAND | Structure-Wood | Rotten | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44989195 | 2019-11-13 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2019-11-13 | Polymer | Post |  |  |  |  | 1.8215e-06 | 3817.45 | 0.0069535
121338962 | F | LC | ETL.2900.TOWR | 40682814 | MOSSLNDG | CENTRAL COAST | 2021-04-20 |  | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Structure-Tower | Anti-Climbing Guard | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40682814 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0068499 | 428.4953
121343097 | E | LC | ETL.1430.TOWR | 40597548 | SACTO | SIERRA | 2021-05-15 |  | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40597548 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2020-08-02 | Glass | Suspension |  |  |  |  | 0.036477 | 142.4642 | 5.1966
121348350 | F | LC | ETL.4870.TOWR | 40576770 | FRESNO | FRESNO | 2021-05-17 |  | ETL.4870 | HELMS-GREGG #1 | Fence / Gate | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40576770 | 1985-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1985-01-01 | Ceramic | Double Dead End |  |  |  |  | 1.5868e-07 | 731.474
121352433 | B | LC | ETL.7930.INSL.NCER | 40851455 | MOSSLNDG | CENTRAL COAST | 2021-05-17 | 2021-07-26 | ETL.7930 | SALINAS-LAURELES | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40824188 |  | Tubular Steel Pole | FSS - Field Switch Structure |  | Non Ceramic | Other |  |  |  |  | 0.00094429 | 63.3245
121363539 | E | LC | ETL.1820.POLE.WDPS | 44562675 | EUREKA | HUMBOLDT | 2021-05-19 | 2021-08-30 | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44562387 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.070289 | 6332.6187
121363904 | E | LC | ETL.6370.POLE.WOOD | 40665636 | CONCORD | EAST BAY | 2021-04-26 | 2021-05-27 | ETL.6370 | CHRISTIE-WILLOW PASS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40665636 |  | Single Wood Pole | SV-PJ-90 - Single Vertical Post Jumper 90 |  | Polymer | [5 empty] | 0.16186 | 521.8005
121373405 | F | LC | ETL.5934.TOWR | 40604885 | PISMOBCH | LOS PADRES | 2021-05-04 |  | ETL.5934 | TEMPLETON-GATES | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40604885 | 1954-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 9.48e-08 | 5082.1426 | 0.00048179
121373830 | F | LC | ETL.6050.TOWR | 40753806 | MOSSLNDG | CENTRAL COAST | 2021-05-21 | 2021-07-30 | ETL.6050 | MOSS LANDING-METCALF | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40753806 | 1966-01-01 | LATTICE STEEL TOWER | Unknown | 1966-01-01 | Ceramic | Suspension |  |  |  |  | 0.00060966 | 0.066432
121374358 | E | LC | ETL.2790.INSL | 40792391 | CONCORD | DIABLO | 2021-05-19 |  | ETL.2790 | MORAGA-SAN LEANDRO #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40761843 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.2896e-06 | 0.065153 | 2.1433e-07
121374526 | F | LC | ETL.1422.TOWR | 40762132 | SACTO | SIERRA | 2021-05-03 |  | ETL.1422 | BRUNSWICK #1 TAP | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40762132 | 1975-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. |  | Ceramic | Suspension |  |  |  |  | 6.8638e-09 | 1471.1865 | 1.0098e-05
121376405 | F | LC | ETL.1070.POLE.WOOD | 40602882 | VICTOR | STOCKTON | 2021-05-05 | 2021-07-01 | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40602882 | 1998-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1998-01-01 | Polymer | Post |  |  |  |  | 0.00050775 | 2436.4434
121380289 | B | LC | ETL.3840.SWIT | 40743434 | VICTOR | STOCKTON | 2021-05-21 | 2021-06-01 | ETL.3840 | STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | Switch | Out of Adjustment | [Repair, Completed] | Tier2 |  |  | COMP | [8 empty] | ITE | NO ATTACHMENTS | Manual
121380819 | B | LC | ETL.1430.INSL | 40831512 | SACTO | SACRAMENTO | 2021-05-21 | 2021-08-09 | ETL.1430 | DRUM-RIO OSO #2 | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40805328 | 1913-01-01 | LATTICE STEEL TOWER | 1VP - 1 Vertical | 1990-01-01 | Ceramic | Post |  |  |  |  | 0.00015759 | 775.2101
121381294 | F | LC | ETL.6500.POLE.WOOD | 40599626 | TABLEMTN | NORTH VALLEY | 2021-05-10 |  | ETL.6500 | COLGATE-PALERMO | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40599626 |  | Single Wood Pole | TPAT - Tri Pin Arm Tramp |  | Porcelain | Pin |  |  |  |  | 0.0026425 | 443.3615
121384178 | B | LC | ETL.3830.TOWR | 40661801 | VICTOR | STOCKTON | 2021-05-21 | 2021-06-02 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40661801 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1989-01-01 | Ceramic | Suspension |  |  |  |  | 3.1167e-05 | 4001.9462
121385737 | E | LC | ETL.1420.TOWR | 40762305 | SACTO | SIERRA | 2021-05-12 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40762305 | 1913-01-01 | LATTICE STEEL TOWER | FDDE - Flat Dead End Construction | 1913-01-01 | Porcelain | Dead End |  |  |  |  | 5.9148e-08 | 1507.6083 | 8.9171e-05
121389462 | E | LC | ETL.6980.POLE.WOOD | 40877391 | LAKEVLLE | HUMBOLDT | 2021-05-15 |  | ETL.6980 | FORT ROSS-GUALALA | Hardware-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40877391 | 1969-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1953-01-01 | Polymer | Suspension |  |  |  |  | 0.18709 | 285.541 | 53.4218
121395366 | E | LC | ETL.8060.POLE.WOOD | 40702026 | SACTO | SIERRA | 2021-05-18 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40702026 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.16554 | 174.093 | 28.819
121395505 | F | LC | ETL.6660.POLE.NWOD | 45084725 | TABLEMTN | NORTH VALLEY | 2021-05-18 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45084725 | 2021-03-04 | Light Duty Steel Pole | T-1 - Tri Post | 2021-03-04 | Polymer | Post |  |  |  |  | 1.291e-10 | 3697.6668
121396136 | E | LC | ETL.7380.INSL | 40801087 | MOSSLNDG | CENTRAL COAST | 2021-05-12 |  | ETL.7380 | LAURELES-OTTER | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40770263 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.10667 | 443.8326 | 47.3416
121397491 | E | LC | ETL.1430.TOWR | 40647572 | SACTO | SIERRA | 2021-05-15 |  | ETL.1430 | DRUM-RIO OSO #2 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40647572 | 1913-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2015-08-13 | Ceramic | Suspension |  |  |  |  | 0.0029035 | 1993.4753 | 5.788
121397768 | E | LC | ETL.1420.TOWR | 40866022 | SACTO | SIERRA | 2021-05-13 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40866022 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1913-01-01 | Porcelain | Suspension |  |  |  |  | 0.0034084 | 15.8837 | 0.054138
121397768 | E | LC | ETL.1420.TOWR | 40866022 | SACTO | SIERRA | 2021-05-13 |  | ETL.1420 | DRUM-RIO OSO #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40866022 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-05-01 | Glass | Suspension |  |  |  |  | 0.0034084 | 15.8837 | 0.054138
121403928 | F | LC | ETL.6870.POLE.WOOD | 40751821 | SACTO | SIERRA | 2021-05-20 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40751821 | 1966-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1966-01-01 | Ceramic | Pin |  |  |  |  | 0.039147 | 199.4555
121404487 | F | LC | ETL.6280.POLE.NWOD | 44259019 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44259019 | 2020-07-21 | Light Duty Steel Pole | T2N | 2020-07-21 | Polymer | Post |  |  |  |  | 1.6696e-08 | 158.2282
121404553 | E | LC | ETL.7270.POLE.WOOD | 40758296 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.7270 | KESWICK-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40758296 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.035564 | 1935.3134 | 68.8269
121404607 | E | LC | ETL.8290.INSL | 40627831 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.8290 | VOLTA-DESCHUTES | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40601142 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.013137 | 3152.3784 | 41.412
121405178 | F | LC | ETL.6640.POLE.WOOD | 40667494 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40667494 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.00081585 | 0.066431
121409196 | E | LC | ETL.6640.POLE.WOOD | 40827026 | TABLEMTN | NORTH VALLEY | 2021-05-21 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40827026 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | [5 empty] | 0.0029203 | 2727.2633 | 7.9644
121422040 | F | LC | ETL.6220.POLE.WOOD | 40752638 | EUREKA | HUMBOLDT | 2021-05-27 | 2021-09-28 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40752638 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.065656 | 1537.8777
121430937 | F | LC | ETL.6220.POLE.WOOD | 40862503 | EUREKA | HUMBOLDT | 2021-05-26 |  | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40862503 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 0.0047315 | 1077.092
121438278 | E | LC | ETL.2540.INSL.CERA | 40693652 | METCALF | SAN JOSE | 2021-05-26 |  | ETL.2540 | METCALF-GREEN VALLEY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44401490 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.1456
121438278 | E | LC | ETL.2540.INSL.CERA | 40693652 | METCALF | SAN JOSE | 2021-05-26 |  | ETL.2540 | METCALF-GREEN VALLEY | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44401490 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.1456
121444981 | E | LC | ETL.4050.POLE.NWOD | 44965651 | LAKEVLLE | SONOMA | 2021-05-27 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44965651 | 2020-04-13 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2020-04-13 | Polymer | Post |  |  |  |  | 5.2602e-07 | 2171.1357 | 0.0011421
121447387 | E | LC | ETL.5390.TOWR | 40643574 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40643574 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 5.0897e-06 | 4864.272 | 0.024758
121454077 | F | LC | ETL.7290.POLE.WOOD | 40759377 | TABLEMTN | NORTH VALLEY | 2021-05-26 | 2021-10-11 | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40759377 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.012812 | 1333.3085
121473707 | F | LC | ETL.1820.POLE.WDPS | 44560674 | EUREKA | HUMBOLDT | 2021-05-28 |  | ETL.1820 | HUMBOLDT-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44560111 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.077199 | 2753.0989
121485942 | F | LC | ETL.7140.POLE.WOOD | 40825709 | LAKEVLLE | NORTH BAY | 2021-06-01 | 2021-06-23 | ETL.7140 | IGNACIO-BOLINAS #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40825709 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | [5 empty] | 0.39994 | 63.3833
121491133 | E | LC | ETL.8060.POLE.WOOD | 40771531 | SACTO | SIERRA | 2021-06-08 | 2021-06-17 | ETL.8060 | SPAULDING-SUMMIT | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL | [11 empty] | 0.0068914 | 443.0452
121492487 | E | LC | ETL.4050.POLE.NWOD | 44214174 | LAKEVLLE | SONOMA | 2021-05-27 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44214174 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post |  |  |  |  | 0.0053414 | 4230.5894 | 22.5972
121493482 | F | LC | ETL.5390.TOWR | 40819057 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5390 | PIT #1-COTTONWOOD | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40819057 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 7.9182e-06 | 1253.9935
121499848 | E | LC | ETL.5650.INSL | 40721302 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40675885 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1924-01-01 | Ceramic | Suspension |  |  |  |  | 2.5666e-06 | 2505.4126 | 0.0064303
121499856 | F | LC | ETL.1710.TOWR | 40758138 | MOSSLNDG | CENTRAL COAST | 2021-06-03 |  | ETL.1710 | GREEN VALLEY-CAMP EVERS | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40758138 | 1970-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1971-01-01 | Ceramic | Suspension |  |  |  |  | 2.4089e-07 | 3.2281
121499899 | F | LC | ETL.6880.POLE.WOOD | 40601375 | LAKEVLLE | NORTH BAY | 2021-06-04 |  | ETL.6880 | FULTON-CALISTOGA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40601375 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.00029483 | 522.1488 | 0.15395
121512829 | F | LC | ETL.7180.POLE.WOOD | 40668110 | LAKEVLLE | NORTH BAY | 2021-06-03 |  | ETL.7180 | IGNACIO-BOLINAS #2 | Right of Way | Encroachment | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40668110 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 1.0042e-05 | 253.482
121516707 | F | LC | ETL.6880.POLE.WOOD | 44274768 | LAKEVLLE | NORTH BAY | 2021-06-05 |  | ETL.6880 | FULTON-CALISTOGA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44274768 | 2017-08-05 | Single Wood Pole | TPD - Tri Post Dead End Construction | 2017-08-05 | Ceramic | Dead End |  |  |  |  | 0.11219 | 1709.667
121516727 | E | LC | ETL.1420.TOWR | 40596150 | SACTO | SIERRA | 2021-06-07 |  | ETL.1420 | DRUM-RIO OSO #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40596150 | 1913-01-01 | LATTICE STEEL TOWER | TPAF - Flat Pin Arm |  | Polymer | [5 empty] | 5.7259e-05 | 3797.0496 | 0.21742
121516761 | F | LC | ETL.1440.POLE.STPS | 44338121 | SACTO | SIERRA | 2021-06-04 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44338120 | 2018-09-06 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 1.4929e-06 | 3069.2839
121516777 | E | LC | ETL.1600.TOWR | 40585743 | LAKEVLLE | SONOMA | 2021-06-05 | 2021-08-05 | ETL.1600 | FULTON-PUEBLO | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40585743 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2019-06-20 | Glass | Suspension |  |  |  |  | 0.0002237 | 174.2843
121516777 | E | LC | ETL.1600.TOWR | 40585743 | LAKEVLLE | SONOMA | 2021-06-05 | 2021-08-05 | ETL.1600 | FULTON-PUEBLO | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40585743 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Porcelain | Suspension |  |  |  |  | 0.0002237 | 174.2843
121519685 | F | LC | ETL.5390.TOWR | 40759685 | TABLEMTN | NORTH VALLEY | 2021-06-08 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40759685 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 6.6092e-07 | 1158.6814 | 0.0007658
121520706 | B | LC | ETL.1450.TOWR | 40579656 | SACTO | SIERRA | 2021-06-10 | 2021-07-07 | ETL.1450 | DRUM-SUMMIT #2 | Switch | Out of Adjustment | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40579656 | 1948-01-01 | LATTICE STEEL TOWER | FSS - Field Switch Structure | 1948-01-01 | Ceramic | Dead End |  |  |  |  | 0.018345 | 3274.9534
121524863 | E | LC | ETL.1450.POLE.WDPS | 44212070 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44212069 |  | 2-Pole Wood | Unknown | [7 empty] | 0.017346 | 31.7066 | 0.54997
121524863 | E | LC | ETL.1450.POLE.WDPS | 44212070 | SACTO | SACRAMENTO | 2021-06-08 |  | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44212069 |  | 2-Pole Wood | Unknown | [7 empty] | 0.017346 | 31.7066 | 0.54997
121525941 | B | LC | ETL.1450.POLE.WOOD | 44150204 | SACTO | SIERRA | 2021-06-12 | 2021-08-31 | ETL.1450 | DRUM-SUMMIT #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44150204 |  | Single Wood Pole | TPSRD - Tramp Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.013591 | 617.1616
121527221 | E | LC | ETL.8350.POLE.WOOD | 40643822 | VICTOR | STOCKTON | 2021-06-08 | 2021-08-26 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40643822 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Porcelain | [5 empty] | 0.0031737 | 553.7256
121530854 | B | LC | ETL.8170.INSL | 40610939 | EUREKA | HUMBOLDT | 2021-06-13 | 2021-09-21 | ETL.8170 | TRINITY-MAPLE CREEK | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
121531366 | B | LC | ETL.5390.INSL.NCER | 45113179 | TABLEMTN | NORTH VALLEY | 2021-06-13 | 2021-08-17 | ETL.5390 | PIT #1-COTTONWOOD | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40865920 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 7.4844e-08 | 607.7349
121582581 | E | LC | ETL.6070.INSL | 40726271 | TABLEMTN | NORTH VALLEY | 2021-06-18 |  | ETL.6070 | ROUND MTN-TABLE MTN #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40684114 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 0.00071626 | 397.6502 | 0.28482
121586879 | E | LC | ETL.3720.INSL.CERA | 40844821 | CONCORD | EAST BAY | 2021-06-22 |  | ETL.3720 | SOBRANTE-G #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40818453 | 1968-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End |  | Porcelain | [5 empty] | 5.1175e-05 | 253.126 | 0.012954
121587663 | B | LC | ETL.2760.INSL.CERA | 40878786 | CONCORD | EAST BAY | 2021-06-22 | 2021-07-26 | ETL.2760 | MORAGA-OAKLAND J | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40857662 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Suspension |  |  |  |  | 0.00017852 | 63.3245
121587663 | B | LC | ETL.2760.INSL.CERA | 40878786 | CONCORD | EAST BAY | 2021-06-22 | 2021-07-26 | ETL.2760 | MORAGA-OAKLAND J | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40857662 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1952-01-01 | Ceramic | Dead End |  |  |  |  | 0.00017852 | 63.3245
121596567 | E | LC | ETL.4050.INSL.CERA | 40579184 | LAKEVLLE | HUMBOLDT | 2021-06-24 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44557876 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle |  | Ceramic | Double Dead End |  |  |  |  | 9.0598e-05
121596567 | E | LC | ETL.4050.INSL.CERA | 40579184 | LAKEVLLE | HUMBOLDT | 2021-06-24 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44557876 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle |  | Ceramic | Double Dead End |  |  |  |  | 9.0598e-05
121596567 | E | LC | ETL.4050.INSL.CERA | 40579184 | LAKEVLLE | HUMBOLDT | 2021-06-24 |  | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44557876 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle |  | Ceramic | Double Dead End |  |  |  |  | 9.0598e-05
121607058 | E | LC | ETL.1070.INSL.NCER | 40827991 | VICTOR | STOCKTON | 2021-06-23 | 2021-08-26 | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 40804199 | 1998-01-01 | Single Wood Pole | 3HPD - 3 Horizontal Post Delta | 1998-01-01 | Polymer | Post |  |  |  |  | 0.00014179 | 2978.6118
121634882 | E | LC | ETL.6070.TOWR | 40684118 | TABLEMTN | NORTH VALLEY | 2021-06-24 |  | ETL.6070 | ROUND MTN-TABLE MTN #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40684118 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2015-05-27 | Ceramic | Suspension |  |  |  |  | 1.9949e-06 | 269.2705 | 0.00053716
121645244 | B | LC | ETL.5420.POLE.WDPS | 44559088 | TABLEMTN | NORTH VALLEY | 2021-06-26 | 2021-09-22 | ETL.5420 | PIT #5-ROUND MTN #1 | Structure-Wood | Rotten | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 952.427
121647174 | F | LC | ETL.6020.TOWR | 40868300 | TABLEMTN | NORTH VALLEY | 2021-06-30 |  | ETL.6020 | MALIN-ROUND MTN #2 | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40868300 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.1e-07 | 332.4042
121662529 | E | LC | ETL.3700.POLE.WDPS | 44296828 | PISMOBCH | LOS PADRES | 2021-06-30 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44296825 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00016233 | 4022.5613 | 0.65299
121667163 | F | LC | ETL.4316.POLE.NWOD | 45102880 | TABLEMTN | NORTH VALLEY | 2021-07-06 |  | ETL.4316 | PARADISE-TABLE MTN | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45102880 | 2021-04-30 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2021-04-30 | Glass | Suspension |  |  |  |  | 3.449e-05 | 1982.3486
121674972 | E | LC | ETL.7575.POLE.WDPS | 44384744 | METCALF | SAN FRANCISCO | 2021-07-03 | 2021-09-16 | ETL.7575 | SNEATH LANE-PACIFICA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44384743 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.36816 | 396.2583
121679202 | E | LC | ETL.1720.INSL.NCER | 40611225 | METCALF | SAN JOSE | 2021-07-03 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44400950 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 4.1988e-05
121679202 | E | LC | ETL.1720.INSL.NCER | 40611225 | METCALF | SAN JOSE | 2021-07-03 |  | ETL.1720 | GREEN VALLEY-LLAGAS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44400950 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 4.1988e-05
121685825 | F | LC | ETL.4393.POLE.STPS | 45074196 | SACTO | SIERRA | 2021-07-06 |  | ETL.4393 | DRUM-HIGGINS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 45074119 | 2021-03-26 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.114e-05 | 2056.7583
121712732 | E | LC | ETL.4220.POLE.STPS | 44986077 | TABLEMTN | NORTH VALLEY | 2021-07-12 |  | ETL.4220 | WOODLEAF-PALERMO | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44921292 | 2019-09-18 | 3-Pole Non Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.00711 | 269.106 | 1.9133
121717638 | F | LC | ETL.1250.POLE.WOOD | 40859621 | FRESNO | YOSEMITE | 2021-07-07 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40859621 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.00012132 | 6429.5964
121718060 | E | LC | ETL.7631.POLE.WOOD | 45107531 | LAKEVLLE | SONOMA | 2021-07-12 |  | ETL.7631 | WOHLER TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 45107531 |  | Single Wood Pole | T-1 - Tri Post |  | Polymer | Post | [5 empty] | 1094.5327
121730729 | B | LC | ETL.4880.INSL | 40881254 | FRESNO | FRESNO | 2021-07-14 | 2021-10-04 | ETL.4880 | HELMS-GREGG #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40858343 | 1985-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1985-01-01 | Ceramic | Suspension |  |  |  |  | 2.0952e-07
121738450 | F | LC | ETL.7130.POLE.WDPS | 44315156 | EUREKA | HUMBOLDT | 2021-07-09 |  | ETL.7130 | HUMBOLDT-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44315155 | 2013-10-26 | 3-Pole Wood | SVDE - Single Vertical Dead End | [7 empty] | 0.17715 | 0.065148
121738838 | E | LC | ETL.6760.POLE.WOOD | 40767300 | SACTO | SIERRA | 2021-07-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40767300 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 0.071123 | 648.7505 | 46.141
121745790 | E | LC | ETL.1540.POLE.NWOD | 44402206 | SACTO | SIERRA | 2021-07-16 |  | ETL.1540 | EL DORADO-MISSOURI FLAT #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44402206 | 2017-07-26 | Light Duty Steel Pole | T-1 - Tri Post | 2017-07-26 | Polymer | Post |  |  |  |  | 4.2458e-08 | 15.8837 | 6.7439e-07
121746307 | E | LC | ETL.2390.INSL.NCER | 40604014 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44390975 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 4.3004e-05
121746307 | E | LC | ETL.2390.INSL.NCER | 40604014 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44390975 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Polymer | Suspension |  |  |  |  | 4.3004e-05
121759998 | F | LC | ETL.2390.POLE.WDPS | 44391104 | VICTOR | STOCKTON | 2021-07-13 |  | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391101 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.4172e-05 | 2437.8394 | 0.058928
121768453 | F | LC | ETL.1810.POLE.WDPS | 44322235 | EUREKA | HUMBOLDT | 2021-07-20 | 2021-10-11 | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 44322234 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 3.3806e-06
121781331 | E | LC | ETL.4223.POLE.WDPS | 45099473 | TABLEMTN | NORTH VALLEY | 2021-07-21 | 2021-10-25 | ETL.4223 | KANAKA TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 42567872 | 1964-01-01 | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.00017232 | 142.4703
121785290 | F | LC | ETL.8350.POLE.WOOD | 40768204 | VICTOR | STOCKTON | 2021-07-21 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40768204 |  | Single Wood Pole | DDE - Double Dead End |  | Glass | [5 empty] | 0.00016313 | 300.6168 | 0.049039
121786403 | E | LC | ETL.9240.TOWR | 43249851 | PISMOBCH | LOS PADRES | 2021-07-22 |  | ETL.9240 | MIDWAY-SANTA MARIA (12KV) | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 43249851 |  | LATTICE STEEL TOWER | [9 empty] | 1475.0885
121820881 | B | LC | ETL.6290.POLE.WOOD | 40876660 | TABLEMTN | NORTH VALLEY | 2021-07-30 | 2021-09-22 | ETL.6290 | CARIBOU-PLUMAS JCT | Emergency | Fire | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [11 empty] | 0.030964 | 126.5956
121883141 | B | LC | ETL.1820.POLE.WDPS | 44562900 | EUREKA | HUMBOLDT | 2021-08-11 | 2021-10-04 | ETL.1820 | HUMBOLDT-TRINITY | Emergency | Fire | [Replace, Completed, Completed] | Tier2 |  |  | COMP | [12 empty] | 79.1724
121940334 | E | LC | ETL.1820.POLE.WDPS | 44562763 | EUREKA | HUMBOLDT | 2021-08-22 |  | ETL.1820 | HUMBOLDT-TRINITY | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44562468 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.028572 | 47.5295 | 1.358
121944786 | E | LC | ETL.4316.TOWR | 40821426 | TABLEMTN | NORTH VALLEY | 2021-08-24 |  | ETL.4316 | PARADISE-TABLE MTN | Splice-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40821426 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Suspension |  |  |  |  | 0.0052868 | 2473.0312 | 13.0745
122041680 | E | LC | ETL.5140.POLE.WDPS | 44552580 | SACTO | SACRAMENTO | 2021-05-29 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 44551524 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.038841 | 4160.9766 | 161.6153
122079297 | E | LC | ETL.8060.INSL.NCER | 45156080 | SACTO | SIERRA | 2021-09-21 |  | ETL.8060 | SPAULDING-SUMMIT | Damper-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45156027 | 2021-08-31 | Single Wood Pole | T2N | 2021-08-31 | Polymer | Post
122154080 | E | LC | ETL.8060.POLE.NWOD | 45163984 | SACTO | SIERRA | 2021-10-06 |  | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 45163984 | 2021-07-26 | Light Duty Steel Pole | T2N | 2021-07-26 | Polymer | Post
122163307 | E | LC | ETL.4392.INSL.NCER | 40792686 | LAKEVLLE | SONOMA | 2021-10-07 |  | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Emergency | Storm Related | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40762053 | 1946-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1997-01-01 | Polymer | Suspension |  |  |  |  | 5.0055e-08 | 1711.4833 | 8.5668e-05
122380610 | F | LC | ETL.6070.TOWR | 40820556 | TABLEMTN | NORTH VALLEY | 2021-11-16 |  | ETL.6070 | ROUND MTN-TABLE MTN #2 | Anchor-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40820556 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-01-15 | Glass | Suspension |  |  |  |  | 1.0061e-07 | 602.4011 | 6.0608e-05
122410197 | E | LC | ETL.8210.POLE.WOOD | 40908572 | VICTOR | STOCKTON | 2021-11-23 |  | ETL.8210 | VALLEY SPRINGS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40908572 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2020-06-29 | Glass | Dead End |  |  |  |  | 0.034053 | 4583.1004 | 156.07
118776203 | F | LC | ETL.5090.TOWR | 40862874 | MOSSLNDG | DE ANZA | 2020-04-03 | 2021-09-28 | ETL.5090 | MONTA VISTA-COYOTE SW STA | Marker (i.e. signs)-Steel | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40862874 | 1970-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1970-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.31938 | 1196.4275
118982449 | E | LC | ETL.4220.POLE.WOOD | 40589653 | TABLEMTN | NORTH VALLEY | 2020-04-28 | 2020-05-18 | ETL.4220 | WOODLEAF-PALERMO | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40589653 | 1962-01-01 | Single Wood Pole | WB - Wishbone | 1962-01-01 | Non Ceramic | Suspension |  |  |  |  | 0.0085956 | 4924.2656
119004903 | F | LC | ETL.5930.TOWR | 40819377 | CONCORD | DIABLO | 2020-05-04 | 2021-04-12 | ETL.5930 | PARKWAY-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40819377 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.9358e-08 | 585.7291
119004903 | F | LC | ETL.5930.TOWR | 40819377 | CONCORD | DIABLO | 2020-05-04 | 2021-04-12 | ETL.5930 | PARKWAY-MORAGA | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40819377 | 1946-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1946-01-01 | Ceramic | Suspension |  |  |  |  | 6.9358e-08 | 585.7291
119019697 | E | LC | ETL.3750.SWIT | 40705186 | CONCORD | DIABLO | 2020-05-12 | 2021-03-17 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Switch | Out of Adjustment | [Repair, Completed] | Tier2 |  |  | COMP | [8 empty] | USCO | VACCUM BOTTLES (1 GAP) | Manual
119037020 | E | LC | ETL.1440.POLE.WDPS | 40866539 | SACTO | SIERRA | 2020-05-15 | 2020-07-29 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL | [11 empty] | 0.00036479
119040852 | E | LC | ETL.6770.POLE.WOOD | 40869653 | SACTO | SACRAMENTO | 2020-05-18 | 2020-07-09 | ETL.6770 | DRUM-SPAULDING | Splice-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40869653 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Non Ceramic | [5 empty] | 0.0013381 | 450.9556
119049921 | E | LC | ETL.6440.POLE.WOOD | 44191453 | TABLEMTN | NORTH VALLEY | 2020-05-14 | 2020-07-06 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44191453 |  | Single Wood Pole | T-1 - Tri Post | [7 empty] | 0.0027425 | 3439.8145
119079020 | E | LC | ETL.3750.TOWR | 44188758 | CONCORD | DIABLO | 2020-05-29 | 2020-06-30 | ETL.3750 | SOBRANTE-GRIZZLY-CLAREMONT #2 | Vegetation | Overgrown | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44188758 | 2008-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | [7 empty] | 2.1728e-06 | 445.731
119081112 | E | LC | ETL.8350.POLE.WOOD | 40803750 | VICTOR | STOCKTON | 2020-05-29 | 2021-06-07 | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119081294 | E | LC | ETL.6760.POLE.WOOD | 40756128 | SACTO | SIERRA | 2020-05-27 | 2021-03-09 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119082775 | E | LC | ETL.3960.TOWR | 40764796 | PISMOBCH | LOS PADRES | 2020-05-15 | 2021-01-12 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40764796 | 1941-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 1951-01-01 | Porcelain | Suspension |  |  |  |  | 5.8051e-09 | 3863.8943
119083129 | E | LC | ETL.8410.POLE.WOOD | 40684541 | LAKEVLLE | HUMBOLDT | 2020-05-15 | 2021-08-17 | ETL.8410 | ELK-GUALALA | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40684541 | 1960-01-01 | Single Wood Pole | 3WV-T - Three Way Vertical Tap | 1960-01-01 | Porcelain | Dead End |  |  |  |  | 0.15846 | 738.6521
119083258 | F | LC | ETL.6760.POLE.WOOD | 40767249 | SACTO | SIERRA | 2020-05-28 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 3 | Within Both | PEND | 40767249 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.040928 | 110.8706
119097660 | F | LC | ETL.5140.POLE.WDPS | 44553756 | SACTO | SACRAMENTO | 2020-05-19 | 2020-11-12 | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44553172 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.003437 | 474.6584
119102789 | B | LC | ETL.4620.INSL | 40578854 | PISMOBCH | LOS PADRES | 2020-05-27 | 2020-08-12 | ETL.4620 | DIABLO-MESA | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119103973 | E | LC | ETL.7300.POLE.WOOD | 40592171 | TABLEMTN |  | 2020-06-03 | 2021-03-17 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119107408 | E | LC | ETL.2540.INSL.CERA | 40842720 | MOSSLNDG | SAN JOSE | 2020-05-20 | 2021-01-20 | ETL.2540 | METCALF-GREEN VALLEY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44401528 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0057969
119107408 | E | LC | ETL.2540.INSL.CERA | 40842720 | MOSSLNDG | SAN JOSE | 2020-05-20 | 2021-01-20 | ETL.2540 | METCALF-GREEN VALLEY | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44401528 |  | 2-Pole Wood | 2PS - 2 Pole SUSP |  | Porcelain | Suspension |  |  |  |  | 0.0057969
119116311 | F | LC | ETL.7290.POLE.WOOD | 40600843 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40600843 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.011253 | 620.1252
119117713 | F | LC | ETL.6720.POLE.WOOD | 40601209 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.6720 | DESABLA-CENTERVILLE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40601209 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00080344 | 47.5251
119119845 | F | LC | ETL.6490.POLE.WOOD | 40696037 | SACTO | SIERRA | 2020-06-03 |  | ETL.6490 | COLGATE-GRASS VALLEY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40696037 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Post |  |  |  |  | 0.0082871 | 3829.6626
119127479 | F | LC | ETL.7300.POLE.WOOD | 40656954 | TABLEMTN |  | 2020-06-03 |  | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40656954 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0021941 | 1287.9495
119146774 | E | LC | ETL.1370.INSL.CERA | 40641796 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-26 | ETL.1370 | DIVIDE-CABRILLO #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119161491 | F | LC | ETL.7260.POLE.WOOD | 40771136 | TABLEMTN | NORTH VALLEY | 2020-06-09 |  | ETL.7260 | KESWICK-CASCADE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40771136 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 2.1349e-05 | 4087.3262
119162732 | E | LC | ETL.6760.INSL.NCER | 40797404 | SACTO | SACRAMENTO | 2020-06-13 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Damper-Wood | Missing | [Install] | Tier2 |  |  | PEND
119169385 | F | LC | ETL.6280.POLE.WOOD | 44414603 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 2 | Within Both | PEND | 44414603 | 2014-08-27 | Single Wood Pole | T-1 - Tri Post | 2014-08-27 | Polymer | Post |  |  |  |  | 4.6629e-06 | 569.452
119178161 | E | LC | ETL.6280.POLE.WOOD | 40585968 | TABLEMTN | NORTH VALLEY | 2020-06-17 |  | ETL.6280 | CARIBOU #2 | Splice-Wood | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | PEND | [12 empty] | 6742.9849
119187849 | E | LC | ETL.7300.POLE.WOOD | 40676511 | TABLEMTN |  | 2020-06-18 | 2021-01-21 | ETL.7300 | KILARC-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119196361 | F | LC | ETL.6470.POLE.WOOD | 40824272 | SACTO | SIERRA | 2020-06-22 | 2021-08-10 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40824272 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.03724 | 269.0426
119201058 | E | LC | ETL.6470.POLE.WOOD | 40824270 | SACTO | SIERRA | 2020-06-23 | 2021-08-02 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.11027 | 110.8481
119228443 | E | LC | ETL.7270.POLE.WOOD | 40909472 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2021-05-21 | ETL.7270 | KESWICK-TRINITY | Vegetation | Overgrown | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40909472 |  | Single Wood Pole | TPD - Tri Post Dead End Construction |  | Polymer | Unknown |  |  |  |  | 0.029325 | 553.9551
119230774 | F | LC | ETL.4050.POLE.WOOD | 40808567 | LAKEVLLE | SONOMA | 2020-06-29 | 2021-04-15 | ETL.4050 | UKIAH-HOPLAND-CLOVERDALE | Guy Wire Mark /Indic-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808567 | 1970-01-01 | Single Wood Pole | SUSP - Suspension (TWR) | 1970-01-01 | Ceramic | Post |  |  |  |  | 4.7704e-05 | 1410.8478
119238526 | E | LC | ETL.1110.POLE.STPS | 44424639 | EUREKA | NORTH VALLEY | 2020-06-30 | 2021-08-11 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Crossarm-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44424637 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 2.6692e-06 | 657.3666
119304808 | E | LC | ETL.8170.POLE.WDPS | 44565604 | EUREKA | HUMBOLDT | 2020-07-02 | 2021-06-11 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44564174 |  | 3-Pole Wood | 3P TRP D - 3 Pole Tramp Double Dead End | [7 empty] | 0.033588 | 1174.8506
119308127 | B | LC | ETL.7140.POLE.STPS | 44928848 | LAKEVLLE | NORTH BAY | 2020-07-03 | 2020-10-26 | ETL.7140 | IGNACIO-BOLINAS #1 | Other | Customer Issue | [Appointment Required, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44928271 | 2020-06-13 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0020446 | 4211.6216
119311445 | E | LC | ETL.1450.POLE.WDPS | 44559010 | SACTO | SACRAMENTO | 2020-07-02 | 2021-09-14 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP | [12 empty] | 31.7066
119321338 | F | LC | ETL.6290.POLE.NWOD | 44761240 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.6290 | CARIBOU-PLUMAS JCT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44761240 | 2019-05-11 | Light Duty Steel Pole | T2N | 2019-05-11 | Polymer | Post |  |  |  |  | 0.0023757 | 4811.106
119325309 | E | LC | ETL.7180.POLE.WDPS | 44360913 | LAKEVLLE | NORTH BAY | 2020-07-06 | 2021-04-06 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44360910 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 4.7751e-06 | 269.3192
119332667 | E | LC | ETL.7300.POLE.WOOD | 40759136 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-03-08 | ETL.7300 | KILARC-DESCHUTES | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40759136 |  | Single Wood Pole | T2N | 2021-03-05 | Polymer | Post |  |  |  |  | 0.0003352 | 1364.7333
119340297 | E | LC | ETL.7030.POLE.WOOD | 40617062 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-01 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40617062 |  | Single Wood Pole | T2N | 2021-05-24 | Polymer | Post |  |  |  |  | 0.0071527 | 159.5787
119340810 | E | LC | ETL.5390.TOWR | 40868865 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-07-09 | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40868865 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 0.00029188 | 1914.7993
119341194 | E | LC | ETL.8170.POLE.NWOD | 44366791 | EUREKA | HUMBOLDT | 2020-07-09 | 2021-09-16 | ETL.8170 | TRINITY-MAPLE CREEK | Hardware-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44366791 | 2013-11-26 | Light Duty Steel Pole | DDE - Double Dead End | 2013-11-26 | Polymer | Suspension |  |  |  |  | 0.00092166 | 300.6727
119341519 | E | LC | ETL.7030.POLE.WOOD | 40825604 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-17 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40825604 |  | Single Wood Pole | T2N | 2021-06-08 | Polymer | Post |  |  |  |  | 0.0096052 | 777.1585
119350867 | E | LC | ETL.1450.POLE.WDPS | 44552537 | SACTO | SACRAMENTO | 2020-07-09 | 2020-11-12 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | DLFL | 44551612 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0023954 | 174.093
119355375 | E | LC | ETL.5430.INSL.NCER | 44993986 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44993940 | 2020-06-27 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-06-27 | Glass | Suspension |  |  |  |  | 4.6271e-05
119355375 | E | LC | ETL.5430.INSL.NCER | 44993986 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.5430 | PIT #5-ROUND MTN #2 | Damper-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44993940 | 2020-06-27 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2020-06-27 | Glass | Suspension |  |  |  |  | 4.6271e-05
119357584 | F | LC | ETL.6280.POLE.WOOD | 40600650 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40600650 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Other |  |  |  |  | 4.8576e-05 | 4729.1396
119368761 | E | LC | ETL.7260.POLE.WOOD | 40759336 | TABLEMTN | NORTH VALLEY | 2020-07-14 |  | ETL.7260 | KESWICK-CASCADE | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40759336 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.00014403 | 3548.2349 | 0.51107
119494353 | F | LC | ETL.9200.POLE.WOOD | 40763589 | MIDWAY | KERN | 2020-07-22 |  | ETL.9200 | TAFT-CUYAMA #1 | Marker (i.e. signs)-Wood | Missing | [Install] |  | Non-HFTD | HFRA Addition | PEND | 40763589 | 1962-01-01 | Single Wood Pole | TPA - Tri Pin Arm | 1962-01-01 | Ceramic | Pin |  |  |  |  | 0.024326
119518788 | E | LC | ETL.8170.POLE.WOOD | 40649269 | EUREKA | HUMBOLDT | 2020-07-28 |  | ETL.8170 | TRINITY-MAPLE CREEK | Damper-Wood | Missing | [Install] | Tier2 |  |  | PEND
119529036 | F | LC | ETL.7490.POLE.WOOD | 40586842 | EUREKA | HUMBOLDT | 2020-07-30 | 2021-02-09 | ETL.7490 | MAPLE CREEK-HOOPA | Guy Wire Mark /Indic-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40586842 |  | Single Wood Pole | TP - Tri Pin | 2020-07-11 | Glass | Dead End |  |  |  |  | 0.22928 | 63.4442
119538600 | F | LC | ETL.8060.POLE.WOOD | 40828181 | SACTO | SACRAMENTO | 2020-07-31 | 2021-01-26 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 |  |  | DLFL
119560172 | F | LC | ETL.6300.POLE.WOOD | 40656505 | TABLEMTN |  | 2020-08-04 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40656505 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 0.0011724 | 664.3499
119575431 | E | LC | ETL.6880.INSL.NCER | 44286127 | LAKEVLLE |  | 2020-08-06 | 2021-03-31 | ETL.6880 | FULTON-CALISTOGA | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40912423 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.027642 | 1396.7732
119591063 | F | LC | ETL.8210.POLE.WOOD | 40908252 | VICTOR | STOCKTON | 2020-08-07 | 2021-09-09 | ETL.8210 | VALLEY SPRINGS #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40908252 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0018538 | 1091.9348
119592641 | F | LC | ETL.8350.POLE.STPS | 44765236 | VICTOR | STOCKTON | 2020-08-07 |  | ETL.8350 | WEST POINT-VALLEY SPRINGS | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
119608409 | E | LC | ETL.7490.POLE.WDPS | 44145859 | EUREKA | HUMBOLDT | 2020-08-13 | 2021-08-18 | ETL.7490 | MAPLE CREEK-HOOPA | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44145856 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 0.029639 | 142.4119
119615321 | B | LC | ETL.1112.POLE.NWOD | 44420224 | FRESNO | FRESNO | 2020-08-14 | 2020-12-14 | ETL.1112 | INDIAN FLAT-YOSEMITE | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44420224 |  | Lattice Steel Pole | SS1 - Susp. Steel Single. CIR |  | Glass | Suspension |  |  |  |  | 0.00059495 | 6664.3394
119619016 | B | LC | ETL.6310.POLE.WOOD | 44274797 | TABLEMTN | NORTH VALLEY | 2020-08-14 | 2020-12-23 | ETL.6310 | CASCADE-BENTON-DESCHUTES | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 44274797 | 2015-12-14 | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | Post |  |  |  |  | 1.1198e-05 | 4594.916
119619187 | B | LC | ETL.8650.TOWR | 40871014 | FRESNO | FRESNO | 2020-08-14 | 2020-12-11 | ETL.8650 | EXCHEQUER-INDIAN FLAT | Other | Customer Issue | [Access Issue, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40871014 | 1929-01-01 | LATTICE STEEL TOWER | DDE-A - Double Dead End Angle | 1929-01-01 | Porcelain | Double Dead End - Suspension |  |  |  |  | 0.0057929 | 6847.8872
119644097 | E | LC | ETL.6480.POLE.WOOD | 42549797 | SACTO | SACRAMENTO | 2020-08-20 | 2021-06-29 | ETL.6480 | COLGATE-CHALLENGE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 42549797 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Pin |  |  |  |  | 0.073699 | 300.6611
119644435 | B | LC | ETL.8365.POLE.WOOD | 40912500 | EUREKA | HUMBOLDT | 2020-08-20 | 2020-11-05 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40912500 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.08143
119649046 | E | LC | ETL.2660.TOWR | 40873254 | SACTO | SACRAMENTO | 2020-08-21 | 2021-02-08 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40873254 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2021-04-16 | Glass | Dead End |  |  |  |  | 1.6883e-08 | 2914.9978
119649046 | E | LC | ETL.2660.TOWR | 40873254 | SACTO | SACRAMENTO | 2020-08-21 | 2021-02-08 | ETL.2660 | MISSOURI FLAT-GOLD HILL #1 | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40873254 | 1967-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1967-01-01 | Ceramic | Dead End |  |  |  |  | 1.6883e-08 | 2914.9978
119653597 | E | LC | ETL.6870.POLE.WOOD | 40767468 | SACTO | SIERRA | 2020-07-13 | 2021-05-17 | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Rotten | [Replace, Completed] | Tier3 |  |  | COMP
119693203 | F | LC | ETL.1440.POLE.WDPS | 44837645 | SACTO | SACRAMENTO | 2020-08-25 | 2021-02-12 | ETL.1440 | DRUM-SUMMIT #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40819191 |  | 3-Pole Wood | 3P DV - 3 Pole Double Vertical | [7 empty] | 0.011379 | 31.7066
119694519 | E | LC | ETL.7270.POLE.WOOD | 40906486 | TABLEMTN | NORTH VALLEY | 2020-08-29 | 2021-08-19 | ETL.7270 | KESWICK-TRINITY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906486 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | 2021-08-15 | Glass | Dead End |  |  |  |  | 0.0025747 | 996.9431
119694923 | A | LC | ETL.6230.POLE.WDPS | 44561445 | MOSSLNDG | CENTRAL COAST | 2020-08-31 | 2020-10-13 | ETL.6230 | BURNS-LONE STAR #1 | Emergency | Fire | [Replace, Completed] | Tier3 |  |  | COMP
119721385 | E | LC | ETL.1400.POLE.WDPS | 44789686 | VICTOR | STOCKTON | 2020-07-29 | 2021-01-14 | ETL.1400 | DONNELLS-MI-WUK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40803723 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00033217 | 31.7081
119724988 | E | LC | ETL.1240.POLE.WDPS | 44386150 | TABLEMTN | NORTH VALLEY | 2020-08-06 |  | ETL.1240 | CASCADE-COTTONWOOD | Shield Wire / OPGW-Wood | No Good/Out of Stdrd | [Repair] |  | Tier 2 | Within Both | PEND | 44386149 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 8.387e-06 | 2791.1111 | 0.023409
119753189 | B | LC | ETL.4670.INSL | 40851651 | VICTOR | STOCKTON | 2020-09-11 | 2021-06-16 | ETL.4670 | ELECTRA-BELLOTA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119766532 | E | LC | ETL.1110.POLE.WDPS | 44424527 | TABLEMTN | HUMBOLDT | 2020-09-08 | 2021-04-07 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 44424525 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0012548 | 9423.3379
119769194 | E | LC | ETL.5440.INSL.CERA | 44150288 | TABLEMTN | NORTH VALLEY | 2020-08-14 |  | ETL.5440 | PIT #6 JCT-ROUND MTN | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | PEND | [5 empty] | Porcelain | Dead End
119781002 | E | LC | ETL.5630.INSL | 40896996 | TABLEMTN | NORTH VALLEY | 2020-09-11 | 2021-09-02 | ETL.5630 | ROCK CREEK-POE | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 |  |  | COMP
119786659 | E | LC | ETL.6490.INSL | 40697096 | SACTO | SACRAMENTO | 2020-09-15 | 2021-03-08 | ETL.6490 | COLGATE-GRASS VALLEY | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119789427 | F | LC | ETL.5140.POLE.STPS | 44690713 | SACTO | SIERRA | 2020-07-28 |  | ETL.5140 | MIDDLE FORK-GOLD HILL | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44141456 | 2017-10-29 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 1.836e-07 | 5398.7822
119852243 | B | LC | ETL.7030.POLE.WOOD | 40759003 | TABLEMTN | NORTH VALLEY | 2020-10-02 | 2020-10-21 | ETL.7030 | HAT CREEK #1-WESTWOOD | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119877771 | E | LC | ETL.5940.TOWR | 40593206 | PISMOBCH | LOS PADRES | 2020-10-09 | 2021-06-16 | ETL.5940 | DIABLO UNIT #1 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40593206 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-10-13 | Glass Silicone Coated | Suspension |  |  |  |  | 2.4976e-06 | 1061
119888116 | B | LC | ETL.7560.POLE.WOOD | 40824475 | SACTO | SACRAMENTO | 2020-10-10 | 2020-12-21 | ETL.7560 | WEIMAR #1 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119888661 | E | LC | ETL.9250.POLE.WOOD | 42574836 | MIDWAY | KERN | 2020-10-08 | 2020-10-19 | ETL.9250 | TEJON-LEBEC | Hardware-Wood | Missing | [Install] |  | Tier 2 | Within Both | DLFL | 42574836 |  | Single Wood Pole | BDE - Buck Dead End |  | Ceramic | Dead End |  |  |  |  | 0.013707 | 4976.3872
119893748 | F | LC | ETL.8170.POLE.WOOD | 40810474 | EUREKA | HUMBOLDT | 2020-10-07 | 2021-02-09 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 40810474 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.1269 | 5399.9375
119932763 | F | LC | ETL.7180.POLE.WOOD | 40808627 | LAKEVLLE | NORTH BAY | 2020-10-20 | 2021-04-19 | ETL.7180 | IGNACIO-BOLINAS #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40808627 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 6.3407e-05 | 333.1015
119973295 | E | LC | ETL.8580.TOWR | 40594396 | PISMOBCH | CENTRAL COAST | 2020-10-29 | 2021-03-02 | ETL.8580 | COALINGA #1-SAN MIGUEL | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] |  | Non-HFTD | HFRA Addition | COMP | 40594396 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-12-13 | Glass | Suspension |  |  |  |  | 1.5925e-08
120013940 | E | LC | ETL.6020.TOWR | 40601283 | TABLEMTN | NORTH VALLEY | 2020-11-12 | 2021-05-11 | ETL.6020 | MALIN-ROUND MTN #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40601283 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 3.1842e-06 | 2548.3853
120044278 | F | LC | ETL.6880.POLE.WOOD | 40912457 | LAKEVLLE | NORTH BAY | 2020-10-06 | 2021-04-14 | ETL.6880 | FULTON-CALISTOGA | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40912457 |  | Single Wood Pole | TPD - Tri Post Dead End Construction | [7 empty] | 0.0074699 | 4444.5719
120110854 | F | LC | ETL.8365.POLE.NWOD | 40912547 | EUREKA | HUMBOLDT | 2020-11-20 | 2021-07-19 | ETL.8365 | GARBERVILLE-LAYTONVILLE | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] |  | Non-HFTD | HFRA Addition | DLFL | 40912547 | 2010-01-01 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End |  | Polymer | Dead End |  |  |  |  | 0.00036579
120229692 | F | LC | ETL.1260.TOWR | 41146799 | CONCORD | EAST BAY | 2020-11-17 |  | ETL.1260 | CHRISTIE-SOBRANTE | Structure-Steel | Paint/Coating | [Other] | Tier2 | Tier 2 | Within Both | PEND | 41146799 | 1954-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1954-01-01 | Porcelain | Suspension |  |  |  |  | 1.7192e-07 | 857.9032 | 0.00014749
120423658 | E | LC | ETL.6520.POLE.WOOD | 40771347 | SACTO | SACRAMENTO | 2021-01-12 | 2021-06-08 | ETL.6520 | COLGATE-SMARTVILLE #2 | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 |  |  | COMP
120692245 | E | LC | ETL.1401.INSL.NCER | 40603525 | VICTOR | STOCKTON | 2021-03-25 |  | ETL.1401 | BEARDSLEY TAP | Insulator-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | PEND | 40579931 | 1956-01-01 | Single Wood Pole | DV-DE - Double Vertical Dead End | 1956-01-01 | Polymer | Dead End |  |  |  |  | 0.0021386 | 1497.7366 | 3.2031
120707534 | E | LC | ETL.3820.TOWR | 40809563 | VICTOR | STOCKTON | 2021-03-26 | 2021-04-08 | ETL.3820 | STANISLAUS-MANTECA #2 | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | DLFL | 40809563 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 4.0266e-07 | 268.9173
120712338 | E | LC | ETL.1350.INSL.CERA | 40827143 | TABLEMTN |  | 2021-03-30 | 2021-08-13 | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120716091 | E | LC | ETL.1730.POLE.WDPS | 44413413 | MOSSLNDG | CENTRAL COAST | 2021-03-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44413411 |  | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 2.4202e-05 | 0.065147 | 1.5767e-06
120717474 | B | LC | ETL.4000.INSL.CERA | 44253852 | VICTOR | STOCKTON | 2021-03-31 | 2021-05-18 | ETL.4000 | TESLA-SALADO-MANTECA | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44253831 | 2013-04-22 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 2013-04-22 | Porcelain | Suspension |  |  |  |  | 0.0012716 | 1254.9044
120719166 | F | LC | ETL.4316.POLE.STPS | 44561312 | TABLEMTN | NORTH VALLEY | 2021-03-31 |  | ETL.4316 | PARADISE-TABLE MTN | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44559134 | 2018-03-14 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00018886 | 2995.1147
120739584 | E | LC | ETL.2900.TOWR | 40650903 | MOSSLNDG | CENTRAL COAST | 2021-04-03 | 2021-07-15 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650903 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1963-01-01 | Porcelain | Suspension |  |  |  |  | 0.0006227 | 6518.4326
120739584 | E | LC | ETL.2900.TOWR | 40650903 | MOSSLNDG | CENTRAL COAST | 2021-04-03 | 2021-07-15 | ETL.2900 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40650903 | 1938-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2020-11-09 | Polymer | Suspension |  |  |  |  | 0.0006227 | 6518.4326
120743196 | E | LC | ETL.3700.POLE.WOOD | 40659144 | PISMOBCH | LOS PADRES | 2021-04-01 |  | ETL.3700 | SISQUOC-SANTA YNEZ SW STA | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40659144 | 1956-01-01 | Single Wood Pole | TPD - Tri Post Dead End Construction | 1989-01-01 | Polymer | Unknown |  |  |  |  | 0.00046048 | 3706.2773 | 1.7067
120748361 | F | LC | ETL.6890.POLE.WOOD | 40580496 | LAKEVLLE | SONOMA | 2021-04-06 | 2021-06-02 | ETL.6890 | FULTON-HOPLAND | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 |  |  | DLFL
120748475 | B | LC | ETL.7140.POLE.WOOD | 40809046 | LAKEVLLE | SONOMA | 2021-04-06 | 2021-06-23 | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809046 |  | Single Wood Pole | FIG4DDE - Figure 4 Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.017728 | 728.338
120764302 | E | LC | ETL.1810.POLE.STPS | 44324153 | EUREKA | HUMBOLDT | 2021-04-08 |  | ETL.1810 | HUMBOLDT-BRIDGEVILLE | Crossarm-Wood | No Good/Out of Stdrd | [Replace] |  | Non-HFTD | HFRA Addition | PEND | 44324152 |  | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 1.0846e-08
120786385 | E | LC | ETL.5510.TOWR | 40818815 | CONCORD | DIABLO | 2021-04-10 |  | ETL.5510 | PITTSBURG-TESLA #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40818815 | 1953-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1953-01-01 | Ceramic | Dead End |  |  |  |  | 2.4597e-08 | 4750.3203 | 0.00011684
120787970 | B | LC | ETL.8250.POLE.WOOD | 44399683 | VICTOR | STOCKTON | 2021-04-10 | 2021-07-27 | ETL.8250 | CLAY-MARTEL | Damper-Wood | Missing | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44399683 | 2015-10-09 | Single Wood Pole | T-1 - Tri Post | 2015-10-09 | Polymer | Post |  |  |  |  | 1.6913e-05 | 1318.29
120806316 | E | LC | ETL.7270.POLE.WDPS | 44421137 | TABLEMTN | NORTH VALLEY | 2021-04-13 | 2021-06-09 | ETL.7270 | KESWICK-TRINITY | Anchor-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL | [12 empty] | 3104.2327
120811869 | E | LC | ETL.5310.INSL | 40680569 | PISMOBCH | LOS PADRES | 2021-04-07 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40651686 | 1960-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 5.5731e-07 | 2345.0251 | 0.0013069
120811888 | F | LC | ETL.9100.POLE.WOOD | 44191203 | PISMOBCH | LOS PADRES | 2020-06-11 | 2021-08-27 | ETL.9100 | SAN LUIS OBISPO-SANTA MARIA * | Structure-Wood | Idle | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 44191203 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Porcelain | [5 empty] | 5.9246e-06 | 1660.8882
120813257 | B | LC | ETL.2910.INSL.CERA | 40713674 | MOSSLNDG | CENTRAL COAST | 2021-04-13 | 2021-05-06 | ETL.2910 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662240 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1991-01-01 | Porcelain | Dead End |  |  |  |  | 0.0045937 | 4730.686
120813257 | B | LC | ETL.2910.INSL.CERA | 40713674 | MOSSLNDG | CENTRAL COAST | 2021-04-13 | 2021-05-06 | ETL.2910 | CRAZY HORSE CANYON-SALINAS-SOLEDAD #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40662240 | 1938-01-01 | LATTICE STEEL TOWER | DC-DDE - Double Circuit Double Dead End | 1991-01-01 | Polymer | Dead End |  |  |  |  | 0.0045937 | 4730.686
120828315 | E | LC | ETL.5310.INSL | 40620898 | PISMOBCH | LOS PADRES | 2021-04-16 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40594717 | 1960-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 1.6948e-06 | 269.2083 | 0.00045627
120833012 | B | LC | ETL.3500.INSL | 40676261 | VICTOR | STOCKTON | 2021-04-16 | 2021-07-14 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40648381 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 0.00038986 | 3244.1206
120850288 | E | LC | ETL.3740.INSL.CERA | 40792424 | CONCORD | EAST BAY | 2021-04-20 |  | ETL.3740 | SOBRANTE-GRIZZLY-CLAREMONT #1 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40761864 | 1922-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1991-01-01 | Ceramic | Suspension |  |  |  |  | 0.038472 | 445.731 | 17.1483
120866599 | A | LC | ETL.1710.TOWR | 40816121 | MOSSLNDG | CENTRAL COAST | 2021-04-07 | 2021-04-27 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Emergency-Steel | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40816121 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-04-23 | Glass | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147
120866599 | A | LC | ETL.1710.TOWR | 40816121 | MOSSLNDG | CENTRAL COAST | 2021-04-07 | 2021-04-27 | ETL.1710 | GREEN VALLEY-CAMP EVERS | Emergency-Steel | Other | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40816121 | 1970-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1971-01-01 | Ceramic | Double Dead End |  |  |  |  | 6.9828e-08 | 0.065147
120866698 | E | LC | ETL.3830.TOWR | 40856450 | VICTOR | STOCKTON | 2021-04-06 |  | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | Hardware-Tower | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40856450 | 1910-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2020-06-12 | Glass | Suspension |  |  |  |  | 4.2589e-07 | 4716.1616 | 0.0020086
120873804 | E | LC | ETL.8990.POLE.NWOD | 40806444 | FRESNO | FRESNO | 2021-04-23 |  | ETL.8990 | MERCED FALLS-EXCHEQUER | Raptor Guard-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40806444 | 1929-01-01 | Lattice Steel Pole | SS2 - Susp. Steel Double CIR. | 2020-11-08 | Glass | Suspension |  |  |  |  | 1.8682e-07 | 49.8123 | 9.3061e-06
120874816 | E | LC | ETL.1250.INSL | 40626066 | FRESNO | FRESNO | 2021-04-23 |  | ETL.1250 | CHOWCHILLA-KERCKHOFF | Insulator-Steel | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40584905 |  | Light Duty Steel Pole | DDE - Double Dead End |  | Ceramic | Double Dead End |  |  |  |  | 8.6079e-06 | 6647.8232 | 0.057223
120874993 | E | LC | ETL.8060.POLE.WOOD | 40810181 | SACTO | SACRAMENTO | 2021-04-23 | 2021-08-09 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40810181 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.058307 | 174.093
120876486 | E | LC | ETL.4040.POLE.NWOD | 45006471 | TABLEMTN | NORTH VALLEY | 2021-04-23 |  | ETL.4040 | TRINITY-COTTONWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 45006471 | 2020-09-18 | Light Duty Steel Pole | 3P DV - 3 Pole Double Vertical | 2020-09-18 | Ceramic | Dead End - Suspension |  |  |  |  | 0.00010391 | 79.1724 | 0.0082271
120889794 | B | LC | ETL.5390.TOWR | 40592489 | TABLEMTN | NORTH VALLEY | 2021-04-27 | 2021-06-01 | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40592489 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 6.6959e-05 | 189.8608
120899893 | E | LC | ETL.3820.TOWR | 40642810 | VICTOR | STOCKTON | 2021-04-29 |  | ETL.3820 | STANISLAUS-MANTECA #2 | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40642810 | 1910-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1989-01-01 | Glass | Suspension |  |  |  |  | 5.6698e-06 | 300.5596 | 0.0017041
120914682 | E | LC | ETL.5930.INSL | 40890771 | LAKEVLLE |  | 2021-05-01 |  | ETL.5930 | PARKWAY-MORAGA | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40867767 | 1960-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1960-01-01 | Ceramic | Double Dead End |  |  |  |  | 5.8494e-09 | 838.481 | 4.9046e-06
120951453 | F | LC | ETL.7060.POLE.WOOD | 42564682 | METCALF | SAN JOSE | 2021-05-07 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | HFRA Removal | PEND | 42564682 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | Unknown |  |  |  |  | 1.3385e-05 | 498.9879
121320023 | B | LC | ETL.1430.INSL.CERA | 44308041 | SACTO | SACRAMENTO | 2021-05-12 | 2021-07-06 | ETL.1430 | DRUM-RIO OSO #2 | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 |  |  | COMP
121331774 | E | LC | ETL.1900.INSL.CERA | 40620516 | FRESNO | FRESNO | 2021-04-16 |  | ETL.1900 | KERCKHOFF-CLOVIS-SANGER #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 |  |  | PEND
121338530 | F | LC | ETL.9250.POLE.NWOD | 42574834 | MIDWAY | KERN | 2021-04-26 | 2021-05-19 | ETL.9250 | TEJON-LEBEC | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 42574834 |  | Light Duty Steel Pole | Unknown |  | Ceramic | [5 empty] | 0.0027625 | 6083.5864
121363630 | E | LC | ETL.1820.POLE.STPS | 44395439 | EUREKA | HUMBOLDT | 2021-05-19 |  | ETL.1820 | HUMBOLDT-TRINITY | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44395438 | 2020-03-04 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.009475 | 6300.0015 | 59.6926
121363929 | E | LC | ETL.5463.TOWR | 40818465 | CONCORD | MISSION | 2021-04-29 | 2021-09-27 | ETL.5463 | PITTSBURG-SAN MATEO | Shield Wire / OPGW-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40818465 | 1964-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1964-01-01 | Ceramic | Suspension |  |  |  |  | 9.7404e-08 | 3154.5959
121367558 | E | LC | ETL.7290.POLE.WOOD | 40817418 | TABLEMTN | NORTH VALLEY | 2021-05-20 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40817418 |  | Single Wood Pole | 3HPD - 3 Horizontal Post Delta |  | Ceramic | Unknown |  |  |  |  | 0.063318 | 1158.6814 | 73.365
121370797 | F | LC | ETL.6950.POLE.WOOD | 40824111 | SACTO | SIERRA | 2021-05-01 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40824111 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.0024839 | 4022.4453
121377008 | E | LC | ETL.6470.POLE.WOOD | 40818478 | SACTO | SIERRA | 2021-05-07 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40818478 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.044051 | 2230.4749 | 98.2539
121384761 | E | LC | ETL.1400.POLE.STPS | 45087053 | VICTOR | YOSEMITE | 2021-05-12 |  | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40803709 |  | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 6.8486e-05 | 5031.312 | 0.34457
121384934 | F | LC | ETL.7212.POLE.WOOD | 40665340 | METCALF | PENINSULA | 2021-05-12 |  | ETL.7212 | SNEATH LANE-HALF MOON BAY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40665340 |  | Single Wood Pole | WB - Wishbone |  | Porcelain | [5 empty] | 0.45551 | 744.3112
121385530 | F | LC | ETL.6320.POLE.NWOD | 44384784 | TABLEMTN | NORTH VALLEY | 2021-05-08 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44384784 | 2019-03-12 | Light Duty Steel Pole | T-1 - Tri Post | 2019-03-12 | Polymer | Post |  |  |  |  | 1.2061e-06 | 2562.7057
121388215 | F | LC | ETL.6470.POLE.WOOD | 44398580 | SACTO | SIERRA | 2021-05-07 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44398580 | 2017-05-18 | Single Wood Pole | T2N | 2017-05-18 | Polymer | Post |  |  |  |  | 0.033493 | 1621.6812
121390051 | F | LC | ETL.6470.POLE.WOOD | 40874816 | SACTO | SIERRA | 2021-05-14 |  | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40874816 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.015863 | 300.6841
121395797 | E | LC | ETL.6660.POLE.NWOD | 44358495 | TABLEMTN | NORTH VALLEY | 2021-05-18 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 44358495 | 2016-10-23 | Light Duty Steel Pole | T-1 - Tri Post | 2016-10-23 | Polymer | Post |  |  |  |  | 5.8503e-09 | 3977.8811 | 2.3272e-05
121401024 | F | LC | ETL.1420.POLE.STPS | 44337068 | SACTO | SACRAMENTO | 2021-05-26 | 2021-07-30 | ETL.1420 | DRUM-RIO OSO #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 44337067 | 2016-08-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 4.5637e-07 | 1328.8579
121402496 | E | LC | ETL.6660.POLE.WOOD | 44357578 | TABLEMTN | NORTH VALLEY | 2021-05-17 |  | ETL.6660 | COTTONWOOD-RED BLUFF | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44357578 | 2017-03-16 | Single Wood Pole | T-1 - Tri Post | 2017-03-16 | Polymer | Post |  |  |  |  | 0.00018706 | 4595.2197 | 0.85959
121405075 | E | LC | ETL.6720.POLE.NWOD | 44324210 | TABLEMTN | NORTH VALLEY | 2021-05-19 |  | ETL.6720 | DESABLA-CENTERVILLE | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44324210 | 2015-11-03 | Fiberglass | T-1 - Tri Post | 2015-11-03 | Polymer | Post |  |  |  |  | 4.4803e-05 | 63.3704 | 0.0028392
121405621 | F | LC | ETL.6640.POLE.WOOD | 40601189 | TABLEMTN | NORTH VALLEY | 2021-05-22 |  | ETL.6640 | COTTONWOOD-BENTON #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40601189 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0016647 | 933.8852
121407893 | E | LC | ETL.8405.INSL.NCER | 40883804 | SACTO | SACRAMENTO | 2021-05-20 |  | ETL.8405 | MIDDLE FORK #1 | Insulator-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40861919 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.023855 | 1075.8865 | 25.665
121420294 | E | LC | ETL.1400.POLE.STPS | 44381771 | VICTOR | YOSEMITE | 2021-05-26 |  | ETL.1400 | DONNELLS-MI-WUK | Hardware-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44381769 | 2017-08-17 | 2-Pole Non Wood | DE - Dead End | [7 empty] | 0.00011602 | 158.2923 | 0.018365
121422510 | E | LC | ETL.7380.POLE.WOOD | 40668275 | MOSSLNDG | CENTRAL COAST | 2021-05-27 |  | ETL.7380 | LAURELES-OTTER | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40668275 |  | Single Wood Pole | FIG4DDE - Figure 4 Double Dead End |  | Ceramic | [5 empty] | 0.46614 | 31.6978 | 14.7755
121424989 | E | LC | ETL.8290.POLE.WOOD | 40825144 | TABLEMTN | NORTH VALLEY | 2021-05-27 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40825144 |  | Single Wood Pole | T2N | 2016-09-30 | Polymer | Post |  |  |  |  | 0.0070077 | 762.9542 | 5.3465
121429875 | E | LC | ETL.7575.INSL.NCER | 40850600 | METCALF | SAN FRANCISCO | 2021-05-27 |  | ETL.7575 | SNEATH LANE-PACIFICA | Insulator-Wood | No Good/Out of Stdrd | [Replace] | Tier3 | Tier 3 | Within Both | PEND | 40823356 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.14492 | 506.7344 | 73.4357
121437658 | B | LC | ETL.5140.INSL | 40890702 | SACTO | SIERRA | 2021-05-28 | 2021-08-12 | ETL.5140 | MIDDLE FORK-GOLD HILL | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40867711 | 1965-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1965-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.1571e-07 | 1233.9089
121468016 | E | LC | ETL.6020.TOWR | 40858259 | TABLEMTN | NORTH VALLEY | 2021-06-03 |  | ETL.6020 | MALIN-ROUND MTN #2 | Hardware-Tower | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40858259 | 1965-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1965-01-01 | Ceramic | Suspension |  |  |  |  | 1.2624e-08 | 71.2617 | 8.9961e-07
121492837 | F | LC | ETL.5630.TOWR | 40751832 | TABLEMTN | NORTH VALLEY | 2021-06-02 |  | ETL.5630 | ROCK CREEK-POE | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40751832 | 1958-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1958-01-01 | Ceramic | Other |  |  |  |  | 7.4454e-05 | 6537.3096
121516465 | F | LC | ETL.1680.POLE.WDPS | 44298668 | LAKEVLLE |  | 2021-06-04 | 2021-09-10 | ETL.1680 | GEYSERS #7-EAGLE ROCK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 44298666 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0018828 | 2708.3875
121521692 | F | LC | ETL.6330.POLE.NWOD | 44166126 | TABLEMTN | NORTH VALLEY | 2021-06-04 | 2021-06-28 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44166126 | 2014-07-28 | Light Duty Steel Pole | T-1 - Tri Post |  | Non Ceramic | Post |  |  |  |  | 1.2538e-06 | 142.5082
121525607 | E | LC | ETL.5390.TOWR | 40817600 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40817600 | 1924-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-01-13 | Glass | Dead End |  |  |  |  | 0.0042706 | 395.846 | 1.6905
121526517 | B | LC | ETL.5390.TOWR | 40758862 | TABLEMTN | NORTH VALLEY | 2021-06-10 | 2021-09-04 | ETL.5390 | PIT #1-COTTONWOOD | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40758862 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.4732e-08 | 4563.5034
121540258 | E | LC | ETL.6890.POLE.WOOD | 40592661 | LAKEVLLE | SONOMA | 2021-06-10 |  | ETL.6890 | FULTON-HOPLAND | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40592661 | 1990-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Ceramic | Suspension |  |  |  |  | 0.0012336 | 2488.3916 | 3.0697
121542040 | E | LC | ETL.6760.POLE.WOOD | 40591320 | SACTO | SIERRA | 2021-06-10 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40591320 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.037324 | 253.1613 | 9.449
121542662 | E | LC | ETL.5390.TOWR | 40595053 | TABLEMTN | NORTH VALLEY | 2021-06-11 |  | ETL.5390 | PIT #1-COTTONWOOD | Foundation/Concrete-Tower | Earth Covered Tower | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40595053 | 1924-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 6.0303e-07 | 3248.3611 | 0.0019588
121543926 | F | LC | ETL.1820.POLE.NWOD | 44976950 | EUREKA | HUMBOLDT | 2021-06-12 |  | ETL.1820 | HUMBOLDT-TRINITY | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44976950 | 2020-03-11 | Light Duty Steel Pole | SV1 - Angle 0-30 Degrees | 2020-03-11 | Glass | Suspension |  |  |  |  | 0.00078571 | 4131.4126
121544178 | E | LC | ETL.1070.POLE.WOOD | 40804187 | VICTOR | YOSEMITE | 2021-06-12 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40804187 | 1957-01-01 | Single Wood Pole | T-1 - Tri Post | 1957-01-01 | Polymer | Dead End |  |  |  |  | 0.00026725 | 1347.2231 | 0.36005
121546499 | E | LC | ETL.7140.POLE.WDPS | 44942600 | LAKEVLLE | NORTH BAY | 2021-06-15 |  | ETL.7140 | IGNACIO-BOLINAS #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 41111795 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.023234 | 1711.6168 | 39.7673
121550780 | F | LC | ETL.5390.TOWR | 40758870 | TABLEMTN | NORTH VALLEY | 2021-06-13 |  | ETL.5390 | PIT #1-COTTONWOOD | Structure-Steel | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40758870 | 1953-01-01 | LATTICE STEEL TOWER | SS1 - Susp. Steel Single. CIR | 2021-01-13 | Glass | Suspension |  |  |  |  | 2.4628e-08 | 4997.1901
121563272 | B | LC | ETL.1350.INSL.NCER | 44993124 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-07-22 | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993113 | 2020-06-04 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-06-04 | Glass | Dead End |  |  |  |  | 3.5698e-05
121563272 | B | LC | ETL.1350.INSL.NCER | 44993124 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-07-22 | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993113 | 2020-06-04 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-06-04 | Glass | Dead End |  |  |  |  | 3.5698e-05
121563272 | B | LC | ETL.1350.INSL.NCER | 44993124 | TABLEMTN | NORTH VALLEY | 2021-06-18 | 2021-07-22 | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44993113 | 2020-06-04 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | 2020-06-04 | Glass | Dead End |  |  |  |  | 3.5698e-05
121573080 | E | LC | ETL.5220.TOWR | 40660531 | METCALF | PENINSULA | 2021-06-16 |  | ETL.5220 | MONTA VISTA-JEFFERSON #1 | Hardware-Tower | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 40660531 | 1963-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1963-01-01 | Ceramic | Dead End |  |  |  |  | 0.041074 | 1709.0729 | 70.1978
121606221 | F | LC | ETL.1183.TOWR | 45098585 | LAKEVLLE | SONOMA | 2021-06-26 | 2021-08-02 | ETL.1183 | CALPINE-WEST FORD FLAT | Marker (i.e. signs)-Steel | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45098585 |  | LATTICE STEEL TOWER | Unknown |  | Unknown | Unknown | [5 empty] | 190.4918
121606872 | F | LC | ETL.1183.POLE.NWOD | 45098578 | LAKEVLLE | SONOMA | 2021-06-26 | 2021-09-10 | ETL.1183 | CALPINE-WEST FORD FLAT | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 45098578 |  | Light Duty Steel Pole | Unknown |  | Unknown | Unknown | [5 empty] | 253.9757
121609831 | E | LC | ETL.5310.INSL | 40845519 | PISMOBCH | LOS PADRES | 2021-06-22 |  | ETL.5310 | MORRO BAY-SOLAR SW STA #2 | Insulator-Steel | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40818911 | 1960-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 5.8123e-06 | 4259.6572 | 0.024759
121621222 | E | LC | ETL.7130.POLE.WDPS | 44315162 | EUREKA | HUMBOLDT | 2021-06-27 |  | ETL.7130 | HUMBOLDT-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44315160 | 2013-10-26 | 3-Pole Wood | SVDE - Single Vertical Dead End | [7 empty] | 0.0095661 | 0.065148 | 0.00062321
121634230 | E | LC | ETL.5630.TOWR | 40656120 | TABLEMTN | NORTH VALLEY | 2021-06-24 |  | ETL.5630 | ROCK CREEK-POE | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40656120 |  | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.0001539 | 1835.0725 | 0.28241
121648536 | E | LC | ETL.6760.POLE.NWOD | 44261352 | SACTO | SIERRA | 2021-06-26 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44261352 | 2016-05-04 | Light Duty Steel Pole | TPAD - Tri Pin Arm Dead End | 2016-05-04 | Porcelain | Post |  |  |  |  | 0.17068 | 949.3081 | 162.0323
121659625 | E | LC | ETL.1730.INSL.CERA | 40901316 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 44413370 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Double Dead End - Suspension |  |  |  |  | 4.1411e-05
121659625 | E | LC | ETL.1730.INSL.CERA | 40901316 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 44413370 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Double Dead End - Suspension |  |  |  |  | 4.1411e-05
121659625 | E | LC | ETL.1730.INSL.CERA | 40901316 | MOSSLNDG | CENTRAL COAST | 2021-06-30 |  | ETL.1730 | GREEN VALLEY-PAUL SWEET | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | PEND | 44413370 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Porcelain | Double Dead End - Suspension |  |  |  |  | 4.1411e-05
121660764 | F | LC | ETL.7060.POLE.WOOD | 40767965 | METCALF | PENINSULA | 2021-06-27 |  | ETL.7060 | HILLSDALE JCT-HALF MOON BAY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40767965 |  | Single Wood Pole | SS1 - Susp. Steel Single. CIR |  | Polymer | [5 empty] | 0.00032152 | 0.066432
121662034 | E | LC | ETL.7550.POLE.WOOD | 40769235 | LAKEVLLE | HUMBOLDT | 2021-07-01 |  | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 40769235 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 7.405e-05 | 1202.3098 | 0.089031
121675115 | F | LC | ETL.7630.POLE.WOOD | 40750312 | LAKEVLLE | SONOMA | 2021-07-05 | 2021-08-12 | ETL.7630 | MONTE RIO-FULTON | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40750312 | 1952-01-01 | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.012696 | 47.5251
121717916 | F | LC | ETL.1450.POLE.NWOD | 45095744 | SACTO | SIERRA | 2021-07-08 | 2021-10-11 | ETL.1450 | DRUM-SUMMIT #2 | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | DLFL | 45095744 |  | Light Duty Steel Pole | DV-DE - Double Vertical Dead End |  | Ceramic | Dead End |  |  |  |  | 1.3749e-06 | 47.5273
121741432 | F | LC | ETL.6852.POLE.NWOD | 40740641 | LAKEVLLE | HUMBOLDT | 2021-07-14 |  | ETL.6852 | CLEAR LAKE-KONOCTI | Marker (i.e. signs)-Steel | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40740641 |  | Tubular Steel Pole | DV-DE - Double Vertical Dead End |  | Polymer | Dead End |  |  |  |  | 0.0047796 | 4447.7559
121744485 | E | LC | ETL.1252.POLE.STPS | 44319949 | FRESNO | YOSEMITE | 2021-07-14 |  | ETL.1252 | OAKHURST TAP | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44319946 |  | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 3.9491e-05 | 3515.5505 | 0.13883
121748455 | E | LC | ETL.6650.POLE.WDPS | 44386692 | TABLEMTN | NORTH VALLEY | 2021-07-13 |  | ETL.6650 | COTTONWOOD-BENTON #2 | Crossarm-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44386691 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.010253 | 16.2334 | 0.16644
121749871 | E | LC | ETL.7390.POLE.WOOD | 40584776 | LAKEVLLE | HUMBOLDT | 2021-07-17 |  | ETL.7390 | LAYTONVILLE-COVELO | Hardware-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40584776 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.33904 | 570.5123 | 193.4285
121750661 | E | LC | ETL.9200.POLE.WDPS | 44976206 | MIDWAY | KERN | 2021-07-15 |  | ETL.9200 | TAFT-CUYAMA #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | PEND | 42696685 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.014778
121755937 | F | LC | ETL.1440.POLE.NWOD | 45109924 | SACTO | SIERRA | 2021-07-19 |  | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 45109924 | 2020-08-10 | Light Duty Steel Pole | DDE - Double Dead End | 2020-08-10 | Glass | Dead End | [5 empty] | 0.065152
121763467 | E | LC | ETL.5970.TOWR | 40587681 | PISMOBCH | LOS PADRES | 2021-07-19 |  | ETL.5970 | DIABLO-MIDWAY #2 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 40587681 | 1972-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2016-09-28 | Ceramic | Suspension |  |  |  |  | 4.1662e-07 | 110.769 | 4.6149e-05
121781811 | F | LC | ETL.2390.POLE.WDPS | 44391047 | VICTOR | STOCKTON | 2021-07-20 |  | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44391046 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.001057 | 3292.7512 | 3.4803
121807309 | B | LC | ETL.6290.POLE.WDPS | 44399518 | TABLEMTN | NORTH VALLEY | 2021-07-27 | 2021-10-27 | ETL.6290 | CARIBOU-PLUMAS JCT | Emergency | Fire | [Replace] | Tier2 | Tier 2 | Within Both | DLFL | 44399516 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.33136 | 1043.9412
121811020 | B | LC | ETL.1350.INSL | 40827127 | TABLEMTN |  | 2021-07-28 | 2021-08-06 | ETL.1350 | CRAG VIEW-CASCADE | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40803388 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Dead End |  |  |  |  | 0.0001627 | 142.6993
121816460 | F | LC | ETL.1070.POLE.WOOD | 40688459 | VICTOR | STOCKTON | 2021-07-28 |  | ETL.1070 | BELLOTA-RIVERBANK-MELONES SW STA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40688459 | 1998-01-01 | Single Wood Pole | TH - TriAngle Post 70 | 1998-01-01 | Polymer | Post |  |  |  |  | 8.4127e-05 | 3105.197
121822281 | E | LC | ETL.6760.POLE.WOOD | 44178366 | SACTO | SIERRA | 2021-07-29 |  | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Vegetation | Overgrown | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44178366 | 2015-03-25 | Single Wood Pole | TPAD - Tri Pin Arm Dead End | 2015-03-25 | Porcelain | Dead End |  |  |  |  | 0.033774 | 1.647 | 0.055626
121949870 | E | LC | ETL.8170.POLE.WOOD | 40810474 | EUREKA | HUMBOLDT | 2021-08-24 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40810474 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.1269 | 5399.9375 | 685.2766
122279717 | E | LC | ETL.2390.POLE.WDPS | 44390960 | VICTOR | STOCKTON | 2021-10-31 |  | ETL.2390 | MELONES-CURTIS | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] | Tier2 | Tier 2 | Within Both | PEND | 44390959 |  | 2-Pole Wood | FSS - Field Switch Structure | [7 empty] | 2.2526e-05 | 3095.6857 | 0.069734
118602596 | E | LC | ETL.7270.POLE.WOOD | 40827889 | TABLEMTN | NORTH VALLEY | 2020-03-04 | 2021-11-29 | ETL.7270 | KESWICK-TRINITY | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed, Completed, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827889 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Porcelain | [5 empty] | 0.050334 | 320.8212 | 16.1482
118764524 | E | LC | ETL.5260.INSL.NCER | 44895221 | PISMOBCH | LOS PADRES | 2020-04-01 | 2020-10-07 | ETL.5260 | MORRO BAY-DIABLO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587023 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End |  | Ceramic | Dead End |  |  |  |  | 2.2805e-08 | 1061
118764524 | E | LC | ETL.5260.INSL.NCER | 44895221 | PISMOBCH | LOS PADRES | 2020-04-01 | 2020-10-07 | ETL.5260 | MORRO BAY-DIABLO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40587023 | 1969-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2020-02-26 | Glass | Dead End |  |  |  |  | 2.2805e-08 | 1061
118775787 | E | LC | ETL.4590.TOWR | 40910137 | TABLEMTN | NORTH VALLEY | 2020-04-03 | 2021-07-27 | ETL.4590 | CRESTA-RIO OSO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910137 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-08-31 | Glass | Suspension |  |  |  |  | 4.1064e-05 | 537.9698
118917206 | F | LC | ETL.7490.POLE.WOOD | 40826079 | EUREKA | HUMBOLDT | 2020-04-14 | 2020-05-22 | ETL.7490 | MAPLE CREEK-HOOPA | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40826079 | 2011-12-30 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.33546
118917206 | F | LC | ETL.7490.POLE.WOOD | 40826079 | EUREKA | HUMBOLDT | 2020-04-14 | 2020-05-22 | ETL.7490 | MAPLE CREEK-HOOPA | Road | Brush Fuel | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40826079 | 2011-12-30 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End |  | Ceramic | Dead End |  |  |  |  | 0.33546
118943410 | E | LC | ETL.7510.POLE.WOOD | 40875537 | LAKEVLLE | SONOMA | 2020-04-23 | 2020-07-03 | ETL.7510 | MENDOCINO-HARTLEY | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40875537 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 7.5832e-05 | 2705.5996
118953120 | E | LC | ETL.1400.POLE.WOOD | 40579920 | VICTOR | YOSEMITE | 2020-04-23 | 2021-05-12 | ETL.1400 | DONNELLS-MI-WUK | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
118960543 | E | LC | ETL.7510.POLE.WOOD | 40699162 | LAKEVLLE | SONOMA | 2020-04-29 | 2020-05-18 | ETL.7510 | MENDOCINO-HARTLEY | Vegetation | Overgrown | [Trim, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40699162 |  | Single Wood Pole | T-1 - Tri Post | 2020-04-13 | Polymer | Post |  |  |  |  | 3.2145e-06 | 3828.5723
118975663 | E | LC | ETL.6980.POLE.WOOD | 40587401 | LAKEVLLE | HUMBOLDT | 2020-04-30 | 2021-01-14 | ETL.6980 | FORT ROSS-GUALALA | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier2 |  |  | DLFL
119041160 | F | LC | ETL.2060.POLE.WOOD | 40808471 | LAKEVLLE | HUMBOLDT | 2020-05-13 |  | ETL.2060 | FORT BRAGG-ELK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40808471 | 1961-01-01 | Single Wood Pole | SS1 - Susp. Steel Single. CIR | 1961-01-01 | Ceramic | Suspension |  |  |  |  | 0.11743 | 0.065148
119082164 | B | LC | ETL.5290.INSL | 40614925 | PISMOBCH | LOS PADRES | 2020-05-26 | 2020-08-12 | ETL.5290 | MORRO BAY-MESA | Insulator-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119083506 | F | LC | ETL.6950.POLE.WOOD | 40876097 | SACTO | SIERRA | 2020-05-28 |  | ETL.6950 | GOLD HILL #1 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 |  |  | PEND
119088029 | E | LC | ETL.6320.POLE.NWOD | 44416322 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Splice-Wood | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | PEND | 44416322 | 2018-10-09 | Light Duty Steel Pole | 3HPD - 3 Horizontal Post Delta | 2018-10-09 | Polymer | Post |  |  |  |  | 1.4604e-06 | 1997.9036 | 0.0029177
119097576 | E | LC | ETL.5650.TOWR | 40813496 | TABLEMTN | NORTH VALLEY | 2020-05-19 | 2021-03-03 | ETL.5650 | ROUND MTN-COTTONWOOD #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40813496 | 1924-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2021-02-15 | Glass | Suspension |  |  |  |  | 3.8938e-06 | 2329.9167
119102699 | F | LC | ETL.6950.POLE.NWOD | 44174902 | SACTO | SIERRA | 2020-05-12 |  | ETL.6950 | GOLD HILL #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44174902 |  | Light Duty Steel Pole | DDE - Double Dead End |  | Porcelain | Dead End |  |  |  |  | 0.058515 | 2360.4771
119103737 | F | LC | ETL.7180.POLE.WDPS | 44360908 | LAKEVLLE | NORTH BAY | 2020-05-19 | 2021-07-02 | ETL.7180 | IGNACIO-BOLINAS #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44360907 |  | 2-Pole Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.0045311 | 146.3688
119113654 | F | LC | ETL.6870.POLE.WOOD | 40586035 | SACTO | SIERRA | 2020-05-28 |  | ETL.6870 | FRENCH MEADOWS-MIDDLE FORK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40586035 | 1966-01-01 | Single Wood Pole | DDE - Double Dead End | 1966-01-01 | Non Ceramic | Dead End |  |  |  |  | 0.17644 | 4619.7144
119114390 | F | LC | ETL.1480.TOWR | 40809073 | LAKEVLLE | HUMBOLDT | 2020-05-21 | 2021-03-03 | ETL.1480 | EAGLE ROCK-REDBUD | Structure-Steel | Debris/Nest/etc. | [Remove, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40809073 | 1978-01-01 | LATTICE STEEL TOWER | DC-DDE-A - Double Circuit Double Dead End Angle | 1978-01-01 | Glass | Dead End |  |  |  |  | 0.00023857 | 3050.2753
119114903 | E | LC | ETL.8170.POLE.WOOD | 40906413 | EUREKA | HUMBOLDT | 2020-06-02 | 2021-06-11 | ETL.8170 | TRINITY-MAPLE CREEK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40906413 |  | Single Wood Pole | DDE - Double Dead End |  | Polymer | [5 empty] | 0.012574 | 5842.8242
119115058 | F | LC | ETL.6470.POLE.WOOD | 40905847 | SACTO | SIERRA | 2020-05-29 | 2021-02-10 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 |  |  | DLFL | [12 empty] | 2784.1987
119115157 | F | LC | ETL.7290.POLE.WOOD | 40826018 | TABLEMTN | NORTH VALLEY | 2020-05-29 |  | ETL.7290 | KILARC-CEDAR CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40826018 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | [5 empty] | 0.0022314 | 334.5242
119117424 | E | LC | ETL.8290.POLE.WOOD | 40769420 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.8290 | VOLTA-DESCHUTES | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40769420 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | Pin |  |  |  |  | 0.00084768 | 3702.9907 | 3.1389
119118508 | F | LC | ETL.6320.POLE.NWOD | 44820180 | TABLEMTN | NORTH VALLEY | 2020-06-01 |  | ETL.6320 | CENTERVILLE-TABLE MTN | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44820180 | 2019-06-30 | Fiberglass | TPD - Tri Post Dead End Construction | 2019-06-30 | Glass | Dead End |  |  |  |  | 0.00061774 | 862.7981
119118716 | F | LC | ETL.8405.POLE.WOOD | 42569713 | SACTO | SIERRA | 2020-05-29 | 2021-07-21 | ETL.8405 | MIDDLE FORK #1 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 42569713 |  | Single Wood Pole | Unknown |  | Polymer | [5 empty] | 0.023338 | 6902.4902
119119194 | F | LC | ETL.6470.POLE.WOOD | 44206642 | SACTO | SIERRA | 2020-06-01 | 2021-10-12 | ETL.6470 | COLGATE-ALLEGHANY | Marker (i.e. signs)-Wood | Missing | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 44206642 |  | Single Wood Pole | TCDE - Tap Construction Dead End |  | Porcelain | Pin |  |  |  |  | 0.010888 | 1044.1248
119119674 | F | LC | ETL.6690.POLE.WOOD | 40815088 | SACTO | SIERRA | 2020-05-28 | 2020-11-12 | ETL.6690 | DEER CREEK-DRUM | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | DLFL | 40815088 |  | Single Wood Pole | DDE-A - Double Dead End Angle |  | Ceramic | [5 empty] | 0.22892 | 158.2976
119130676 | E | LC | ETL.4590.TOWR | 40910154 | TABLEMTN | NORTH VALLEY | 2020-06-04 | 2021-04-19 | ETL.4590 | CRESTA-RIO OSO | Structure-Tower | No Good/Out of Stdrd | [Repair] | Tier3 | Tier 3 | Within Both | DLFL | 40910154 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 4.9556e-05 | 0.065151
119153526 | E | LC | ETL.7260.POLE.WOOD | 40617565 | TABLEMTN | NORTH VALLEY | 2020-06-09 | 2021-06-01 | ETL.7260 | KESWICK-CASCADE | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | DLFL | 40617565 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Ceramic | Pin |  |  |  |  | 1.3382e-05 | 2124.5115
119167345 | F | LC | ETL.6280.POLE.WOOD | 44722645 | TABLEMTN | NORTH VALLEY | 2020-06-15 |  | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44722645 |  | Single Wood Pole | FDDE - Flat Dead End Construction |  | Polymer | Dead End |  |  |  |  | 6.0521e-06 | 126.5956
119175142 | F | LC | ETL.6280.POLE.WOOD | 40599708 | TABLEMTN | NORTH VALLEY | 2020-06-16 |  | ETL.6280 | CARIBOU #2 | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40599708 |  | Single Wood Pole | T2N | 2020-06-26 | Polymer | Post |  |  |  |  | 4.7809e-06 | 537.8195
119185467 | E | LC | ETL.5440.POLE.WDPS | 44558361 | TABLEMTN |  | 2020-06-18 | 2020-06-30 | ETL.5440 | PIT #6 JCT-ROUND MTN | Damper-Steel | Missing | [Install] | Tier2 |  |  | DLFL
119197543 | B | LC | ETL.3500.TOWR | 40643033 | VICTOR | STOCKTON | 2020-06-19 | 2020-07-06 | ETL.3500 | SALT SPRINGS-TIGER CREEK | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40643033 | 1930-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 1930-01-01 | Ceramic | Suspension |  |  |  |  | 2.407e-05 | 1186.6569
119198559 | F | LC | ETL.6470.POLE.WOOD | 40760749 | SACTO | SIERRA | 2020-06-23 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40760749 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.12205 | 110.8102
119198834 | E | LC | ETL.6470.POLE.WOOD | 40767326 | SACTO | SIERRA | 2020-06-23 | 2021-08-31 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40767326 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | [5 empty] | 0.061003 | 205.7345
119199136 | F | LC | ETL.6470.POLE.WOOD | 40664637 | SACTO | SIERRA | 2020-06-22 |  | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40664637 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.03845 | 205.7851
119199841 | E | LC | ETL.6470.POLE.WOOD | 40679468 | SACTO | SIERRA | 2020-06-23 | 2021-08-05 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed, Completed] | Tier3 |  |  | COMP | [11 empty] | 0.085966 | 158.2723
119200199 | E | LC | ETL.6470.POLE.WOOD | 40664628 | SACTO | SIERRA | 2020-06-23 | 2021-08-02 | ETL.6470 | COLGATE-ALLEGHANY | Structure-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119200211 | E | LC | ETL.6220.POLE.WOOD | 40875290 | EUREKA | HUMBOLDT | 2020-06-22 | 2021-11-02 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Anchor-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40875290 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.066257 | 1789.2865 | 118.5523
119200320 | F | LC | ETL.6310.POLE.WOOD | 40817332 | TABLEMTN | NORTH VALLEY | 2020-06-23 |  | ETL.6310 | CASCADE-BENTON-DESCHUTES | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 | Tier 2 | Within Both | PEND | 40817332 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 3.3404e-06 | 4293.4263
119201579 | F | LC | ETL.7300.POLE.NWOD | 45115720 | TABLEMTN | NORTH VALLEY | 2020-06-23 |  | ETL.7300 | KILARC-DESCHUTES | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 45115720 | 2019-10-07 | Light Duty Steel Pole | FSS - Field Switch Structure | [8 empty] | 3833.8523
119204214 | F | LC | ETL.8640.POLE.NWOD | 44172588 | FRESNO | YOSEMITE | 2020-06-23 |  | ETL.8640 | EXCHEQUER-MARIPOSA | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44172588 | 2016-02-18 | Light Duty Steel Pole | TH - TriAngle Post 70 | 2016-02-18 | Polymer | Post |  |  |  |  | 7.3858e-09 | 335.2511
119209240 | E | LC | ETL.7300.POLE.WOOD | 40816244 | TABLEMTN |  | 2020-06-24 | 2020-09-02 | ETL.7300 | KILARC-DESCHUTES | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40816244 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.00019191 | 5053.5459
119229011 | B | LC | ETL.8290.POLE.WOOD | 40769424 | TABLEMTN | NORTH VALLEY | 2020-06-29 | 2021-04-22 | ETL.8290 | VOLTA-DESCHUTES | Insulator Bond Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40769424 |  | Single Wood Pole | TP - Tri Pin |  | Ceramic | [5 empty] | 0.01404 | 4750.8926
119236396 | E | LC | ETL.1650.POLE.WDPS | 44298334 | LAKEVLLE | SONOMA | 2020-06-30 | 2021-03-20 | ETL.1650 | GEYSERS #3-CLOVERDALE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44298333 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 7.6343e-06 | 1884.5717
119238141 | F | LC | ETL.7270.POLE.WOOD | 40906112 | TABLEMTN | NORTH VALLEY | 2020-06-30 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906112 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0057111 | 3119.219
119238907 | E | LC | ETL.2740.INSL.CERA | 40621983 | CONCORD | EAST BAY | 2020-06-30 | 2021-06-10 | ETL.2740 | MORAGA-OAKLAND #3 | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119296189 | E | LC | ETL.6900.INSL.CERA | 40828733 | LAKEVLLE | SONOMA | 2020-06-29 |  | ETL.6900 | WINDSOR-FITCH MOUNTAIN | Insulator-Wood | No Good/Out of Stdrd | [Replace] |  | Tier 2 | Within Both | PEND | 40804780 | 1980-01-01 | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | Post |  |  |  |  | 3.1552e-06 | 395.7669 | 0.0012487
119307966 | E | LC | ETL.1450.POLE.WDPS | 44549969 | SACTO | SACRAMENTO | 2020-07-01 | 2020-08-11 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549508 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00013568 | 269.0477
119314245 | F | LC | ETL.8060.POLE.WOOD | 40828161 | SACTO | SIERRA | 2020-07-02 | 2021-05-17 | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40828161 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.018388 | 166.227
119317601 | F | LC | ETL.7270.POLE.WOOD | 40909529 | TABLEMTN | NORTH VALLEY | 2020-07-06 |  | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40909529 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 0.0015448 | 5300.8838
119334383 | E | LC | ETL.7030.POLE.WOOD | 40827600 | TABLEMTN | NORTH VALLEY | 2020-07-08 | 2021-06-10 | ETL.7030 | HAT CREEK #1-WESTWOOD | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827600 |  | Single Wood Pole | T2N | 2021-06-03 | Polymer | Post |  |  |  |  | 0.0060113 | 79.1577
119334457 | F | LC | ETL.1440.POLE.WOOD | 40870574 | SACTO | SIERRA | 2020-07-01 | 2020-08-19 | ETL.1440 | DRUM-SUMMIT #1 | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40870574 | 1956-01-01 | Single Wood Pole | 3P SV - 3 Pole Single Vertical | 1956-01-01 | Ceramic | Suspension |  |  |  |  | 0.00063129 | 0.065152
119335289 | F | LC | ETL.4040.POLE.STPS | 44647159 | TABLEMTN | NORTH VALLEY | 2020-07-08 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 44646920 | 2018-08-17 | 2-Pole Non Wood | 2P DDE - 2 Pole Double Dead End | [7 empty] | 0.00010378 | 2223.9963
119338500 | E | LC | ETL.1440.POLE.WOOD | 40597045 | SACTO | SIERRA | 2020-07-08 | 2021-06-23 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 |  |  | COMP
119341096 | F | LC | ETL.7030.POLE.WOOD | 40868490 | TABLEMTN | NORTH VALLEY | 2020-07-09 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Other | Other | [Other] | Tier2 | Tier 2 | Within Both | PEND | 40868490 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.011289 | 698.4329
119341531 | E | LC | ETL.7030.POLE.WOOD | 40770761 | TABLEMTN | NORTH VALLEY | 2020-07-09 | 2021-06-14 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40770761 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0097254 | 428.6199
119357086 | F | LC | ETL.7030.POLE.WOOD | 40667954 | TABLEMTN | NORTH VALLEY | 2020-07-10 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40667954 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.011289 | 808.4792
119362869 | F | LC | ETL.8560.POLE.WDPS | 44171821 | PISMOBCH | LOS PADRES | 2020-07-13 | 2021-07-06 | ETL.8560 | CAYUCOS-CAMBRIA | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44171819 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.0049507 | 776.9783
119375765 | E | LC | ETL.7030.POLE.WOOD | 40827571 | TABLEMTN | NORTH VALLEY | 2020-07-15 | 2021-06-22 | ETL.7030 | HAT CREEK #1-WESTWOOD | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40827571 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.00042471 | 0.06515
119461643 | F | LC | ETL.7030.POLE.WOOD | 40589874 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-06-17 | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40589874 |  | Single Wood Pole | T2N | 2017-09-27 | Polymer | Post |  |  |  |  | 0.010043 | 0.06515
119461785 | F | LC | ETL.6280.POLE.WOOD | 44259134 | TABLEMTN | NORTH VALLEY | 2020-07-16 | 2021-08-11 | ETL.6280 | CARIBOU #2 | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL | [11 empty] | 3.2921e-05 | 1012.3085
119477227 | E | LC | ETL.1440.POLE.WDPS | 44765210 | SACTO | SACRAMENTO | 2020-07-20 | 2021-06-17 | ETL.1440 | DRUM-SUMMIT #1 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] |  | Tier 2 | Within Both | COMP | 40876963 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0020261 | 731.1277
119483414 | E | LC | ETL.8060.POLE.WOOD | 40826218 | SACTO | SACRAMENTO | 2020-07-21 | 2021-09-01 | ETL.8060 | SPAULDING-SUMMIT | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826218 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.087146 | 784.8264
119487569 | F | LC | ETL.6440.POLE.WOOD | 40826844 | TABLEMTN | NORTH VALLEY | 2020-07-22 | 2021-01-04 | ETL.6440 | COLEMAN-RED BLUFF | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40826844 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | [5 empty] | 0.0011282 | 4056.3687
119488491 | F | LC | ETL.5300.TOWR | 40753269 | PISMOBCH | LOS PADRES | 2020-07-22 | 2021-05-10 | ETL.5300 | MORRO BAY-SOLAR SW STA #1 | Road | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40753269 | 1960-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 1962-01-01 | Ceramic | Suspension |  |  |  |  | 1.7301e-06 | 3863.8943
119511867 | F | LC | ETL.5250.TOWR | 40865513 | CONCORD | DIABLO | 2020-07-27 | 2021-03-01 | ETL.5250 | MORAGA-CASTRO VALLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40865513 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 2021-07-20 | Glass | Dead End |  |  |  |  | 4.0269e-07 | 363.8189
119511867 | F | LC | ETL.5250.TOWR | 40865513 | CONCORD | DIABLO | 2020-07-27 | 2021-03-01 | ETL.5250 | MORAGA-CASTRO VALLEY | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40865513 | 1952-01-01 | LATTICE STEEL TOWER | DDE - Double Dead End | 1952-01-01 | Ceramic | Double Dead End |  |  |  |  | 4.0269e-07 | 363.8189
119521469 | F | LC | ETL.7850.POLE.WOOD | 40648555 | EUREKA | HUMBOLDT | 2020-07-29 |  | ETL.7850 | RIO DELL JCT-BRIDGEVILLE | Vegetation | Overgrown | [Trim] |  | Non-HFTD | HFRA Addition | PEND | 40648555 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 5.0179e-06 | 641.5788 | 0.0032194
119529597 | F | LC | ETL.4040.POLE.STPS | 44784278 | TABLEMTN | NORTH VALLEY | 2020-07-29 |  | ETL.4040 | TRINITY-COTTONWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] |  | Tier 3 | Within Both | PEND | 44784129 | 2019-07-14 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.051548 | 2238.5257
119550262 | F | LC | ETL.8170.POLE.WOOD | 40827986 | EUREKA | HUMBOLDT | 2020-08-03 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40827986 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 0.083857 | 142.4119
119558337 | E | LC | ETL.7490.POLE.WOOD | 40650885 | EUREKA | HUMBOLDT | 2020-08-04 |  | ETL.7490 | MAPLE CREEK-HOOPA | Vegetation | Overgrown | [Remove] | Tier3 | Tier 3 | Within Both | PEND | 40650885 | 2011-01-01 | Single Wood Pole | T-1 - Tri Post |  | Ceramic | [5 empty] | 0.0054218 | 142.4245 | 0.77219
119569383 | E | LC | ETL.6880.POLE.WOOD | 40912463 | LAKEVLLE | NORTH BAY | 2020-08-06 | 2021-04-27 | ETL.6880 | FULTON-CALISTOGA | Crossarm-Wood | No Good/Out of Stdrd | [Replace] | Tier3 |  |  | DLFL
119569606 | F | LC | ETL.2790.TOWR | 40808549 | CONCORD | DIABLO | 2020-08-06 | 2021-03-23 | ETL.2790 | MORAGA-SAN LEANDRO #3 | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40808549 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 3.379e-06 | 31.6978
119575401 | E | LC | ETL.6220.POLE.WOOD | 40614562 | EUREKA | HUMBOLDT | 2020-08-06 | 2020-10-06 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Guy Wire-Wood | No Good/Out of Stdrd | [Repair] |  | Non-HFTD | HFRA Addition | DLFL | 40614562 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.090063
119577530 | B | LC | ETL.7180.POLE.WOOD | 40809516 | LAKEVLLE | NORTH BAY | 2020-08-07 | 2020-09-24 | ETL.7180 | IGNACIO-BOLINAS #2 | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40809516 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Porcelain | [5 empty] | 7.8079e-06 | 1912.3527
119600382 | E | LC | ETL.7930.POLE.WOOD | 40613882 | MOSSLNDG | CENTRAL COAST | 2020-08-11 | 2021-08-16 | ETL.7930 | SALINAS-LAURELES | Conductor-Wood | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40613882 |  | Single Wood Pole | T-1 - Tri Post |  | Ceramic | Post |  |  |  |  | 0.0035527 | 0.065147
119611219 | E | LC | ETL.4392.INSL.NCER | 40791360 | LAKEVLLE | SONOMA | 2020-08-13 | 2021-04-19 | ETL.4392 | EAGLE ROCK-FULTON-SILVERADO | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier3 |  |  | COMP
119626931 | E | LC | ETL.6760.POLE.WOOD | 40611270 | SACTO | SACRAMENTO | 2020-08-17 | 2021-06-09 | ETL.6760 | DRUM-GRASS VALLEY-WEIMAR | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
119636942 | E | LC | ETL.7140.POLE | 40648877 | LAKEVLLE | NORTH BAY | 2020-08-18 | 2021-05-19 | ETL.7140 | IGNACIO-BOLINAS #1 | Crossarm-Wood | No Good/Out of Stdrd | [Replace, Completed] |  | Tier 2 | Within Both | COMP | 40648877 |  | Single Wood Pole | T-1 - Tri Post | 2021-04-27 | Polymer | Post |  |  |  |  | 0.0020528 | 1868.0144
119677273 | E | LC | ETL.7820.INSL.CERA | 44149280 | LAKEVLLE |  | 2020-08-25 | 2021-03-15 | ETL.7820 | POTTER VALLEY-WILLITS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44149274 | 2014-12-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2014-12-08 | Ceramic | Suspension |  |  |  |  | 9.1759e-08
119677273 | E | LC | ETL.7820.INSL.CERA | 44149280 | LAKEVLLE |  | 2020-08-25 | 2021-03-15 | ETL.7820 | POTTER VALLEY-WILLITS | Insulator-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44149274 | 2014-12-08 | 2-Pole Non Wood | 2PS - 2 Pole SUSP | 2014-12-08 | Ceramic | Suspension |  |  |  |  | 9.1759e-08
119688445 | E | LC | ETL.2060.POLE.STPS | 44653298 | LAKEVLLE | HUMBOLDT | 2020-08-24 | 2021-08-23 | ETL.2060 | FORT BRAGG-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44652960 | 2018-09-15 | 3-Pole Non Wood | 3P DDE - 3 Pole Double Dead End | [7 empty] | 0.066725 | 261.5632
119692809 | E | LC | ETL.1110.TOWR | 40676690 | EUREKA | HUMBOLDT | 2020-08-27 | 2021-02-08 | ETL.1110 | BRIDGEVILLE-COTTONWOOD | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40676690 | 1952-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Porcelain | Suspension |  |  |  |  | 1.8871e-06 | 63.351
119696242 | E | LC | ETL.4100.TOWR | 40591392 | SACTO | SACRAMENTO | 2020-08-31 | 2021-02-22 | ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | Structure-Tower | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40591392 | 1913-01-01 | LATTICE STEEL TOWER | SS2 - Susp. Steel Double CIR. | 2018-05-29 | Glass Silicone Coated | Suspension |  |  |  |  | 9.0633e-07 | 6000.2266
119720513 | A | LC | ETL.6240.POLE.WOOD | 40612373 | MOSSLNDG | CENTRAL COAST | 2020-09-05 | 2020-09-19 | ETL.6240 | BURNS-LONE STAR #2 | Emergency | Fire | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40612373 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Polymer | [5 empty] | 0.12626 | 110.8153
119755625 | E | LC | ETL.7550.INSL.NCER | 40577995 | LAKEVLLE |  | 2020-08-26 | 2021-04-07 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | DLFL | 44211120 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 0.00050251
119755625 | E | LC | ETL.7550.INSL.NCER | 40577995 | LAKEVLLE |  | 2020-08-26 | 2021-04-07 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | DLFL | 44211120 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 0.00050251
119755625 | E | LC | ETL.7550.INSL.NCER | 40577995 | LAKEVLLE |  | 2020-08-26 | 2021-04-07 | ETL.7550 | MENDOCINO-WILLITS-FORT BRAGG | Insulator | Contaminated | [Ground Wash] | Tier3 | Tier 3 | Within Both | DLFL | 44211120 |  | 3-Pole Wood | 3P DDE - 3 Pole Double Dead End |  | Polymer | Suspension |  |  |  |  | 0.00050251
119782922 | E | LC | ETL.6220.POLE.WOOD | 40769396 | EUREKA | HUMBOLDT | 2020-09-14 | 2021-10-21 | ETL.6220 | BRIDGEVILLE-GARBERVILLE | Structure-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40769396 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Porcelain | [5 empty] | 0.38893 | 889.3207 | 345.8845
119785031 | E | LC | ETL.7780.POLE.WOOD | 40614151 | LAKEVLLE | HUMBOLDT | 2020-09-11 | 2021-09-01 | ETL.7780 | PHILO JCT-ELK | Guy Wire-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40614151 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | [5 empty] | 3.0971e-05 | 0.065148
119787188 | E | LC | ETL.4590.TOWR | 40910146 | TABLEMTN | NORTH VALLEY | 2020-09-16 | 2021-09-09 | ETL.4590 | CRESTA-RIO OSO | Foundation/Concrete-Tower | No Good/Out of Stdrd | [Repair, Completed, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40910146 |  | LATTICE STEEL TOWER | SUSP - Suspension (TWR) |  | Ceramic | Suspension |  |  |  |  | 8.0923e-07 | 142.445
119790036 | E | LC | ETL.1450.POLE.WDPS | 44553646 | SACTO | SACRAMENTO | 2020-09-18 | 2021-05-11 | ETL.1450 | DRUM-SUMMIT #2 | Insulator-Wood | No Good/Out of Stdrd | [Replace, Completed, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44553173 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.0075903 | 31.7066
119793919 | B | LC | ETL.6290.INSL.CERA | 42721999 | TABLEMTN | NORTH VALLEY | 2020-09-09 | 2020-10-02 | ETL.6290 | CARIBOU-PLUMAS JCT | Splice-Wood | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 42721901 |  | Single Wood Pole | SV1 - Angle 0-30 Degrees |  | Porcelain | [5 empty] | 0.53215 | 950.3212
119794956 | F | LC | ETL.6690.POLE.WOOD | 40603296 | SACTO | SIERRA | 2020-08-05 | 2021-07-06 | ETL.6690 | DEER CREEK-DRUM | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | DLFL | 40603296 |  | Single Wood Pole | TH - TriAngle Post 70 |  | Non Ceramic | Other |  |  |  |  | 0.057024 | 142.4769
119816383 | F | LC | ETL.7270.POLE.NWOD | 44649299 | TABLEMTN | NORTH VALLEY | 2020-08-29 | 2021-08-30 | ETL.7270 | KESWICK-TRINITY | Structure-Wood | Debris/Nest/etc. | [Remove, Completed] | Tier2 | Tier 2 | Within Both | COMP | 44649299 | 2018-08-17 | Light Duty Steel Pole | TPD - Tri Post Dead End Construction | 2018-08-17 | Polymer | Dead End |  |  |  |  | 0.00023965 | 205.7693
119835547 | F | LC | ETL.8170.POLE.WOOD | 44420777 | EUREKA | HUMBOLDT | 2020-09-02 | 2020-12-31 | ETL.8170 | TRINITY-MAPLE CREEK | Marker (i.e. signs)-Wood | Missing | [Install] | Tier2 |  |  | DLFL
119848580 | F | LC | ETL.7290.POLE.NWOD | 44645377 | TABLEMTN | NORTH VALLEY | 2020-09-09 |  | ETL.7290 | KILARC-CEDAR CREEK | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier3 | Tier 3 | Within Both | PEND | 44645377 | 2018-07-31 | Light Duty Steel Pole | T2N | 2018-07-31 | Polymer | Post |  |  |  |  | 0.00036338 | 1634.3816
119869445 | E | LC | ETL.5960.TOWR | 40658784 | PISMOBCH | LOS PADRES | 2020-10-07 | 2021-06-04 | ETL.5960 | DIABLO-GATES #1 | Guy Wire-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier3 | Tier 3 | Within Both | COMP | 40658784 | 1973-01-01 | LATTICE STEEL TOWER | SUSP - Suspension (TWR) | 2018-06-11 | Glass | Suspension |  |  |  |  | 1.2541e-05 | 79.1393
119893634 | F | LC | ETL.6300.POLE.WDPS | 45015255 | TABLEMTN | NORTH VALLEY | 2020-10-07 |  | ETL.6300 | CARIBOU-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 44225925 | 2014-11-07 | 3-Pole Wood | 3P DDE-A - 3 Pole Double Dead End Angle | [7 empty] | 1.4267e-06 | 1123.0226
119925069 | F | LC | ETL.8060.POLE.WOOD | 44156134 | SACTO | SIERRA | 2020-10-19 |  | ETL.8060 | SPAULDING-SUMMIT | Marker (i.e. signs)-Wood | No Good/Out of Stdrd | [Install] | Tier2 | Tier 2 | Within Both | PEND | 44156134 | 2013-09-20 | Single Wood Pole | TH - TriAngle Post 70 | 2013-09-20 | Polymer | Post |  |  |  |  | 0.0045457 | 0.065152
119992241 | F | LC | ETL.7030.POLE.WOOD | 40770837 | TABLEMTN | NORTH VALLEY | 2020-10-02 |  | ETL.7030 | HAT CREEK #1-WESTWOOD | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40770837 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.023763 | 126.76
120045843 | F | LC | ETL.8170.POLE.WOOD | 40906449 | EUREKA | HUMBOLDT | 2020-10-07 |  | ETL.8170 | TRINITY-MAPLE CREEK | Structure-Wood | Debris/Nest/etc. | [Remove] | Tier2 | Tier 2 | Within Both | PEND | 40906449 |  | Single Wood Pole | TPAD - Tri Pin Arm Dead End |  | Ceramic | [5 empty] | 0.078044 | 94.9939
120079439 | E | LC | ETL.1450.POLE.WDPS | 44550022 | SACTO | SACRAMENTO | 2020-08-06 | 2021-09-28 | ETL.1450 | DRUM-SUMMIT #2 | Structure-Wood | Rotten | [Replace, Completed] | Tier3 | Tier 3 | Within Both | COMP | 44549459 |  | 2-Pole Wood | 2PS - 2 Pole SUSP | [7 empty] | 0.00053387 | 79.1687
120097815 | E | LC | ETL.4950.INSL | 41130021 | LAKEVLLE | SONOMA | 2020-11-25 | 2021-04-29 | ETL.4950 | FULTON-LAKEVILLE | Insulator-Steel | No Good/Out of Stdrd | [Replace, Completed] | Tier2 |  |  | COMP
120119316 | E | LC | ETL.7990.POLE.WOOD | 40908954 | SACTO | SACRAMENTO | 2020-12-02 |  | ETL.7990 | SMARTVILLE-NICOLAUS #1 | Structure-Wood | No Good/Out of Stdrd | [Replace] | Tier2 | Tier 2 | Within Both | PEND | 40908954 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Porcelain | Unknown |  |  |  |  | 0.00016503 | 4340.0908 | 0.71627
120120693 | E | LC | ETL.7030.POLE.WOOD | 40866448 | TABLEMTN | NORTH VALLEY | 2020-07-10 | 2021-05-12 | ETL.7030 | HAT CREEK #1-WESTWOOD | Splice-Steel | No Good/Out of Stdrd | [Repair, Completed] | Tier2 | Tier 2 | Within Both | COMP | 40866448 |  | Single Wood Pole | TPA - Tri Pin Arm |  | Ceramic | Pin |  |  |  |  | 0.0093712 | 1981.2402