## Discovery Log
**This Discovery Log reflects Data Requests completed as of 05:00PM each Wednesday
SDG&E 2023 WMP Discovery Log
Question Count | Party Name | DR Set # | Data Request | Question No. | Question ID | Question | Response | Requestor | Date Rec'd | Final Due Date | Date Sent | Link | Number of Atchs | NDA Required | WMP Section | Category | Sub Category
1 | CalPA | 2023-01 | CalPA-2023-01 | 1 | CalPA-2023-01.1 | Please provide a copy of each WMP-related document, submission, or report you submit to the Office of Energy Infrastructure Safety (Energy Safety) in 2023 that is related to your WMP. Provide the copy to Cal Advocates within one business day of the document’s submittal to Energy Safety. (If you have submitted the document to Energy Safety in 2023 prior to this data request, please provide a copy as soon as possible and no later than 10 business days from the issuance of this data request.) This request is limited to materials or documents that (1) are related to work plans, initiative targets, risk models, risk spend efficiency (RSE) calculations, or WMP change orders; and (2) are provided to Energy Safety to provide additional details or context concerning information or statements in your WMP (and any subsequent revisions or change orders affecting your WMP). | SDG&E generally objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, and 7. Subject to the foregoing objections, SDG&E will address the request in Question 1 as reports are submitted to Energy Safety. | Aaron Louie | 2023-02-07 | 2023-02-15 | 2023-02-15 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-01.pdf | 0 | Yes | WMP Pre-Submissions | Administrative | N/A | N/A
2 | CalPA | 2023-01 | CalPA-2023-01 | 2 | CalPA-2023-01.2 | Please provide a copy of your WMP pre-submission within two business days of its submission to Energy Safety. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 5, and 6. SDG&E further objects to the request on the grounds that it is not consistent with the 2023-2025 WMP Process and Evaluation Guidelines (2023 Guidelines) issued by Energy Safety. Per the 2023 Guidelines, the WMP pre-submission is not a public document and does not commence the WMP Review Process (2023 Guidelines at 3). “The completeness check is not a substantive review of WMP content; a substantive review occurs during the WMP evaluation process.” (Id.) Through public dissemination of the WMP pre-submission beyond Energy Safety’s completeness check, Cal Advocates attempts to further extend the WMP review period established by Public Utilities Code Section 8386.3(a) by an additional six weeks. This is both inconsistent with Section 8386.3(a) but also the spirit of the 2023 Guidelines, which establish that the pre-submission process occurs “prior to commencing evaluation.” (2023 Guidelines at 3). SDG&E respectfully requests that, to preserve the three-month review period, Cal Advocates refrain from any public dissemination of the pre-submission. SDG&E further notes that, due to the nature of the pre-submission completeness check process, there may be potential changes to the WMP pre-submission that may occur between now and the actual WMP submission date on March 27, either as required by Energy Safety or as made by SDG&E. Subject to the foregoing objections, SDG&E responds as follows: SDG&E’s 2023-2025 WMP Pre-submission is attached. | Aaron Louie | 2023-02-07 | 2023-02-15 | 2023-02-15 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-01.pdf | 0 | No | WMP Pre-Submissions | Administrative | N/A | N/A
3 | CalPA | 2023-01 | CalPA-2023-01 | 3 | CalPA-2023-01.3 | Provide a copy of all documents or files that are referenced in your WMP Quarterly Data Reports and submitted to Energy Safety (including but not limited to all PDFs, spatial data files, non-spatial data files, and confidential attachments) on the same business day that the document is sent to Energy Safety. | SDG&E generally objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, and 7. Subject to the foregoing objections, SDG&E will address the request as documents and files are made available. | Aaron Louie | 2023-02-07 | 2023-05-01 | 2023-02-15 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-01.pdf | 0 | No | WMP QDR | Administrative | N/A | N/A
4 | CalPA | 2023-01 | CalPA-2023-01 | 4 | CalPA-2023-01.4 | Provide a copy to Cal Advocates of all your confidential responses to WMP discovery requests, on the same business day that you send the documents to the issuer of the discovery request. This includes: a) Confidential responses to WMP discovery requests issued by Energy Safety. b) Confidential responses to WMP discovery requests issued by other entities. | SDG&E generally objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, and 7. Subject to the foregoing objections, SDG&E will address the request as documents and files are made available. | Aaron Louie | 2023-02-07 | N/A | 2023-02-15 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-01.pdf | 0 | No | WMP DRs | Administrative | N/A | N/A
5 | CalPA | 2023-02 | CalPA-2023-02 | 1 | CalPA-2023-02.1 | Please identify and provide a copy of all quality assurance or quality control (QA/QC) reports conducted by internal entities that were completed since January 1, 2022 and that examined any programs, initiatives, or strategies described in your 2022 WMP Update. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, and 7. Subject to the foregoing objections, SDG&E responds as follows: Emergency Management SDG&E did not activate our PSPS protocols in 2022 therefore there are no QA/QC reports for actual events. In 2022 Emergency Management did conduct After-Action Reviews (AAR) for the following PSPS exercises: • PSPS Functional Exercise Aug 2022 • PSPS Tabletop with External Partners Jun 2022 • PSPS Notification Functional Exercise May 2022 Where external partners participated in the exercises, they were also included in development of the AAR report. Opportunities for input varied between in-person AAR workshops and online surveys. Each AAR also includes an Improvement Plan (IP) to capture items where corrective actions have been identified and assigned. AAR’s are completed in accordance with FEMA Homeland Security Exercise and Evaluation Program (HSEEP) guidelines. Electric Distribution Operations Electric Distribution Operations records emergency outage data for the entire service territory. We perform an internal two-stage review of all emergency outage data to ensure customer impact and restoration steps are accurate, but there are no QA/QC reports generated by Electric Distribution Operations as part of our review. The outage data we gather is audited internally by the Electric Reliability department.Vegetation Management Vegetation Management Quality Assurance team has several documents attached. They are summaries of pole brush audits, pre-inspection audits and post tree trimming work audits. Vegetation management QA team audits Wood Pole Inspection (WPI) These audits are performed on a monthly basis of completed pole inspections. Construction The SDG&E Portfolio & Project Management (PPM) Quality Assurance & Quality Control (QA/QC) department, in collaboration with WMP program and project leaders, examines WMP projects to verify compliance of project designs and construction to applicable SDG&E standards, specifications, and industry codes. Throughout 2022, thousands of facilities’ design packages were reviewed and, after construction, field inspected, assessed, and/or audited. After performing pre- and post-construction reviews and inspections, observations are presented to the project leads for resolution. PPM QA/QC completed assessments for approximately 5,000 work packages (3,500 work packages comprise WMP efforts), which identified approximately 46,000 pre-construction observations (Figure 1) and 6,000 post-construction findings. The figure below shows the estimated composition of findings identified in 2022 for all projects, including WMP projects, which comprise a subset of these data. Figure 1 depicts the most common pre-construction review observations related to material selection and general design errors. These observations are provided to the responsible Designer or Engineer for consideration and resolution, prior to issuance to construction. The composition of observations identified during post-construction inspections are: (1) as-built condition conflicts with current SDG&E Standards, (2) field conditions do not match design, (3) missing or incorrect hardware or pole tag markings, and (4) communication (Communication Infrastructure Provider (CIP), i.e. third party communication providers) line is not transferred to new facility. Over 2022, the average findings per structure totaled 1.31. These efforts fulfill one of several components of quality assurance and quality control due diligence for WMP programs and projects. Safety Management System SDG&E submits the attached Audit Advisory Memorandum issued March 2, 2022 (“21-204 – SDG&E Safety Management System Program Assessment”). Sempra’s Audit Services performed an advisory review of SDG&E’s Safety Management System (SMS). The scope of this Audit Services advisory included a documentation review of SMS governance framework and processes with a primary objective to support a successful launch, including areas where investments maybe necessary to ensure enduring success of the program, such as additional resources and technology. Transmission and Substation Ops SDG&E submits its Transmission Construction and Maintenance Quality Control Verification Report. The attached report (“Transmission Construction and Maintenance Quality Control Verification Report 2022”) describes audits performed in 2022, including only structures in the HFTD Meteorology SDG&E network of weather stations • SDG&E operates a dense network of surface weather network, currently made of 222 weather stations, and it is foundational to SDG&E’s ability to understand and predict the potential of elevated fire weather events and their impacts on local communities in its service territory. It is imperative that this weather network remains operational at all costs as it allows us to have a real-time monitoring of weather conditions that could be crucial in accurately determining the precise timing and location of powerline de-energizations required during the Public Safety Power Shutoff (PSPS) events. During the course of the year in 2022, SDG&E performs maintenance work to its weather stations by calibrating its sensors and replacing its batteries that are not in their optical states. 221 weather stations were calibrated in 2022. SDG&E supercomputing clusters in support of performing high-resolution numerical weather prediction forecast simulations that are tailored to the SDG&E service territory • To stay informed on future weather conditions that could lead to increased wildfire risk and other hazardous conditions, SDG&E performs ensembles of the state-of-the-art numerical weather prediction model forecast simulations on its in-house supercomputers every day. This allows SDG&E to monitor and to predict the wildfire risk by calculating its Fire Potential Index (FPI), which is a planning and decision-supporting tool designed to reduce the wildfire risk by examining the susceptibility of the environment to fire and its daily calculations are shared broadly with the community. Therefore, ensuring that the inhouse supercomputing clusters remain in healthy mode is critical. Noting that the currently in-production computing infrastructures were reaching the end of expective lifetime, SDG&E have taken a proactive action and purchased new supercomputing clusters in 2022. Purchasing the new supercomputing clusters means setting up the latest version of the numerical weather prediction model and optimizing its configuration that will be running operationally, so SDG&E have performed the model validation simulations for a selection of high-impact weather conditions ranging from Santa Ana winds, winter storms/atmospheric rivers, and monsoonal thunderstorms Advancing the science of fire spread modeling • To increase the accuracy of predicting the rate of fire spread, SDG&E has collaborated with an academic partner (SJSU: San Jose State University) to further advance the science of fire spread modeling. The SJSU fire spread model is an improvement over the popularly used fire spread model by incorporating the effects of two-way coupling between the atmosphere and fire-induced heat fluxes into the model. SJSU has also been developing the new live fuel moisture model that can be used in their coupled weather-fire model. ML-based model of predicting vegetation-related outages • SDG&E have established an external collaborative partnership with San Diego Supercomputer Center (SDSC) to construct a ML-based model of predicting vegetationrelated outages by examining previous vegetation-related outages and weather conditions that were associated with them. The daily output from the model will be useful in safe and reliable operations of the grid system. Running a large ensemble of weather forecasts to improve the prediction of Santa Ana winds • Given intrinsic uncertainty associated with numerical weather prediction, it is imperative to measure and quantify the uncertainty in the forecasted weather conditions, especially if high-impact weather conditions, such as gusty Santa Ana winds, are expected over the service territory. For this reasons, SDG&E have partnered with UC San Diego CW3E (Center for Western Weather and Water Extreme) to perform a large ensemble (200 members) of the weather forecasts for uncertainty quantification and use the 200-member ensemble to derive an index (Santa Ana Index) that characterizes the potential impact of predicted gusty offshore winds. Customer Programs Within SDG&E, the Customer Programs department facilitates the operation of the Generator Assistance Program (GAP), which offers point-of-sale rebates (via instant rebate coupons) and downstream rebates (via post-purchase application) for portable generator and battery units to qualifying customers in HFTD Tiers 2 and 3. This program is managed by a third-party and the QA/QC processes includes the following. It should be noted that no formal QA/QC reports are generated, but the third-party utilizes this structure to notify SDG&E of any QA/QC updates that are needed: • Fraud QA: Run weekly reports to prevent ineligible or fraudulent reservations using bogus email accounts (example: fred@fakemail.xyz) • Coupon Participation limit QA: A weekly verification that checks coupon reservations against each program’s past participation rules and logic (e.g. 1 coupon limit per eligible customer per year). An automated workflow uses these rules and compares them against the coupons that have been reserved to make sure everything is working properly. The process checks against duplicate addresses, account numbers, IP addresses, customer names, phone numbers, email addresses, etc., to make sure that each customer is participating per the GAP program’s participation limit rules. • Coupon/Rebate Application QA: Run weekly reports to verify all coupons and rebate applications are correctly filled out (no missing data, all naming conventions, product URLs, amounts are correct, etc.), all program specific information is being populated and that statuses are correct. • Portal QA: Monthly review of the program portal to verify accurate data, system performance, and product availability Asset Management SDG&E submits the attached 20 files which document QA/QC audits performed by our districts that perform our electric distribution asset inspections. These audits are performed by SDG&E’s Electric Construction Supervisors on a quarterly basis. These files consist of a summary document that outlines the number of audits required for the overhead detailed inspections (1.5% of the inspections completed), a detailed listing of those audits requiring to be performed, and audits for our overhead repairs (typically 1%). Drone Inspection Program SDG&E performs quality assurance reviews on all inspections completed as part of its Drone Investigation Assessment and Repair (DIAR) Program. After the Inspector completes the inspection, a Supervisor reviews the assessment and images before approving the inspection results. If any discrepancies are identified, the Supervisor will provide feedback to the Inspector during regular team meetings and the inspection findings will be updated prior to finalization. The images and findings are then processed through the machine learning models in production. Similarly, if there are any variations between the results of the machine learning model findings and the Inspector’s findings, that information will be reviewed and validated by the Supervisor. Information will be sent back to the Supervisor and the missed issues will be included in the inspection findings prior to finalization. Access and Functional Needs PSPS 112221 After Action Review_PSPS Partners 120621 After a PSPS event, 211 prepares and submits a detailed summary of actions completed and services provided to SDG&E medical baseline and/or access and functional needs customers that call in during a PSPS event. Details summarized in the report includes: calls intake, referral services such as, hotel stays, transportation, and back-up power unit if needed. AudioEye Issue Report sdge.com-02_16_2023 Effective real-time communications with customer affected by PSPS and other power outages is critical for the health and safety of all customers. One of our most important customer communication channels is the SDGE.com website and the PSPS preparedness and event information within the site. The Audio Eye Issue Report is run every week and constant improvements and accessibility enhancements are being made to address issues identified within the report. Accessibility of the website, to the WCAG 2.1 AA success criteria, is a constant focus and high importance for SDG&E. AudioEye monitors SDGE.com and SDGEnews.com for accessibility issues and provides technical reports and remediation solutions with our Web Team. AE-STAR-sdge.com-2023-02-16 The AudioEye Sustainable Testing and Remediation (STAR) Plan provides SDG&E’s Web Team with a road map of corrective measures each week to enhance and comply with accessibility guidelines (WCAG 2.1 AA) | Aaron Louie | 2023-02-07 | 2023-02-22 | 2023-02-22 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-02.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-02%20Q1%20Attachment.zip | 1 | No | 2022 WMP | QA/QC | N/A | N/A
6 | CalPA | 2023-02 | CalPA-2023-02 | 2 | CalPA-2023-02.2 | Please identify and provide a copy of all quality assurance or quality control (QA/QC) reports conducted by external entities that were completed since January 1, 2022 and that examined any programs, initiatives, or strategies described in your 2022 WMP Update. External entities include, but are not limited to, consultants, contractors, auditors, court-appointed monitors, and Independent Evaluators. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, and 7. Subject to the foregoing objections, SDG&E responds as follows: Transmission and Substation Operations In 2022, the CPUC ESRB conducted 4 audits as follows: • June 13-17 – Orange County District Substation Audit • December 5-9 – Northeast District Substation Audit • December 12-16 – Metro District Substation Audit • December 12-16 – Mountain/Inland/Coastal Transmission Audit Copies of the CPUC audit reports for the three substation audits are provided as part of this data request response. The audit for the December Mountain/Inlad/Coastl Transmission area has not yet been received from the CPUC. SDG&E references the “2022 California Independent System Operator Corporation (ISO) Maintenance Review – Final Report” attached hereto. The report published November 2022 documents the ISO 2022 annual maintenance review of SDG&E’s filed maintenance practices for transmission facilities placed under the ISO operational control. Electric Regional Operations In 2022, the CPUC ESRB conducted one audit associated with distribution operations and maintenance as follows: • August 1-5 – Beach Cities District Audit A copy of the CPUC audit report for Beach Cities District is provided as part of this data request response. Emergency Management Emergency Management activities are typically audited by external entities the year following the activities, for example, 2022 activities will be audited in 2023. Therefore, there are no QA/QC reports conducted by external entities in 2022 for 2022 WMP activities. | Aaron Louie | 2023-02-07 | 2023-02-22 | 2023-02-22 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-02.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-02%20Q2%20Attachment.zip | 1 | No | 2022 WMP | QA/QC | N/A | N/A
7 | CalPA | 2023-02 | CalPA-2023-02 | 3 | CalPA-2023-02.3 | Provide an Excel table of all defects in the year 2022 found by Energy Safety’s Compliance Branch (as rows) that includes the following information in separate columns. a) Associated circuit name b) Defect type c) Description of defect d) WMP initiative (from your 2022 WMP update) associated with defect e) Date that the defect was identified f) Date that the defect was corrected g) If the defect has not yet been corrected as of the issuance date of this data request, a brief explanation h) Priority level of corresponding corrective tag i) Geographic latitude of defect in decimal degrees, truncated to seven decimal places j) Geographic longitude of defect in decimal degrees, truncated to seven decimal places | SDG&E objects to the request on the grounds set forth in General Objections Nos. 5 and 8. Subject to the foregoing objections, SDG&E responds as follows: N/A | Aaron Louie | 2023-02-07 | 2023-02-22 | 2023-02-22 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-02.pdf | 0 | No | 2022 WMP | Defects | N/A | N/A
8 | CalPA | 2023-03 | CalPA-2023-03 | 1 | CalPA-2023-03.1 | Provide an Excel table of all distribution circuits existing as of January 1, 2023 (as rows) that includes the following information in separate columns. a) Circuit name b) Circuit ID number c) Total circuit miles d) Circuit miles in Non-HFTD Areas e) Circuit miles in Other HFTD f) Circuit miles in HFTD Tier 2 g) Circuit miles in HFTD Tier 3 h) Circuit voltage i) Circuit SAIDI (System Average Interruption Duration Index) for 2021 j) Circuit SAIDI (System Average Interruption Duration Index) for 2022 k) Circuit SAIFI (System Average Interruption Frequency Index) for 2021 l) Circuit SAIFI (System Average Interruption Frequency Index) for 2022 m) Circuit MAIFI (Momentary Average Interruption Frequency Index) for 2021 n) Circuit MAIFI (Momentary Average Interruption Frequency Index) for 2022 o) Total customer-minutes of de-energization on the circuit due to PSPS events in 2021 (sum of customer-minutes across all PSPS events). p) Total customer-minutes of de-energization on the circuit due to PSPS events in 2022 (sum of customer-minutes across all PSPS events). q) Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2021. r) Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2022. s) Number of trees that were worked on for EVM in Non-HFTD in 2021 t) Number of trees that were worked on for EVM in Non-HFTD in 2022 u) Number of trees that were worked on for EVM in Other HFTD in 2021 v) Number of trees that were worked on for EVM in Other HFTD in 2022 w) Number of trees that were worked on for EVM in HFTD Tier 2 in 2021 x) Number of trees that were worked on for EVM in HFTD Tier 2 in 2022 y) Number of trees that were worked on for EVM in HFTD Tier 3 in 2021 z) Number of trees that were worked on for EVM in HFTD Tier 3 in 2022 aa) Miles of covered conductor installed in Non-HFTD in 2021 bb) Miles of covered conductor installed in Non-HFTD in 2022 cc) Miles of covered conductor installed in Other HFTD in 2021 dd) Miles of covered conductor installed in Other HFTD in 2022 ee) Miles of covered conductor installed in HFTD Tier 2 in 2021 ff) Miles of covered conductor installed in HFTD Tier 2 in 2022 gg) Miles of covered conductor installed in HFTD Tier 3 in 2021 hh) Miles of covered conductor installed in HFTD Tier 3 in 2022 ii) Number of poles replaced in Non-HFTD in 2021 jj) Number of poles replaced in Non-HFTD in 2022 kk) Number of poles replaced in Other HFTD in 2021 ll) Number of poles replaced in Other HFTD in 2022 mm) Number of poles replaced in HFTD Tier 2 in 2021 nn) Number of poles replaced in HFTD Tier 2 in 2022 oo) Number of poles replaced in HFTD Tier 3 in 2021 pp) Number of poles replaced in HFTD Tier 3 in 2022 qq) Miles of underground conductor installation in Non-HFTD in 2021 rr) Miles of underground conductor installation in Non-HFTD in 2022 ss) Miles of underground conductor installation in Other HFTD in 2021 tt) Miles of underground conductor installation in Other HFTD in 2022 uu) Miles of underground conductor installation in HFTD Tier 2 in 2021 vv) Miles of underground conductor installation in HFTD Tier 2 in 2022 ww) Miles of underground conductor installation in HFTD Tier 3 in 2021 xx) Miles of underground conductor installation in HFTD Tier 3 in 2022 yy) Miles of LiDAR inspection in Non-HFTD in 2021 zz) Miles of LiDAR inspection in Non-HFTD in 2022 aaa) Miles of LiDAR inspection in Other HFTD in 2021 bbb) Miles of LiDAR inspection in Other HFTD in 2022 ccc) Miles of LiDAR inspection in HFTD Tier 2 in 2021 ddd) Miles of LiDAR inspection in HFTD Tier 2 in 2022 eee) Miles of LiDAR inspection in HFTD Tier 3 in 2021 fff) Miles of LiDAR inspection in HFTD Tier 3 in 2022 ggg) Number of detailed overhead inspections in Non-HFTD in 2021 hhh) Number of detailed overhead inspections in Non-HFTD in 2022 iii) Number of detailed overhead inspections in Other HFTD in 2021 jjj) Number of detailed overhead inspections in Other HFTD in 2022 kkk) Number of detailed overhead inspections in HFTD Tier 2 in 2021 lll) Number of detailed overhead inspections in HFTD Tier 2 in 2022 mmm) Number of detailed overhead inspections in HFTD Tier 3 in 2021 nnn) Number of detailed overhead inspections in HFTD Tier 3 in 2022 ooo) Number of sectionalization devices installed in Non-HFTD in 2021 ppp) Number of sectionalization devices installed in Non-HFTD in 2022 qqq) Number of sectionalization devices installed in Other HFTD in 2021 rrr) Number of sectionalization devices installed in Other HFTD in 2022 sss) Number of sectionalization devices installed in HFTD Tier 2 in 2021 ttt) Number of sectionalization devices installed in HFTD Tier 2 in 2022 uuu) Number of sectionalization devices installed in HFTD Tier 3 in 2021 vvv) Number of sectionalization devices installed in HFTD Tier 3 in 2022 | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see response provided in “CalPA-SDGE-2023WMP-DR03.xlsx.” | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03%20Attachment.xlsx | 1 | No | Other | Circuit Info | N/A | N/A
9 | CalPA | 2023-03 | CalPA-2023-03 | 2 | CalPA-2023-03.2 | Provide an Excel table of all transmission circuits existing as of January 1, 2023 (as rows) that includes the following information in separate columns. a) Circuit name b) Circuit ID number c) Total circuit miles d) Circuit miles in Non-HFTD Areas e) Circuit miles in Other HFTD f) Circuit miles in HFTD Tier 2 g) Circuit miles in HFTD Tier 3 h) Circuit voltage i) Total customer-minutes of de-energization on the circuit due to PSPS events in 2021 (sum of customer-minutes across all PSPS events). j) Total customer-minutes of de-energization on the circuit due to PSPS events in 2022 (sum of customer-minutes across all PSPS events). k) Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2021. l) Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2022. m) Number of support structures replaced in Non-HFTD in 2021 n) Number of support structures replaced in Non-HFTD in 2022 o) Number of support structures replaced in Other HFTD in 2021 p) Number of support structures replaced in Other HFTD in 2022 q) Number of support structures replaced in HFTD Tier 2 in 2021 r) Number of support structures replaced in HFTD Tier 2 in 2022 s) Number of support structures replaced in HFTD Tier 3 in 2021 t) Number of support structures replaced in HFTD Tier 3 in 2022 u) Miles of LiDAR inspection in Non-HFTD in 2021 v) Miles of LiDAR inspection in Non-HFTD in 2022 w) Miles of LiDAR inspection in Other HFTD in 2021 x) Miles of LiDAR inspection in Other HFTD in 2022 y) Miles of LiDAR inspection in HFTD Tier 2 in 2021 z) Miles of LiDAR inspection in HFTD Tier 2 in 2022 aa) Miles of LiDAR inspection in HFTD Tier 3 in 2021 bb) Miles of LiDAR inspection in HFTD Tier 3 in 2022 cc) Number of detailed aerial inspections in Non-HFTD in 2021 dd) Number of detailed aerial inspections in Non-HFTD in 2022 ee) Number of detailed aerial inspections in Other HFTD in 2021 ff) Number of detailed aerial inspections in Other HFTD in 2022 gg) Number of detailed aerial inspections in HFTD Tier 2 in 2021 hh) Number of detailed aerial inspections in HFTD Tier 2 in 2022 ii) Number of detailed aerial inspections in HFTD Tier 3 in 2021 jj) Number of detailed aerial inspections in HFTD Tier 3 in 2022 kk) Number of detailed climbing inspections in Non-HFTD in 2021 ll) Number of detailed climbing inspections in Non-HFTD in 2022 mm) Number of detailed climbing inspections in Other HFTD in 2021 nn) Number of detailed climbing inspections in Other HFTD in 2022 oo) Number of detailed climbing inspections in HFTD Tier 2 in 2021 pp) Number of detailed climbing inspections in HFTD Tier 2 in 2022 qq) Number of detailed climbing inspections in HFTD Tier 3 in 2021 rr) Number of detailed climbing inspections in HFTD Tier 3 in 2022 ss) Number of detailed ground inspections in Non-HFTD in 2021 tt) Number of detailed ground inspections in Non-HFTD in 2022 uu) Number of detailed ground inspections in Other HFTD in 2021 vv) Number of detailed ground inspections in Other HFTD in 2022 ww) Number of detailed ground inspections in HFTD Tier 2 in 2021 xx) Number of detailed ground inspections in HFTD Tier 2 in 2022 yy) Number of detailed ground inspections in HFTD Tier 3 in 2021 zz) Number of detailed ground inspections in HFTD Tier 3 in 2022 aaa) Number of sectionalization devices installed in Non-HFTD in 2021 bbb) Number of sectionalization devices installed in Non-HFTD in 2022 ccc) Number of sectionalization devices installed in Other HFTD in 2021 ddd) Number of sectionalization devices installed in Other HFTD in 2022 eee) Number of sectionalization devices installed in HFTD Tier 2 in 2021 fff) Number of sectionalization devices installed in HFTD Tier 2 in 2022 ggg) Number of sectionalization devices installed in HFTD Tier 3 in 2021 hhh) Number of sectionalization devices installed in HFTD Tier 3 in 2022 iii) Miles of transmission ROW expansion performed in Non-HFTD in 2021 jjj) Miles of transmission ROW expansion performed in Non-HFTD in 2022 kkk) Miles of transmission ROW expansion performed in Other HFTD in 2021 lll) Miles of transmission ROW expansion performed in Other HFTD in 2022 mmm) Miles of transmission ROW expansion performed in HFTD Tier 2 in 2021 nnn) Miles of transmission ROW expansion performed in HFTD Tier 2 in 2022 ooo) Miles of transmission ROW expansion performed in HFTD Tier 3 in 2021 ppp) Miles of transmission ROW expansion performed in HFTD Tier 3 in 2022 | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see response provided in “CalPA-SDGE-2023WMP-DR03.xlsx.” | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03%20Attachment.xlsx | 1 | No | Other | Circuit Info | N/A | N/A
10 | CalPA | 2023-03 | CalPA-2023-03 | 3 | CalPA-2023-03.3 | Provide an Excel table of all distribution circuits existing as of January 1, 2022 (as rows) that were removed or decommissioned in 2022, either partially or entirely. This includes permanent removal, removal of overhead lines that were moved underground, or overhead lines that were decommissioned but not physically removed. Include the following information in separate columns. a) Circuit name b) Circuit ID number c) Circuit miles removed or decommissioned in Non-HFTD Areas d) Circuit miles removed or decommissioned in Other HFTD e) Circuit miles removed or decommissioned in HFTD Tier 2 f) Circuit miles removed or decommissioned in HFTD Tier 3 g) Reason(s) for removal or decommissioning | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see response provided in “CalPA-SDGE-2023WMP-DR03.xlsx.” | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03%20Attachment.xlsx | 1 | No | Other | Circuit Info | N/A | N/A
11 | CalPA | 2023-03 | CalPA-2023-03 | 4 | CalPA-2023-03.4 | Provide an Excel table of all transmission circuits existing as of January 1, 2022 (as rows) that were removed or decommissioned in 2022, either partially or entirely. This includes permanent removal, removal of overhead lines that were moved underground, or overhead lines that were decommissioned but not physically removed. Include the following information in separate columns. a) Circuit name b) Circuit ID number c) Circuit miles removed or decommissioned in Non-HFTD Areas d) Circuit miles removed or decommissioned in Other HFTD e) Circuit miles removed or decommissioned in HFTD Tier 2 f) Circuit miles removed or decommissioned in HFTD Tier 3 g) Reason(s) for removal or decommissioning | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see response provided in “CalPA-SDGE-2023WMP-DR03.xlsx.” | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03%20Attachment.xlsx | 1 | No | Other | Circuit Info | N/A | N/A
12 | CalPA | 2023-03 | CalPA-2023-03 | 5 | CalPA-2023-03.5 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influenced where you performed work in 2022. a) EVM b) Covered conductor installation c) Undergrounding d) Distribution pole replacement e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of distribution assets i) Aerial inspections of transmission assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request on the grounds that it misstates facts or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as a component of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. While SDG&E’s EVM program does not scope work prioritizing circuit risk scores, it does focus on applying expanded post-trim clearances on targeted species identified as higher risk due to growth potential, failure characteristics, and relative outage frequency. The criteria for determining post‐trim clearances included multiple factors such as species, height, growth rate, health, location of defect, site conditions, pruning schedule, and proper pruning cuts. In 2022, SDG&E continued to perform required clearing activities on subject poles located within the SRA as required by Public Resources Code Section 4292. The SRA does not align completely with the HFTD boundary, so as an extra precautionary measure, SDG&E will consider additional poles located outside SRA where Public Resources Code Section 4292 does not apply, including on poles located within the Local Responsibility Areas. Additionally in 2022, SDG&E continued to perform vegetation fuels reduction activities surrounding poles located within the HFTD. For this activity, SDG&E does use the Circuit Risk Index and WiNGS modeling to determine areas to perform this work. b) Covered conductor installation The Wildfire Risk Scores are an output from the WiNGS-Planning Model and support with the prioritization of hardening. Currently, Risk Spend Efficiencies (RSEs) in the WiNGS-Planning are used to inform how to invest in mitigations that reduce risk. The WiNGS-Planning analyzes each circuit-segment to recommend strategic undergrounding (UG), covered conductor (CC) or no UG / CC. Although the risk reduction targets are often aimed at cost effectiveness, annual performance objectives, mileage targets, and other limitations and constraints are also considered to inform investment decisions. c) Undergrounding Please see response 5 (b). d) SDG&E did not complete any work for the Distribution Pole Replacement program in 2022. The future planned work for this program will have multiple risk categories and will be prioritized based on these categories. • Phase 1 (approximately 85 poles): Pole set in concrete and steel reinforced or pole set in concrete and not steel reinforced • Phase 2 (approximately 58 poles): Pole set in soil and steel reinforced • Phase 3 (approximately 1,379 poles): Pole set in soil and not steel reinforced e) SDG&E Grid Sectionalization program receives feedback from meteorology for PSPS opportunities based on new grid hardening projects such as Covered Conductor and Strategic Undergrounding in addition to stand-alone switch installations. SDG&E District Engineers also perform evaluations on the value of new switches by prioritizing customer impacts; they provide recommendations based on historical events and submit work order requests for new installations. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. Per GO 165, detailed inspections of overhead facilities are currently completed on a 5-year cycle for all overhead structures, including those in the HFTD. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine where inspections are performed, non-routine ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, SDG&E prioritizes detailed inspections in the HFTD prior to fire season. Detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores did not influence where detailed inspections of transmission assets in 2022 were performed. h) The drone inspection program began in 2019, and its scope included all distribution structures in Tier 2 and Tier 3 of the HFTD and coastal canyon areas within the WUI. SDG&E successfully completed this program in 2022 inspecting every structure in the aforementioned regions. Circuit risk ranking in combination with a list of circuits that had previously been subject to a Public Safety Power Shutoff (PSPS) event was used to prioritize which circuits were inspected prior to others within that HFTD. For Tier 2 HFTD circuits, the circuit risk ranking was provided in response to CALPA DR5 Q9. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores did not influence where aerial inspections of transmission assets in 2022 were performed. Aerial inspections were instead prioritized based on historical outage or fault data. j) In 2022, all distribution circuits within the HFTD had Light Detection and Ranging (LiDAR) data captured and processed. SDG&E did not utilize modeled wildfire risk scores to determine the scope of this program because all distribution circuits in the HFTD were included. k) SDG&E did not perform LiDAR inspections of transmission assets in 2022 except where there was distribution underbuilt on the structure. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2022 WMP | Wildfire Risk Score | N/A | N/A
13 | CalPA | 2023-03 | CalPA-2023-03 | 6 | CalPA-2023-03.6 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influenced how work in 2022 was sequenced. a) EVM b) Covered conductor installation c) Undergrounding d) Distribution pole replacement e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of distribution assets i) Aerial inspections of transmission assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request to the extent it misstates facts and/or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as part of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. b) Covered conductor installation The Wildfire Risk Scores are an output from the WiNGS-Planning Model and support with the prioritization of hardening. Additional considerations such as efficiencies that can reduce the resource burden are considered. Limiting projects to geographically proximate locations can optimize survey time (reducing travel times for teams fielding the fire hardening scope), limit mobilization/demobilization for construction crews, and optimize use of existing laydown yards. Long-term planning is also considered to ensure that year-over-year mileage targets are met. After the circuit-segment mitigation projects have been selected and prioritized, a desktop scoping and feasibility study is performed which includes geography, prior hardening, loading, standards, land/environmental, operational improvements, easement constraints, reliability improvements, and construction cost savings all help to dictate the sequence of projects. c) Undergrounding Please see response 6 (b). d) For the Distribution Pole Replacement Program, Phase 1 poles would be addressed first, followed by Phase 2 then Phase 3. However, permitting, land rights, environmental mitigation, customer concerns, or a combination of these factors will drive the ultimate schedule on each pole's replacement. Where feasible, poles will be bundled together in a single work package to minimize the impact to the community and gain efficiency in the design, environmental, permitting, land rights, and construction process. In most cases a single work order package will bundle poles that are adjacent or within a few spans of each other and will require similar land rights, permitting, and/or land rights. e) SDG&E Grid Sectionalization program is sequenced based on input from multiple stakeholders who determine where the greatest customer impacts can be realized. When this evaluation is performed in association with work being performed associated with hardening initiatives such as Covered Conductor or Strategic Undergrounding, it is sequenced according to that program. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. GO 165 also prescribes the acceptable interval, a 4month period within the calendar year, which dictates the sequencing of inspections throughout the year. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine the sequencing of inspections, SDG&E prioritizes detailed inspections in the HFTD prior to fire season and has shifted inspections into earlier intervals to address risk. Non-routine, ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores did not influence how detailed inspections of transmission assets in 2022 were sequenced. h) The drone inspection program began in 2019, and its scope included all distribution structures in Tier 2 and Tier 3 of the HFTD and coastal canyon areas within the WUI. SDG&E successfully completed this program in 2022 inspecting every structure in aforementioned regions. Circuit risk ranking in combination with a list of circuits that had previously been subject to a Public Safety Power Shutoff (PSPS) event was used to prioritize which circuits were inspected prior to others within that HFTD. For Tier 2 HFTD circuits, the circuit risk ranking was provided CALPA DR5 Q9. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores did not influence how aerial inspections of transmission assets in 2022 were sequenced. j) LiDAR inspections of distribution assets were captured for the entire HFTD. The sequencing of the work was not based on risk scores. The LiDAR data was captured by capturing all the circuits in a certain region to minimize the number of flights required to complete the data capture. k) SDG&E did not perform LiDAR inspections of transmission assets in 2022 except where there was distribution underbuilt on the structure. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2022 WMP | Wildfire Risk Score | N/A | N/A
14 | CalPA | 2023-03 | CalPA-2023-03 | 7 | CalPA-2023-03.7 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence where you plan to perform work in 2023. a) EVM b) Covered conductor installation c) Undergrounding d) Distribution pole replacement e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of distribution assets i) Aerial inspections of transmission assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request to the extent it misstates facts and/or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as part of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. While SDG&E’s EVM program does not scope work prioritizing circuit risk scores, it does focus on applying expanded post-trim clearances on targeted species identified as higher risk due to growth potential, failure characteristics, and relative outage frequency. The criteria for determining post‐trim clearances included multiple factors such as species, height, growth rate, health, location of defect, site conditions, pruning schedule, and proper pruning cuts. In 2023, SDG&E will continue to perform required clearing activities on subject poles located within the SRA as required by Public Resources Code Section 4292. The SRA does not align completely with the HFTD boundary, so as an extra precautionary measure, SDG&E will consider additional poles located outside SRA where Public Resources Code Section 4292 does not apply, including on poles located within the Local Responsibility Areas. Additionally in 2023, SDG&E will continue to perform vegetation fuels reduction activities surrounding poles located within the HFTD. For this activity, SDG&E does use the Circuit Risk Index and WiNGS modeling to determine areas to perform this work. b) Covered conductor installation Please see response 5 (b). c) Undergrounding Please see response 5 (b). d) SDG&E Distribution Pole Replacement does not utilize the modeled Wildfire Risk Scores to plan pole replacement work within specific circuits or circuit segments. The program will have multiple risk categories and will be prioritized based on these categories. • Phase 1 (approximately 85 poles): Pole set in concrete and steel reinforced or pole set in concrete and not steel reinforced • Phase 2 (approximately 58 poles): Pole set in soil and steel reinforced • Phase 3 (approximately 1,379 poles): Pole set in soil and not steel reinforced e) SDG&E Grid Sectionalization program receives feedback from meteorology for PSPS opportunities based on new grid hardening projects such as Covered Conductor and Strategic Undergrounding in addition to stand-alone switch installations. SDG&E District Engineers also perform evaluations on the value of new switches by prioritizing customer impacts; they provide recommendations based on historical events and submit work order requests for new installations. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. Per GO 165, detailed inspections of overhead facilities are currently completed on a 5-year cycle for all overhead structures, including those in the HFTD, and is not expected to change in 2023. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine where inspections are performed, non-routine, ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, SDG&E prioritizes detailed inspections in the HFTD prior to fire season. Detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence where detailed inspections of transmission assets in 2023 are performed. h) The structures selected for SDG&E’s 2023 aerial drone inspections are identified by using a semiautomated Inspection Prioritization Model that combines PoF and consequence of failure (CoF) to determine structure risk and account for navigation efficiency. The program considers the riskiest 15 percent of overhead distribution structures within the HFTD and WUI. The model aligns with existing methods considering MAVF to identify and quantify risk and is easily modified to account for new attributes or changes in scope. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence where aerial inspections of transmission assets in 2023 are performed. j) Because the entire HFTD was captured in 2022, a large-scale LiDAR collection initiative will not be implemented again for several years. However, LiDAR will continue to be captured to support pole loading calculations as needed for system hardening projects such as covered conductor and traditional overhead hardening, which are scoped in part utilizing modeled wildfire risk scores. LiDAR is needed to complete PLS-CADD during pre-construction and post-construction to verify compliance with GO95 and SDG&E standards and specifications. k) SDG&E will not perform LiDAR inspections of transmission assets in 2023. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2023 WMP | Wildfire Risk Score | N/A | N/A
15 | CalPA | 2023-03 | CalPA-2023-03 | 8 | CalPA-2023-03.8 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence how work in 2023 will be sequenced. a) EVM b) Covered conductor installation c) Undergrounding d) Distribution pole replacement e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of distribution assets i) Aerial inspections of transmission assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request to the extent it misstates facts and/or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as part of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. b) Covered conductor installation Please see response 6 (b). c) Undergrounding Please see response 6 (b). d) For the Distribution Pole Replacement Program, Phase 1 poles would be addressed first, followed by Phase 2 then Phase 3. However, permitting, land rights, environmental mitigation, customer concerns, or a combination of these factors will drive the ultimate schedule on each pole's replacement. Where feasible, poles will be bundled together in a single work package to minimize the impact to the community and gain efficiency in the design, environmental, permitting, land rights, and construction process. In most cases a single work order package will bundle poles that are adjacent or within a few spans of each other and will require similar land rights, permitting, and/or land rights. e) SDG&E Grid Sectionalization program is sequenced based on input from multiple stakeholders who determine where the greatest customer impacts can be realized. When this evaluation is performed in association with work being performed associated with hardening initiatives such as Covered Conductor or Strategic Undergrounding it is sequenced according to that program. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. GO 165 also prescribes the acceptable interval, a 4month period within the calendar year, which dictates the sequencing of inspections throughout the year and is not expected to change in 2023. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine the sequencing of inspections, SDG&E prioritizes detailed inspections in the HFTD prior to fire season and has shifted inspections into earlier intervals to address risk. Non-routine, ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence how detailed inspections of transmission assets in 2023 are sequenced. h) In 2023, the aerial drone inspection program considers the riskiest 15 percent of overhead distribution structures within the HFTD and WUI as described in Response 7h. The sequencing of these inspections is determined by navigation efficiencies and obtaining necessary landowner authorizations. For example, inspections within Department of Defense areas require waiver approval by the board and permission by the base depending on the area within the based that flights are requested. In addition, we have specific authorization to perform inspections on State Parks lands and need to provide advance notification with U.S. Forest Service, Bureau of Land Management, Tribal Governments and other entities, such as water districts. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence how aerial inspections of transmission assets in 2023 are sequenced. j) Because the entire HFTD was captured in 2022, a large-scale LiDAR collection initiative will not be implemented again for several years. However, LiDAR will continue to be captured to support pole loading calculations as needed for system hardening projects such as covered conductor and traditional overhead hardening, which are scoped in part utilizing modeled wildfire risk scores. LiDAR is needed to complete PLS-CADD during pre-construction and post-construction to verify compliance with GO95 and SDG&E standards and specifications. k) SDG&E will not perform LiDAR inspections of transmission assets in 2023. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2023 WMP | Wildfire Risk Score | N/A | N/A
16 | CalPA | 2023-03 | CalPA-2023-03 | 9 | CalPA-2023-03.9 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence where you plan to perform work in 2024. l) EVM m) Covered conductor installation n) Undergrounding o) Distribution pole replacement p) Grid sectionalization q) Detailed inspections of distribution assets r) Detailed inspections of transmission assets s) Aerial inspections of distribution assets t) Aerial inspections of transmission assets u) LiDAR inspections of distribution assets v) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request to the extent it misstates facts and/or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as part of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. While SDG&E’s EVM program does not scope work prioritizing circuit risk scores, it does focus on applying expanded post-trim clearances on targeted species identified as higher risk due to growth potential, failure characteristics, and relative outage frequency. The criteria for determining post‐trim clearances included multiple factors such as species, height, growth rate, health, location of defect, site conditions, pruning schedule, and proper pruning cuts. In 2024, SDG&E will continue to perform required clearing activities on subject poles located within the SRA as required by Public Resources Code Section 4292. The SRA does not align completely with the HFTD boundary, so as an extra precautionary measure, SDG&E will consider additional poles located outside SRA where Public Resources Code Section 4292 does not apply, including on poles located within the Local Responsibility Areas. Additionally in 2024, SDG&E will continue to perform vegetation fuels reduction activities surrounding poles located within the HFTD. For this activity, SDG&E does use the Circuit Risk Index and WiNGS modeling to determine areas to perform this work. b) Covered conductor installation Please see response 5 (b). c) Undergrounding Please see response 5 (b). d) SDG&E Distribution Pole Replacement does not utilize the modeled Wildfire Risk Scores to plan pole replacement work within specific circuits or circuit segments. The program will have multiple risk categories and will be prioritized based on these categories. • Phase 1 (approximately 85 poles): Pole set in concrete and steel reinforced or pole set in concrete and not steel reinforced • Phase 2 (approximately 58 poles): Pole set in soil and steel reinforced • Phase 3 (approximately 1,379 poles): Pole set in soil and not steel reinforced e) SDG&E Grid Sectionalization program receives feedback from meteorology for PSPS opportunities based on new grid hardening projects such as Covered Conductor and Strategic Undergrounding in addition to stand-alone switch installations. SDG&E District Engineers also perform evaluations on the value of new switches by prioritizing customer impacts; they provide recommendations based on historical events and submit work order requests for new installations. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. Per GO 165, detailed inspections of overhead facilities are currently completed on a 5-year cycle for all overhead structures, including those in the HFTD, and is not expected to change in 2024. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine where inspections are performed, non-routine, ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, SDG&E prioritizes detailed inspections in the HFTD prior to fire season. Detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence where detailed inspections of transmission assets in 2024 are performed. h) The structures selected for SDG&E’s 2024 aerial drone inspections will be identified using a semiautomated Inspection Prioritization Model that combines PoF and consequence of failure (CoF) to determine structure risk and account for navigation efficiency. The program considers the riskiest 15 percent of overhead distribution structures within the HFTD and WUI. The model aligns with existing methods considering MAVF to identify and quantify risk and is easily modified to account for new attributes or changes in scope. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence where aerial inspections of transmission assets in 2024 are performed. j) Because the entire HFTD was captured in 2022, a large-scale LiDAR collection initiative will not be implemented again for several years. However, LiDAR will continue to be captured to support pole loading calculations as needed for system hardening projects such as covered conductor and traditional overhead hardening, which are scoped in part utilizing modeled wildfire risk scores. LiDAR is needed to complete PLS-CADD during pre-construction and post-construction to verify compliance with GO95 and SDG&E standards and specifications. k) SDG&E will not perform LiDAR inspections of transmission assets in 2024. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2024 WMP | Wildfire Risk Score | N/A | N/A
17 | CalPA | 2023-03 | CalPA-2023-03 | 10 | CalPA-2023-03.10 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence how work in 2024 will be sequenced. a) EVM b) Covered conductor installation c) Undergrounding d) Distribution pole replacement e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of distribution assets i) Aerial inspections of transmission assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request to the extent it misstates facts and/or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as part of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. b) Covered conductor installation Please see response 6 (b). c) Undergrounding Please see response 6 (b). d) For the Distribution Pole Replacement Program, Phase 1 poles would be addressed first, followed by Phase 2 then Phase 3. However, permitting, land rights, environmental mitigation, customer concerns, or a combination of these factors will drive the ultimate schedule on each pole's replacement. Where feasible, poles will be bundled together in a single work package to minimize the impact to the community and gain efficiency in the design, environmental, permitting, land rights, and construction process. In most cases a single work order package will bundle poles that are adjacent or within a few spans of each other and will require similar land rights, permitting, and/or land rights. e) SDG&E Grid Sectionalization program is sequenced based on input from multiple stakeholders who determine where the greatest customer impacts can be realized. When this evaluation is performed in association with work being performed associated with hardening initiatives such as Covered Conductor or Strategic Undergrounding it is sequenced according to that program. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. GO 165 also prescribes the acceptable interval, a 4month period within the calendar year, which dictates the sequencing of inspections throughout the year and is not expected to change in 2024. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine the sequencing of inspections, SDG&E prioritizes detailed inspections in the HFTD prior to fire season and has shifted inspections into earlier intervals to address risk. Non-routine, ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence how detailed inspections of transmission assets in 2024 are sequenced. h) In 2024, the aerial drone inspection program will consider the riskiest 15 percent of overhead distribution structures within the HFTD and WUI as described in Response 9h. The sequencing of the work will be performed as described in response in 8h, the sequencing of these inspections will be determined by navigation efficiencies and obtaining necessary landowner authorizations. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence how aerial inspections of transmission assets in 2023 are sequenced. j) Because the entire HFTD was captured in 2022, a large-scale LiDAR collection initiative will not be implemented again for several years. However, LiDAR will continue to be captured to support pole loading calculations as needed for system hardening projects such as covered conductor and traditional overhead hardening, which are scoped in part utilizing modeled wildfire risk scores. LiDAR is needed to complete PLS-CADD during pre-construction and post-construction to verify compliance with GO95 and SDG&E standards and specifications. k) SDG&E will not perform LiDAR inspections of transmission assets in 2024. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2024 WMP | Wildfire Risk Score | N/A | N/A
18 | CalPA | 2023-04 | CalPA-2023-04 | 1 | CalPA-2023-04.1 | For any WMP initiative for which you forecast capital expenditures in 2023 to be at least two times actual capital expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: 1. a. Emergency preparedness plan b. WMP.1008 c. Community outreach, public awareness, and communications efforts d. 7.3.9.2 e. The projected increase is related to construction of the Wildfire and Climate Resilience Center (WCRC). The construction costs are a one-time expense that are expected to be mostly spent in 2023. Information on the WCRC will be reported in SDG&E’s 2023 WMP in section 8.4.3.4. 2. a. Transmission OH Hardening – Distribution Underbuild b. WMP.545 c. Overhead transmission fire hardening (Distribution Underbuilt) d. 7.3.3.17.2.3 e. The expected construction in 2022 experienced permitting delays resulted in lower construction costs. SDG&E only completed 0.6 miles of hardening for this initiative in 2022 which drove the lower than expected spend in 2022. 3. a. Microgrids b. WMP.462 c. Microgrids d. 7.3.3.8.2 e. SDG&E experienced delays acquiring appropriate and sufficient land rights for the microgrid projects and has been delayed in deploying the permanent renewable solutions. This has shifted spend from 2022 into 2023 and 2024. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-04.pdf | 0 | No | 2023 WMP | Capital Expenditure | N/A | N/A
19 | CalPA | 2023-04 | CalPA-2023-04 | 2 | CalPA-2023-04.2 | For any WMP initiative for which you forecast capital expenditures in 2024 to be at least two times actual capital expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: 1. a. Strategic Undergrounding b. WMP.473 c. Undergrounding of electric lines and/or equipment d. 7.3.3.16 e. The number of miles completed for strategic undergrounding is increasing from 65 miles completed in 2022 to 125 miles planned for 2024. 2. a. Transmission OH Hardening – Distribution Underbuild b. WMP.545 c. Overhead transmission fire hardening (Distribution Underbuilt) d. 7.3.3.17.2.3 e. The expected construction in 2022 experienced permitting delays and resulted in lower construction costs. SDG&E only completed 0.6 miles of hardening for this initiative in 2022 which drove the lower than expected spend in 2022. 3. a. Microgrids b. WMP.462 c. Microgrids d. 7.3.3.8.2 e. SDG&E experienced delays acquiring appropriate and sufficient land rights for the microgrid projects and has been delayed in deploying the permanent renewable solutions. This has shifted spend from 2022 into 2023 and 2024. 4. a. Environmental monitoring systems (Advanced weather monitoring) b. WMP.447 c. Advanced weather monitoring and weather stations d. 7.3.2.1 e. SDG&E plans to continue improvements to the weather station network such as upgrading batteries, charging regulators, and enhancing weather sensor dashboards. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-04.pdf | 0 | No | 2024 WMP | Capital Expenditure | N/A | N/A
20 | CalPA | 2023-04 | CalPA-2023-04 | 3 | CalPA-2023-04.3 | For any WMP initiative for which you forecast operating expenditures in 2023 to be at least two times actual operating expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: 1. a. Strategic Undergrounding b. WMP.473 c. Undergrounding of electric lines and/or equipment d. 7.3.3.16 e. SDG&E had lower than expected operating expenditures (0.14% of capital expenditure) for undergrounding completed in 2022. SDG&E expects operating expenditures to increase to 0.2% of capital expenditures in 2023. 2. a. Early Fault Detection b. WMP.1195 c. N/A (was included within Installation of system automation equipment) d. N/A (was included within 7.3.3.9) e. Early Fault Detection is a relatively new program and only incurred operating expenses of one thousand dollars in 2022. As the program grows and more sensors are installed, and more data is ingested, the operating expenses will increase. 3. a. A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment b. WMP.442 c. A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment d. 7.3.1.1 e. The increased costs associated with this initiative are driven by higher expected labor costs in 2023 associated with additional full time employees that started halfway through 2022 and four additional employees with a planned start date in the second quarter of 2023. Non-labor costs also increase for this initiative as there are additional expenses for contractors associated with developing and validating SDG&E’s risk modeling. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-04.pdf | 0 | No | 2023 WMP | Capital Expenditure | N/A | N/A
21 | CalPA | 2023-04 | CalPA-2023-04 | 4 | CalPA-2023-04.4 | For any WMP initiative for which you forecast operating expenditures in 2024 to be at least two times actual operating expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: 1. a. Avian Protection b. WMP.972 c. Avian Mitigation d. 7.3.3.18.3 e. SDG&E had lower than expected operating expenditures (0.86% of capital expenditure) for the avian protection work completed in 2022. SDG&E expects operating expenditures to increase to 4% of capital expenditures in 2024. 2. a. Generator Grant Program b. WMP.466 c. Generator Grant Program d. 7.3.3.11.1 e. SDG&E had lower than expected expenditures associated with the Generator Grant Program in 2022 because SDG&E did not experience any PSPS events. The lack of PSPS activations drove participation in SDG&E’s resiliency programs down in 2022. Expenditures in 2024 are expected to return to normal levels of participation assuming PSPS activations return to average levels. 3. a. Generator Assistance Program b. WMP.467 c. Generator Assistance Program d. 7.3.3.11.3 e. SDG&E had lower than expected expenditures associated with the Generator Assistance Program in 2022 because SDG&E did not experience any PSPS events. The lack of PSPS activations drove participation in SDG&E’s resiliency programs down in 2022. Expenditures in 2024 are expected to return to normal levels of participation assuming PSPS activations return to average levels. 4. a. Strategic Undergrounding b. WMP.473 c. Undergrounding of electric lines and/or equipment d. 7.3.3.16 e. SDG&E had lower than expected operating expenditures (0.14% of capital expenditure) for undergrounding completed in 2022. SDG&E expects operating expenditures to increase to approximately 1% of capital expenditures in 2024. 5. a. Early Fault Detection b. WMP.1195 c. N/A (was included within Installation of system automation equipment) d. N/A (was included within 7.3.3.9) e. Early Fault Detection is a relatively new program and only incurred operating expenses of one thousand dollars in 2022. As the program grows and more sensors are installed, and more data is ingested, the operating expenses will increase. 6. a. Allocation methodology development and application b. WMP.523 c. Allocation methodology development and application d. 7.3.8.1 e. SDG&E had lower than expected operating expenditures for this initiative in 2022 due to lower than planned labor costs. SDG&E expects to hire additional FTEs in 2024 to assist with additional workload including wildfire mitigation personnel, risk management, and PSPS. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-04.pdf | 0 | No | 2024 WMP | Capital Expenditure | N/A | N/A
22 | CalPA | 2023-05 | CalPA-2023-05 | 1 | CalPA-2023-05.1 | a) Have you identified transportation corridors within your service territory where falling or failing lines or poles could currently limit egress and/or ingress during an emergency? b) If the answer to part (a) is yes, please describe how you identify such transportation corridors. c) If available, please provide a geospatial data file that contains all current identified transportation corridors with ingress and egress hazards. | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Corridors in SDG&E’s service territory where asset failure could limit egress/ingress during an emergency have not been identified. SDG&E is prepared to support the needs of first responders through participation in the County Evacuation Committee, the staffing of 24/7 response staff to respond to incidents, and regular training with first responder agencies. During real world incidents requiring evacuation, SDG&E serves as a cooperator at the incident command post and follows the ICS command structure to ensure life safety is the highest priority. b) N/A c) N/A | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf | 0 | No | Other | Egress | N/A | N/A
23 | CalPA | 2023-05 | CalPA-2023-05 | 2 | CalPA-2023-05.2 | In response to Data Request CalAdvocates-SDG&E-2022WMP-13 on March 30, 2022, SDG&E provided information regarding its Wildfire Risk Reduction Model (WRRM-Ops) and stated “Currently the Technosylva Wildfire Analyst Enterprise software does not incorporate suppression effectiveness into simulations. However, development of a suppression effectiveness model is currently underway and being tested for implementation during the California 2022 fire season.” a) What is the current status of the effort to develop a suppression effectiveness model described in the quote above? b) Has SDG&E updated its WRRM-Ops model since its response referenced above, to incorporate fire suppression effectiveness? c) If the answer it part (b) is yes, when did SDG&E start to incorporate the additional factor of fire suppression effectiveness into its wildfire risk simulations? | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Due to the number of variables that would go into accurate suppression modeling and that these variables would be significantly impacted by human and other factors it has been determined that incorporating suppression into operational models can create issues when applying model outputs to real world outcomes. WFA does model what is named their Initial Attack Index and is referenced in the CalAdvocates-SDG&E-2022WMP-13, from available inputs which may enable a SME to estimate the effectiveness of suppression. Factors that are considered by a SME include but are not limited to staffing levels, location relative to responding resources, other active incidents, and the accessibility of the incident. By excluding suppression, model outputs can more effectively be compared to each other because of consistent assumptions. It is also important to remember that the operational picture may change minute to minute and tactical actions taken in the field are typically based on real world observation. b) No, see answer a. c) NA | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf | 0 | No | Other | CalAdvocates-SDG&E-2022WMP-13 | N/A | N/A
24 | CalPA | 2023-05 | CalPA-2023-05 | 3 | CalPA-2023-05.3 | Provide an Excel table of all distribution circuit-segments that traverse HFTD areas (i.e., the segment has greater than 0 circuit-miles in HFTD) existing as of January 1, 2023. The Excel table should list each such circuit-segment as a row and include the following information in separate columns. For items (n) and (r), please include all relevant risk scores. For example, include vegetation risk score, conductor risk score, and any other driver-specific risk scores you have developed. Please insert additional columns as needed to accommodate this: a) Circuit name for the circuit that each segment is part of b) Circuit ID for the circuit that each segment is part of c) Name or ID number of each circuit segment d) Nominal voltage e) Total circuit-miles on the circuit-segment f) Overhead circuit-miles on the circuit-segment in Non-HFTD Areas g) Overhead circuit-miles on the circuit-segment in HFTD Tier 2 h) Overhead circuit-miles on the circuit-segment in HFTD Tier 3 i) Underground circuit-miles on the circuit-segment in Non-HFTD Areas j) Underground circuit-miles on the circuit-segment in HFTD Tier 2 k) Underground circuit-miles on the circuit-segment in HFTD Tier 3 l) Probability of ignition score for the circuit-segment, according to the risk model you used for your 2022 WMP filing m) Consequence of ignition score for the circuit-segment, according to the risk model you used for your 2022 WMP filing n) Total wildfire risk score(s) for the circuit-segment, according to the risk model you used for your 2022 WMP filing. Insert additional columns if needed o) Power Safety Power Shutoff (PSPS) risk score for the circuit-segment, according to the risk model you used for your 2022 WMP filing p) Probability of ignition score for the circuit-segment, according to the risk model you are using for your 2023-2025 WMP filing q) Consequence of ignition score for the circuit-segment, according to the risk model you are using for your 2023-2025 WMP filing r) Total wildfire risk score(s) for the circuit-segment, according to the risk model you are using for your 2023-2025 WMP filing. Insert additional columns if needed s) Power Safety Power Shutoff (PSPS) risk score for the circuit-segment, according to the risk model you are using for your 2023-2025 WMP filing. | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see attachment named “dr_ca_5_q3_nb_output_RDF_2023_03_03.xlsx” Circuit/segment IDs are reflective of the current state of the system, segment configuration and mileage. Risk scores from the 2023-2025 WMP used WiNGS 3.0 model version and risk scores from the 2022 WMP correlate to WiNGS 1.0 model version. Each risk score field is suffixed with its corresponding model version for clarity. A column header with the requested attributes is provided above the SDG&E report’s column headers to help correlate the results to the original request. While the risk scores for both model versions have been provided, direct comparison of these risk scores cannot be done effectively due to changing risk in the territory, system configuration changes, and updates between versions. Each model version contains several enhancements to improve risk quantification which adjust the risk scores. The models should be viewed as independent of each other with separate temporal and logical constraints. | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf https://www.sdge.com/sites/default/files/regulatory/dr_ca_5_q3_nb_output_RDF_2023_03_03_Q3.xlsx | 1 | No | Other | Circuits | N/A | N/A
25 | CalPA | 2023-05 | CalPA-2023-05 | 4 | CalPA-2023-05.4 | Provide a geodatabase file containing the outputs from your current wildfire risk model (i.e., the model you are using for your 2023-2025 WMP filing), at the circuit-segment level. (This data should be equivalent to the previous question, but in GIS format.) Please provide, as line features, the most recent spatial data for all circuit segments for which your current risk model calculates circuit segment-level expected risk (i.e., probability of ignition multiplied by the consequence of ignition). Include the following attributes for each circuit segment: a) Items (a) through (c) of the previous question b) Items (p) through (s) of the previous question. | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see “WMP_DR_CA_05_Q4.gdb.7z.” The attached zipped gdb file is encrypted according to SDG&E’s GIS electric data policy. The cypher for this gdb is WmPwMpWMPwmp1! This gdb contains records from question 3 joined to the segments in the wings_circuit_segment feature class. A single record in the table from question 3 will typically join to two records in the feature class because the feature class contains two records per segment, one for overhead and one for underground. | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf https://www.sdge.com/sites/default/files/regulatory/WMP_DR_CA_05_Q4.gdb_.7z | 1 | No | 2023 WMP | Wilfire Risk Model | N/A | N/A
26 | CalPA | 2023-05 | CalPA-2023-05 | 5 | CalPA-2023-05.5 | Please fill out the attached spreadsheet, CalAdvocates-SDGE-2023WMP-05_Attachment, Tab 1, requesting information regarding your asset inspections in 2022. | Please see “CalAdvocates-SDGE-2023WMP-05_Q5.xlsx” | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf https://www.sdge.com/sites/default/files/regulatory/CalAdvocates-SDGE-2023WMP-05_Q5.xlsx | 1 | No | Other | CalAdvocates-SDGE-2023WMP-05 | N/A | N/A
27 | CalPA | 2023-05 | CalPA-2023-05 | 6 | CalPA-2023-05.6 | Please augment Table 13 of the non-spatial data tables in your WMP Quarterly Data Report for Q4 of 2022, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. Add the following information in separate columns: a) Name of the associated circuit b) ID number of the associated circuit c) Geographic latitude in decimal degrees, truncated to seven decimal places d) Geographic longitude in decimal degrees, truncated to seven decimal places e) Object/damage code or other internal SDG&E description of defect. | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Additional columns were added in the file “ Copy of Table 13 Q4 2022 QDR Submission_Q6.xlsx” and can be found in the orange columns “M-Q.” It should be noted that circuit information on structures that are not associated to a primary distribution circuit are shown as “N/A”. Where circuit name is “Stub Pole” the corresponding structure does not have an associated circuit. Additionally, the locations (latitude and longitude) of assets that are 230 kV or above are not included due to confidentiality. | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf https://www.sdge.com/sites/default/files/regulatory/Copy%20of%20Table%2013%20Q4%202022%20QDR%20Submission_Q6.xlsx | 1 | No | Other | QDR | N/A | N/A
28 | CalPA | 2023-05 | CalPA-2023-05 | 7 | CalPA-2023-05.7 | Regarding Table 13 of the non-spatial data tables in your WMP Quarterly Data Report for Q4 of 2022: a) In column “f. Due date of the original work order,” there are four rows with a due date of “#”. Please explain what this means or correct those entries. b) In column “f. Due date of the original work order,” the majority of the rows list the due date as “N/A.” Please explain why these work orders have no due date. c) In column “g. GO 95 rule 18 priority level of the original work order,” the majority of the rows list the priority level as “N/A.” Please explain why these work orders have no priority level. d) Does SDG&E have an internal system of priority levels for corrective notifications that differs from the system of priority levels specified in GO 95 Rule 18? e) If the answer to part (d) is yes, please explain SDG&E’s internal priority system. f) Does SDG&E ever re-inspect corrective notifications before they are resolved? g) If the answer to part (f) is yes, under what circumstances does SDG&E conduct re-inspections? | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Three of the four entries were inadvertently included in Table 13. Work order numbers 101797, 126966, and 90774 are work orders assigned to third party communications infrastructure providers to perform corrective work and are not work orders for which SDG&E is responsible. The fourth work order, 129910, was also inadvertently included at the time of reporting due to timing of the business process. The order was in the process of being evaluated to assign a due date, and thus should not have been included in Table 13. Table 13 will be amended to exclude these four work orders and will be submitted to Energy Safety per revision guidelines. b) The 8,581 work orders with “N/A” as the due date of the original work order are work orders that resulted from drone inspections. Because drone inspections are supplemental inspections to routine detailed and patrol inspections mandated under GO 165 and part of our auditable corrective maintenance program, there is no mandatory due date associated. However, SDG&E evaluates drone inspection findings, generates corrective work orders, and prioritizes the work with the remaining backlog of corrective work. c) The 8,581 work orders with N/A as the GO 95 rule 18 priority level are work orders that resulted from drone inspections. Because drone inspections are supplemental inspections to routine detailed and patrol inspections mandated under GO 165 and part of our auditable corrective maintenance program, there is no associated GO 95 rule 18 priority level. However, SDG&E evaluates drone inspection findings, generates corrective work orders, and prioritizes the work with the remaining backlog of corrective work. d) Yes, SDG&E utilizes internal severity levels for distribution drone inspections. Work orders resulting from distribution drone inspections are prioritized based on severity using the following designations at the time of inspection: Emergency, Priority, and NonCritical. Emergency work orders are completed immediately (typically within 1-3 days) and Priority work orders are prioritized over Non-Critical work orders during both engineering/design and construction phases. e) Yes. f) Work orders resulting from routine inspections are subject to a deferral approval process with management personnel if warranted under reasonable circumstances. Each deferral request is reviewed, and various factors are considered prior to approval, such as the reason for the delay and any potential safety concerns including anticipated weather conditions and current condition of the underlying issue. As part of that review, the issue may be re-assessed for safety to ensure the priority level of the corrective work remains appropriately assigned since the issue was first identified. In addition, SDG&E performs pre-event patrols and may review the condition of facilities associated with open work orders prior to and after certain weather events. Again, this is dependent on the type of work order and whether that work order is associated with a condition (e.g. crossarm damage versus missing signage) that could pose a safety risk. | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf | 0 | No | Other | QDR | N/A | N/A
29 | CalPA | 2023-06 | CalPA-2023-06 | 1 | CalPA-2023-06.1 | Provide your workplan that describes where you will undertake EVM projects in 2023. This workplan should be in an Excel format, with circuit-segments as rows. Please include the following information in separate columns in the Excel spreadsheet at a minimum: a) Circuit name b) Circuit ID number c) Circuit-segment name d) Circuit-segment ID number e) EVM miles to be completed in 2023 f) Risk ranking of the circuit-segment. | SDG&E does not annually forecast where specific EVM projects will occur. The pre-inspection and tree trim activities follow an annual master schedule based on the Vegetation Management Area (VMA). The exact locations where EVM tree trim clearances will be performed are unknown until after the pre-inspection activity occurs and the trimming is completed. The tree trimmer determines which trees will require greater clearances based on multiple criteria including species, growth rate, tree health, and proper pruning practices. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | EVM | N/A | N/A
30 | CalPA | 2023-06 | CalPA-2023-06 | 2 | CalPA-2023-06.2 | Provide your workplan that describes where you will undertake EVM projects in 2024. This workplan should be in an Excel format, with circuit-segments as rows. Please include the following information in separate columns in the Excel spreadsheet at a minimum:. a) Circuit name b) Circuit ID number c) Circuit-segment name d) Circuit-segment ID number e) EVM miles to be completed in 2024 f) Risk ranking of the circuit-segment. | Please see response to Question 1. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | EVM | N/A | N/A
31 | CalPA | 2023-06 | CalPA-2023-06 | 3 | CalPA-2023-06.3 | Please provide a list of any incidents in 2022 where the actions of a VM contractor posed a safety risk to workers and/or the public. “Safety risk” here is defined as any occurrence on a worksite where the contractor’s actions created a safety hazard for either workers or the general public. For each instance, please provide: a) The date you were informed of the safety issue b) The date that the original work that created the safety issue was performed c) Whether the safety issue concerned a transmission or distribution circuit d) The vegetation management initiative involved in the original work e) A brief description of the safety issue involved. | Please see attachment titled, “SDGEResponse_CalAdvocates_DR-06.xlsx” at the tab for response 3. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06%20Attachment%20Q3.xlsx | 1 | No | Other | Vegetation Management | N/A | N/A
32 | CalPA | 2023-06 | CalPA-2023-06 | 4 | CalPA-2023-06.4 | Provide your workplan that describes where and when you will perform system hardening on distribution circuits in 2023. For projects that you expect to partially complete in 2023 (i.e., projects that started before 2023 and are expected to continue in 2023, or projects that are expected to be completed after 2023), please include the project and report the work what you forecast will actually be performed in calendar year 2023. For each project, include the following information in separate columns, at a minimum: a) Order number b) Program c) Circuit ID number d) Circuit-segment name or ID number (if the project affects more than one circuit-segment, please identify each one) e) Relevant wildfire risk score(s) from the wildfire risk model that you are using to estimate distribution risk in your 2023-2025 WMP filing f) The expected or actual start date of the project g) The expected completion date of the project h) Length (in circuit miles) of covered conductor to be installed in 2023 i) Length (in circuit miles) of underground conductor to be installed in 2023 j) Length (in circuit miles) of overhead conductor to be permanently removed in 2023 and replaced by underground conductor (note that this may differ slightly from the previous item due to differing overhead and underground routes) k) Length (in circuit miles) of overhead conductor to be permanently removed in 2023 and not replaced with covered conductor or undergrounded) l) Length (in circuit miles) of any bare-wire overhead system hardening project to be installed in 2023 (if this is greater than zero, please describe the type of system hardening project) m) Length (in circuit miles) of any other type of system hardening project to be installed in 2023 (if this is greater than zero, please describe the type of system hardening project). | Please see attachment titled, “SDGEResponse_CalAdvocates_DR-06.xlsx” at the tab for response 4. 8 | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | System hardening | N/A | N/A
33 | CalPA | 2023-06 | CalPA-2023-06 | 5 | CalPA-2023-06.5 | Provide your workplan that describes where and when you will perform system hardening on distribution circuits in 2024. For projects that you expect to partially complete in 2024 (i.e., projects that are expected to start before 2024 and are expected to continue in 2024, or projects that are expected to be completed after 2024), please include the project and report the work that you forecast will actually be performed in calendar year 2024. For each project, include the following information in separate columns, at a minimum: a) Order number b) Program c) Circuit ID number d) Circuit-segment name or ID number (if the project affects more than one circuit-segment, please identify each one) e) Relevant wildfire risk score(s) from the wildfire risk model that you are using to estimate distribution risk in your 2023-2025 WMP filing f) The expected or actual start date of the project g) The expected completion date of the project. h) Length (in circuit miles) of covered conductor to be installed in 2024 i) Length (in circuit miles) of underground conductor to be installed in 2024 j) Length (in circuit miles) of overhead conductor to be permanently removed in 2024 and replaced by underground conductor (note that this may differ slightly from the previous item due to differing overhead and underground routes) k) Length (in circuit miles) of overhead conductor to be permanently removed in 2024 and not replaced with covered conductor or undergrounded) l) Length (in circuit miles) of any bare-wire overhead system hardening project to be installed in 2024 (if this is greater than zero, please describe the type of system hardening project) m) Length (in circuit miles) of any other type of system hardening project to be installed in 2024 (if this is greater than zero, please describe the type of system hardening project). | Please see attachment titled, “SDGEResponse_CalAdvocates_DR-06.xlsx” at the tab for response 5. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | System hardening | N/A | N/A
34 | CalPA | 2023-06 | CalPA-2023-06 | 6 | CalPA-2023-06.6 | For each of your 2023-2025 WMP system hardening initiatives, please provide disaggregated information related to expenditures and circuit miles treated in the attached table, CalAdvocates- SDGE-2023WMP-06_Attachment, Tab 1. Add columns as needed. | Relocation of Overhead to Underground (refer to cost break-out for WMP.473 of Table 11 submitted to OEIS and Table 8-3 of 2023 WMP Filing ) – The combined expenditures for both Capital and Operating expense for the 2022-2024 timeframe are as follows: $126.9M for 2022 ($126.7M capital, $0.2M Opex), $196.6M for 2023 ($196.2M Capital, $0.4M Opex), and $295M for 2024 ($292M Capital, $3M Opex). These expenditures will support the completion of 65 miles in 2022, 84 miles in 2023, and 125 miles in 2024. Covered Conductor (refer to cost break-out for WMP.455 of Table 11 submitted to OEIS and Table 8-3 of 2023 WMP Filing) – The combined expenditures for both Capital and Operating expense for the 2022-2024 timeframe are as follows: $93M for 2022 ($90M capital, $3M Opex), $79M for 2023 ($76.8M Capital, $2.2M Opex), and $59.8M for 2024 ($59.2M Capital, $0.6M Opex). These expenditures will support the completion of 63 miles for the 2022 and 60 miles each for the 2023-2024 timeframe. Traditional Hardening (refer to cost break-out for WMP.475 of Table 11 submitted to OEIS and Table 8-3 of 2023 WMP Filing) – The combined expenditures for both Capital and Operating expense for the 2022-2024 timeframe are as follows: $26.5M for 2022 ($23.3M capital, $3.2M Opex), $3.8M for 2023 ($2M Capital, $1.8M Opex), and $0.9M for 2024 ($0.8M Capital, $0.1M Opex). These expenditures will support the completion of 27 miles in 2022, and 2 miles in 2023. Distribution Underbuild (refer to cost break-out for WMP.545 of Table 11 submitted to OEIS and Table 8-3 of 2023 WMP Filing) – This initiative is capital only. The total expenditures for the 2022-2024 timeframe are as follows: $3.2M for 2022, $11.4M for 2023, and $14.8M for 2024. These expenditures will support the completion of 0.6 miles in 2022, 7 miles in 2023, and 1 mile in 2024. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | 2023 WMP | System hardening initiatives | N/A | N/A
35 | CalPA | 2023-06 | CalPA-2023-06 | 7 | CalPA-2023-06.7 | Please provide a spreadsheet listing (as rows) each undergrounding project completed during the period of January 1, 2022, through December 31, 2022. For each project, please provide the following information (as columns): a) Project ID number or other identifier b) Circuit ID c) ID of each circuit segment that was entirely undergrounded in the project d) ID of each circuit segment that was partially undergrounded in the project e) County or counties where undergrounding took place f) Project start date g) Project completion date h) Total circuit-miles undergrounded i) Total miles of trenching required j) Total life-cycle electric costs5 of the project (i.e., costs attributed to your electric facilities), including costs for planning, design, permitting, and construction k) Total life-cycle costs of the project, including costs attributed to non-electric utilities, including costs for planning, design, permitting, and construction l) Whether this was a Rule 20 project (yes/no) m) Whether this was a WMP project (yes/no) n) Whether this was a post-wildfire rebuild project (yes/no) o) Whether you shared trenches for this project with any telecommunications utilities (yes/no) p) Whether you shared trenches for this project with gas facilities (yes/no). | Please see attachment titled, “SDGEResponse_CalAdvocates_DR-06.xlsx” at the tab for response 7. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06%20Attachment%20Q7.zip | 1 | No | Other | Undergrounding | N/A | N/A
36 | CalPA | 2023-06 | CalPA-2023-06 | 8 | CalPA-2023-06.8 | Please provide a geodatabase file with a polyline feature for each undergrounding project completed during the period of January 1, 2022 through December 31, 2022. In addition to the spatial location, please provide the following attributes for each project: a) Project ID number or other identifier, matching part (a) of the previous question b) Circuit ID c) Project completion date. | Please see “CalPA_DR06_Question7.zip.” | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | Geodatabase-Undergrounding | N/A | N/A
37 | CalPA | 2023-06 | CalPA-2023-06 | 9 | CalPA-2023-06.9 | Identify any ignitions in 2022 associated with assets where you had an existing corrective notification at the time of the ignition. Please provide a spreadsheet listing each such ignition (as rows) with the following information in separate columns: a) Unique ignition ID b) Date of ignition c) Cause of ignition d) Type of asset associated with the ignition e) Acres burned f) Number of structures burned, if any g) Number of injuries associated with ignition, if any h) Asset ID of asset associated with ignition i) Circuit ID number of circuit associated with ignition j) Notification number(s) for the existing maintenance tag on the asset in question. | SDG&E did not experience any ignitions in 2022 associated with assets with an existing corrective notification at the time of ignition. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | Ignitions | N/A | N/A
38 | CalPA | 2023-06 | CalPA-2023-06 | 10 | CalPA-2023-06.10 | Regarding your PSPS circuit modeling capabilities: a) Please describe your present circuit modeling capabilities with regard to PSPS decisionmaking (“PSPS circuit modeling capabilities”), including with what level of granularity they are able to determine how circuit hardening efforts or other changes to a line segment will affect PSPS thresholds. b) Please describe any improvements to the present PSPS circuit modeling capabilities that you expect to implement in 2023. c) Please describe any improvements to the present PSPS circuit modeling capabilities that you expect to implement in 2024. d) Please describe the expected state of your PSPS circuit modeling capabilities at the conclusion of the 2023-2025 WMP cycle. | a) For the WiNGS-Planning Model, the PSPS risk is calculated at the segment level and is influenced by the maximum upstream segment PSPS probability. Mitigations that occur upstream of segments will also influence the risk of PSPS on downstream segments. Thus, the PSPS impact on a segment cannot be viewed in isolation and must be considered in the context of the electric network (other segments on the same circuit with their respective mitigations). When a segment is fully undergrounded back to the substation, the model would consider the risk of PSPS to be removed. When a segment is mitigated with covered conductor, we consider the PSPS threshold to be reduced based on associated wind alert speed updates. For WiNGS-Ops, models are developed at the segment level and take as inputs the circuit characteristics at the time that the model is run, which can be as granular as daily. Therefore, circuit hardening or other changes to a line segment, once recorded in SDG&E’s analytical data warehouses, are immediately reflected in WiNGS-Ops model outputs, which influences the decision to de-energize. Segments that have been hardened will show a lower quantified risk score, thereby lowering PSPS thresholds. b) The following updates are expected in 2023 for WiNGS-Planning: The current PSPS likelihood assessment is relatively new and is expected to be revamped in the current WMP cycle. Future enhancements already identified will include how weather conditions and ignition risk affect the annual likelihood of implementing PSPS. Although in the WiNGS-Planning Model the PSPS consequence assessment considers type of customers, it can be improved with further development of social vulnerability or availability of redundant back-up power systems that could reduce the impacts of a PSPS. The following updates are expected in 2023 for WiNGS-Ops : • Create PSPS scenarios with different event durations. • Revisit Subject Matter Expert AFN customer scaling factors in the Safety component. • Revisit Safety assumption of fatalities per customer minutes de-energized. • Review and update existing Financial assumptions. • Review and update existing Reliability assumptions. c) The following updates are expected in 2024 for WiNGS-Planning: • SDG&E will develop a model to estimate PSPS duration for all customer segments. • SDGE& will develop an egress model to capture PSPS hazard and exposure potential • SDG&E will incorporate community vulnerability into its models • SDGE& will incorporate an economic impact measurement into its model to capture PSPS hazard and exposure potential The following updates are expected in 2024 for WiNGS-Ops: • Revisit Subject Matter Expert AFN customer scaling factors in the Safety component. • Revisit Safety assumption of fatalities per customer minutes de-energized. • Review and update existing Financial assumptions. • Review and update existing Reliability assumptions. If ICE 2.0 model results are available and considered appropriate, update PSPS model assumptions with ICE 2.0 model estimates d) SDG&E plans to explore and evaluate the addition of missing model factors based on the assessment of data and resource availability as well as incremental value added. In the 2023 to 2025 WMP cycle, factors will be integrated where data is available and resources will be engaged to incorporate those factors into the models. Factors to be evaluated include PSPS likelihood and wildfire and PSPS consequence. Factors such as social vulnerability and the potential impact of long-term-duration fires will be evaluated to see if PSPS likelihood, and PSPS consequence can be improved. SDG&E also plans to identify opportunities for additional factors and initiate data gathering in the current WMP cycle to work towards integrating those factors in future WMP cycles. This will be a continuous process of evaluating what can be integrated meaningfully and what may need to be considered in future years to enhance quality and quantity of data over time. Where possible, proxies may be leveraged, and assumptions will be tracked and documented to fulfill the requirements. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | PSPS | N/A | N/A
39 | GreenPower | 2023-01 | GreenPower-2023-01 | 1 | GreenPower-2023-01.1 | Please provide San Diego Gas and Electric’s Pre-submission 2023-2025 WMP Base Plan filed on February 13, 2023, with the OEIS per the 2023 WMP Guidelines and Schedule document. Including all attachments and associated supporting documents required for the Pre-submission 2023-2025 WMP Base Plan filing. | See attached “SDGE 2023-2025 WMP Pre-Submittal.pdf” | Gregg Morris | 2023-03-01 | 2023-03-06 | 2023-03-02 | https://www.sdge.com/sites/default/files/regulatory/GreenPower-2023-01.pdf | 1 | No | WMP Pre-Submissions | Administrative | N/A | N/A
40 | GreenPower | 2023-02 | GreenPower-2023-02 | 1 | GreenPower-2023-02.1 | Please confirm and report on the accuracy of Table 15 “Ignition Likelihood” (Column J), “Ignition Risk” (Column H), and “Overall Utility Risk” (Column G) values, in the 2022 Quarter 4 Data Report (QDR) filed on February 1, 2023. GPI has identified a potential calculation error in the 2022 Quarter 4 Data Report (QDR) filed on February 1, 2023. The “Ignition Likelihood” field in Table 15, Column J does not equal the sum of the “Equipment Likelihood of Ignition” (Column K), “Contact from Vegetation Likelihood of Ignition” (Column L), and “Contact from Object Likelihood of Ignition” (Column M. An example is provided in Table 1. This is contrary to SCE’s Table 15 calculation method where: • Ignition Likelihood (Column J) = SUM (Equipment Likelihood of Ignition (Column K), Contact from Vegetation Likelihood of Ignition (Column L), Contact from Object Likelihood of Ignition (Column M)) An error in the “Ignition Likelihood” variable will also affect the accuracy of the “Ignition Risk” (Column H) and “Overall Utility Risk (Column G)” calculations (Table 1): • Ignition Risk (Column H) = Ignition Likelihood (Column J) x Wildfire Consequence (Column P) • Overall Utility Risk (Column G) = Ignition Risk (Column H) + PSPS Risk (Column I) An error in Column J “Ignition Likelihood” can also alter circuit/segment risk ranking, the top 5% risk segment list, and resulting risk mitigation work locations. In your response, please provide the following: (1) The equation used to calculate “Ignition Likelihood” in the original Quarter 4 QDR filing submission (Table 15, Column J); (2) Any necessary corrections to the “Ignition Likelihood” metric calculation including the equation used and output; (3) Any corrections to the “Ignition Risk” and “Overall Utility Risk” metrics, including equations used and output; (4) An explanation of whether corrections from 1-3 alter the ranking of the top 5 % risk-ranked circuits/segment spans or the circuits/segments that are included in Table 15; (5) An updated 2022 QDR Excel workbook that includes any corrections necessary for Table 15; | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 9. SDG&E further notes that, pursuant to the 2023 Wildfire Mitigation Plan Guidelines, the three business day data request turnaround does not go into effect for stakeholders until the submission of SDG&E’s Final Wildfire Mitigation Plan on March 27, 2023. SDG&E reserves the right to continue processing data request responses within the normal, 10-day turnaround, prior to March 27 and again subsequent to a decision on SDG&E’s 2023 WMP submission. Subject to and without waiving the foregoing objections, SDG&E responds as follows: In response to the data request for QDR Table 15 filed on February 1, 2023, SDG&E confirms the accuracy of the table as-is and, likewise, the methodology and formulas used to calculate “Ignition Likelihood” (Column J), “Ignition Risk” (Column H), and “Overall Utility Risk” (Column G). In summary, the approach used to calculate “Ignition Likelihood” will not equal the sum of the “Equipment Likelihood of Ignition” (Column K), “Contact from Vegetation Likelihood of Ignition” (Column L), and “Contact from Object Likelihood of Ignition” (Column M) due to the disparate approaches for calculating columns L and M. Columns A, E, F, G, H, and P, are derived from the WiNGS Planning model, which has an embedded ignition adjustment process separate from the values presented in columns K, L, M, N. More specifically, “Contact from Vegetation Likelihood of Ignition” (Column L) , “Contact from Object Likelihood of Ignition” (Column M) and “Equipment Likelihood of Ignition” are separate modules containing calculations not directly tied to “Ignition Likelihood”. Subsequently, “Ignition Risk”, the “Overall Utility Risk”, and the top 5% of risk segments will not be affected. (1) The equation used to calculate “Ignition Likelihood” in the original Quarter 4 QDR filing submission (Table 15, Column J); The equation used to calculate “Ignition Likelihood” (Table 15, Column J) is derived from the WiNGS Planning Ignition Rate Normalization Factor model that leverages the Likelihood of Risk Event by segment (this will be included in SDG&E’s forthcoming 2023 WMP 2023, in section 6.2.2.1). Ignition Likelihood is calculated using an annual ignition rate for the HFTD. The annual ignition rate is adjusted to account for local conditions including wind speed, historical tree strikes, vegetation density, asset hardening, and asset health. The normalization factor model used to leverage the ignition likelihood metric used in Table 15 is as follows: Adj. Ignition Rate = Initial Ignition Rate × Ignition Adj. Factori × Normalization Factor-i. Where, Initial Ignition Rate is the initial ignition rate prior to implementation of adjustment factor i, Ignition Adj. Factori is the adjustment factor metric tied to the adjustment factor i, Normalization Factori is the normalization factor tied to adjustment factor i, Adj. Ignition Rate is the adjusted ignition rate after implementation of adjustment factor i and i is the specific adjustment factor (e.g., wind speed, tree strikes, etc.). The normalization part of the process implementation is performed to maintain the same global annual ignition rate after each adjustment step. Thereby, the ignition rate is adjusted relatively among each circuit-segment according to each individual risk factor, while the global ignition rate across the full scope of circuit-segments remains constant. (2) Any necessary corrections to the “Ignition Likelihood” metric calculation including the equation used and output; Due to the unassociated approaches for calculating “Ignition Risk” vs. “Contact from Vegetation Likelihood of Ignition” and “Contact from Object Likelihood of Ignition”, SDG&E does not report any corrections to the Ignition Likelihood metric, including the equation used and final output. (3) Any corrections to the “Ignition Risk” and “Overall Utility Risk” metrics, including equations used and output; SDG&E does not report any corrections necessary for the Ignition Risk and Overall Utility Risk metrics, including the equations used and final outputs. (4) An explanation of whether corrections from 1-3 alter the ranking of the top 5 % risk-ranked circuits/segment spans or the circuits/segments that are included in Table 15; (5) An updated 2022 QDR Excel workbook that includes any corrections necessary for Table 15; SDG&E does not report a change in the top 5% of risk-ranked circuit segments and will not currently submit an updated 2022 QDR Excel workbook for Table 15. | Gregg Morris | 2023-03-07 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/GreenPower-2023-01.pdf | 0 | No | Other | Validation of Ignition Likelihood | N/A | N/A
41 | MGRA | 2023-021 | MGRA-2023-021 | 1 | MGRA-2023-021.1 | Please provide for Asset Point data for Camera, Fuse, Support Structure, and Weather Station. | SDG&E has provided a compiled database inclusive of all 2022 data provided to Energy Safety. Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Asset Data | N/A | N/A
42 | MGRA | 2023-021 | MGRA-2023-021 | 2 | MGRA-2023-021.2 | Provide Asset Line data for Transmission Line (as permitted as non-confidential), Primary Distribution Line, and Secondary Distribution Line. | Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Asset Data | N/A | N/A
43 | MGRA | 2023-021 | MGRA-2023-021 | 3 | MGRA-2023-021.3 | Provide PSPS Event data. Include Event Log, Event Line, Event Polygon data. Please exclude customer meter data. Provide all PSPS Event Asset Damage data including photos. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 2, 5, 8 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E did not have any PSPS events in 2022. | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | PSPS | N/A | N/A
44 | MGRA | 2023-021 | MGRA-2023-021 | 4 | MGRA-2023-021.4 | Provide Risk Event Point data, including Wire Down, Ignition, Transmission unplanned outage (as classified non-confidential), Distribution Unplanned Outage data, Distribution Vegetation Caused Unplanned Outage, Risk Event Asset Log. | Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Risk Event Data | N/A | N/A
45 | MGRA | 2023-021 | MGRA-2023-021 | 5 | MGRA-2023-021.5 | Provide photo data for Risk Events. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 2, 5, 8 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not currently have or provide photo data for risk events to Energy Safety. | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Photo Data | N/A | N/A
46 | MGRA | 2023-021 | MGRA-2023-021 | 6 | MGRA-2023-021.6 | Under Initiatives, please provide Grid Hardening data, including Hardening Log, Hardening Point, and Hardening Line data. Inspection data is not requested at this time. | Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Grid Hardening data | N/A | N/A
47 | MGRA | 2023-021 | MGRA-2023-021 | 7 | MGRA-2023-021.7 | Under Initiatives, please provide Other Initiative data for point, line, polygon features and the Other Initiative Log. | Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Other Initiative data | N/A | N/A
48 | MGRA | 2023-021 | MGRA-2023-021 | 8 | MGRA-2023-021.8 | Under Other Required Data, please provide Red Flag Warning Day polygon data. | Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Red Flag Warning Day polygon data | N/A | N/A
49 | MGRA | 2023-021 | MGRA-2023-021 | 9 | MGRA-2023-021.9 | Please provide a layer indicating calculated circuit-level risk using the methodology presented in the WMP. a. If independent probability and consequence layers exist, please provide these independently as well. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not currently have or provide circuit-level risk information in a geodatabase format to Energy Safety as it has not yet fully developed this capability for its quarterly submissions. SDG&E currently plans to include this data with the next QDR submission to Energy Safety. | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Layers | N/A | N/A
50 | CalPA | 2023-07 | CalPA-2023-07 | 1 | CalPA-2023-07.1 | SDG&E’s 2022 WMP stated that a planned enhancement for Initiative 7.3.5.2 (“Detailed inspections and management practices for vegetation clearances around distribution electrical lines and equipment”) was to “Explore the use of the WiNGS-Planning risk model to evaluate the effectiveness of vegetation management operations risk models to support future prioritization and implementation of tree trimming.”4 There is no mention of this sort in SDG&E’s 2023 WMP submission. a) Did SDG&E conduct the above-mentioned exploration in 2022? b) If the answer to subpart (a) is “yes,” please provide SDG&E’s conclusions regarding the use of the WiNGs-Planning risk model for the abovementioned purpose. c) If the answer to subpart (a) is “no,” please explain why not. d) If the answer to subpart (a) is “no,” does SDG&E plan to conduct the abovementioned exploration? e) If the answer to subpart (d) is “yes,” please state when SDG&E intends to do so. | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Yes, SDGE evaluated the application of WiNGS-Planning risk model for the user case of prioritizing vegetation operational activities. b) The conclusion is that WiNGS Planning model alone is not the best approach for identifying the trees or vegetation management areas that need to be prioritized for routine or non-routine inspections or tree trims, nor is it the best approach for informing relative risk for trees at the asset or circuit section. The purpose of the WiNGS Planning model is to identify the best deployment of underground and covered conductor for long term risk strategy. The WiNGS-Planning model includes limited height, which is one of variables to the system during extreme weather conditions. To predict where tree risks and hazard conditions are more likely to occur, annual tree inspection and tree trimming records are the key data inputs to train the machine learning model. Vegetation management mitigates all observed hazardous conditions impacting the electrical system, and trees identified with an urgent condition are prioritized for the tree trimming or removal activities. Therefore, SDGE’s conclusion is that the independent model developed by Logic20/20 that incorporates attributes collected from operational activities is a superior approach to determine the prioritization and implementation of tree trimming. See response in Question 3 for additional details regarding this model. The first iteration of such an independent model was completed in 2022. c) N/A d) N/A e) N/A | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 2022 WMP | Initiative 7.3.5.2 | N/A | N/A
51 | CalPA | 2023-07 | CalPA-2023-07 | 2 | CalPA-2023-07.2 | SDG&E’s 2022 WMP stated regarding initiative 7.3.5.16 (“Removal and remediation of trees with strike potential to electric lines and equipment”) (hereinafter “this initiative”), SDG&E plans to further evolve this program over the next 10 years by leveraging enhanced VRI and WiNGS-Planning modeling data to develop a more strategic approach to identify areas of high risk and prioritization of mitigation efforts. SDG&E will also utilize LiDAR to improve its assessment of hazard trees.5 a) Does the above statement still represent SDG&E’s plans for this initiative? b) If the answer to subpart (a) is “no,” please describe how SDG&E’s plans for this initiative have changed since February 2022. c) If the answer to subpart (a) is “yes,” please provide SDG&E’s progress to date on implementing the plans described in the quote above. | a) Yes. However, as mentioned in 1 b), SDG&E anticipates that the independent model that is designed to incorporate all tree related attributes and additional environmental attributes is a superior approach to assess trees with strike potential. Once such a model is established, vegetation management does not rule out use of the application of WiNGS Planning model when it needs to prioritize segments within the risk areas indicated by the independent model. The overall risk or a particular risk score from the WiNGS Planning model might be considered during this risk-based decision-making process. SDG&E is still assessing the overall modeling and prioritization strategy of its vegetation management operations. b) N/A c) SDG&E provides progress for the development of independent vegetation contact risk model below. • Vegetation Tree Contact Risk Model with the San Diego Supercomputing Center. This model development leverages tree attributes collected from operational vegetation management activities and meteorology data such as wind gust and soil moisture in an effort to predict future vegetation contact given predicted weather conditions. The developers are currently integrating overhead conductors into the model and analyzing the model performance. SDG&E anticipates a first iteration of this model sometime near the end of 2023. LiDAR data implementation to enhance operational and vegetation contact risk modeling. SDG&E processed LiDAR data for 10 HFTD circuits in 2022 as proof of concept. In 2023, SDG&E is evaluating the methods and efforts to process the remaining circuits in the HFTD so that LiDAR data can be integrated into risk modeling. The timeline is not determined yet. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 2022 WMP | Initiative 7.3.5.16 | N/A | N/A
52 | CalPA | 2023-07 | CalPA-2023-07 | 3 | CalPA-2023-07.3 | SDG&E states on p. 6 of its 2023 WMP, “The Company [SDG&E] engaged a third-party to review the off-cycle schedule to determine whether there were advantages to modify the schedule based on a risk comparison of the Vegetation Management Areas (VMAs).” a) Please describe the scope, schedule, and methodology of the abovementioned third-party review. b) Please identify who conducted the abovementioned third-party review. c) When was the abovementioned third-party review completed? d) Please provide the results of the abovementioned third-party review. e) Please provide any documents generated from the abovementioned third-party review (e.g. reports, workpapers, etc.). f) Has SDG&E incorporated any findings or recommendations from the abovementioned third-party review into the methodology of its off-cycle patrol scheduling? g) If the answer to subpart (f) is “yes,” please describe how SDG&E has done so. h) If the answer to subpart (f) is “no,” please explain why not. | a) Scope: The scope was to utilize historical vegetation management data (inspection and trimming inspection records) and produce a risk-based approach to better inform the timing of non-routine HFTD vegetation inspections. The analysis used historical vegetation activity data (inspections and trims) to generate influential variables that capture a tree’s characteristics, growth patterns, and past activity. The scores produced from the model were then used to aggregate the level of influential variables up to the VMAs or segments to generate a risk-based approach to scheduling. Schedule: Below is the timeline and schedule that was used to deliver the work: b) Logic 20/20 is a business and technology consulting firm headquartered in Seattle, Washington. c) The review was completed at the end of 2022. d) Please see attachment titled, “SDGE_WMP-07 Q.3”. e) Please see attachment titled, “SDGE_WMP-07 Q.3”. f) Yes. g) This was the first iteration of a predictive model to prioritize inspection schedules. SDG&E intends to incorporate some of the recommendations from this study beginning in 2023. SDG&E plans to conduct the off-cycle patrol activities in the higher risk-ranked VMAs closer to the start of peak fire season (September 1), and to schedule the remaining HFTD VMA patrols in the preceding months to create parity in the schedule and without conflicting with other Vegetation Management activities in those same months. h) N/A | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07%20Attachment%20Q3.pdf | 1 | No | 1 | 1 EXECUTIVE SUMMARY Page 1 | 1.1.1.4 | 1.1.1.4 Vegetation Management and Inspections Page6
53 | CalPA | 2023-07 | CalPA-2023-07 | 4 | CalPA-2023-07.4 | SDG&E states on p. 252 of its 2023 WMP, “The fuels management activity6 is currently not included in this application [Epoch] at this time.” a) Why is the fuels management activity not included in the Epoch application? b) Could inclusion of fuels management activity in the Epoch application improve the activity’s efficacy? c) Does SDG&E intend to include fuels management activity in the Epoch application at a later date? d) If the answer to subpart (c) is “yes,” please specify when SDG&E intends to include fuels management activity in Epoch. e) If the answer to subpart (c) is “no,” please explain why not. | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) The development of the PowerWorks work management system and Epoch preceded the inception of the fuels management program by several years and, therefore, was not originally designed to accommodate this activity. Doing so would require a substantial software upgrade to the work management system including the creation of new electronic work order types for this activity, the development of new electronic activity forms, development of new invoicing integrations, and additional system user credentialing of contractors not currently working in Epoch. b) The inclusion of the fuels management activity in the Epoch application alone would not necessarily improve the efficacy of this activity. It may help create efficiencies in this activity over time as the program grows, more pole structures are added to the population of work sites, and if/where repeated, annual work creates a maintenance cycle. c) SDG&E may explore the feasibility and potential benefits for future integration of this activity within Epoch, but has not yet decided if this is a necessary enhancement given the effort and potential cost. d) SDG&E does not have a date at this time when this activity may be included in Epoch. e) See c) and d) above. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.1 | 8.2.1 Overview Page 254
54 | CalPA | 2023-07 | CalPA-2023-07 | 5 | CalPA-2023-07.5 | SDG&E states on p. 252 of its 2023 WMP, “In general, a 15 percent sample [of vegetation management activities] is selected to be performed after activities are completed.” a) Please state the basis for choosing a sampling rate of 15 percent for vegetation management activities, as opposed to a higher sampling rate. b) Provide any supporting documentation for the choice of a 15% sampling rate, in the context referenced above. | a) SDG&E uses a 15% random rate as the baseline for auditing its vegetation management activities because it considers this an acceptable and representative sample of the population of completed work to reflect contractor performance. Vegetation management audit results do not yield a high percentage of fail rates that may otherwise inform of the need for a higher sample percentage rate, therefore, a 15% sample was selected. Increasing audit sample size for all activities would also require an increase in the number of audit resources at additional rate-payer expense. b) Please see SDG&E’s 2023-2025 Wildfire Mitigation Plan (https://www.sdge.com/2023-wildfire-mitigation-plan) , Table 8-18 on page 312 for audit result findings. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.1 | 8.2.1 Overview Page 254
55 | CalPA | 2023-07 | CalPA-2023-07 | 6 | CalPA-2023-07.6 | SDG&E states on p. 252 of its 2023 WMP, “Vegetation Management performs a QA/QC audit (WMP.505) on a percentage of all activities. In general, a 15 percent sample is selected to be performed after activities are completed.” a) Please describe the procedure for the QA/QC audit that is performed on a 15 percent sample of vegetation management activities, referenced above. b) Please explain how SDG&E determines whether a particular VM worksite/project passes or fails the QA/QC audit referenced above. c) Please describe what happens if a particular VM worksite/project fails the audit referenced above. d) Does SDG&E analyze the results of these QA/QC audits by contractor to evaluate or compare the performance of VM contractors? | a) SDG&E utilizes Scheduling Work Orders (SWO) generated in in the SDG&E work management tool called CityWorks server. The SWO is unique to the Vegetation Management Area (VMA), and all assets (trees or poles) within the work order. City Works uses a randomizer to generate the audit sample population. The SWO is assigned to the contractor for issuance to the field auditor(s). The field auditor receives the assigned work via a dispatch work order (DWO) on their Mobil Data terminal (MDT). Each asset to be audited has a work point that links to the electronic record. Each audit asset is evaluated in the field and updated in the system as a pass or fail. b) Within Epoch, each audit asset has tabs and drop-down selections to identify pass or fail, and with additional codes such as insufficient clearance, debris left on site, no trim performed, and or poor trimming to document reason for failure to meet SDG&E scope of work, state and regulatory compliance, and arboricultural and industry standards. c) Failed assets within the SWO are recorded and returned to the contractor for review and correction. Audit failures not disputed by the contractor are re-worked at no additional cost to SDG&E. d) Yes, SDG&E reviews the completed audit results internally and meets regularly with contractors to further review the audit result. The meetings cover trends, recognize positive performance, and discuss actionable items on identified areas for improvement. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.1 | 8.2.1 Overview Page 254
56 | CalPA | 2023-07 | CalPA-2023-07 | 7 | CalPA-2023-07.7 | SDG&E states on p. 261 of its 2023 WMP that detailed vegetation inspections “are scheduled and performed using a system of geographic VMA. The service territory is comprised of 133 VMAs.” How does SDG&E decide the boundaries for its vegetation management areas? | The VMA boundaries are static and were delineated variably using city boundaries, SDG&E Districts, roads, and a relative parity in the dispersal of inventory tree units located within. The service territory is further delineated by jurisdictional and fire designation areas including the SRA, LRA, and HFTD. These areas determine which rules and regulations apply. Each VMA has a unique three-digit number. The first digit identifies the SDG&E District. The second digit identifies whether a VMA is located within the State Responsibility Area (SRA). If the second digit is 5 or higher, it is within the SRA. The third digit is the sequential numeric assignment of the VMAs when first created. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1 | 8.2.2.1 Detailed Vegetation Inspections Page 264
57 | CalPA | 2023-07 | CalPA-2023-07 | 8 | CalPA-2023-07.8 | SDG&E states on p. 264 of its 2023 WMP, “During the post-trim QA/QC audit activity, an audit contractor performs a cursory vegetation inspection of all overhead lines within each VMA.” a) Please explain how a cursory inspection is performed on “all overhead lines within each VMA” as referenced above, while only a 15% sample of work is audited. b) Please describe the procedure that audit contractors use to perform a “cursory vegetation inspection of all overhead lines” as referenced above. | a) The cursory inspection during the post-trim audit activity consists of a visual assessment of trees in proximity to the overhead lines to verify vegetation clearance will hold compliance for the remainder of the VMA annual cycle. Data is not collected for trees not being audited unless it is determined the tree requires work due to vegetation clearance or presents a hazardous condition to the overhead line. Trees that require work will first be evaluated to see if the work was assigned during the trim activity. If so, the tree is failed for the audit and returned to the tree contractor for corrective action. If the tree was not part of the original work assigned, the auditor would enter the information and submit a follow-on work order to prune the tree. The cursory inspection is performed simultaneously with the VMA 15% sample of work being audited. b) Please response to a). | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1.2 | 8.2.2.1.2 Frequency or Triggers Page 267
58 | CalPA | 2023-07 | CalPA-2023-07 | 9 | CalPA-2023-07.9 | SDG&E states on p. 264 of its 2023 WMP that since its 2022 WMP submission it “Engaged with a third party to study the correlation between enhanced tree trim clearances and reduction of vegetation-caused outages.” a) Please describe the scope, goals, analytical methods, and duration of the abovementioned third party study. b) Please identify who conducted the abovementioned third-party study. c) Has the abovementioned third-party study been completed? d) If the answer to subpart (c) is “yes,” please provide the results of the study. e) If the answer to subpart (c) is “yes,” please provide any documents generated by the study (e.g. reports, workpapers, etc.) f) If the answer to subpart (c) is “no,” please state when SDG&E expects the study to be complete | a) Please see SDG&E’s 2023-2025 Wildfire Mitigation Plan "Areas for Continued Improvement and Required Progress of the IOUs’ 2022 WMP Update Progression of Effectiveness of Enhanced Clearances Joint Study”, beginning on page 930. The same is also addressed in Appendix D: Areas for Continued Improvement SDGE-22-20 “Progression of Effectiveness of Enhanced Clearances Joint Study”, on page 534. b) Third-party vendor, EPRI, was hired in 2022 to conduct the study. c) This multi-year study is not yet completed. d) N/A e) N/A f) This study is scheduled to be completed by the end of 2025. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1.3 | 8.2.2.1.3 Accomplishments, Roadblocks, and Updates Page 267
59 | CalPA | 2023-07 | CalPA-2023-07 | 10 | CalPA-2023-07.10 | SDG&E states on p. 264 of its 2023 WMP that since its 2022 WMP submission it “Continued engagement with the San Diego Supercomputing Center (SDSC) to study the relationship between expanded clearances and reduction in tree-related outages.” a) Is the abovementioned study the same study referred to in Question 9? b) If the answer to subpart is (a) is “no,” please explain how it differs from the study referred to in Question 9. c) If the answer to part (a) is “no,” please respond to parts (a) and (c) - (f) of the previous question (Question 9), but with respect to the SDSC study instead of the third-party study. | a) Yes. The reference cited above should have been the ongoing study being performed by EPRI with the joint IOU’s. b) N/A c) N/A | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270
60 | CalPA | 2023-07 | CalPA-2023-07 | 11 | CalPA-2023-07.11 | SDG&E states on p. 265 of its 2023 WMP that a change it may implement to its detailed vegetation inspections is to “Further integrate and operationalize land-based (vehicle and personnel) LiDAR, satellite imagery technology, and risk analyses into detailed inspection activities and decision-making.” a) How does SDG&E plan to integrate LiDAR into detailed inspection activities and decision-making? b) How does SDG&E plan to integrate satellite imagery technology into detailed inspection activities and decision-making? c) How does SDG&E plan to integrate risk analyses into detailed inspection activities and decision-making? d) How does SDG&E expect the above-mentioned integrations will improve its detailed inspections activities and decision-making? | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E processed LiDAR data for 10 HFTD circuits in 2022 as proof of concept. In 2023, SDG&E is evaluating the methods and efforts to process the remaining circuits in the HFTD so that LiDAR data can be integrated into risk modeling. This data will provide additional situational awareness to capture the holistic picture of the vegetation conditions to inform the detailed inspections in HFTD. b) SDG&E is exploring the use of satellite imagery to assess the power of satellite data to inform near-real time risk, planning, monitoring, and operations across the entire service territory with preliminary use cases in vegetation encroachment, tree-strike, and change detection (e.g., per-pole and per-span risk). This proof of concept will explore the potential for a one-stop-shop for multiple Enterprise use cases with state-of-the-art, cost-effective, feasible, and scalable satellite data and workflows. c) LiDAR and satellite imagery may improve SDG&E’s risk modeling capabilities with the inclusion of additional data related to clearance history, strike tree population, environmental conditions, topography, soil moisture, species diversity, etc. Information from these technologies may also assist in analyses and planning. For field inspection activities, SDG&E is exploring how information from these technologies may improve decision making. This may include the addition of risk-ranking information for the inspector within the electronic record that indicates relative risk at the specific tree asset level, and/or where the tree is located. Such information may be helpful in deciding whether a tree requires work, the scope of work, and the prioritization. d) See c) above. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1.3 | 8.2.2.1.3 Accomplishments, Roadblocks, and Updates Page 267
61 | CalPA | 2023-07 | CalPA-2023-07 | 12 | CalPA-2023-07.12 | SDG&E states on p. 265 of its 2023 WMP that a change it may implement to its detailed vegetation inspections is to “Further integrate VRI into inspection activities for the HFTD.” a) How does SDG&E intend to further integrate VRI into inspection activities for the HFTD? b) How does SDG&E anticipate further integrating VRI into inspection activities for the HFTD will improve its inspection activities going forward? | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) As mentioned in Question 1, Logic20/20’s independent model is designed to support inspection activities. The Vegetation Risk Index (VRI) is a situational awareness tool, not a risk model, that categorizes circuits and transmission lines based on tree species, tree height, tree count, and historical vegetation-related outages. With the VRI now available within the mobile application (Epoch), Vegetation Management field users will continue to use VRI as an additional tool in conjunction with the data outputs from Logic20/20’s model to inform where risk levels are relatively higher, and where additional VM work may be prudent. b) SDG&E is working with San Diego Super Computing Center to develop the predictive that incorporates wind conditions to better refine the risk score that can inform vegetation field inspections in HFTD. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1.3 | 8.2.2.1.3 Accomplishments, Roadblocks, and Updates Page 267
62 | CalPA | 2023-07 | CalPA-2023-07 | 13 | CalPA-2023-07.13 | SDG&E states on p. 265 of its 2023 WMP that a change it may implement to its detailed vegetation inspections is to “Further engage third party study on risk modeling at the tree asset and span level” (sic). a) Please describe the scope, goals, analytical methods, and duration of the abovementioned study. b) What are the anticipated outputs of the abovementioned study? c) How does SDG&E anticipate utilizing the outputs of the abovementioned study in its vegetation risk modeling or VM work prioritization? | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Scope: One potential application of the model outlined in Question 3 is to support the detailed inspection activities by displaying the key features trained in the model in Epoch. Goals: Such data variables would serve as a situational awareness tool to help inspectors to make informed decisions on the follow-up work. Analytical method: The model is trained using logistical regression methods. Features that are informational to inspection activities are identified by vegetation management. They will be aggregated at VMA or segment level. The final method is currently under evaluation. The duration of this implementation is planned to be by the end of the 2023-2025 WMP cycle. b) Anticipated outputs of this model application include the display of frequency of hazard trees, memos, and outages, as well as wind gusts and other environmental data points in Epoch. c) As mentioned in a), these data points generated from the predictive model could potentially be used to inform the prioritization of the hazard and memo trees during routine inspections. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1.3 | 8.2.2.1.3 Accomplishments, Roadblocks, and Updates Page 267
63 | CalPA | 2023-07 | CalPA-2023-07 | 14 | CalPA-2023-07.14 | SDG&E states on p. 266 of its 2023 WMP regarding its off-cycle inspection activities, The VMA ranking provides input for generating the off-cycle HFTD schedule, which evenly distributes labor across the first 8 months of the year, provides time between the detailed and off-cycle inspections, and places the riskiest areas to be inspected closest to fire season. a) How does VMA ranking generate or influence SDG&E’s off-cycle HFTD inspection schedule? b) What inputs other than VMA ranking, to the off-cycle HFTD inspection schedule exist? | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Using historic, aggregated tree asset level data to rank HFTD VMAs may assist with informed-decision making when scheduling the order of off-cycle inspections activities in advance of peak fire season. For example, tree conflict avoidance may best be achieved by performing the off-cycle inspection activity of the highest-ranked VMAs in the fall-summer timeframe so these circuits can be trimmed in advance of September, generally considered the beginning of peak Santa Ana and wildfire risk season in SDG&E’s service territory. b) Additional inputs to the off-cycle HFTD inspection schedule include the relative time period between the routine schedule of the other vegetation management activities, contractor resource allocation, and the ability to combine off-cycle patrols with other concurrent VM activities. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.2 | 8.2.2.2.2 Frequency or Triggers Page 269
64 | CalPA | 2023-08 | CalPA-2023-08 | 1 | CalPA-2023-08.1 | SDG&E states on p. 268 of its 2023 WMP that a change to its off-cycle inspection activity within the next five years is to “Continue to research and modify off-cycle HFTD schedule were necessary to optimize risk reduction” (sic). a) What are SDG&E’s research needs in regards to the above? b) How does SDG&E intend to conduct the abovementioned research? c) What data sources or experiments does SDG&E intend to use to support the abovementioned research? d) What modifications does SDG&E anticipate making to the off-cycle HFTD schedule? Please describe any such changes. |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270
65 | CalPA | 2023-08 | CalPA-2023-08 | 2 | CalPA-2023-08.2 | SDG&E states on p. 268 of its 2023 WMP that a change to its off-cycle inspection activity within the next five years is to “Identify proper resource need and allocation to perform the off-cycle HFTD inspection timely and efficiently.” a) Why has SDG&E not already accomplished the abovementioned identification of proper resource need and allocation, given that the off-cycle HFTD inspection program is already in place? b) Please identify SDG&Es current progress to date on identifying the proper resource need and allocation to perform the off-cycle HFTD inspection timely and efficiently. c) Please identify what SDG&E needs to do in order to identify the abovementioned resource need and allocation. d) Please provide the number of SDG&E’s off-cycle HFTD inspections that were completed on time in 2022 and the total number of off-cycle HFTD inspections. e) Were SDG&E’s off-cycle HFTD inspections completed timely in 2022? |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270
66 | CalPA | 2023-08 | CalPA-2023-08 | 3 | CalPA-2023-08.3 | SDG&E states on p. 268 of its 2023 WMP that a change to its off-cycle inspection activity within the next five years is to “Identify additional and proactive HFTD inspection activity opportunities such as pre-PSPS and adverse weather condition and event patrols.” a) Please describe how SDG&E intends to identify the abovementioned opportunities. b) What does a pre-PSPS inspection, referenced above, entail? c) What do “adverse weather condition and event patrols” referenced above entail? d) How will SDG&E assess the effectiveness of “additional and proactive HFTD inspection activity opportunities” referenced above? e) At what threshold of effectiveness would SDG&E propose the abovementioned opportunities as permanent programs or WMP initiatives? |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270
67 | CalPA | 2023-08 | CalPA-2023-08 | 4 | CalPA-2023-08.4 | SDG&E states on p. 268 of its 2023 WMP that a change to its off-cycle inspection activity within the next five years is to “Further integrate and operationalize risk and condition-based data such as meteorology and environmental conditions into ground-level decision-making.”a) Please describe how SDG&E intends to accomplish the abovementioned integration and operationalization. b) How will the process described in your answer to subpart (a) improve ground-level decision-making regarding off-cycle inspections? |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270
68 | CalPA | 2023-08 | CalPA-2023-08 | 5 | CalPA-2023-08.5 | SDG&E states on p. 269 of its 2023 WMP that “SDG&E sponsored a third-party study of its Fuels Treatment activities in 2022 to review the efficacy of the program and potential risk reduction.” a) What were the findings of the abovementioned study? b) Please identify who performed the abovementioned study. c) How has SDG&E integrated the findings of the abovementioned study into its planned fuels treatment activities for 2023-2025? d) Please provide any documents that were generated from the abovementioned study (e.g. reports, workpapers, etc.). |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.3 | 8.2.3 Vegetation and Fuels Management Page 271
69 | CalPA | 2023-08 | CalPA-2023-08 | 6 | CalPA-2023-08.6 | SDG&E states on p. 269 of its 2023 WMP that an enhancement to its fuels treatment activity in 2023 will be to “Continue to assess cost/benefit and research alternatives such as fire retardants.” a) How does SDG&E intend to accomplish the abovementioned assessment and research? b) Please describe SDG&E’s progress to date regarding assessing cost/benefit of its fuels treatment program. c) Please describe SDG&E’s progress to date on the abovementioned research of alternatives |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.3 | 8.2.3 Vegetation and Fuels Management Page 271
70 | CalPA | 2023-08 | CalPA-2023-08 | 7 | CalPA-2023-08.7 | SDG&E states on p. 269 of its 2023 WMP that an enhancement to its fuels treatment activity in 2023 will be to “Engage third party to study the methodology and effectiveness of the fuels treatment activity.” a) Will the abovementioned third party study be a continuation of the third party study referred to in Question 5, or a new study? b) If your answer to subpart (a) is “a new study,” please identify how the scope of work of the new study will be different from the previous study referenced in Question 5, and how it will add to the findings from the previous study. c) If your answer to subpart (a) is “a continuation of the third party study referred to in Question 5,” please identify how SDG&E’s continuation of that study will add to its findings and improve SDG&E’s fuels treatment program. |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.3 | 8.2.3 Vegetation and Fuels Management Page 271
71 | CalPA | 2023-08 | CalPA-2023-08 | 8 | CalPA-2023-08.8 | SDG&E states on p. 280 of its 2023 WMP that a change to its Vegetation Management Enterprise System since its last WMP is to add “New mapping capabilities to electronically track and document inspection progression” a) Please list and describe the abovementioned new mapping capabilities. b) How are the abovementioned new mapping capabilities currently improving SDG&E’s inspection programs? c) Does SDG&E intend to add mapping capabilities beyond what it has already? d) If your answer to subpart (c) is “yes,” please list and describe the planned future enhancements. |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.4.6 | 8.2.4.6 Changes Since the Last WMP Submission Page 282
72 | CalPA | 2023-08 | CalPA-2023-08 | 9 | CalPA-2023-08.9 | SDG&E states on p. 280 of its 2023 WMP that a change to its Vegetation Management Enterprise System since its last WMP is to add “New data fields to electronically record customer refusals and other deferred work which negates the need for hard copy forms” and the “creation of a refusal/deferred work dashboard to track and manage time-sensitive tree work.” a) Please list and describe the abovementioned new data fields. b) How are the abovementioned new data fields improving SDG&E’s ability to respond to customer refusals and complete deferred work? |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.4.6 | 8.2.4.6 Changes Since the Last WMP Submission Page 282
73 | CalPA | 2023-08 | CalPA-2023-08 | 10 | CalPA-2023-08.10 | SDG&E states on p. 281 of its 2023 WMP regarding its QA/QC, “A higher sampling percentage is used for some enhanced vegetation management activities in the HFTD, including a 100 percent post-trim audit of all completed trim and removal work generated from the off-cycle HFTD inspection activities.” a) Is the abovementioned 100% post-trim audit conducted for all trim and removal activities in the HFTD, or just those that result from an off-cycle inspection? b) If the answer to subpart (a) is the latter, please explain why SDG&E does not audit 100% of all trim and removal work in the HFTD. |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.5.2 | 8.2.5.2 Sample Size Page 283
74 | CalPA | 2023-08 | CalPA-2023-08 | 11 | CalPA-2023-08.11 | SDG&E states on p. 282 of its 2023 WMP: A 100-percent audit of all completed tree trimming and removal work generated during the off-cycle, HFTD patrol activity was performed where feasible. SDG&E is considering the development of compliance-based audits as a measure of system status and reliability. Such audits may be performed across multiple VMAs and create benchmarking for the performance of vegetation management operations. a) Please identify where the abovementioned 100 percent audit has not been feasible. b) How has SDG&E overcome, or how does SDG&E plan to overcome (as applicable), roadblocks to attaining the 100 percent audit of all completed tree trimming and removal work generated during the off-cycle HFTD patrol activity? c) Please describe the scope, goals, methodology, and benchmarks of the abovementioned compliance-based audits. d) What statute(s) or General Order(s) would SDG&E’s compliance-based audits referenced above be complying with? e) How will SDG&E determine which VMAs to conduct the abovementioned compliance-based audits in? f) Please describe the benchmarking SDG&E intends to develop and perform for vegetation management operations performance. |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.5.6 | 8.2.5.6 Process Changes Since the Last WMP Submission Page 284
75 | CalPA | 2023-08 | CalPA-2023-08 | 12 | CalPA-2023-08.12 | SDG&E states on p. 252 of its 2023 WMP, “Contractors are required to provide the necessary training to their workforce on the technical capabilities to perform the work.” a) Please identify what necessary training is required for contractors to perform SDG&E’s vegetation management work. b) Does SDG&E inform VM contractors what training is necessary to perform SDG&E’s VM work? c) Does SDG&E review the training or certifications that its contractors provide to their workforces? d) Does SDG&E verify that contractors’ workforces are properly trained to perform SDG&E’s vegetation management work? e) Please describe SDG&E’s process, if any, that is currently in place to review contractor workforce qualifications and/or ability to perform SDG&E’s VM work? |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.1 | 8.2.1 Overview Page 254
76 | CalPA | 2023-08 | CalPA-2023-08 | 13 | CalPA-2023-08.13 | SDG&E states on p. 266 of its 2023 WMP, “Any priority tree work identified during the off-cycle HFTD patrol is expedited as needed via the “Memo” process to mitigate the risk.” a) Please state how many “Memo” processes were initiated related to priority tree work identified in HFTD 2 areas during 2022. b) Please state how many “Memo” processes were initiated related to priority tree work identified in HFTD 3 areas during 2022. |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.2 | 8.2.2.2.2 Frequency or Triggers Page 269
77 | CalPA | 2023-08 | CalPA-2023-08 | 14 | CalPA-2023-08.14 | SDG&E states on p. 266 of its 2023 WMP: In early 2022, a third-party vendor was engaged to conduct an efficacy study of the off-cycle HFTD patrol schedule to determine the optimum schedule based on historical tree risk within each HFTD VMA… The study also considered increasing the 3-month off-cycle HFTD schedule to an 8-month schedule (January to August) and prioritizing the patrol activity for the riskiest VMAs closer to the month of September. This risk-based approach generates a machine learning model that scores trees based on descriptive features, historical growth patterns, and historical priority “Memo” trims. a) Please identify who conducted the abovementioned third-party study? Please provide name of individual or business and address if available. b) Has the above-mentioned study been completed, as of the 2023 WMP submission date? c) If the answer to subpart (b) is “yes,” please provide the results of the study. d) If the answer to subpart (b) is “yes,” please any documents generated by the study (e.g. reports, workpapers, etc.). e) If the answer to subpart (b) is “no,” please state when SDG&E expects the study to be complete. f) After the abovementioned third-party study is complete, does SDG&E plan on using the abovementioned risk-based approach and “machine learning model that scores trees” as an enhancement to its WiNGS-Planning model? g) Does SDG&E have additional plans to refine the abovementioned risk-based approach to improve SDG&E’s off-cycle inspections process? h) For this 2023-2025 WMP cycle, does SDG&E plan on continuing with an 8-month off-cycle inspection schedule? |  | Aaron Louie | 2023-04-05 | 2023-04-13 |  |  |  |  | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.2 | 8.2.2.2.2 Frequency or Triggers Page 269
78 | CalPA | 2023-09 | CalPA-2023-09 | 1 | CalPA-2023-09.1 | Regarding Appendix F, OEIS Table 9-2 (Frequently De-energized Circuits) on WMP Appendix F p. 12-17: a) Please clarify if Entry 9 is missing or if Table 9-2 entries were misnumbered. b) If there was an error in OEIS Table 9-2, please provide a corrected version. c) Please explain why covered conductor is not considered as a mitigation for these Frequently De-energized Circuits. | a) Table 9-2 was misnumbered. b) See attached updated Appendix F, which includes an updated Table 9-2. This update will also be included in SDG&E’s non-substantive errata of the 2023-2025 Wildfire Mitigation Plan to be submitted on April 26, 2023. c) The Covered Conductor Program has the potential to raise the threshold for PSPS events to higher wind speeds compared to bare conductor hardening; however, as of the end of 2022 no circuits have been fully hardened with covered conductor and therefore the threshold for PSPS events has not been raised on any circuits with covered conductor installed. Based on benchmarking with other IOUs and SDG&E’s testing of covered conductors, the PSPS wind speed threshold for fully covered circuit segments is expected to be set to between 55 and 60 mph. As discussed in the response to Areas for Continued Improvement SDGE-22-11 in Appendix D of the 2023-2025 Wildfire Mitigation Plan, SDG&E expects to complete covered conductor testing and finalize this threshold by December 2023. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09%20Attachment%20Q1.pdf | 1 | No | Appendix F | OEIS Table 9-2 | N/A | N/A
79 | CalPA | 2023-09 | CalPA-2023-09 | 2 | CalPA-2023-09.2 | SDG&E states on p. 418 of its 2023 WMP that, “In advance of an approaching Santa Ana Wind event, the WiNGS-Ops model is utilized as an additional data point to determine if there are areas in the service territory where the wildfire risk could outweigh the risk of PSPS.” Please list all additional “data points” that SDG&E uses, besides the WiNGS-Ops model, to determine if the wildfire risk could outweigh the risk of PSPS during an approaching Santa Ana Wind event. | Multiple factors inform the decision to de-energize. These factors are quantified into infrastructure and environmental risk factors. Infrastructure risk includes information in the field based on unresolved damage found during inspections, active temporary construction/configuration of the electrical system that may cause equipment to have de-rated mechanical strength, and a CRI that identifies locations in the electrical system with a potential of having higher failure rates. Field environment issues may also include real-time observations from QEWs, local fire authority response and fire suppression ability at the time of an event, and wind conditions. These factors are compiled and summarized by circuit section to assist with decisions to de-energize parts of the electrical system (see PSPS Decision-Making Framework). Baseline alert wind speeds are used to quantify infrastructure risk into actionable criteria. They are determined separately for each device tied to a weather station and are based on a variety of factors such as wind speeds, the VRI, and the CRI. Alert wind speed thresholds are lowered if the VRI or the CRI rating is high (see PSPS Decision-Making Framework). Other factors such as maintenance issues, existing construction, other real time observations, ongoing fires and/or ignitions, suppression capabilities, and/or system protection could lower the thresholds for specific events. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09.pdf | 0 | No | 9.2 | 9.2 Protocols on PSPS Page 416 | 9.2.2 | 9.2.2 Method that Evaluates Relative Consequences of PSPS and Wildfires Page 419
80 | CalPA | 2023-09 | CalPA-2023-09 | 3 | CalPA-2023-09.3 | Regarding PSPS and its relationship to Sensitive Relay Profile (SRP) settings: a) Please describe in detail the decision-making process for a scenario in which SDG&E anticipates PSPS conditions but decides to use SRP settings instead. b) Please list all dates in 2021 and 2022 when SDG&E anticipated PSPS conditions but utilized SRP settings instead, if this occurred. c) Please provide a narrative of the decision-making process for any instances listed in part (b) above. d) Please describe how SDG&E utilizes SRP during a PSPS event period. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E does not use SRP instead of PSPS as these two mitigations are not treated the same or used as substitutes for one another. SDG&E will utilize SRP if PSPS de-energizations are predicted or if the FPI is Extreme. These settings are implemented only during the at-risk period, not seasonally, and only in regions impacted by extreme weather. The following bullet points summarize the conditions which would warrant SRP enablement: • If the FPI is Extreme in Mountain Empire and/or Ramona, Tier 3 should have Sensitive Relay Settings enabled. • If the FPI is Extreme in Eastern and/or Northeast, the entire HFTD (Tier 2 and Tier 3) should have Sensitive Relay Settings enabled. • If the FPI is Extreme in Orange County, then the HFTD in Orange County should have Sensitive Relay Settings enabled. • If the FPI is Extreme in any of the San Diego County coastal districts (North Coast, Beach Cities, Metro) all the Coastal Circuits with Fire Risk should have Sensitive Relay Settings enabled. • If any circuits are identified for potential PSPS in Mountain Empire and/or Ramona in the Tier 3 HFTD, all circuits in the Tier 3 HFTD should have Sensitive Relay Settings enabled for the predicted PSPS district(s). • If any circuits are identified for potential PSPS in Eastern and/or Northeast or Tier 2 in Mountain Empire and Ramona, the HFTD (Tier 2 and Tier 3) should have Sensitive Relay Settings enabled for the predicted PSPS district(s). • If any circuits are identified for potential PSPS in Orange County, then the HFTD in Orange County should have Sensitive Relay Settings enabled. • If any circuits are identified for potential PSPS that are on the Coastal Circuits with Fire Risk list, then all the Coastal Circuits with Fire Risk should have Sensitive Relay Settings enabled for the predicted district(s). b) As stated above, SDG&E does not use SRP instead of PSPS as these two mitigations are not treated the same or used as substitutes for one another. c) As stated in parts a and b, SDG&E does not use SRP instead of PSPS as these two mitigations are not treated the same or used as substitutes for one another. d) SRP settings are enabled when the FPI is Extreme or PSPS de-energizations are predicted. These settings are implemented only during the at-risk period, not seasonally, and only in regions impacted by extreme weather. When SRP is enabled, SDG&E has dedicated crews staffed for restoration and readiness response. Line SCADA crews are staffed 24/7, ready to respond to collect relay event records. Once collected, the records are sent to System Protection Engineering for review, who are also on 24/7 standby whenever SRP is enabled. These records help determine proper operation and aid in determining fault location. Feedback is then provided to the operations teams for better situational awareness. Protocols for testing/reclosing/restoration are no different between SRP and non-SRP conditions when under Extreme FPI or PSPS conditions. Automatic testing is not performed, and reclosing is disabled. A complete patrol is required, and step restore is performed for all outages. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09.pdf | 0 | No | Other | PSPS | N/A | N/A
81 | CalPA | 2023-09 | CalPA-2023-09 | 4 | CalPA-2023-09.4 | Regarding OneVoice communication to customers for SRP: a) In what circumstances does SDG&E plan to use OneVoice communication while SRP is enabled. b) Please list each type of situation for which SDG&E plans to use OneVoice to communicate with a customer regarding SRP. c) Please provide an example of the message SDG&E will send to a customer for each situation in which SDG&E uses OneVoice to communicate with a customer regarding SRP. d) When did SDG&E start using OneVoice to inform customers regarding SRP? e) At what point (i.e., or number of hours) prior to enabling SRP does SDG&E use OneVoice to notify customers? f) At what point (i.e., number of hours) after an SRP caused outage does SDG&E use OneVoice to notify customers? g) At what point (i.e., number of hours) after the line is restored does SDG&E use OneVoice to notify customers? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not alter communications to customers when SRP is enabled. Outage response is no different for SRP outages versus non-SRP outages during an event. Outages are mapped on SDG&E’s public outage website with an estimated restoration time and information on outage cause. SDG&E staffs 24/7 System Protection support to review all SRP outages in real time to provide situational awareness to our operations teams in support of faster restorations. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09.pdf | 0 | No | Other | OneVoice | N/A | N/A
82 | CalPA | 2023-09 | CalPA-2023-09 | 5 | CalPA-2023-09.5 | WMP p. 375, OEIS Table 8-50 (Key Gaps and Limitations in Public Emergency Communication Strategy), states in part that “SDG&E has not been able to test notifications and messaging that were updated for the 2022 season. This messaging will be reviewed for any improvements in 2023…” Regarding SDG&E’s notifications and messaging for emergencies: a) Please provide a list of the improvements or enhancements that SDG&E made for the 2022 season. b) Please provide a list of the improvements or enhancements that SDG&E has made for the 2023 season (since the 2022 season). c) Does SDG&E conduct tests on its emergency communication processes to ensure customers are being appropriately notified? d) If the answer to part c) above is yes, when did SDG&E most recently conduct such testing? e) If the answer to part c) above is yes, please provide the results of SDG&E’s testing on its emergency communication processes. | a) A number of enhancements were made in 2022 to Enterprise Notification System (ENS) to improve data consistency across reporting and dashboards specific to PSPS events. The enhanced ENS data capabilities will support improved accuracy and consistency of data reporting in the post-event reports. Enhancements include: • Direct sync between the PSPS Dashboard and the ENS Dashboard to ensure customer counts and device lists match; • ENS data directly syncs with mobile platforms such as the Public Safety Partner Portal and mobile app to indicate customers who are de-energized and re-energized; • Enhanced notification reporting section of the ENS dashboard that allows for pre-incident, end of day, post-incident, and ad hoc reporting data to be readily available. Access opened to other key EOC positions to encourage more self-service and wider ability to cross reference and QA/QC data for post-event and post-season reporting. b) Enhancements for 2023 include Notification System Testing (NST) and streamlining data processes. Several solutions use the same data through different processes. Efforts will be made to streamline the data feeds which will lead to the eventual creation of “Enterprise Services”, a service to provide a single source of truth for data relating to PSPS de-energizations. c) SDG&E is creating a Notification System Testing (NST) program to test the notification system on a bi-annual basis. Pending internal approval, SDG&E anticipates testing will begin in Q2 2023. d) N/A - Testing has not yet been implemented. e) N/A - Testing has not yet been implemented. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09.pdf | 0 | No | 8.4 | 8.4 Emergency Preparedness Page 334 | 8.4.4.3 | 8.4.4.3 Current Gaps and Limitations Page 379
83 | OEIS | 2023-01 | OEIS-2023-01 | 1 | OEIS-2023-01.1 | Regarding Appendix B Items That Are Currently Optional Or “By Request” Only Provide the following, which are outlined in the 2023-2025 Wildfire Mitigation Plan Technical Guidelines, Appendix B. If the data is tabular (formulas, tables, graphs, charts) provide it in MS Excel. If the data is text-heavy, provide the information in MS Word. a. Detailed Model Documentation for each model and sub-model discussed in SDG&E’s response to Section 6.1.2 Summary of Risk Models (Technical documentation should be presented according to ASTM E 1472 – Standard Guide for Documenting Computer Software for Fire Models). i. Include a list of assumptions and known model limitations according to ASTM E 1895 – Standard Guide for Determining Uses and Limitations of Deterministic Fire Models. ii. Present verification and validation documentation according to the SFPE’s Guidelines for Substantiating a Fire Model for a Given Application or ASTM E 1355 – Standard Guide for Evaluating the Predicting Capability of Deterministic Fire Models. At a minimum, the documentation must include:1 (1) Purpose of the model/problem identification (2) Model version (3) Theoretical foundation (4) Mathematical foundation (5) External dependencies (6) Model substantiation (7) Sensitivity b. Model Substantiation:2 i. For each model, provide documentation of the following model substantiation studies: (1) Validation data (2) Model verification (3) Model validation (4) Model calibration c. Additional Models Supporting Risk Calculation:3 i. For each additional model that supports the risk calculations, provide weather analysis and fuel conditions. d. Calculation of Risk and Risk Components: Likelihood:4 i. More detailed information on: (1) Ignition Likelihood (2) Equipment Likelihood of Ignition (3) Contact from Vegetation Likelihood of Ignition (4) Contact from Object Likelihood of Ignition (5) Burn Probability (6) PSPS Likelihood e. Calculation of Risk and Risk Components: Consequence5 i. More detailed information on: (1) Wildfire Consequence (2) Wildfire Hazard Intensity (3) Wildfire Exposure Potential (4) Wildfire Vulnerability f. Calculation of Risk and Risk Components: PSPS Consequence6 i. More detailed information on: (1) PSPS Exposure Potential (2) Community Vulnerability to PSPS g. Calculation of Risk and Risk Components: Risk7 i. More detailed information on: (1) Ignition Risk (2) PSPS Risk (3) Overall Utility Risk | Link to the 2023 WMP: https://www.sdge.com/2023-wildfire-mitigation-plan WMP technical documentation: Attached as ”Model Documentation_Wings Planning V1.pdf,” and “Model Documentation_WiNGS-Ops V1.pdf.” WiNGS Planning: i. Reference section 6.2.3 of WMP 2023, page 73. ii. Reference section 2.6 of technical document for WiNGS Planning. At a minimum, the documentation must include:8 (1) Purpose of the model/problem identification – reference section 1.1 - Technical document for Wings Planning (2) Model version = reference section 1.2 - Technical document for Wings Planning (3) Theoretical foundation – reference section 2.3 - Technical document for Wings Planning (4) Mathematical foundation – reference section 2.4 - Technical document for Wings Planning (5) External dependencies –reference section 2.5.1 - Technical document for Wings Planning (6) Model substantiation - reference section 2.6 - Technical document for Wings Planning (7) Sensitivity – reference section 2.6.2 - Technical document for Wings Planning b. Model Substantiation:9 i. For each model, provide documentation of the following model substantiation studies: (1) Validation data reference section 2.6.2 - Technical document for Wings Planning (2) Model verification - reference section 2.6.1 - Technical document for Wings Planning (3) Model validation - reference section 2.6.2 - Technical document for Wings Planning (4) Model calibration - reference section 2.6.3 - Technical document for Wings Planning c. Additional Models Supporting Risk Calculation:10 i. For each additional model that supports the risk calculations, provide weather analysis and fuel conditions. Reference section 2.5 - Technical document for Wings Planning d. Calculation of Risk and Risk Components: Likelihood:11 i. More detailed information on: reference section 6.2.2.1, page 68 - Technical document for Wings Planning (1) Ignition Likelihood (2) Equipment Likelihood of Ignition (3) Contact from Vegetation Likelihood of Ignition (4) Contact from Object Likelihood of Ignition (5) Burn Probability (6) PSPS Likelihood e. Calculation of Risk and Risk Components: Consequence12 i. More detailed information on: - reference WMP 2023 section 6.2.2.2 page 70 (1) Wildfire Consequence (2) Wildfire Hazard Intensity (3) Wildfire Exposure Potential (4) Wildfire Vulnerability f. Calculation of Risk and Risk Components: PSPS Consequence13 i. More detailed information on: reference WMP 2023 section 6.2.2.2 page 70 (1) PSPS Exposure Potential (2) Community Vulnerability to PSPS g. Calculation of Risk and Risk Components: Risk14 i. More detailed information on: reference section 6.2.1 and 6.2.2 of WMP 2023, page 59 and 64 (1) Ignition Risk (2) PSPS Risk (3) Overall Utility Risk WiNGS Ops: i. Reference section 6.2.3 of WMP 2023, page 73 ii. Reference section 2.6 of technical document for WiNGS Ops (1) Purpose of the model/problem identification – Section 1.1 - Technical documentation for WiNGS Ops (2) Model version - (3) Theoretical foundation – Section 2.2.1 – Technical documentation for WiNGS Ops (4) Mathematical foundation Section 2.2.1 - Technical documentation for WiNGS Ops (5) External dependencies – (6) Model substantiation - Section 2.6 - Technical documentation for WiNGS Ops (7) Sensitivity – Section 2.6.2 - Technical documentation for WiNGS Ops b. Model Substantiation:15 Section 2.6 - Technical documentation for WiNGS Ops i. For each model, provide documentation of the following model substantiation studies: (1) Validation data (2) Model verification – Section 2.6.1 - Technical documentation for WiNGS Ops (3) Model validation – Section 2.6.2 - Technical documentation for WiNGS Ops (4) Model calibration – Section 2.2.3 - Technical documentation for WiNGS Ops | Sara Moore | 2023-04-07 | 2023-04-12 | 2023-04-12 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01%20Attachment%20Q1%20%26%20Q2.zip | 1 | No | 6 | 6 RISK METHODOLOGY AND ASSESSMENT PAGE 52 | 6.1.2 | 6.1.2 Summary of Risk Models Page 54
84 | OEIS | 2023-01 | OEIS-2023-01 | 2 | OEIS-2023-01.2 | Regarding Comprehensive System Diagram for All Risk Models Used Provide comprehensive system diagrams in MS Visio or PPT for all risk models, including: 1. A comprehensive diagram for operational models 2. A comprehensive diagram for planning models Section 6.1.2, Summary of Risk Models, asks for a summary of risk models in table form with specific fields. Section 6.2.1, Risk and Risk Component Identification, asks for a chart that demonstrates the components of overall utility risk. This request is comprehensive of all models that work together in the Decision-Making Framework (DMF). The requested diagram should show: a. Interaction between the models presented graphically (e.g., inputs and outputs coming to and going from models to other models) b. Organization with the use of swimlanes where applicable c. Starting and ending points d. Decisions and process flows e. Use of a legend and colors to classify inputs/output types and model-to-model interactions f. The full cycle of models working together and creating feedback for model adjustments and fine-tuning | a.WiNGS Planning (Figure 6-7 – WMP 2023) WiNGS Ops Risk Calculation Process Flow Diagram (Figure 6-5 – WMP 2023) WiNGS-Ops (Figure 6-8 – WMP 2023) b. Please see response/figures in part a. c. Please see response/figures in part a. d. WiNGS Planning – Mitigation initiative prioritization (Figure 7-4 – WMP 2023) WiNGS Ops – PSPS Decision Making Framework e. Please see response/figures in part a. f. Please see “Model Documentation_Wings Planning V1.pdf,” section 2.6.2 Validation and 2.6.3 Calibration. Additionally see the “Model Documentation_WiNGS-Ops V1.pdf” section 2.6.2 Validation and 2.6.3 Calibration. | Sara Moore | 2023-04-07 | 2023-04-12 | 2023-04-12 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01%20Attachment%20Q1%20%26%20Q2.zip | 1 | No | 6 | 6 RISK METHODOLOGY AND ASSESSMENT PAGE 52 | 6.1.2 | 6.1.2 Summary of Risk Models Page 54
85 | OEIS | 2023-01 | OEIS-2023-01 | 3 | OEIS-2023-01.3 | Regarding Portfolio Level Risk Analysis and Risk Spend Efficiency a. Provide an example of how risks are aggregated to a portfolio, and if and how interdependencies between the risks are explicitly captured in the portfolio. Response should be provided in Excel. Also include the level of organization for the portfolio (e.g., asset, geographical or business unit). b. Are tail-risks calculated on a portfolio of risks? If so, provide an example. c. Are probability distributions and interdependencies used as inputs to outputs for the bowties used in SDG&E’s WMP submission (see examples present in Appendix B)? If so, provide an example using the bowtie charts presented in SDG&E’s Appendix B submission. As appropriate, the response should be provided in Excel. d. Provide an example of how risk spend efficiency (RSE) deals with interdependent risks, and mutually exclusive risks. As appropriate, the response should be provided in Excel. e. Is RSE calculated for both average and tail? If so, provide an example. The response should be provided in Excel. | a. Per the WiNGS-Planning model risk inputs, inputs are assessed and treated as independent risk drivers and metrics that support the calculation of the risk scores, per the weighted sum framework of the model. The WiNGS-Planning model granularity is at the circuit-segment level. For the portfolio level reporting of the risk scores from the model, the risk scores are subsequently sum aggregated from the circuit-segment level to the portfolio level granularity. See attached .csv file “Question 3a - WF and PSPS risk scores - 2023 wmp output.csv” for the output of circuit-segment risk scores prior to sum aggregation to the portfolio level granularity, indicating how risk scores are aggregated. b. The top 5%, top 20%, and bottom 80% are calculated on the WiNGS Planning output. Please see SDG&E WMP 2023 - table 6.5 for a reference of the top 5% wildfire risk circuit segments. c. Assuming the bowties referred to are the flow diagrams (Figures 1 & 2) present in 2023 WMP Appendix B, two probability distributions are used as inputs to the model: FIRE SIMULATIONS (WRRM metrics) (percentiles) (Figure 2) and WEATHER DATA (percentiles) (Figure 2). No interdependencies are used as inputs. d. Per the WiNGS-Planning model risk inputs, inputs are assessed and treated as independent risk drivers and metrics that support the calculation of the risk scores. As such, RSE does not need to deal with interdependent or mutually exclusive risks as they are not present as inputs to the model. e. Within WiNGS-Planning, an RSE value is calculated for each circuit-segment mitigation combination. The RSE value is neither an average nor a tail value, but a single RSE value calculated from the risk reduction and cost assessed associated to the selected circuit-segment mitigation combination. | Sara Moore | 2023-04-07 | 2023-04-12 | 2023-04-12 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01%20Attachment%20Q3.zip | 1 | No | Other | Portfolio Level Risk Analysis and Risk Spend Efficiency | N/A | N/A
86 | OEIS | 2023-01 | OEIS-2023-01 | 4 | OEIS-2023-01.4 | Regarding Cost-Benefit Within and Overall Decision-Making Framework a. If projects are justified based on a multi-attribute value functions/cost basis, what threshold or hurdle is used? b. How is the chance that a project exceeds the threshold computed? c. If projects are justified based on a multi-attribute value functions/cost basis, what threshold or hurdle is used? | a. A financial analysis was conducted analyzing different portfolios ultimately identified the risk mitigation and hardening strategy that reflected the inflection point between risk and cost. The RSE threshold is set to meet targeted risk reduction percentages over time, while also meeting construction mileage targets. To achieve the desired risk reduction, the RSE threshold based on the model that forms the basis of SDG&E’s 2023 Wildfire Mitigation Plan was 29. The WiNGS model employs a decision tree to select mitigations. The decision tree does not compare covered conductor RSE to underground RSE. The first branch on the decision tree is to measure the validity of undergrounding per segment. Each segment is qualified as whether it meets the RSE for undergrounding. If the segment meets or exceeds the undergrounding RSE, the model recommends undergrounding as the proposed mitigation. Segments that do not meet the undergrounding RSE, are then evaluated for covered conductor mitigations. If the RSE for covered conductor is met or exceeded, the proposed mitigation is covered conductor. When neither condition is met, no mitigation is recommended. b. For every mitigation project informed by the WiNGS-Planning model, the project is required to have met the threshold framework described above and have had an optimal recommended mitigation assigned to it. Therefore, every project will have met the threshold prior to implementation. c. Please see response a. | Sara Moore | 2023-04-07 | 2023-04-12 | 2023-04-12 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01.pdf | 0 | No | Other | Cost-Benefit Within and Overall Decision-Making Framework | N/A | N/A
559 |  |  | - |  | -.
560 |  |  | - |  | -.
561 |  |  | - |  | -.
562 |  |  | - |  | -.
563 |  |  | - |  | -.
564 |  |  | - |  | -.
565 |  |  | - |  | -.
566 |  |  | - |  | -.
567 |  |  | - |  | -.
568 |  |  | - |  | -.
569 |  |  | - |  | -.
570 |  |  | - |  | -.
571 |  |  | - |  | -.

## WMP Sections (hidden)
1 | 1 EXECUTIVE SUMMARY Page 1 | 1
1.1 | 1.1 Summary of 2020–2022 WMP Cycle Page 1 | 1
1.1.1 | 1.1.1 Major Lessons Learned Page 4 | 4
1.1.1.1 | 1.1.1.1 Risk Methodology and Assessment Page 4 | 4
1.1.1.2 | 1.1.1.2 Wildfire Mitigation StrategyPage 5 | 5
1.1.1.3 | 1.1.1.3 Grid Design, Operations, and Maintenance Page 5 | 5
1.1.1.4 | 1.1.1.4 Vegetation Management and Inspections Page6 | 6
1.1.1.5 | 1.1.1.5 Situational Awareness and Forecasting Page 6 | 6
1.1.1.6 | 1.1.1.6 Emergency Preparedness Page 6 | 6
1.1.1.7 | 1.1.1.7 Community Outreach and Engagement Page 7 | 7
1.1.1.8 | 1.1.1.8 PSPS Page 7 | 7
1.2 | 1.2 Summary of 2023–2025 Base WMP Page7 | 7
1.2.1 | 1.2.1 Framework Page 8 | 8
1.2.2 | 1.2.2 Goal of the WMP Page 9 | 9
1.2.3 | 1.2.3 Plan Objectives Page 9 | 9
2 | 2 RESPONSIBLE PERSONS Page 11 | 11
3 | 3 STATUTORY REQUIREMENTS CHECKLIST Page 13 | 13
4 | 4 OVERVIEW OF WMP Page 16 | 16
4.1 | 4.1 Primary Goal Page 16 | 16
4.2 | 4.2 Plan Objectives Page 16 | 16
4.2.1.1 | 4.2.1.1 Risk Methodology and Assessment Page 16 | 16
4.2.1.2 | 4.2.1.2 Wildfire Mitigation Strategy Page 16 | 16
4.2.1.3 | 4.2.1.3 Grid Design, Operations, and Maintenance Page 16 | 16
4.2.1.4 | 4.2.1.4 Vegetation Management and Inspections Page 17 | 17
4.2.1.5 | 4.2.1.5 Situational Awareness and Forecasting Page 17 | 17
4.2.1.6 | 4.2.1.6 Emergency Preparedness Page 17 | 17
4.2.1.7 | 4.2.1.7 Community Outreach and Engagement Page 18 | 18
4.2.1.8 | 4.2.1.8 Public Safety Power Shutoff Page 18 | 18
4.3 | 4.3 Proposed Expenditures Page 18 | 18
4.4 | 4.4 Risk Informed Framework Page 19 | 19
4.4.1 | 4.4.1 Risk Assessment: Identification, Analysis, Evaluation, and Prioritization Page 21 | 21
4.4.2 | 4.4.2 Risk Strategy: Plan Development, Investment Decisions, Implementation, and Review Page 22 | 22
5 | 5 OVERVIEW OF THE SERVICE TERRITORY Page 25 | 25
5.1 | 5.1 Service Territory Page 25 | 25
5.2 | 5.2 Electrical Infrastructure Page 26 | 26
5.3 | 5.3 Environmental Settings Page 27 | 27
5.3.1 | 5.3.1 Fire Ecology Page 27 | 27
5.3.1.1 | 5.3.1.1 Ecological Regions Page 27 | 27
5.3.1.2 | 5.3.1.2 Climate and Weather Conditions Page 28 | 28
5.3.1.3 | 5.3.1.3 Fire Return Intervals Page 28 | 28
5.3.2 | 5.3.2 Catastrophic Wildfire History Page 29 | 29
5.3.3 | 5.3.3 High Fire Threat Districts Page 31 | 31
5.3.4 | 5.3.4 Climate Change Page 33 | 33
5.3.4.1 | 5.3.4.1 General Climate Conditions Page 33 | 33
5.3.4.2 | 5.3.4.2 Climate Change Phenomena and Trends Page35 | 35
5.3.5 | 5.3.5 Topography Page 39 | 39
5.4 | 5.4 Community Values at Risk Page 40 | 40
5.4.1 | 5.4.1 Urban, Rural, and Highly Rural Customers Page 40 | 40
5.4.2 | 5.4.2 Wildland-Urban Interfaces Page 41 | 41
5.4.3 | 5.4.3 Communities at Risk from Wildfire Page 41 | 41
5.4.3.1 | 5.4.3.1 Individuals at Risk from Wildfire Page 41 | 41
5.4.3.2 | 5.4.3.2 Social Vulnerability and Exposure to Electrical Corporation Wildfire Risk Page 42 | 42
5.4.3.3 | 5.4.3.3 Sub-Divisions with Limited Egress or No Secondary Egress Page 43 | 43
5.4.4 | 5.4.4 Critical Facilities and Infrastructure at Risk from Wildfire Page 44 | 44
5.4.5 | 5.4.5 Environmental Compliance and Permitting Page 46 | 46
5.4.5.1 | 5.4.5.1 Processes to Ensure Compliance Page 46 | 46
5.4.5.1.1 | 5.4.5.1.1 Environmental Services Page 46 | 46
5.4.5.1.2 | 5.4.5.1.2 Programmatic Endangered Species Act Permitting/Authorization Page 46 | 46
5.4.5.1.3 | 5.4.5.1.3 Cultural Resources Program Page 48 | 48
5.4.5.1.4 | 5.4.5.1.4 Municipal and State Agency Permits Page 49 | 49
5.4.5.2 | 5.4.5.2 Overcoming Roadblocks Page 50 | 50
5.4.5.3 | 5.4.5.3 Notable Changes to Environmental Compliance and/or Permitting Procedures Page 51 | 51
6 | 6 RISK METHODOLOGY AND ASSESSMENT PAGE 52 | 52
6.1 | 6.1 Methodology Page 52 | 52
6.1.1 | 6.1.1 Overview Page 52 | 52
6.1.2 | 6.1.2 Summary of Risk Models Page 54 | 54
6.2 | 6.2 Risk Analysis Framework Page 59 | 59
6.2.1 | 6.2.1 Risk and Risk Component Identification Page 59 | 59
6.2.2 | 6.2.2 Risk and Risk Components Calculation Page 64 | 64
6.2.2.1 | 6.2.2.1 Likelihood Page 68 | 68
6.2.2.2 | 6.2.2.2 Consequence Page 70 | 70
6.2.2.3 | 6.2.2.3 Risk Page 72 | 72
6.2.3 | 6.2.3 Key Assumptions and Limitations Page 73 | 73
6.3 | 6.3 Risk Scenarios Page 75 | 75
6.3.1 | 6.3.1 Design Basis Scenarios Page 76 | 76
6.3.2 | 6.3.2 Extreme-Event/High Uncertainty Scenarios Page 79 | 79
6.4 | 6.4 Risk Analysis Results and Presentation Page 80 | 80
6.4.1 | 6.4.1 Top Risk Areas within the HFRA Page 81 | 81
6.4.1.1 | 6.4.1.1 Geospatial Maps of Top-Risk Areas within the HFRA Page 83 | 83
6.4.1.2 | 6.4.1.2 Proposed Updates to HFTD Page 83 | 83
6.4.2 | 6.4.2 Top Risk-Contributing Circuits/Segments/Spans Page 84 | 84
6.4.3 | 6.4.3 Other Key Metrics Page 85 | 85
6.4.3.1 | 6.4.3.1 FPI Page 85 | 85
6.4.3.2 | 6.4.3.2 Red Flag Warning Page 85 | 85
6.4.3.3 | 6.4.3.3 High Wind Warnings Page 85 | 85
6.5 | 6.5 Enterprise System for Risk Assessment Page 86 | 86
6.6 | 6.6 Quality Assessment and Control Page 87 | 87
6.6.1 | 6.6.1 Independent Review Page 87 | 87
6.6.2 | 6.6.2 Model Controls, Design, and Review Page 89 | 89
6.6.2.1 | 6.6.2.1 Modularization Page 89 | 89
6.6.2.2 | 6.6.2.2 Reanalysis Page 89 | 89
6.6.2.3 | 6.6.2.3 Version Control Page 90 | 90
6.7 | 6.7 Risk Assessment Improvement Plan Page 90 | 90
6.7.1 | 6.7.1 RA-1-A Evaluate Additional Wildfire and PSPS Risk Assessment Factors Page 94 | 94
6.7.1.1 | 6.7.1.1 Problem Statement Page 94 | 94
6.7.1.2 | 6.7.1.2 Planned Improvement Page 94 | 94
6.7.1.3 | 6.7.1.3 Anticipated Benefit Page 95 | 95
6.7.1.4 | 6.7.1.4 Region Prioritization Page 95 | 95
6.7.2 | 6.7.2 RA-1-B Enhance Model Design and Architecture Page 95 | 95
6.7.2.1 | 6.7.2.1 Problem Statement Page 95 | 95
6.7.2.2 | 6.7.2.2 Planned Improvement Page 95 | 95
6.7.2.3 | 6.7.2.3 Anticipated Benefit Page 95 | 95
6.7.3 | 6.7.3 RA-2-A Evaluate Design and Extreme-Event Scenarios Page 96 | 96
6.7.3.1 | 6.7.3.1 Problem Statement Page 96 | 96
6.7.3.2 | 6.7.3.2 Planned Improvement Page 96 | 96
6.7.3.3 | 6.7.3.3 Anticipated Benefit Page 96 | 96
6.7.4 | 6.7.4 RA-3-A Establish Process to Continuously Evaluate HFTD Boundaries Page 96 | 96
6.7.4.1 | 6.7.4.1 Problem Statement Page 96 | 96
6.7.4.2 | 6.7.4.2 Planned Improvement Page 97 | 97
6.7.4.3 | 6.7.4.3 Anticipated Benefit Page 97 | 97
6.7.5 | 6.7.5 RA-3-B Enhance Model Documentation Page 97 | 97
6.7.5.1 | 6.7.5.1 Problem Statement Page 97 | 97
6.7.5.2 | 6.7.5.2 Planned Improvement Page 97 | 97
6.7.5.3 | 6.7.5.3 Anticipated Benefit Page 97 | 97
6.7.6 | 6.7.6 RA-4-A Improve Procedure for Independent Reviews of Data and Models Page 97 | 97
6.7.6.1 | 6.7.6.1 Problem Statement Page 97 | 97
6.7.6.2 | 6.7.6.2 Planned Improvement Page 98 | 98
6.7.6.3 | 6.7.6.3 Anticipated Benefit Page 98 | 98
6.7.7 | 6.7.7 RA-4-B Enhance Model Validation Process Page 98 | 98
6.7.7.1 | 6.7.7.1 Problem Statement Page 98 | 98
6.7.7.2 | 6.7.7.2 Planned Improvement Page 98 | 98
6.7.7.3 | 6.7.7.3 Anticipated Benefit Page 98 | 98
6.1.1 | 6.1.1 RA-5-A Deploy and Enhance WiNGS-Ops and WiNGS-Planning Visualization Platforms Page 99 | 99
6.7.7.4 | 6.7.7.4 Problem Statement Page 99 | 99
6.7.7.5 | 6.7.7.5 Planned Improvement Page 99 | 99
6.7.7.6 | 6.7.7.6 Anticipated Benefit Page 99 | 99
6.7.7.7 | 6.7.7.7 Region Prioritization Page 99 | 99
7 | 7 WILDFIRE MITIGATION STRATEGY DEVELOPMENT PAGE 100 | 100
7.1 | 7.1 Risk Evaluation Page 100 | 100
7.1.1 | 7.1.1 Approach Page 100 | 100
7.1.2 | 7.1.2 Key Stakeholders for Decision Making Page 100 | 100
7.1.3 | 7.1.3 Risk-Informed Prioritization Page 102 | 102
7.1.3.1 | 7.1.3.1 Selection of Areas for Mitigation Page 102 | 102
7.1.3.1.1 | 7.1.3.1.1 Geographic Scale used in Prioritization Page 102 | 102
7.1.3.1.2 | 7.1.3.1.2 Statistical Approach used to Select Candidates Page 102 | 102
7.1.3.1.3 | 7.1.3.1.3 Feasibility Constraints Page 103 | 103
7.1.3.2 | 7.1.3.2 Prioritized List of Risks Page 104 | 104
7.1.4 | 7.1.4 Mitigation Selection Process Page 104 | 104
7.1.4.1 | 7.1.4.1 Identifying and Evaluating Mitigation Initiatives Page 105 | 105
7.1.4.1.1 | 7.1.4.1.1 Procedures to Develop Mitigation Initiatives Page 105 | 105
7.1.4.1.2 | 7.1.4.1.2 Mitigation Initiatives that Address Local Wildfire Risk Drivers Page 105 | 105
7.1.4.1.3 | 7.1.4.1.3 Characterization of Uncertainties and Incorporation into the Decision-Making Process Page 106 | 106
7.1.4.1.4 | 7.1.4.1.4 Potential Mitigation Initiatives Page 106 | 106
7.1.4.1.5 | 7.1.4.1.5 MAVF and other Specific Risk Factors Page 108 | 108
7.1.4.2 | 7.1.4.2 Mitigation Initiative Prioritization Page 108 | 108
7.1.4.2.1 | 7.1.4.2.1 Evaluation of Potential Mitigation Initiatives Page 108 | 108
7.1.4.2.2 | 7.1.4.2.2 Identification of Mitigation Initiatives Page 109 | 109
7.1.4.2.3 | 7.1.4.2.3 Resource Optimization Page 111 | 111
7.1.4.2.4 | 7.1.4.2.4 Mitigation Initiative Prioritization to Reduce both Wildfire and PSPS Risk Page 113 | 113
7.1.4.3 | 7.1.4.3 Mitigation Initiative Scheduling Page 116 | 116
7.1.4.3.1 | 7.1.4.3.1 Mitigation Initiative Scheduling Page 116 | 116
7.1.4.3.2 | 7.1.4.3.2 Interim Mitigation Process Page 116 | 116
7.1.4.3.3 | 7.1.4.3.3 Monitoring Progress toward Targets with Known Limitations and Constraints Page 116 | 116
7.1.4.3.4 | 7.1.4.3.4 Measuring Effectiveness of Mitigation Initiatives Page 116 | 116
7.2 | 7.2 Wildfire Mitigation Strategy Page 117 | 117
7.2.1 | 7.2.1 Overview of Mitigation Initiatives and Activities Page 118 | 118
7.2.2 | 7.2.2 Anticipated Risk Reduction Page 120 | 120
7.2.2.1 | 7.2.2.1 Projected Overall Risk Reduction Page 120 | 120
7.2.2.2 | 7.2.2.2 Risk Impact of Mitigation Initiatives Page 123 | 123
7.2.2.3 | 7.2.2.3 Projected Risk Reduction on Highest-Risk Circuits Over the Three-Year WMP Cycle Page 125 | 125
7.2.3 | 7.2.3 Interim Mitigation Activities Page 127 | 127
8 | 8 WILDFIRE MITIGATIONS Page 129 | 129
8.1 | 8.1 Grid Design, Operations, and Maintenance Page 129 | 129
8.1.1 | 8.1.1 Overview Page 129 | 129
8.1.1.1 | 8.1.1.1 Objectives Page 131 | 131
8.1.1.2 | 8.1.1.2 Targets Page 140 | 140
8.1.1.3 | 8.1.1.3 Performance Metrics Page 145 | 145
8.1.1.3.1 | 8.1.1.3.1 Distribution Inspection Findings and Open Work Orders Page 147 | 147
8.1.1.3.2 | 8.1.1.3.2 Distribution Equipment related HFTD Ignitions and Outages Rate Page 148 | 148
8.1.1.3.3 | 8.1.1.3.3 Transmission Inspection Findings and Open Work Orders in HFTD Page 148 | 148
8.1.1.3.4 | 8.1.1.3.4 Transmission Equipment related HFTD Outages and Ignitions Page 149 | 149
8.1.2 | 8.1.2 Grid Design and System Hardening Page 150 | 150
8.1.2.1 | 8.1.2.1 Covered Conductor Installation Page 150 | 150
8.1.2.1.1 | 8.1.2.1.1 Utility Initiative Tracking ID Page 150 | 150
8.1.2.1.2 | 8.1.2.1.2 Overview of the Activity Page 150 | 150
8.1.2.1.3 | 8.1.2.1.3 Impact of the Activity on Wildfire Risk Page 151 | 151
8.1.2.1.4 | 8.1.2.1.4 Impact of the Activity on PSPS Risk Page 151 | 151
8.1.2.1.5 | 8.1.2.1.5 Updates to Initiative Page 152 | 152
8.1.2.2 | 8.1.2.2 Undergrounding of Electric Lines and/or Equipment Page 152 | 152
8.1.2.2.1 | 8.1.2.2.1 Utility Initiative Tracking ID Page 152 | 152
8.1.2.2.2 | 8.1.2.2.2 Overview of the Activity Page 152 | 152
8.1.2.2.3 | 8.1.2.2.3 Impact of the Activity on Wildfire Risk Page 153 | 153
8.1.2.2.4 | 8.1.2.2.4 Impact of the Activity on PSPS Risk Page 153 | 153
8.1.2.2.5 | 8.1.2.2.5 Updates to the Activity Page 153 | 153
8.1.2.3 | 8.1.2.3 Distribution Pole Replacements and Reinforcements Page 154 | 154
8.1.2.3.1 | 8.1.2.3.1 Utility Initiative Tracking ID Page 154 | 154
8.1.2.3.2 | 8.1.2.3.2 Overview of the Activity Page 154 | 154
8.1.2.3.3 | 8.1.2.3.3 Impact of the Activity on Wildfire Risk Page 155 | 155
8.1.2.3.4 | 8.1.2.3.4 Impact of the Activity on PSPS Risk Page 155 | 155
8.1.2.3.5 | 8.1.2.3.5 Updates to the Activity Page 155 | 155
8.1.2.4 | 8.1.2.4 Transmission Pole/Tower Replacements and Reinforcements Page 155 | 155
8.1.2.4.1 | 8.1.2.4.1 Utility Initiative Tracking ID Page 155 | 155
8.1.2.4.2 | 8.1.2.4.2 Overview of the Activity Page 155 | 155
8.1.2.4.3 | 8.1.2.4.3 Impact of the Activity on Wildfire Risk Page 155 | 155
8.1.2.4.4 | 8.1.2.4.4 Impact of the Activity on PSPS Risk Page 155 | 155
8.1.2.4.5 | 8.1.2.4.5 Updates to the Activity Page 156 | 156
8.1.2.5 | 8.1.2.5 Traditional Overhead Hardening Page 156 | 156
8.1.2.5.1 | 8.1.2.5.1 Distribution Overhead System Hardening (Traditional) Page 156 | 156
8.1.2.5.2 | 8.1.2.5.2 Transmission System Hardening Program Page 157 | 157
8.1.2.6 | 8.1.2.6 Emerging Grid Hardening Technology Installations and Pilots Page 160 | 160
8.1.2.7 | 8.1.2.7 Microgrids Page 160 | 160
8.1.2.7.1 | 8.1.2.7.1 Utility Initiative Tracking ID Page 160 | 160
8.1.2.7.2 | 8.1.2.7.2 Overview of the Activity Page 160 | 160
8.1.2.7.3 | 8.1.2.7.3 Impact of the Activity on Wildfire Risk Page 160 | 160
8.1.2.7.4 | 8.1.2.7.4 Impact of the Activity on PSPS Risk Page 161 | 161
8.1.2.7.5 | 8.1.2.7.5 Updates to the Activity Page 161 | 161
8.1.2.8 | 8.1.2.8 Installation of System Automation Equipment Page 162 | 162
8.1.2.8.1 | 8.1.2.8.1 Advanced Protection Page 162 | 162
8.1.2.8.2 | 8.1.2.8.2 Early Fault Detection Page 165 | 165
8.1.2.8.3 | 8.1.2.8.3 Distribution Communications Reliability Improvements Page 168 | 168
8.1.2.9 | 8.1.2.9 Line Removal (in HFTD) Page 169 | 169
8.1.2.9.1 | 8.1.2.9.1 Utility Initiative Tracking ID Page 169 | 169
8.1.2.9.2 | 8.1.2.9.2 Overview of the Activity Page 169 | 169
8.1.2.9.3 | 8.1.2.9.3 Impact of the Activity on Wildfire Risk Page 170 | 170
8.1.2.9.4 | 8.1.2.9.4 Impact of the Activity on PSPS Risk Page 170 | 170
8.1.2.9.5 | 8.1.2.9.5 Updates to the Activity Page 170 | 170
8.1.2.10 | 8.1.2.10 Other Grid Topology Improvements to Minimize Risk of Ignitions Page 170 | 170
8.1.2.10.1 | 8.1.2.10.1 SCADA Capacitors Maintenance and Replacement Program Page 170 | 170
8.1.2.10.2 | 8.1.2.10.2 Expulsion Fuse Replacement Program Page 172 | 172
8.1.2.10.2 | 8.1.2.10.3 Hotline Clamp Replacement Program Page 174 | 174
8.1.2.10.4 | 8.1.2.10.4 Lightning Arrestor Removal and Replacement Page 175 | 175
8.1.2.10.5 | 8.1.2.10.5 Avian Protection Program Page 177 | 177
8.1.2.10.6 | 8.1.2.10.6 Strategic Pole Replacement Program Page 178 | 178
8.1.2.10.7 | 8.1.2.10.7 Wireless Fault Indicators (WFIs) Page 180 | 180
8.1.2.11.11 | 8.1.2.11 Other Grid Topology Improvements to Mitigate or Reduce PSPS Events Page 181 | 181
8.1.2.11.1 | 8.1.2.11.1 PSPS Sectionalizing Enhancement Program Page 181
8.1.2.11.2 | 8.1.2.11.2 Standby Power Programs (Fixed Backup Power: Residential/Commercial) Page 182 | 182
8.1.2.11.3 | 8.1.2.11.3 Generator Grant Program Page 184 | 184
8.1.2.11.4 | 8.1.2.11.4 Generator Assistance Program Page 186 | 186
8.1.2.12 | 8.1.2.12 Other Technologies and Systems not Listed Above Page 187 | 187
8.1.2.12.1 | 8.1.2.12.1 Utility Initiative Tracking ID Page 187 | 187
8.1.2.12.2 | 8.1.2.12.2 Overview of the Activity Page 187 | 187
8.1.2.12.3 | 8.1.2.12.3 Impact of the Activity on Wildfire Risk Page 187 | 187
8.1.2.12.4 | 8.1.2.12.4 Impact of the Activity on PSPS Risk Page 187 | 187
8.1.2.12.5 | 8.1.2.12.5 Updates to the Activity Page 188 | 188
8.1.3 | 8.1.3 Asset Inspections Page 188 | 188
8.1.3.1 | 8.1.3.1 Distribution Overhead Detailed Inspections (WMP.478) Page 189 | 189
8.1.3.2 | 8.1.3.2 Transmission Overhead Detailed Inspections (WMP.479) Page 191 | 191
8.1.3.3 | 8.1.3.3 Distribution Infrared Inspections (WMP.481) Page 195 | 195
8.1.3.4 | 8.1.3.4 Transmission Infrared Inspections (WMP.482) Page 197 | 197
8.1.3.5 | 8.1.3.5 Distribution Wood Pole Intrusive Inspections (WMP.483) Page 199 | 199
8.1.3.6 | 8.1.3.6 Transmission Wood Pole Intrusive Inspections (WMP.1190) Page 202 | 202
8.1.3.7 | 8.1.3.7 Drone Assessments (WMP.552) Page 202 | 202
8.1.3.8 | 8.1.3.8 Distribution Overhead Patrol Inspections (WMP.488) Page 208 | 208
8.1.3.9 | 8.1.3.9 Transmission Overhead Patrol Inspections (WMP.489) Page 210 | 210
8.1.3.10 | 8.1.3.10 Transmission 69kV Tier 3 Visual Inspections (WMP.555) Page 213 | 213
8.1.3.11 | 8.1.3.11 Substation Patrol Inspections (WMP.492) Page 214 | 214
8.1.3.12 | 8.1.3.12 Discontinued Asset Inspection Programs Page 216 | 216
8.1.3.12 | 8.1.3.12.1 LiDAR Inspections of Transmission and Distribution Electric Lines and Equipment Page 216 | 216
8.1.3.12 | 8.1.3.12.2 HFTD Tier 3 Distribution Pole Inspections Page 217 | 217
8.1.4 | 8.1.4 Equipment Maintenance and Repair Page 217 | 217
8.1.4.1 | 8.1.4.1 Maintenance, Repair, and Replacement Strategies Page 217 | 217
8.1.4.2 | 8.1.4.2 Impact of Inspection Programs Page 219 | 219
8.1.5 | 8.1.5 Asset Management and Inspection Enterprise System(s) Page 220 | 220
8.1.5.1 | 8.1.5.1 Distribution Systems Page 220 | 220
8.1.5.2 | 8.1.5.2 Transmission Systems Page 220 | 220
8.1.5.3 | 8.1.5.3 Substation Systems Page 221 | 221
8.1.5.4 | 8.1.5.4 Integrated Asset Management Systems Page 222 | 222
8.1.5.4 | 8.1.5.4.1 WMP Data Platform Page 222 | 222
8.1.5.4 | 8.1.5.4.2 Asset 360 Page 223 | 223
8.1.5.4.3 | 8.1.5.4.3 Intelligent Image Processing Page 25 | 225
8.1.6 | 8.1.6 Quality Assurance and Quality Control Page 226 | 226
8.1.6.1 | 8.1.6.1 QA/QC of Transmission Inspections (WMP.1191) Page 227 | 227
8.1.6.2 | 8.1.6.2 QA/QC of Distribution Detailed Inspections (WMP.491) Page 227 | 227
8.1.6.3 | 8.1.6.3 QA/QC of Distribution Drone Assessments (WMP.1192) Page 228 | 228
8.1.6.4 | 8.1.6.4 QA/QC of Transmission & Distribution Wood Pole Intrusive Inspections (WMP.1193) Page 228 | 228
8.1.6.5 | 8.1.6.5 QA/QC of Substation Inspections (WMP.1194) Page 228 | 228
8.1.7 | 8.1.7 Open Work Orders Page 229 | 229
8.1.7.1 | 8.1.7.1 Procedures/Programs Documenting the Work Order Process Page 229 | 229
8.1.7.2 | 8.1.7.2 Prioritization of Work Orders Page 231 | 231
8.1.7.3 | 8.1.7.3 Plan for Eliminating a Backlog of Work Orders, if Applicable Page 231 | 231
8.1.7.4 | 8.1.7.4 Trends with Respect to Open Work Orders Page 231 | 231
8.1.7.5 | 8.1.7.5 Open work orders over time Page 231 | 231
8.1.7.6 | 8.1.7.6 Aging report for work orders past due Page 233 | 233
8.1.8 | 8.1.8 Grid Operations and Procedures Page 234 | 234
8.1.8.1 | 8.1.8.1 Equipment Settings to Reduce Wildfire Risk Page 234 | 234
8.1.8.1.1 | 8.1.8.1.1 Protective Equipment and Device Settings Page 234 | 234
8.1.8.1.2 | 8.1.8.1.2 Automatic recloser settings Page 234 | 234
8.1.8.1.3 | 8.1.8.1.3 Settings of other Emerging Technologies Page 236 | 236
8.1.8.2 | 8.1.8.2 Grid Response Procedures and Notifications Page 236 | 236
8.1.8.3 | 8.1.8.3 Personnel Work Procedures and Training in Conditions of Elevated Fire Risk Page 236 | 236
8.1.8.3.1 | 8.1.8.3.1 Procedures for Determining Operating Conditions Page 237 | 237
8.1.8.3.2 | 8.1.8.3.2 Procedures Regarding Deployment of Fire Mitigation Resources and Equipment Page 237 | 237
8.1.8.3.3 | 8.1.8.3.3 Aviation Firefighting Program Page 238 | 238
8.1.9 | 8.1.9 Workforce Planning Page 240 | 240
8.1.9.1 | 8.1.9.1 Asset Inspection Qualification Improvement Plans Page 252 | 252
8.1.9.1.1 | 8.1.9.1.1 Extended Reality Page 252 | 252
8.1.9.1.2 | 8.1.9.1.2 Line Checker Program Page 252 | 252
8.1.9.1.3 | 8.1.9.1.3 Safety Observations Page 252 | 252
8.1.9.1.4 | 8.1.9.1.4 Near Misses Reported 253 | 253
8.1.9.2 | 8.1.9.2 Grid Hardening Qualification Improvement Plans Page 254 | 254
8.1.9.3 | 8.1.9.3 Risk Event Inspection Improvement Plans 254 | 254
8.2 | 8.2 Vegetation Management and Inspection Page 254 | 254
8.2.1 | 8.2.1 Overview Page 254 | 254
8.2.1.1 | 8.2.1.1 Objectives Page 256 | 256
8.2.1.2 | 8.2.1.2 Targets Page 259 | 259
8.2.1.3 | 8.2.1.3 Performance Metrics Identified by the Electrical Corporation Page 261 | 261
8.2.1.3.1 | 8.2.1.3.1 Vegetation Inspections and Clearance in the HFTD Page 261 | 261
8.2.1.3.2 | 8.2.1.3.2 Vegetation Outages and Ignitions in the HFTD Page 262 | 262
8.2.2 | 8.2.2 Vegetation Inspections Page 263 | 263
8.2.2.1 | 8.2.2.1 Detailed Vegetation Inspections Page 264 | 264
8.2.2.1.1 | 8.2.2.1.1 Process Page 264 | 264
8.2.2.1.2 | 8.2.2.1.2 Frequency or Triggers Page 267 | 267
8.2.2.1.3 | 8.2.2.1.3 Accomplishments, Roadblocks, and Updates Page 267 | 267
8.2.2.2 | 8.2.2.2 Off-Cycle Patrol Inspections Page 268 | 268
8.2.2.2.1 | 8.2.2.2.1 Process Page 268 | 268
8.2.2.2.2 | 8.2.2.2.2 Frequency or Triggers Page 269 | 269
8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270 | 270
8.2.3 | 8.2.3 Vegetation and Fuels Management Page 271 | 271
8.2.3.1 | 8.2.3.1 Pole Clearing Page 273 | 273
8.2.3.1.1 | 8.2.3.1.1 Utility Initiative Tracking ID Page 273 | 273
8.2.3.1.2 | 8.2.3.1.2 Overview of the Initiative Page 273 | 273
8.2.3.1.3 | 8.2.3.1.3 Governing Standards and Electrical Corporation Standard Operating Procedures Page 275 | 275
8.2.3.1.4 | 8.2.3.1.4 Updates to the Initiative Page 275 | 275
8.2.3.2 | 8.2.3.2 Wood and Slash Management Page 276 | 276
8.2.3.2.1 | 8.2.3.2.1 Utility Initiative Tracking ID Page 276 | 276
8.2.3.2.2 | 8.2.3.2.2 Overview of the Initiative Page 276 | 276
8.2.3.2.3 | 8.2.3.2.3 Governing Standards and Electrical Corporation Standard Operating Procedures 276 | 276
8.2.3.2.4 | 8.2.3.2.4 Updates to the Initiative Page 276 | 276
8.2.3.3 | 8.2.3.3 Clearance Page 276 | 276
8.2.3.3.1 | 8.2.3.3.1 Utility Initiative Tracking ID Page 277 | 277
8.2.3.3.2 | 8.2.3.3.2 Overview of the Initiative Page 277 | 277
8.2.3.3.3 | 8.2.3.3.3 Governing Standards and Electrical Corporation Standard Operating Procedures Page 278 | 278
8.2.3.3.4 | 8.2.3.3.4 Updates to the Initiative Page 279 | 279
8.2.3.4 | 8.2.3.4 Fall-in Mitigation Page 279 | 279
8.2.3.4.1 | 8.2.3.4.1 Utility Initiative Tracking ID Page 279 | 279
8.2.3.4.2 | 8.2.3.4.2 Overview of the Initiative Page 279 | 279
8.2.3.4.3 | 8.2.3.4.3 Governing Standards and Electrical Corporation Standard Operating Procedures Page 279 | 279
8.2.3.4.4 | 8.2.3.4.4 Updates to the Initiative Page 279 | 279
8.2.3.5 | 8.2.3.5 Substation Defensible Space Page 279 | 279
8.2.3.6 | 8.2.3.6 High-Risk Species Page 279 | 279
8.2.3.7 | 8.2.3.7 Fire-Resilient Right-of-Ways Page 280 | 280
8.2.3.8 | 8.2.3.8 Emergency Response Vegetation Management Page 280 | 280
8.2.3.8.1 | 8.2.3.8.1 Utility Initiative Tracking ID Page 280 | 280
8.2.3.8.2 | 8.2.3.8.2 Overview of the Initiative Page 280 | 280
8.2.3.8.3 | 8.2.3.8.3 Governing Standards and Electrical Corporation Standard Operating Procedures Page 281 | 281
8.2.3.8.4 | 8.2.3.8.4 Updates to the Initiative Page 281 | 281
8.2.4 | 8.2.4 Vegetation Management Enterprise System Page 281 | 281
8.2.4.1 | 8.2.4.1 Vegetation Inventory and Condition Database(s) Page 281 | 281
8.2.4.2 | 8.2.4.2 Internal Documentation of the Database(s) Page 281 | 281
8.2.4.3 | 8.2.4.3 Integration with Systems in Other Lines of Business Page 282 | 282
8.2.4.4 | 8.2.4.4 Integration with the Auditing System(s) Page 282 | 282
8.2.4.5 | 8.2.4.5 Internal Processes for Updating the System and Planned Updates Page 282 | 282
8.2.4.6 | 8.2.4.6 Changes Since the Last WMP Submission Page 282 | 282
8.2.5 | 8.2.5 Quality Assurance / Quality Control (QA/QC) Page 282 | 282
8.2.5.1 | 8.2.5.1 QA/QC Procedure/Program (WMP.505) Page 282 | 282
8.2.5.2 | 8.2.5.2 Sample Size Page 283 | 283
8.2.5.3 | 8.2.5.3 Who Performs QA/QC Page 284 | 284
8.2.5.4 | 8.2.5.4 Auditor Qualifications Page 284 | 284
8.2.5.5 | 8.2.5.5 QA/QC Findings and Incorporation of Lessons Learned Page 284 | 284
8.2.5.6 | 8.2.5.6 Process Changes Since the Last WMP Submission Page 284 | 284
8.2.6 | 8.2.6 Open Work Orders Page 284 | 284
8.2.6.1 | 8.2.6.1 Work Order Procedures Page 284 | 284
8.2.6.2 | 8.2.6.2 Work Order Prioritization Page 285 | 285
8.2.6.3 | 8.2.6.3 Work Order Backlogs Page Page 285 | 285
8.2.6.4 | 8.2.6.4 Work Order Trends Page 285 | 285
8.2.7 | 8.2.7 Workforce Planning Page 286 | 286
8.3 | 8.3 Situational Awareness and Forecasting Page 291 | 291
8.3.1 | 8.3.1 Overview Page 291 | 291
8.3.1.1 | 8.3.1.1 Objectives Page 292 | 292
8.3.1.2 | 8.3.1.2 Targets Page 298 | 298
8.3.1.3 | 8.3.1.3 Performance Metrics Page 298 | 298
8.3.2 | 8.3.2 Environmental Monitoring Systems Page 301 | 301
8.3.2.1 | 8.3.2.1 Existing Systems, Technologies, and Processes Page 301 | 301
8.3.2.1.1 | 8.3.2.1.1 Weather Stations and Normalized Difference Vegetation Index (NDVI) Cameras Page 301 | 301
8.3.2.1.2 | 8.3.2.1.2 Fuel Moisture Page 302 | 302
8.3.2.1.3 | 8.3.2.1.3 Air Quality Management Program (WMP.970) Page 302 | 302
8.3.2.2 | 8.3.2.2 Evaluation and Selection of New Systems Page 302 | 302
8.3.2.3 | 8.3.2.3 Planned Improvements Page Page 303 | 303
8.3.2.3.1 | 8.3.2.3.1 Weather Station Network and NDVI Cameras Page 303 | 303
8.3.2.3.2 | 8.3.2.3.2 Fuel Moisture Page Page 303 | 303
8.3.2.3.3 | 8.3.2.3.3 Air Quality Management Program Page 304 | 304
8.3.2.4 | 8.3.2.4 Evaluating Mitigation Initiatives Page 306 | 306
8.3.2.4.1 | 8.3.2.4.1 Weather Stations and NDVI Cameras Page 306 | 306
8.3.2.4.2 | 8.3.2.4.2 Fuel Moisture Page 306 | 306
8.3.2.4.3 | 8.3.2.4.3 Air Quality Management Program Page 306 | 306
8.3.3 | 8.3.3 Grid Monitoring Systems Page 307 | 307
8.3.3.1 | 8.3.3.1 Existing Systems, Technologies, and Procedures Page 307 | 307
8.3.3.2 | 8.3.3.2 Evaluation and Selection of New Systems Page 310 | 310
8.3.3.3 | 8.3.3.3 Planned Improvements Page 310 | 310
8.3.3.4 | 8.3.3.4 Evaluating Mitigation Initiatives Page 310 | 310
8.3.3.5 | 8.3.3.5 Enterprise System for Grid Monitoring Page 311 | 311
8.3.3.5.1 | 8.3.3.5.1 Database(s) Utilized for Storage Page 311 | 311
8.3.3.5.2 | 8.3.3.5.2 Internal Documentation of Database(s) Page 311 | 311
8.3.3.5.3 | 8.3.3.5.3 Integration with Systems in other Lines of Business Page 311 | 311
8.3.3.5.4 | 8.3.3.5.4 QA/QC or Auditing of the System Page 312 | 312
8.3.3.5.5 | 8.3.3.5.5 Updating the Enterprise System Including Database(s) Page 312 | 312
8.3.3.5.6 | 8.3.3.5.6 Changes to the Initiative since the Last WMP Submission Page 313 | 313
8.3.4 | 8.3.4 Ignition Detection Systems Page 313 | 313
8.3.4.1 | 8.3.4.1 Existing Ignition Detection Sensors and Systems Page 313 | 313
8.3.4.1.1 | 8.3.4.1.1 Satellite Based Remote Sensing Page 314 | 314
8.3.4.1.2 | 8.3.4.1.2 Cameras Page Page 315 | 315
8.3.4.1.3 | 8.3.4.1.3 WFA - Fire Growth Potential Software Page 316 | 316
8.3.4.1.4 | 8.3.4.1.4 AI Smoke Detection Algorithm . 316 | 316
8.3.4.2 | 8.3.4.2 Evaluation and Selection of New Detection Systems Page 317 | 317
8.3.4.2.1 | 8.3.4.2.1 Impact of new Detection Technologies Page 318 | 318
8.3.4.2.2 | 8.3.4.2.2 Efficacy of New Technologies Page 318 | 318
8.3.4.2.3 | 8.3.4.2.3 Budgeting Process Page 318 | 318
8.3.4.3 | 8.3.4.3 Planned Integration of New Detection Technologies Page 318 | 318
8.3.4.4 | 8.3.4.4 Evaluating Mitigation Initiatives Page 319 | 319
8.3.4.4.1 | 8.3.4.4.1 Satellite Based Remote Sensing Page 319 | 319
8.3.4.4.2 | 8.3.4.4.2 Cameras Page 319 | 319
8.3.4.4.3 | 8.3.4.4.3 Fire Grown Potential Software Page 319 | 319
8.3.4.4.4 | 8.3.4.4.4 AI Smoke Detection Page .. 319 | 319
8.3.4.5 | 8.3.4.5 Enterprise System for Ignition Detection Page 320 | 320
8.3.4.5.1 | 8.3.4.5.1 Database(s) Utilized for Storage Page 320 | 320
8.3.4.5.2 | 8.3.4.5.2 Internal Documentation of Database(s) Page 320 | 320
8.3.4.5.3 | 8.3.4.5.3 Integration with Systems in other Lines of Business Page 320 | 320
8.3.4.5.4 | 8.3.4.5.4 QA/QC or Auditing of the System Page 320 | 320
8.3.4.5.5 | 8.3.4.5.5 Internal Processes for Updating Enterprise System Including Database(s) Page 320 | 320
8.3.4.5.6 | 8.3.4.5.6 Changes to the Initiative since the Last WMP Submission Page 320 | 320
8.3.5 | 8.3.5 Weather Forecasting Page 320 | 320
8.3.5.1 | 8.3.5.1 Existing Modeling Approach Page 320 | 320
8.3.5.1.1 | 8.3.5.1.1 Weather Research and Forecasting (WRF) Page 321 | 321
8.3.5.1.2 | 8.3.5.1.2 SAWTI Page 322 | 322
8.3.5.2 | 8.3.5.2 Known Limitations of Existing Approach Page 322 | 322
8.3.5.3 | 8.3.5.3 Planned Improvements Page 323 | 323
8.3.5.4 | 8.3.5.4 Evaluating Mitigation Initiatives Page 324 | 324
8.3.5.5 | 8.3.5.5 Enterprise System for Weather Forecasting Page 327 | 327
8.3.5.5.1 | 8.3.5.5.1 Database(s) Utilized for Storage Page 327 | 327
8.3.5.5.2 | 8.3.5.5.2 Internal Documentation of Database(s) Page 328 | 328
8.3.5.5.3 | 8.3.5.5.3 Integration with Systems in other Lines of Business Page 328 | 328
8.3.5.5.4 | 8.3.5.5.4 QA/QC or Auditing of the System Page 328 | 328
8.3.5.5.5 | 8.3.5.5.5 Internal Processes for Updating Enterprise System Including Database(s) Page 329 | 329
8.3.5.5.6 | 8.3.5.5.6 Changes to the Initiative since the Last WMP Submission Page 329 | 329
8.3.6 | 8.3.6 Fire Potential Index Page 329 | 329
8.3.6.1 | 8.3.6.1 Existing Calculation Approach and Use Page 329 | 329
8.3.6.1.1 | 8.3.6.1.1 Efficacy Study: Determination of Average Distribution Ignition Percentages by Location and Operating Risk Condition Page 332 | 332
8.3.6.2 | 8.3.6.2 Known Limitations of Existing Approach Page 333 | 333
8.3.6.3 | 8.3.6.3 Planned Improvements Page 334 | 334
8.4 | 8.4 Emergency Preparedness Page 334 | 334
8.4.1 | 8.4.1 Overview Page 334 | 334
8.4.1.1 | 8.4.1.1 Objectives Page 336 | 336
8.4.1.2 | 8.4.1.2 Targets Page 339 | 339
8.4.1.3 | 8.4.1.3 Performance Metrics Identified by the Electrical Corporation Page 340 | 340
8.4.2 | 8.4.2 Emergency Preparedness Plan Page 341 | 341
8.4.2.1 | 8.4.2.1 Overview of Wildfire and PSPS Emergency Preparedness ..... 341 | 341
8.4.2.1.1 | 8.4.2.1.1 Purpose and Scope of the Plan Page 341 | 341
8.4.2.1.2 | 8.4.2.1.2 Overview of Wildfire and PSPS Protocols, Policies, and Procedures Page 342 | 342
8.4.2.1.3 | 8.4.2.1.3 Key Personnel, Qualifications, and Training Page 345 | 345
8.4.2.1.4 | 8.4.2.1.4 Resource Planning and Allocation Page 345 | 345
8.4.2.1.5 | 8.4.2.1.5 Drills, Simulations, and Tabletop Exercises Page 345 | 345
8.4.2.1.6 | 8.4.2.1.6 Coordination and Collaboration with Public Safety Partners Page 345 | 345
8.4.2.1.7 | 8.4.2.1.7 Notification of and Communication during and after a Wildfire or PSPS Event Page 345 | 345
8.4.2.1.8 | 8.4.2.1.8 Improvements/Updates since the Last WMP Submission Page 346 | 346
8.4.2.2 | 8.4.2.2 Key Personnel, Qualifications, and Training Page 346 | 346
8.4.2.2.1 | 8.4.2.2.1 Personnel Qualifications Page 346 | 346
8.4.2.2.2 | 8.4.2.2.2 Personnel and External Contractor Training Page 358 | 358
8.4.2.3 | 8.4.2.3 Drills, Simulations, and Tabletop Exercises Page 360 | 360
8.4.2.4 | 8.4.2.4 Schedule for Updating and Revising Plan Page 363 | 363
8.4.3 | 8.4.3 External Collaboration and Coordination Page 365 | 365
8.4.3.1 | 8.4.3.1 Emergency Planning Page 365 | 365
8.4.3.2 | 8.4.3.2 Communication Strategy with Public Safety Partners Page 368 | 368
8.4.3.3 | 8.4.3.3 Mutual Aid Agreements Page 372 | 372
8.4.3.4 | 8.4.3.4 Wildfire and Climate Resilience Center (WCRC) Page 374 | 374
8.4.4 | 8.4.4 Public Emergency Communication Strategy Page 375 | 375
8.4.4.1 | 8.4.4.1 Protocols for Emergency Communications Page 376 | 376
8.4.4.2 | 8.4.4.2 Messaging Page 378 | 378
8.4.4.3 | 8.4.4.3 Current Gaps and Limitations Page 379 | 379
8.4.5 | 8.4.5 Preparedness and Planning for Service Restoration Page 379 | 379
8.4.5.1 | 8.4.5.1 Overview of Service Restoration Plan Page 379 | 379
8.4.5.2 | 8.4.5.2 Planning and Allocation of Resources Page 381 | 381
8.4.5.3 | 8.4.5.3 Drills, Simulations, and Tabletop Exercises Page 382 | 382
8.4.6 | 8.4.6 Customer Support in Wildfire and PSPS Emergencies Page 385 | 385
8.4.6.1 | 8.4.6.1 Outage Reporting Page 385 | 385
8.4.6.2 | 8.4.6.2 Support for Low-Income Customers Page 385 | 385
8.4.6.3 | 8.4.6.3 Billing Adjustments Page 385 | 385
8.4.6.4 | 8.4.6.4 Deposit Waivers Page 386 | 386
8.4.6.5 | 8.4.6.5 Extended Payment Plans Page 386 | 386
8.4.6.6 | 8.4.6.6 Suspension of Disconnection and Nonpayment Fees Page 386 | 386
8.4.6.7 | 8.4.6.7 Repair Processing and Timing Page 386 | 386
8.4.6.8 | 8.4.6.8 Medical Baseline Support Services Page 386 | 386
8.4.6.9 | 8.4.6.9 Access to Electrical Corporation Representatives Page 387 | 387
8.5 | 8.5 Community Outreach and Engagement Page 388 | 388
8.5.1 | 8.5.1 Overview Page 388 | 388
8.5.1.1 | 8.5.1.1 Objectives Page 389 | 389
8.5.1.2 | 8.5.1.2 Targets Page 391 | 391
8.5.1.3 | 8.5.1.3 Performance Metrics Identified by the Electrical Corporation Page 391 | 391
8.5.2 | 8.5.2 Public Outreach and Education Awareness Program Page 392 | 392
8.5.2.1 | 8.5.2.1 Description of the program(s) Page 392 | 392
8.5.2.1.1 | 8.5.2.1.1 Wildfire and PSPS Safety Communications Prior to Events Page 392 | 392
8.5.2.1.2 | 8.5.2.1.2 Wildfire Safety Communications During PSPS Events Page 393 | 393
8.5.2.1.3 | 8.5.2.1.3 PSPS Notifications Page 393 | 393
8.5.2.1.4 | 8.5.2.1.4 Wildfire Safety Communications After an Event Page 394 | 394
8.5.2.2 | 8.5.2.2 Target Community Groups across the Service Territory Page 394 | 394
8.5.2.3 | 8.5.2.3 Community Partners Page 395 | 395
8.5.2.4 | 8.5.2.4 Outreach and Awareness Programs Page 397 | 397
8.5.3 | 8.5.3 Engagement with Access and Functional Needs Populations Page 401 | 401
8.5.3.1 | 8.5.3.1 Overview Page 401 | 401
8.5.3.2 | 8.5.3.2 Summary of Key AFN Demographics Page 401 | 401
8.5.3.3 | 8.5.3.3 Evaluation of Challenges and Needs during a Wildfire or PSPS Event Page 402 | 402
8.5.3.4 | 8.5.3.4 Plans to Address Needs of the AFN Customer Base Page 402 | 402
8.5.3.5 | 8.5.3.5 Ongoing Feedback Practices Page 402 | 402
8.5.4 | 8.5.4 Collaboration on Local Wildfire Mitigation Planning Page 403 | 403
8.5.5 | 8.5.5 Best Practice Sharing with Other Electrical Corporations Page 405 | 405
9 | 9 PUBLIC SAFETY POWER SHUTOFF Page 407 | 407
9.1 | 9.1 Overview Page 407 | 407
9.1.1 | 9.1.1 Key PSPS Statistics Page 407 | 407
9.1.2 | 9.1.2 Identification of Frequently De-energized Circuits Page 408 | 408
9.1.3 | 9.1.3 Objectives Page 412 | 412
9.1.4 | 9.1.4 Targets Page 414 | 414
9.1.5 | 9.1.5 Performance Metrics Page 415 | 415
9.2 | 9.2 Protocols on PSPS Page 416 | 416
9.2.1 | 9.2.1 Protocols that Determine the Need for PSPS Page 416 | 416
9.2.2 | 9.2.2 Method that Evaluates Relative Consequences of PSPS and Wildfires Page 419 | 419
9.2.3 | 9.2.3 Decision-Making Process for Initiating a PSPS Page 419 | 419
9.2.4 | 9.2.4 Protocols for Mitigating Public Safety Impacts of PSPS Page 421 | 421
9.3 | 9.3 Communication Strategy for PSPS Page 422 | 422
9.4 | 9.4 Key Personnel, Qualifications, and Training for PSPS Page 422 | 422
9.5 | 9.5 Planning and Allocation of Resources for Service Restoration due to PSPS Page 422 | 422
10 | 10 LESSONS LEARNED Page .... 423 | 423
10.1 | 10.1 Summary Page 423 | 423
10.2 | 10.2 Identification of Lessons Learned Page 423 | 423
10.2.1 | 10.2.1 Internal Monitoring and Evaluation Page 423 | 423
10.2.2 | 10.2.2 Feedback from Energy Safety or Other Authoritative Bodies Page 425 | 425
10.2.3 | 10.2.3 Collaborations with Other Electrical Corporations Page 426 | 426
10.2.4 | 10.2.4 Lessons Learned from Catastrophic Wildfires Page 427 | 427
10.3 | 10.3 Lessons Learned Page 429 | 429
11 | 11 CORRECTIVE ACTION PROGRAM Page 434 | 434
11.1 | 11.1 Prevent Recurrence of Risk Events Page 434 | 434
11.2 | 11.2 Address Findings from Internal and External Wildfire Investigations Page 435 | 435
11.3 | 11.3 Address Areas for Continued Improvement Identified by Energy Safety as Part of the WMP Evaluation Page 436 | 436
11.4 | 11.4 Process for Reviewing Improvement Area Page 436 | 436
11.4.1 | 11.4.1 Identify Insufficient Occurrence and Response Page 436 | 436
11.4.2 | 11.4.2 Identify Actions to Reduce Recurrence Page 436 | 436
11.4.3 | 11.4.3 Track Implementation Page 437 | 437
11.4.4 | 11.4.4 Improve External Communication Page 437 | 437
11.4.5 | 11.4.5 Integrate Lessons Learned Across Industry Page 438 | 438
11.4.6 | 11.4.6 Share Lessons Learned with Others Page 439 | 439
12 | 12 NOTICES OF VIOLATION AND DEFECT Page 440 | 440
List of Tables | List of Tables
Table 1-1 | Table 1-1: Successes and Lessons Learned for the 2020-2022 WMP Cycle........... 2 | . 2
Table 2-1 | Table 2-1: WMP Section Program Owners Page ... 11 | 11
Table 3-1 | Table 3-1: Statutory Requirements Checklist .. 13 | 13
Table 4-1 | Table 4-1: Summary of WMP Expenditures Page .. 18 | 18
Table 4-2 | Table 4-2: Risk-Informed Approach Components ......... 23 | 23
Table 5-1 | Table 5-1: Service Territory High-Level Statistics .......... 25 | 25
Table 5-2 | Table 5-2: Overview of Key Electrical Equipment ......... 27 | 27
Table 5-3 | Table 5-3: Existing Vegetation Types in the Service Territory ... 28 | 28
Table 5-4 | Table 5-4: Catastrophic Electrical Corporation Wildfires........... 30 | 30
Table 5-5 | Table 5-5: HFTD Statistics Page ... 33 | 33
Table 5-6 | Table 5-6: CFI Customers in Tier 2 of the HFTD ............ 44 | 44
Table 5-7 | Table 5-7: CFI Customers in Tier 3 of the HFTD ............ 45 | 45
Table 5-8 | Table 5-8: Relevant State and Federal Environmental Laws, Regulations, and Permitting Requirements for Implementing the WMP Page 49 | 49
Table 6-1 | Table 6-1: Enterprise CoRE MAVF Attributes Page 53 | 53
Table 6-2 | Table 6-2: Sub-Attributes of Health & Safety .. 53 | 53
Table 6-3 | Table 6-3: Sub-Attributes of Reliability Page ......... 53 | 53
Table 6-4 | Table 6-4: Summary of Risk Models Page . 54 | 54
Table 6-5 | Table 6-5: Risk Components for LoRE Page ........... 68 | 68
Table 6-6 | Table 6-6: Risk Components for Consequence 70 | 70
Table 6-7 | Table 6-7: Pre-Mitigation Analysis Risk Quantification Scores .. 72 | 72
Table 6-8 | Table 6-8: Risk Modeling Assumptions and Limitations ............ 73 | 73
Table 6-9 | Table 6-9: Summary of Design Basis Scenarios 76 | 76
Table 6-1 | Table 6-10: Summary of Design Parameters in WiNGS-Planning Visualization Application ......... 78 | 78
Table 6-1 | Table 6-11: Summary of Extreme-Event Scenarios ....... 80 | 80
Table 6-1 | Table 6-12: Summary of Top-Risk Segments Page 84 | 84
Table 6-1 | Table 6-13: Summary of Key Metrics by Statistical Frequency .. 86 | 86
Table 6-1 | Table 6-14: WiNGS-Planning and WiNGS-Ops Review Findings and Recommendations . 88 | 88
Table 6-1 | Table 6-15: Version Control Hierarchy for WiNGS-Planning 3.0 (in development) .......... 90 | 90
Table 6-1 | Table 6-16: Utility Risk Assessment Improvement Plan ............ 92 | 92
Table 7-1 | Table 7-1: Stakeholder Roles and Responsibilities in the Decision-Making Process ...... 101 | 101
Table 7-2 | Table 7-2: Risk Segment Scoped Mileage 2022-2027 . 103 | 103
Table 7-3 | Table 7-3: Prioritized Areas in the Service Territory Based on Overall Utility Risk ......... 104 | 104
Table 7-4 | Table 7-4: List and Description of Electrical Corporation-Specific WMP Mitigation Initiatives for 3-year and 10-year Outlooks Page ........ 118 | 118
Table 7-5 | Table 7-5: Wildfire Risk Reduction Projection ............ 124 | 124
Table 7-6 | Table 7-6: Summary of Risk Reduction for Top-Risk Segments ............ 126 | 126
Table 7-7 | Table 7-7: Interim Mitigations Initiatives Page .... 127 | 127
Table 8-1 | Table 8-1: Grid Design, Operations, and Maintenance Objectives (3-year plan) ........... 131 | 131
Table 8-2 | Table 8-2: Exemplar Grid Design, Operations, and Maintenance Objectives (10-year plan) ...... 136 | 136
Table 8-3 | Table 8-3: Grid Design, Operations, and Maintenance Targets by Year ............ 140 | 140
Table 8-4 | Table 8-4: Asset Inspections Targets by Year . 142 | 142
Table 8-5 | Table 8-5: Grid Design, Operations, and Maintenance Performance Metrics Results by Year ... 146 | 146
Table 8-6 | Table 8-6: Risk reduction estimation of the Covered Conductor Program........ 151 | 151
Table 8-7 | Table 8-7: Risk Reduction Estimation for the Strategic Undergrounding Program ........ 153 | 153
Table 8-8 | Table 8-8: Risk Reduction Estimation for Distribution Overhead Hardening .... 157 | 157
Table 8-9 | Table 8-9: Risk Reduction Estimation for Transmission Overhead Hardening .. 158 | 158
Table 8-10 | Table 8-10: Risk Reduction Estimation for Transmission-Distribution Underbuilt ......... 159 | 159
Table 8-11 | Table 8-11: Risk Reduction Estimation for Advance Protection ........... 163 | 163
Table 8-12 | Table 8-12: Risk Reduction Estimation for Advance Protection ........... 167 | 167
Table 8-13 | Table 8-13: Risk Reduction Estimation for SCADA Capacitors . 171 | 171
Table 8-14 | Table 8-14: Risk Reduction Estimation for the Expulsion Fuse Replacement Program .. 172 | 172
Table 8-15 | Table 8-15: CAL FIRE and Expulsion Fuse Operation 2015-2021 .......... 173 | 173
Table 8-16 | Table 8-16: CAL FIRE and Expulsion Fuse Operation 2015-2021 by HFTD Tier .. 174 | 174
Table 8-17 | Table 8-17: Risk Reduction Estimation for the HLC Program... 174 | 174
Table 8-18 | Table 8-18: Risk Reduction Estimation for Lightning Arrestor Program ............ 176 | 176
Table 8-19 | Table 8-19: Risk Reduction Estimation for Avian Covers ......... 177 | 177
Table 8-20 | Table 8-20: Risk Reduction Estimation for the Strategic Pole Replacement Program ... 179 | 179
Table 8-21 | Table 8-21: Risk Reduction for Wireless Fault Indicator Program ........ 181 | 181
Table 8-22 | Table 8-22: Asset Inspection Frequency, Method, and Criteria ........... 188 | 188
Table 8-23 | Table 8-23: GO 95, Rule 18 Inspection Finding Priority Levels 189 | 189
Table 8-24 | Table 8-24: Risk Reduction Estimation Methodology for the CMP ...... 191 | 191
Table 8-25 | Table 8-25: Risk Reduction Estimation Methodology for the Transmission Overhead Inspection Program Page ... 194 | 194
Table 8-26 | Table 8-26: Risk Reduction Methodology for Distribution Infrared Inspections Program .......... 196 | 196
Table 8-27 | Table 8-27: Risk Reduction Estimation for Transmission Infrared Inspections . 199 | 199
Table 8-28 | Table 8-28: Risk Reduction Methodology for Distribution Wood Pole Intrusive Inspections ..... 201 | 201
Table 8-29 | Table 8-29: Risk Reduction Methodology for the DIAR Program ......... 207 | 207
Table 8-30 | Table 8-30: Risk Reduction Estimation Methodology for Distribution Patrol Inspections .......... 210 | 210
Table 8-31 | Table 8-31: Risk Reduction Methodology for Transmission Overhead Patrol Inspections ......... 212 | 212
Table 8-32 | Table 8-32: Risk Reduction Estimation for Transmission Aerial 69KV Tier 3 Visual Inspections . 214 | 214
Table 8-33 | Table 8-33: Findings that Trigger Autogenerated Corrective Maintenance Order......... 216 | 216
Table 8-34 | Table 8-34: Maintenance and Replacement Strategies ........... 218 | 218
Table 8-35 | Table 8-35: Risk Event Rate with Pending Infractions 219 | 219
Table 8-36 | Table 8-36: Grid Design and Maintenance QA/QC Program ... 226 | 226
Table 8-37 | Table 8-37: Aging Report for Current Past Due Work Orders .. 233 | 233
Table 8-38 | Table 8-38: Ignition Rate with SRP Enabled Page 234 | 234
Table 8-39 | Table 8-39: Results of Reclosure Protocols in Ignition Avoidance ........ 235 | 235
Table 8-40 | Table 8-40: Effect of Special Work Procedures on Ignitions .... 237 | 237
Table 8-41 | Table 8-41: Effect of CFRs on Ignitions Page ....... 238 | 238
Table 8-42 | Table 8-42: Workforce Planning, Distribution Asset Inspections ......... 240 | 240
Table 8-43 | Table 8-43: Workforce Planning, Transmission Asset Inspections ....... 242 | 242
Table 8-44 | Table 8-44: Workforce Planning, Substation Asset Inspections ........... 244 | 244
Table 8-45 | Table 8-45: Workforce Planning, Distribution Grid Hardening 245 | 245
Table 8-46 | Table 8-46: Workforce Planning, Transmission Grid Hardening ........... 248 | 248
Table 8-47 | Table 8-47: Workforce Planning, Risk Event Inspection .......... 250 | 250
Table 8-48 | Table 8-48: Employee-Conducted Safety Observations .......... 252 | 252
Table 8-49 | Table 8-49: Employee-Submitted Near Misses ........... 253 | 253
Table 8-50 | Table 8-50: Vegetation Management Initiative Objectives (3-year plan) ......... 256 | 256
Table 8-51 | Table 8-51: Vegetation Management Initiative Objectives (10-year plan) ....... 257 | 257
Table 8-52 | Table 8-52: Vegetation Management Initiative Targets by Year .......... 259 | 259
Table 8-53 | Table 8-53: Vegetation Inspections Targets by Year... 260 | 260
Table 8-54 | Table 8-54: Vegetation Management and Inspection Performance Metrics Results by Year ..... 261 | 261
Table 8-55 | Table 8-55: Vegetation Management Inspection Frequency, Method, and Criteria ...... 263 | 263
Table 8-56 | Table 8-56: Vegetation Management QA/QC Program ........... 284 | 284
Table 8-57 | Table 8-57: Number of Past Due Vegetation Management Work Orders (Tree Units) Categorized by Age Page ... 286 | 286
Table 8-58 | Table 8-58: Vegetation Management Qualifications and Training ....... 288 | 288
Table 8-59 | Table 8-59: Situational Awareness Initiative Objectives (3-year plan) . 292 | 292
Table 8-60 | Table 8-60: Situational Awareness Initiative Objectives (10-year plan) ............ 296 | 296
Table 8-61 | Table 8-61: Situational Awareness Initiative Targets by Year .. 298 | 298
Table 8-62 | Table 8-62: Situational Awareness and Forecasting Performance Metrics Results by Year ....... 298 | 298
Table 8-63 | Table 8-63: Summary of Existing Systems, Technologies, and Procedures ....... 301 | 301
Table 8-64 | Table 8-64: Planned Improvements to Environmental Monitoring Systems .... 304 | 304
Table 8-65 | Table 8-65: Grid Operation Monitoring Systems ........ 308 | 308
Table 8-66 | Table 8-66: Planning Improvements to Grid Operation Monitoring Systems ... 310 | 310
Table 8-67 | Table 8-67: Ignition Detection Systems Currently Deployed ... 313 | 313
Table 8-68 | Table 8-68: Planning Improvements to New Fire Detection and Alarm Systems ........... 318 | 318
Table 8-69 | Table 8-69: Planned Improvements to Weather Forecasting Systems 323 | 323
Table 8-70 | Table 8-70: Fire Potential Features Page 331 | 331
Table 8-71 | Table 8-71: 5-Year Average Ignition Rate Page ... 332 | 332
Table 8-72 | Table 8-72: Emergency Preparedness Initiative Objectives (3-year plan) ......... 336 | 336
Table 8-73 | Table 8-73: Emergency Preparedness Initiative Objectives (10-year plan) ....... 338 | 338
Table 8-74 | Table 8-74: Emergency Preparedness Initiative Targets by Year .......... 339 | 339
Table 8-75 | Table 8-75: Emergency Preparedness Performance Metrics Results by Year ... 340 | 340
Table 8-76 | Table 8-76: Key Gaps and Limitations in Integrating Wildfire- and PSPS-Specific Strategies into Emergency Plan Page .... 346 | 346
Table 8-77 | Table 8-77: Emergency Preparedness Staffing and Qualifications ....... 348 | 348
Table 8-78 | Table 8-78: Electrical Corporation Personnel Training Program .......... 358 | 358
Table 8-79 | Table 8-79: Contractor Training Program Page ... 359 | 359
Table 8-80 | Table 8-80: Internal Drill, Simulation, and Tabletop Exercise Program 360 | 360
Table 8-81 | Table 8-81: External Drill, Simulation, and Tabletop Exercise Program ............ 360 | 360
Table 8-82 | Table 8-82: Wildfire-Specific Updates to the CEADPP 364 | 364
Table 8-83 | Table 8-83: State and Local Agency Collaboration(s) . 366 | 366
Table 8-84 | Table 8-84: Key Gaps and Limitations in Collaboration Activities with State and Local Agencies............ 367 | 367
Table 8-85 | Table 8-85: High-Level Communication Protocols, Procedures, and Systems with Public Safety Partners Page ... 369 | 369
Table 8-86 | Table 8-86: Key Gaps and Limitations in Communication Coordination with Public Safety Partners ...... 371 | 371
Table 8-87 | Table 8-87: High-Level Mutual Aid Agreement for Resources During a Wildfire or De-Energization Incident Page ... 373 | 373
Table 8-88 | Table 8-88: Protocols for Emergency Communication to Public Stakeholder Groups ... 377 | 377
Table 8-89 | Table 8-89: Key Gaps and Limitations in Public Emergency Communication Strategy .. 379 | 379
Table 8-90 | Table 8-90: Internal Drill, Simulation, and Tabletop Exercise Program for Service Restoration . 382 | 382
Table 8-91 | Table 8-91: External Drill, Simulation, and Tabletop Exercise Program for Service Restoration 383 | 383
Table 8-92 | Table 8-92: CRC Locations and Services Page ...... 386 | 386
Table 8-93 | Table 8-93: Community Outreach and Engagement Initiative Objectives (3-year plan) 389 | 389
Table 8-94 | Table 8-94: Community Outreach and Engagement Initiative Objectives (10-year plan) ........... 390 | 390
Table 8-95 | Table 8-95: Community Outreach and Engagement Initiative Targets by Year 391 | 391
Table 8-96 | Table 8-96: PSPS Outreach and Engagement Initiative Targets by Year............ 391 | 391
Table 8-97 | Table 8-97: Community Outreach and Engagement Performance Metrics Results by Year ....... 391 | 391
Table 8-98 | Table 8-98: List of Target Communities Page ...... 394 | 394
Table 8-99 | Table 8-99: List of Community Partners Page ..... 395 | 395
Table 8-100 | Table 8-100: Community Outreach and Education Programs . 398 | 398
Table 8-101 | Table 8-101: Collaboration in Local Wildfire Mitigation Planning* ...... 403 | 403
Table 8-102 | Table 8-102: Key Gaps and Limitations in Collaborating on Local Wildfire Mitigation Planning. 404 | 404
Table 8-103 | Table 8-103: Best Practice Sharing with Other Electrical Corporations ............ 406 | 406
Table 9-1 | Table 9-1: PSPS Event Statistics Page ..... 407 | 407
Table 9-2 | Table 9-2: Frequently De-energized Circuits* 409 | 409
Table 9-3 | Table 9-3: PSPS Objectives (3-year plan) Page .... 412 | 412
Table 9-4 | Table 9-4: PSPS Objectives (10-year plan) Page .. 413 | 413
Table 9-5 | Table 9-5: PSPS Targets by Year Page ..... 414 | 414
Table 9-6 | Table 9-6: PSPS Performance Metrics Results by Year 415 | 415
Table 10-1 | Table 10-1: Double Down Initiatives Page ........... 424 | 424
Table 10-2 | Table 10-2: Areas for Continued Improvement .......... 425 | 425
Table 10-3 | Table 10-3: Lessons Learned Page .......... 429 | 429
Table 12-1 | Table 12-1: List of Open Compliance Violations and Defects .. 440 | 440
List of Figures
Figure 1-1 | Figure 1-1: Enterprise Risk Management Framework for Development of the WMP ....... 9 | . 9
Figure 4-1 | Figure 4-1: Summary of WMP Expenditures Page . 19 | 19
Figure 4-2 | Figure 4-2: Enterprise Risk Management Framework .. 21 | 21
Figure 5-1 | Figure 5-1: Utility Service Territory of the Enterprise Risk Management Framework ..... 25 | 25
Figure 5-2 | Figure 5-2: Service Territory (polygons) and Distribution of Customers Served . 26 | 26
Figure 5-3 | Figure 5-3: Catastrophic Wildfire Map Page .......... 31 | 31
Figure 5-4 | Figure 5-4: Map of HFTD in the Service Territory ......... 32 | 32
Figure 5-5 | Figure 5-5: Annual Mean Climatology for the Service Territory 34 | 34
Figure 5-6 | Figure 5-6: Mean Annual Temperature for the Service Territory 1900s-2020s .. 36 | 36
Figure 5-7 | Figure 5-7: Mean Annual Precipitation for the Service Territory 1900s-2020s ... 36 | 36
Figure 5-8 | Figure 5-8: Projected Change in Minimum and Maximum Daily Temperatures . 37 | 37
Figure 5-9 | Figure 5-9: Extreme Fire Weather Days in the Service Territory ............ 39 | 39
Figure 5-10 | Figure 5-10: AFN Customers in the Service Territory ... 42 | 42
Figure 5-11 | Figure 5-11: Communities at Risk in the Service Territory ........ 43 | 43
Figure 6-1 | Figure 6-1: Enterprise CoRE MAVF Page ... 52 | 52
Figure 6-2 | Figure 6-2: Risk Identification Step of the Enterprise Risk Management Framework ...... 59 | 59
Figure 6-3 | Figure 6-3: Enterprise Utility Risk Overview Page . 60 | 60
Figure 6-4 | Figure 6-4: WiNGS-Planning Risk Calculation Process Flow Diagram ..... 61 | 61
Figure 6-5 | Figure 6-5: WiNGS-Ops Calculation Process Flow Diagram ....... 63 | 63
Figure 6-6 | Figure 6-6: Risk Analysis Step of the Enterprise Risk Management Framework . 65 | 65
Figure 6-7 | Figure 6-7: WiNGS-Planning Calculation Schematic ..... 66 | 66
Figure 6-8 | Figure 6-8: WiNGS-Ops Calculation Schematic 67 | 67
Figure 6-9 | Figure 6-9: WiNGS Visualization Interface Page .... 79 | 79
Figure 6-10 | Figure 6-10: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework ......... 81 | 81
Figure 6-11 | Figure 6-11: Higher-Risk Urban Areas in Relation to HFTD ........ 82 | 82
Figure 6-12 | Figure 6-12: Map of Service Territory with Circuits Categorized in terms of Wildfire Risk ........... 83 | 83
Figure 7-1 | Figure 7-1: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework ......... 100 | 100
Figure 7-2 | Figure 7-2: WiNGS-Planning: Wildfire Hardening Targets ....... 108 | 108
Figure 7-3 | Figure 7-3: Circuit 358-682F: Example of Prior Hardening ...... 111 | 111
Figure 7-4 | Figure 7-4: High-Level Mitigation Prioritization to Reduce Wildfire and PSPS Risk ........ 113 | 113
Figure 7-5 | Figure 7-5: Risk Mitigation Plan Development & Documentation Step of the Enterprise Risk Management Framework Page ........... 117 | 117
Figure 7-6 | Figure 7-6: Projected Overall Wildfire and PSPS Risk Reduction .......... 122 | 122
Figure 8-1 | Figure 8-1: Risk-Informed Investment decision & Risk Mitigation Implementation Step of the Enterprise Risk Management Framework Page ....... 129 | 129
Figure 8-2 | Figure 8-2: Distribution Inspection Findings and Open Work Orders ... 147 | 147
Figure 8-3 | Figure 8-3: Distribution Equipment related HFTD Ignitions and Outages Rate . 148 | 148
Figure 8-4 | Figure 8-4: Transmission Inspection Findings and Open Work Orders in HFTD 149 | 149
Figure 8-5 | Figure 8-5: Transmission Equipment related HFTD Outages and Ignitions ....... 150 | 150
Figure 8-6 | Figure 8-6: FPB Installation at Mobile Home Park Community ............ 183 | 183
Figure 8-7 | Figure 8-7: Distribution Detailed Overhead Inspections Process Flow . 190 | 190
Figure 8-8 | Figure 8-8: Transmission Detailed Overhead Inspections Process Flow ............ 193 | 193
Figure 8-9 | Figure 8-9: Distribution Infrared Inspections Process Flow ..... 195 | 195
Figure 8-10 | Figure 8-10: Transmission Infrared Inspections Process Flow . 198 | 198
Figure 8-11 | Figure 8-11: Wood Pole Intrusive Inspections Process Flow (Transmission and Distribution) ... 200 | 200
Figure 8-12 | Figure 8-12: Distribution Drone Inspections Process Flow ...... 204 | 204
Figure 8-13 | Figure 8-13: DIAR Inspection Prioritization Model ..... 206 | 206
Figure 8-14 | Figure 8-14: Distribution Patrol Inspections Process Flow ...... 209 | 209
Figure 8-15 | Figure 8-15: Transmission Patrol Overhead Inspections Process Flow 211 | 211
Figure 8-16 | Figure 8-16: Transmission Tier 3 69kV Inspections Process Flow ......... 213 | 213
Figure 8-17 | Figure 8-17: Substation Patrol Inspection Workflow .. 215 | 215
Figure 8-18 | Figure 8-18: Asset Criticality and Maintenance/Replacement Strategies ......... 218 | 218
Figure 8-19 | Figure 8-19: WMP Data Platform Page ... 223 | 223
Figure 8-20 | Figure 8-20: Asset 360 3-Year Roadmap Page ..... 225 | 225
Figure 8-21 | Figure 8-21: IIP 3-Year Roadmap Page ... 226 | 226
Figure 8-22 | Figure 8-22: Open Work Orders: Corrective Maintenance ...... 230 | 230
Figure 8-23 | Figure 8-23: Distribution Open Work Orders . 232 | 232
Figure 8-24 | Figure 8-24: Transmission Open Work Orders – Not Past Due 233 | 233
Figure 8-25 | Figure 8-25: Results of Reclosure Protocols in Fault Avoidance ........... 235 | 235
Figure 8-26 | Figure 8-26: Vegetation Inspections and Clearance in the HFTD ......... 262 | 262
Figure 8-27 | Figure 8-27: Vegetation Outages and Ignitions in the HFTD.... 263 | 263
Figure 8-28 | Figure 8-28: Detailed Vegetation Inspections Process Flow .... 266 | 266
Figure 8-29 | Figure 8-29: Fuels Modification Sites Using CRI and WRRM ... 272 | 272
Figure 8-30 | Figure 8-30: Pole Clearing (Brushing) Process Flow .... 274 | 274
Figure 8-31 | Figure 8-31: Enhanced Clearance Process Flow .......... 278 | 278
Figure 8-32 | Figure 8-32: Auditing Pre-Inspection, Tree Trim, and Pole Clearing Process Flow ......... 283 | 283
Figure 8-33 | Figure 8-33: Open Work Orders in the HFTD . 286 | 286
Figure 8-34 | Figure 8-34: Smoke Detection Image Identified by AI Smoke Detection Algorithm ...... 317 | 317
Figure 8-35 | Figure 8-35: SAWTI Across Time and Incidences of Major Wildfires .... 325 | 325
Figure 8-36 | Figure 8-36: Wind Gust Machine Learning Validation for West Alpine 326 | 326
Figure 8-37 | Figure 8-37: Example of ML Gust Forecast Model Output ...... 327 | 327
Figure 8-38 | Figure 8-38: Historical Major Wildfire Correlation to FPI ........ 333 | 333
Figure 8-39 | Figure 8-39: EOC Activation Levels Page 343 | 343
Figure 8-40 | Figure 8-40: SDG&E Response Phases Page ........ 344 | 344
Figure 8-41 | Figure 8-41: WCRC Floor Plan Page ........ 375 | 375
Figure 8-42 | Figure 8-42: Key Components of Service Restoration Procedures ....... 380 | 380
Figure 9-1 | Figure 9-1: Risk-Informed Investment Decision & Risk Mitigation Implementation Step of the Enterprise Risk Management Framework Page ....... 407 | 407
Figure 9-2 | Figure 9-2: Frequently De-Energized Circuits 411 | 411
Figure 9-3 | Figure 9-3: PSPS Customers Impact by RFW .. 416 | 416
Figure 9-4 | Figure 9-4: PSPS System Impact by RFW Page .... 416 | 416
Figure 9-5 | Figure 9-5: PSPS Decision-Making Framework ........... 420 | 420
Figure 10-1 | Figure 10-1: Monitoring & Review Step of the Enterprise Risk Management Framework ......... 423 | 423
Figure 11-1 | Figure 11-1: Monitoring & Review Step of the Enterprise Risk Management Framework ......... 434 | 434
Figure 12-1 | Figure 12-1: Monitoring & Review Step of the Enterprise Risk Management Framework ......... 440 | 440