## Distribution OH
Checklist Date: | 2023-02-02
Critical Attribute | Critical attribute is defined as any question that identifies a condition that could lead to either an ignition point or wire down situation that could result in a potential fire ignition.
New Order | Section | Question / Displayed Language | Answer / Input | Rules | Critical Attribute (Asset Strategy) - 2023
0 | Asset Details | Currently in Inspect Leave as is | Currently in Inspect Leave as is |  | No
1.0 | Access & Confirmations | In what role are you performing this work? | GO165 Compliance Inspector | Input value, go to next element | No
1.1 | Access & Confirmations | In what role are you performing this work? | Other | Input value, go to next element | No
2.0 | Access & Confirmations | Did you gain access to the Haloed Structure? | Yes | Input value, go to next element | No
2.1 | Access & Confirmations | Did you gain access to the Haloed Structure? | No | Input value, User select a reason and create an independent EC notification | No
2.1.1 | Access & Confirmations, Did you gain access to the Haloed Structure? , No | (if no): Please Select a reason | Customer Access Appointment | Input value, User select a reason and create an independent EC notification | No
2.1.2 | Access & Confirmations, Did you gain access to the Haloed Structure? , No | (if no): Please Select a reason | Angry Customer | Input value, User select a reason and create an independent EC notification | No
2.1.3 | Access & Confirmations, Did you gain access to the Haloed Structure? , No | (if no): Please Select a reason | Customer Refusal | Input value, User select a reason and create an independent EC notification | No
2.1.4 | Access & Confirmations, Did you gain access to the Haloed Structure? , No | (if no): Please Select a reason | Locked gate/blocked access | Input value, User select a reason and create an independent EC notification | No
2.1.5 | Access & Confirmations, Did you gain access to the Haloed Structure? , No | (if no): Please Select a reason | No access due to vegetation | Input value, User select a reason and create an independent EC notification | No
2.1.6 | Access & Confirmations, Did you gain access to the Haloed Structure? , No | (if no): Please Select a reason | No safe access | Input value, User select a reason and create an independent EC notification | No
2.1.7 | Access & Confirmations, Did you gain access to the Haloed Structure? , No | (if no): Create an EC | EC-Create form | Input value, User select a reason and create an independent EC notification | No
3.0 | Access & Confirmations | Is this Asset approved for an Inspection? Approved Assets are as follows: 1. Distribution Pole /Tower 2.Transmission Pole with Distribution Under-Build (steel or wood) 3. Idle Pole 4. Tree Connect | Yes | Input value, go to next element | No
3.1 | Access & Confirmations | Is this Asset approved for an Inspection? Approved Assets are as follows: 1. Distribution Pole /Tower 2.Transmission Pole with Distribution Under-Build (steel or wood) 3. Idle Pole 4. Tree Connect | No | Input value, User select a reason and attach photos (map screenshot and at least two field photos), and enters text in Comments | No
3.1.1 | Access & Confirmations, Is this Asset approved for an Inspection?, No | (If No): Select one of the following | Structure does not exist in the field. | Input value, User select a reason and attach photos (map screenshot and at least two field photos), and enters text in Comments | No
3.1.2 | Access & Confirmations, Is this Asset approved for an Inspection?, No | (If No): Select one of the following | Structure is in the field; Structure is Customer-Owned. It is inspected by the customer. | Input value, User select a reason and attach photos (map screenshot and at least two field photos), and enters text in Comments | No
3.1.3 | Access & Confirmations, Is this Asset approved for an Inspection?, No | (If No): Select one of the following | Structure is in the field; Pole is a Streetlight-only pole. It is inspected by another program. | Input value, User select a reason and attach photos (map screenshot and at least two field photos), and enters text in Comments | No
3.1.4 | Access & Confirmations, Is this Asset approved for an Inspection?, No | (If No): Select one of the following | Structure is in the field; Pole is a Communication-only pole. It is inspected by another program. | Input value, User select a reason and attach photos (map screenshot and at least two field photos), and enters text in Comments | No
3.1.5 | Access & Confirmations, Is this Asset approved for an Inspection?, No | (If No): Select one of the following | Structure is in the field; Pole is a Transmission-only pole. It is inspected by another program. | Input value, User select a reason and attach photos (map screenshot and at least two field photos), and enters text in Comments | No
3.1.6 | Access & Confirmations, Is this Asset approved for an Inspection?, No | (If No): Attach photos of the related asset discrepency Minimum Requirement: Attach a map screenshot and at least two field photos | Photo upload element with minimum 3 photo required | Input value, User select a reason and attach photos (map screenshot and at least two field photos), and enters text in Comments | No
3.1.7 | Access & Confirmations, Is this Asset approved for an Inspection?, No | (If No): Comments | Open Text box, required | Input value, User select a reason and attach photos (map screenshot and at least two field photos), and enters text in Comments | No
4.0 | Access & Confirmations | Did you perform a visual 360-degree Inspection of this Structure? | Yes | Input value, go to next element | No
4.1 | Access & Confirmations | Did you perform a visual 360-degree Inspection of this Structure? | No | Input value, create an independent EC notification | No
4.1.1 | Access & Confirmations , Did you perform a visual 360-degree Inspection of this Structure?, No | (if no): Create an EC | EC-Create form | Input value, create an independent EC notification | No
5 | Access & Confirmations | Did you perform a visual inspection of all associated conductor(s) from structure to mid-span in all directions or to the weather-head or to the termination point? | Yes | Input value, go to next element | No
5.1 | Access & Confirmations | Did you perform a visual inspection of all associated conductor(s) from structure to mid-span in all directions or to the weather-head or to the termination point? | No | Input value, create an independent EC notification | No
5.1.1 | Access & Confirmations , Did you perform a visual inspection of all associated conductor(s) from structure to mid-span in all directions or to the weather-head or to the termination point?, No | (if no): Create an EC | EC-Create form | Input value, create an independent EC notification | No
6.0 | Structure | Select type of structure * Distribution-only Structure (Pole, Tower, Lattice, Push Pole, Stub) * Transmission with Distribution Underbuild * Tree Connect | Distribution-only Structure (Pole, Tower, Lattice, Push Pole, Stub) | User must choose 1 of 3 Pill buttons Transmission with Distribution Underbuild selection displays secondary structure type: 1) Steel 2) Non-steel | No
6.0.2 | Structure, Distribution-only Structure / Barcode | Is there a pole number on this stucture ? | Yes | Pillbox OPTIONS - REQUIRED This question should function like the current distribution form | No
6.0.3 | Structure, Distribution-only Structure / Barcode | Is there a pole number on this stucture ? | No | PILL BOX OPTIONS This question should work exactly the same as the current prod distribution question | No
6.0.4 | Structure, Distribution-only Structure / Barcode | Is the pole number damaged? | Yes pillbox |  | No
6.0.5 | Structure, Distribution-only Structure / Barcode | Is the pole number damaged? | No pillbox |  | No
6.0.6 | Structure, Distribution-only Structure / Barcode | Were you able to install a new pole bardcode? | Yes pillbox |  | No
6.0.7 | Structure, Distribution-only Structure / Barcode | Were you able to install a new pole bardcode? | No pillbox |  | No
6.0.8 | Structure, Distribution-only Structure / Barcode | Scan the new barcode or manually enter if unable to scan | Text box and scanning ability- Max 9 characters | structure type - Distribution Pole) If Yes - Were you able to install a new barcode text box and scanning ability- Max 9 characters | No
6.0.9 | Structure, Distribution-only Structure / Barcode | Were you able to install a new pole barcode? | Yes pillbox |  | No
6.0.10 | Structure, Distribution-only Structure / Barcode | Were you able to install a new pole barcode? | No pillbox |  | No
6.0.11 | Structure, Distribution-only Structure / Barcode | Scan the current barcode or manually enter if unable to scan | Text box and scanning ability- Max 9 characters |  | No
6.0.12 | Structure, Distribution-only Structure / Barcode | I am at the correct location | Checkbox |  | No
6.0.13 | Structure, Distribution-only Structure / Barcode | Hostile Customer nearby | "Select the reason you were unable to install it" | structure type - Distribution Pole) If No - Were you able to install a new pole barcode? PILL BOX. DROP DOWN | No
6.0.14 | Structure, Distribution-only Structure / Barcode | Rough terrain/Slope danger | "Select the reason you were unable to install it" | structure type - Distribution Pole) If No - Were you able to install a new pole barcode? PILL BOX. DROP DOWN | No
6.0.15 | Structure, Distribution-only Structure / Barcode | Surrounded by posion oak/ivy,ticks,rattlesnakes | "Select the reason you were unable to install it" | structure type - Distribution Pole) If No - Were you able to install a new pole barcode? PILL BOX. DROP DOWN | No
6.0.16 | Structure, Distribution-only Structure / Barcode | Hiked in: Exhausted supply of pole number tags | "Select the reason you were unable to install it" | structure type - Distribution Pole) If No - Were you able to install a new pole barcode? PILL BOX. DROP DOWN | No
6.0.17 | Structure, Distribution-only Structure / Barcode | Hiked in: Exhausted supply material/tools to attach tag | "Select the reason you were unable to install it" | structure type - Distribution Pole) If No - Were you able to install a new pole barcode? PILL BOX. DROP DOWN | No
6.0.18 | Structure, Distribution-only Structure / Barcode | Other | "Select the reason you were unable to install it" | structure type - Distribution Pole) If No - Were you able to install a new pole barcode? PILL BOX. DROP DOWN | No
6.0.19 | Structure, Distribution-only Structure / Barcode | Display comments box "Enter another reason" | Text box | structure type - Distribution Pole) If Other | No
6.0.20 | Structure, Distribution-only Structure / Barcode | N/A | Matches - Scannable | Inspect sends automatically when all of the following conditions are met: - Is there a pole number on this structure? = Yes - Is the pole number damaged? = No - Current barcode value is populated via the scan feature - Current barcode value matches the value in GIS | No
6.0.21 | Structure, Distribution-only Structure / Barcode | N/A | Does Not Match - Scannable - There is valid value in GIS | Inspect sends automatically when all of the following conditions are met: - Is there a pole number on this structure? = Yes - Is the pole number damaged? = No - Current barcode value is populated via the scan feature - Current barcode value does not match the value in GIS An RW will automatically be created. | No
6.0.22 | Structure, Distribution-only Structure / Barcode | N/A | Matches - Not Scanable | Inspect sends automatically when all of the following conditions are met: - Is there a pole number on this structure? = Yes - Is the pole number damaged? = No - Current barcode value is populated via manual entry - Current barcode value matches the value in GIS | No
6.0.23 | Structure, Distribution-only Structure / Barcode | N/A | Does Not Match - Not Scannable - There is valid value in GIS | Inspect sends automatically when all of the following conditions are met: - Is there a pole number on this structure? = Yes - Is the pole number damaged? = No - Current barcode value is populated via manual entry - Current barcode value does not match the value in GIS An RW will automatically be created. | No
6.0.24 | Structure, Distribution-only Structure / Barcode | N/A | Damaged - Replaced Pole Number | Inspect sends automatically when all of the following conditions are met: - Is there a pole number on this structure? = Yes - Is the pole number damaged? = Yes - Were you able to install a new pole barcode? = Yes An RW will automatically be created. | No
6.0.25 | Structure, Distribution-only Structure / Barcode | N/A | Installed New Pole Number | Inspect sends automatically when all of the following conditions are met: - Is there a pole number on this structure? = No - Were you able to install a new pole barcode? = Yes An RW will automatically be created. | No
6.0.26 | Structure, Distribution-only Structure | Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
6.0.27 | Structure, Distribution-only Structure | Pole leaning or out of plumb by more than 10% of its height above the ground | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
6.0.27 | Structure, Distribution-only Structure | Select if there are risks (including ignition risk), hazards or other maintenance conditions not previously captured in the checklist above for the structure as described in the job aid | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
6.0.1 | Structure | Structure (Distribution Pole) | No Structure damage or compelling abnormal conditions to report | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification | No
6.1 | Structure | Select type of structure | Transmission with Distribution Underbuild (2 Options: Steel or Non-Steel) | PILL BOX OPTIONS - LIMIT DISPLAYED ITEMS BASED ON COLUMN "P" INDICATION (i.e. "(Distribution Pole)") Transmission with Distribution Underbuild selection should display a new question below it This question should function like the current distribution form | No
6.1.1 | Structure (Transmission with Distribution Underbuild - Steel) | (If structure type = Transmission with Distribution Underbuild) What kind of transmission structure is present? | Steel Transmission structure | PILLBOX OPTIONS - REQUIRED This question should function like the current distribution form | No
6.1.2 | Structure (Transmission with Distribution Underbuild - Steel) | Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
6.1.3 | Structure (Transmission with Distribution Underbuild - Steel) | Pole leaning or out of plumb by more than 10% of its height above the ground | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
6.1.4 | Structure (Transmission with Distribution Underbuild - Steel) | Distribution riser on structure | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
6.1.5 | Structure (Transmission with Distribution Underbuild - Steel) | Distribution transformer serving an external customer installed without a common neutral present | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
6.1.6 | Structure (Transmission with Distribution Underbuild - Steel) | Climbing space obstructed | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
6.1.7 | Structure (Transmission with Distribution Underbuild - Steel) | Select if there are risks (including ignition risk), hazards or other maintenance conditions not previously captured in the checklist above for the structure as described in the job aid | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
6.1.8 | Structure (Transmission with Distribution Underbuild - Non-Steel) | (If structure type = Transmission with Distribution Underbuild) What kind of transmission structure is present? | Non-Steel Transmission structure | PILLBOX OPTIONS - REQUIRED This question should function like the current distribution form | No
6.1.9 | Structure (Transmission with Distribution Underbuild - Non-Steel) | Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
6.1.10 | Structure (Transmission with Distribution Underbuild - Non-Steel) | Pole leaning or out of plumb by more than 10% of its height above the ground | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
6.1.11 | Structure (Transmission with Distribution Underbuild - Non-Steel) | Missing or broken distribution bridging | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
6.1.12 | Structure (Transmission with Distribution Underbuild - Non-Steel) | Select if there are risks (including ignition risk), hazards or other maintenance conditions not previously captured in the checklist above for the structure as described in the job aid | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
6.2.0 | Structure (Tree Connect) | Select type of structure | Tree Connect |  | No
6.2.1 | Structure (Tree Connect) | Structure (Tree Connect) | Select one option for the current field condition, then create the required notification | REQUIRED : If user selects type of structure as Tree connect. Statement | N/A
6.2.2 | Structure (Tree Connect) | Structure (Tree Connect) | Tree is in good condition. Tree is green. Guidance: No EC Required. If there is a pending clearance pole tag, then cancel the tag. | Single Pillbox Only 1 of the following can be selected. When one of the options is selected, display the appropriate guidance under the selection. | No
6.2.3 | Structure (Tree Connect) | Structure (Tree Connect) | Tree is NOT in good condition; non-emergency compelling conditions, hazards, or risks are present. Tree may be dead, dying or green. Guidance: Create EC notification OR if there is a pending tag, update pending EC to match field condition | Single Pillbox Only 1 of the following can be selected. When one of the options is selected, display the appropriate guidance under the selection. Display Create an EC option in the Declarations section and make it required. | Yes
6.2.4 | Structure (Tree Connect) | Structure (Tree Connect) | An immediate emergncy hazard exists. Tree may be dead, dying or green Guidance: Create Priority-A EC notification Standby until relieved. | Single Pillbox Only 1 of the following can be selected. When one of the options is selected, display the appropriate guidance under the selection. Display Create an EC option in the Declarations section. Keep the current logic where it is required if there are no pending ECs and optional otherwise. | Yes
6.2.5 | Structure (Tree Connect) | Structure (Tree Connect) | Tree condition cannot be adequately assessed. Guidance: Create EC notification for assesment or if there is a pending assessment or clearance pole tag, update the pending EC to match field conditions. | Single Pillbox Only 1 of the following can be selected. When one of the options is selected, display the appropriate guidance under the selection. If there is a pending EC with the FDA Tree/Vine, Tree Connect, Assessment or Tree/Vine, Decayed/Rotten, Install CL Pole no additional logic is required. If there are no pending ECs or no pending ECs with either of the FDAs mentioned above, display Create an EC subform right under the guidance and make it required. Default the primary FDA to Tree/Vine, Tree Connect, Assessment, Priority B. | Yes
7.0 | Conductor | Does this structure have PG&E owned conductor? | Yes | PILLBOX OPTIONS - REQUIRED Answering "Yes" Displays entire Conductor Section (Column "I") Answering "No hides entire Conductor Section (Column "I") | No
7.1 | Conductor | Does this structure have PG&E owned conductor? | No | PILLBOX OPTIONS - REQUIRED Answering "Yes" Displays entire Conductor Section (Column "I") Answering "No hides entire Conductor Section (Column "I") | No
7.2 | Conductor | Provide comments about wire configuration (i.e. Line & Buck, 4-way corner, tangent, etc.) (Optional) | <OPTIONAL COMMENTS FIELD> | Display text box if above answer in column Q is "Yes" *Not required to be filled out | No
7.3 | Conductor | Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
7.4 | Conductor | Primary covered conductor ( "tree wire") has exposed, energized sections (such as rotated Kaddas covers, splices, connectors, flying bells) that are not covered or jacket has visible damages or signs of tracking | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
7.5 | Conductor | Conductor has splices tied into insulator or slices in contact with the tie wire, preventing free movement of splice with conductor | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
7.6 | Conductor | Primary or secondary conductor has diminished clearance mid span or uneven conductor sag | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
7.7 | Conductor | Open wire secondary conductor with rack construction has missing spreader brackets for spans > 135' | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
7.8 | Conductor | Hand or preform tie wire broken, damaged, burnt,corroded, loose, showing signs of wearing, missing, or missing armor rod | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
7.9 | Conductor | Jumper burnt or jumper clearance issues | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
7.10 | Conductor | Service conductor has diminished clearance | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
7.11 | Conductor | Select if there are risks (including ignition risk), hazards or other maintenance conditions not previously captured in the checklist above for the conductor as described in the job aid | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
7.12 | Conductor | No conductor damage or compelling abnormal conditions to report on primary, secondary, and/or service conductor | Checkbox | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification | No
8.0 | Equipment | Does this structure have equipment? | Yes | PILLBOX BUTTONS - REQUIRED Answering "Yes" Displays entire Equipment Section (Column "I") Answering "No hides entire Equipment Section (Column "I") | No
8.1 | Equipment | Does this structure have equipment? | No | PILLBOX BUTTONS - REQUIRED Answering "Yes" Displays entire Equipment Section (Column "I") Answering "No hides entire Equipment Section (Column "I") | No
8.2 | Equipment / Transformer | Transformer cutouts broken, damaged, cracked, loose, or flashed | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
8.3 | Equipment / Transformer | Transformer flashed or corroded, e.g integrity of the metal is breached - holes in metal, cover not securable, metal is damaged, separation, layering, or bubbling | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Section (NEW) (Column "P") If Checkbox is selected - display "Follow COE Process" (do not require an EC Notification) and comments box | Yes
8.4 | Equipment / Transformer | Transformer shows signs of leaking, seeping, or weeping oil | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
| Equipment / Transformer | Transformer has primary and/or secondary bushing and/or terminations damaged or broken | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
8.5 | Equipment / Transformer | Internal Fault Device has activated (overheated) on the transformer (orange band is visible) | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
8.6 | Equipment / Transformer | Obvious paralleled transformer condition at this location (checkbox) - Conventional transformers in obvious parallel connection, no self-protected (SP) transformer present (pillbox) - Self-protected (SP) transformers in obvious parallel connection with conventional transformers (pillbox) - Self-protected (SP) transformers in obvious parallel connection, no conventional transformer present (pillbox) | Checkbox, pill button | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
8.7 | Equipment / Transformer | Select if there are risks (including ignition risk), hazards or other maintenance conditions not previously captured in the checklist above for the equipment as described in the job aid | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
8.8 | Equipment / Transformer | "No equipment damage or compelling abnormal conditions to report (Transformer) | Pill button | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification | No
8.9 | Equipment / Other Equipment | Display Header "Other Equipment" Idle transformer at location is energized |  | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
8.10 | Equipment / Other Equipment | Operating number missing, broken, illegible, not installed in field or incorrectly installed in field | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
8.11 | Equipment / Other Equipment | Lightning arresters broken, damaged, flashed, or the ground lead disconnect activated | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
8.12 | Equipment / Other Equipment | Fuses corroded on the mounting or ending fittings, hanging upside-down, missing compenents, cracked, deteriorated, burnt or charring, paint finish flaking or cracked, layers exposed, red cap missing (E fuses only) | Checkbox |  | Yes
8.13 | Equipment / Other Equipment | Other equipment leaking/seeping/weeping pil or corroded | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
8.14 | Equipment / Other Equipment | Radial/EOL (End-of-Line) configuration riser/pothead broken damaged, loose, or flashed. | Checkbox |  | Yes
8.15 | Equipment / Other Equipment | Select if there are risks (including ignition risk), hazards or other maintenance conditions not previously captured in the checklist above for the equipment as described in the job aid | Checkbox |  | No
8.16 | Equipment / Other Equipment | No equipment damage or compelling abnormal conditions to report (Other Equipment Issues) | Pill button |  | No
8.17 | Equipment / Follow the Critical Equipment COE process | Display Header "Follow the Critical Equipment COE process" Line protection cutouts for loop configuration broken, damaged, cracked, loose, or flashed | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Section (NEW) (Column "P") If Checkbox is selected - display "Follow COE Process" (do not require an EC Notification) and comments box | N/A
8.18 | Equipment / Follow the Critical Equipment COE process | The critical operating equipment has visible signs of rust, corrosion, cracking, arcing, tracking, contamination, or damaged components | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | N/A
8.19 | Equipment / Follow the Critical Equipment COE process | Loop configurtion riser/pothead broken, damaged, loose or flashed | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Section (NEW) (Column "P") If Checkbox is selected - display "Follow COE Process" (do not require an EC Notification) and comments box | N/A
8.20 | Equipment / Follow the Critical Equipment COE process | No equipment damage or compelling abnormal conditions to report (Critical Opearating Equipment) | Pill button | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
9.0 | Anchors & Guys | Does or should this location have a Guy? | Yes | PILLBOX OPTIONS - REQUIRED If Yes, Display "Anchors & Guys" Section (Column "I") If No, Collapse "Anchors & Guys" Section (Column "I") | No
9.1 | Anchors & Guys | Does or should this location have a Guy? | No | PILLBOX OPTIONS - REQUIRED If Yes, Display "Anchors & Guys" Section (Column "I") If No, Collapse "Anchors & Guys" Section (Column "I") | No
9.2 | Anchors & Guys | Attach close-up photo of the ancho(s) | Photo capture/upload element | Minimum 1 photo required, multiple photos are acceptable | No
9.3 | Anchors & Guys | Necessary guys missing or loose | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
9.4 | Anchors & Guys | Guy wire broken, damaged, clearance issues, corroded, strain or abrasion | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
9.5 | Anchors & Guys | Guy bob or strain insulator (aka "Fish Stick") broken or missing | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
9.6 | Anchors & Guys | Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
9.7 | Anchors & Guys | Guy marker missing, damaged, or broken |  |  | No
9.8 | Anchors & Guys | Select if there are risks (including ignition risk), hazards or other maintenance conditions not previously captured in the checklist above for the anchor & guy as described in the job aid | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
9.9 | Anchors & Guys | No Anchor/Guy damage or compelling abnormal conditions to report | Pill button | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification | No
10.0 | Hardware Framing | Is Hardware Framing present on this structure? | Yes | PILLBOX BUTTONS - REQUIRED Answering "Yes" Displays entire Hardware Framing Section (Column "I") Answering "No hides entire Hardware / Framing Section (Column "I") | No
10.1 | Hardware Framing | Is Hardware Framing present on this structure? | No | PILLBOX BUTTONS - REQUIRED Answering "Yes" Displays entire Hardware Framing Section (Column "I") Answering "No hides entire Hardware / Framing Section (Column "I") | No
10.2 | Hardware Framing | Hardware Framing Issues High sign missing, broken, or illegible (backwards / upside down) | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
10.3 | Hardware Framing | Secondary connectors (mini wedge and Insulink) installed on primary conductor | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.4 | Hardware Framing | Tap clamps installed incorrectly | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.5 | Hardware Framing | Connector connections made with dissimilar metals installed incorrectly (copper over aluminum) | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.6 | Hardware Framing | Connector(s) corroded or damaged (potential to drop conductor) | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.7 | Hardware Framing | Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.8 | Hardware Framing | Crossarm bonding needs to be repaired | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.9 | Hardware Framing | Animal mitigation broken, damaged, or missing (if required) | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.10 | Hardware Framing | Bird Protection broken, damaged, deteriorated, or missing (if required) | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.11 | Hardware Framing | Steel lattice tower guard missing | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.12 | Hardware Framing | Molding missing, broken, damaged, or loose | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
10.13 | Hardware Framing | Insulators or king pin chipped, cracked, corroded, contaminated, flashed, have signs of tracking, broken or damaged | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.14 | Hardware Framing | Insulators or conductor squatting or floating | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | Yes
10.15 | Hardware Framing | Grounds exposed, broken, damaged, disconnected, loose, unsecured, or missing (if required) | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification Note: follow-up question in current distribution form was removed intentionally | Yes
10.16 | Hardware Framing | Pole steps are less than 8' 6" above the ground or any other accessible surface | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
10.17 | Hardware Framing | Visibility strips missing, broken, mismatched, or no longer reflective | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create EC Notification | No
10.18 | Hardware Framing | Select if there are risks (including ignition risk), hazards or other maintenance conditions not previously captured in the checklist above for the hardware as described in the job aid | Checkbox |  | No
10.19 | Hardware Framing | No Hardware Framing damage or compelling abnormal conditions to report | Pill button | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification | No
11.0 | Vegetation - EC specific Notifications | Tree causing strain or abrasion to single-service service drop (open-wire/triplex/quadplex) | Checkbox | Checkbox Prompt user to create EC if checkbox is selected | Yes
11.1 | Vegetation - EC specific Notifications | Structure, climbing space, or equipment is overgrown with vegetation | Checkbox | Checkbox Prompt user to create EC if checkbox is selected | Yes
11.2 | Vegetation - EC specific Notifications | Down guy above insulator is overgrown with vegetation and needs trimming | Checkbox | Checkbox Prompt user to create EC if checkbox is selected | Yes
11.3 | Vegetation - EC specific Notifications | Open-wire secondary is overgrown with vegetation (no strain or abrasion present) | Checkbox | Checkbox Prompt user to create EC if checkbox is selected | Yes
11.4 | Vegetation - EC specific Notifications | Open-wire service conductor(s) are overgrown with vegetation (no strain or abrasion present) | Checkbox | Checkbox Prompt user to create EC if checkbox is selected | Yes
11.5 | Vegetation - EC specific Notifications | No vegetation issues or compelling abnormal conditions to report for the EC in accordance with G0165 | Pill button | PILL BOX OPTIONS This question should work exactly the same as the current prod distribution question | No
11.6 | Vegetation - Veg Specific Notifications | Tree causing strain or abrasion to secondary (open-wire, rack or AWAC feeding more than one service OR open-wire secondary between two primary poles) | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create Veg Notification | Yes
11.7 | Vegetation - Veg Specific Notifications | Trees/Branches aloft are dead or broken and can strike facilities (structure and/or conductor) | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *Create Veg Notification | Yes
11.8 | Vegetation - Veg Specific Notifications | "Distribution Facility / Pole located in State Responsibility Area (SRA) / Federal Responsibility Area (FRA) / High Fire Threat District (HFTD) with vegetation within 4’ of primary conductor or PG&E Equipment | Checkbox | Checkbox will only be displayed for HFTD (Tier 3/2) poles, FRA and SRA | No
11.9 | Vegetation - Veg Specific Notifications | Vegetation removal required within 4' of energized conductor for 60 or 70kV, 10' of energized conductor up to 230 kV. | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") If selected require *Create vegetation notification Show if Structure type is Tranmission pole | Yes
| Vegetation - Veg Specific Notifications | Structure with nonexempt equipment: At ground level within the 10’ radius where flammable materials are present. Including but not limited to: ground litter, duff and dead or desiccated vegetation | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") If selected, require *Create vegetation notification Show only if not Tier 2 and Tier 3 structures. Checkbox, If selected Trigger to report a veg corrective, display for SRA, FRA and T2/T3 | Yes
| Vegetation - Veg Specific Notifications | Structure with nonexempt equipment: From 0 to 8 feet above ground level within the 10' radius where flammable trash, debris or other materials, grass, herbaceous and brush vegetation, and/or all limbs and foliage of living trees are present. | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") If selected, require *Create vegetation notification | Yes
| Vegetation - Veg Specific Notifications | Structure with nonexempt equipment: From 8 feet to horizontal plane of highest point of conductor attachment within the 10’ radius where dead, diseased or dying limbs and foliage and any dead, diseased or dying trees are present. | Checkbox | CHECKBOX, At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") If selected, require *Create vegetation notification Show only from May 1 - November 30. | Yes
| Vegetation - Veg Specific Notifications | No vegetation issues or compelling abnormal conditions to report for the Vegetation EC inaccordance with GO95, PRC 4292, PRC 4293 | PILLBOX At Least 1 Required Per Overall Section Section *DO NOT REQUIRE EC Notification” | PILLBOX At Least 1 Required Per Overall Section Section (Column "P") *DO NOT REQUIRE EC Notification” | No
12.0 | Other Required Data | Other Required Data Items | Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | CHECKBOX - OPTIONAL Show ONLY for Tier 2 or NON-HFTD. User should not be able to see this question on a tier 3 structure If Checked, require Photo Add a header to the photo "Attach photo (PCB transformer" *DO NOT REQUIRE EC Notification | No
12.1 | Other Required Data | Other Required Data Items | Additional inspector comments | CHECKBOX - OPTIONAL If Checked, require Comments *DO NOT REQUIRE EC Notification | No
12.2 | Other Required Data | Other Required Data Items | No Other Required Data items to report | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification | No
13.0 | Attach Photos | Attach Photos | Attach 2 Photos of entire pole from 2 locations | This Section should work exactly the same as the current prod distribution question Note: This should be moved to the end, before Declarations, after Other Required Data | No
13.1 | Attach Photos | Attach Photos | Attach Photo of the Top 1/3 of the pole | This Section should work exactly the same as the current prod distribution question Note: This should be moved to the end, before Declarations, after Other Required Data | No
13.2 | Attach Photos | Attach Photos | Attach Photo of the Middle 1/3 of the pole | This Section should work exactly the same as the current prod distribution question Note: This should be moved to the end, before Declarations, after Other Required Data | No
13.3 | Attach Photos | Attach Photos | Attach Photo of bottom 1/3 of the pole | This Section should work exactly the same as the current prod distribution question Note: This should be moved to the end, before Declarations, after Other Required Data | No
14.0 | Declarations | Observed an Idle Facility | Checkbox | CHECKBOX - OPTIONAL If Checked, show dollow up question "Please select a reason" *DO NOT REQUIRE EC Notification | No
14.1 | Declarations | Pending Idle Facility Notification | List all open IF notifiocation on the structure |  | No
14.2 | Declarations | Pending EC Notification for Idle Facility, De-energize | List all open EC Notification for Idle Facility, De-energize |  | No
14.3 | Declarations | Please select a reason | Pole is not mapped Idle. It is de-energized. | PILLBOX BUTTONS If user selects: Show follow up text "Please follow current Idle Facility Process" (Do not require EC Notification) | No
14.4 | Declarations | Please select a reason | Pole is not mapped Idle. It is energized | PILLBOX BUTTONS Show follow up text "Please follow current Idle Facility Process and Create a new or pending EC" | No
14.5 | Declarations | Please select a reason | This is mapped Idle Facility | PILLBOX BUTTONS, | No
14.6 | Declarations | Please select a reason | Pole is mapped. It is energized |  | No
14.7 | Declarations | Other Declaration Items | Minor Work performed at this location | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification If selected, go to OH Log Minor Work form (required) - current functionality | No
14.8 | Declarations | Other Declaration Items | Third-Party Utility Infraction at this location | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification If selected, go to TPU form (required) - current functionality | No
14.9 | Declarations | Other Declaration Items | Third-Party Non-Utility Infraction at this location | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification If selected, go to TPNU form (required) - current functionality | No
14.10 | Declarations | Other Declaration Items | Observed dead or dying raptor at this location | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification If selected, display "Please follow current bird form process." | No
14.11 | Declarations | Other Declaration Items | Observed a Transmission issue on a Transmission structure with Distribution underbuild | CHECKBOX - OPTIONAL If Checked, require Comments and Photo Add a header to the photo "Photo of the Transmission issue on a Transmission structure with Distribution underbuild" *DO NOT REQUIRE EC Notification | No
14.12 | Declarations | Other Declaration Items | Location requires a map correction | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification If user selects checkbox, make follow-up CHECKBOXES of applicable responses REQUIRED. User is able to select multiple options. If user selects this answer, show location picker, require two photos, one including a screenshot of the map, and display comment box | No
14.13 | Declarations | Select all that apply | Operating numbers - incorrectly mapped | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification like current functionality in prod. | No
14.14 | Declarations | Select all that apply | Structure is mapped at the wrong location | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification like current functionality in prod. | No
14.15 | Declarations | Select all that apply | Structure is mapped as joint pole, but is solely owned | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification like current functionality in prod. | No
14.16 | Declarations | Select all that apply | Structure is mapped as solely owned, but has utility attachment in the field | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification like current functionality in prod. | No
14.17 | Declarations | Select all that apply | Significant issues with where streets are in the field vs. on the map | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification like current functionality in prod. | No
14.18 | Declarations | Select all that apply | Street name on map is not correct | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification like current functionality in prod. | No
14.19 | Declarations | Select all that apply | Conductor characteristics are obviously inaccurate | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification like current functionality in prod. | No
14.20 | Declarations | Select all that apply | Inaccurately mapped equipment | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification like current functionality in prod. | No
14.21 | Declarations | Select all that apply | Primary tree wire exists in the field but mapped as bare conductor | CHECKBOX - OPTIONAL *DO NOT REQUIRE EC Notification like current functionality in prod. | No
14.22 | Declarations |  | Set Location | Map is displayed with the GPS coordinates. User is able to click on the map to move the pin. Required field if user selects "location requires a map correction" | No
14.23 | Declarations |  | Attach Photos for a Map Correction | Required (min 1 photod) field if user selects "location requires a map correction" | No
14.24 | Declarations |  | Comments | Required field if user selects "location requires a map correction" | No
14.25 | Declarations | Declaration Items | No Declarations items to report | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification | No
14.26 | Declarations | Report a new EC or Pending EC | Report a New EC | Checkbox - OPTIONAL only if 115 "Pending EC notification at this location" is selected otherwise required. Create an EC Hyperlink is visible if checkbox is selected Only show this question if an EC is required in the previous sections otherwise question will not be visible. | No
14.27 | Declarations | Report a new EC or Pending EC | Pending EC Notification at this location | CHECKBOX - OPTIONAL only if 114 "Report a New EC" is selected otherwise required. Search for an EC Hyperlink is visible if checkbox is selected Only show this question if an EC is required in the previous sections otherwise question will not be visible. | No
14.28 | Reasons for reinspection | Please select a reason for reinspection (This is for internal use only and will not be included in the inspection form record) | I was at the wrong location | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification Multi- select | No
14.29 | Reasons for reinspection | Please select a reason for reinspection (This is for internal use only and will not be included in the inspection form record) | I attached wrong photos or forgot to report a condition | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification Multi- select | No
14.30 | Reasons for reinspection | Please select a reason for reinspection (This is for internal use only and will not be included in the inspection form record) | I made a mistake in the checklist | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification Multi- select | No
14.31 | Reasons for reinspection | Please select a reason for reinspection (This is for internal use only and will not be included in the inspection form record) | Other | PILLBOX At Least 1 REQUIRED per overall Grouping identified in "Question (NEW)" Column (Column "P") *DO NOT REQUIRE EC Notification Multi- select If Other - Display text box "Give us other reasons." | No