## ET Ground & Climbing Forms
Main Sort | Steel Ground | Climbing | Non-Steel Ground | LC Required | Section | Question | Answer | Requirement | Form Field | Rules
1 | YES | YES | YES | NO | You are reinspecting this asset | Please select a reason for inspection | I was at the wrong location |  | single selection list
2 | YES | YES | YES | NO | You are reinspecting this asset | Please select a reason for inspection | I attached the wrong photos of forgot to report a condition |  | single selection list
3 | YES | YES | YES | NO | You are reinspecting this asset | Please select a reason for inspection | I made a mistake in the checklist |  | single selection list
4 | YES | YES | YES | NO | You are reinspecting this asset | Please select a reason for inspection | Other |  | single selection list | If selected- Give us other reasons. (provide text box)
5 | YES | YES | YES | N/A | Asset Details | Checklist Version | <Metadata/Autopopulated> | Required | Hidden - Payload only | pass the version number in the CharID remarks field since it is not always a decimal number. Always send over YES to SAP
6 | YES | YES | YES | N/A | Asset Details | Digital App Version | <Metadata/Autopopulated> | Required | Hidden - Payload only | pass the version number in the CharID remarks field since it is not always a decimal number. Always send over YES to SAP
7 | YES | YES | YES | N/A | Asset Details | Date Inspected | <Metadata/Autopopulated> | Required | Display | Default to current date and allow edits
8 | YES | YES | YES | N/A | Asset Details | GPS Location when form initiated | <Metadata/Autopopulated> | Required | Display | Hide during inspection process - show on summary screen
9 | YES | YES | YES | N/A | Asset Details | Work Center | <Metadata/Autopopulated> | Required | Display | Autopopulate from SAP
10 | YES | YES | YES | N/A | Asset Details | Structure Number | <Metadata/Autopopulated> | Required | Display | Autopopulate from SAP
11 | YES | YES | YES | N/A | Asset Details | ETL Number | <Metadata/Autopopulated> | Required | Display | Autopopulate from SAP
12 | YES | YES | YES | N/A | Asset Details | Transmission Line Name | <Metadata/Autopopulated> | Required | Display | Autopopulate from SAP
13 | YES | YES | YES | N/A | Asset Details | Voltage | <Metadata/Autopopulated> | Required | Display | Autopopulate from SAP
14 | YES | YES | YES | N/A | Asset Details | SAP Equipment ID | <Metadata/Autopopulated> | Required | Display | Autopopulate from SAP
15 | YES | YES | YES | N/A | Asset Details | Inspection Order Number | <Metadata/Autopopulated> | Required | Display | Autopopulate from SAP
16 | YES | YES | YES | N/A | Asset Details | GIS Latitude | <Metadata/Autopopulated> | Required | Display | ET GIS
17 | YES | YES | YES | N/A | Asset Details | GIS Longitude | <Metadata/Autopopulated> | Required | Display | ET GIS
18 | YES | YES | YES | N/A | Asset Details | GIS Elevation | <Metadata/Autopopulated> | Required | Display
19 | YES | YES | YES | N/A | Asset Details | Structure Type | <Metadata/Autopopulated> | Required | Display | Autopopulate from SAP currently pill box option - change to autopopulate
20 | YES | YES | YES | N/A | Asset Details | Person completing form | <Metadata/Autopopulated> | Required | Display | text field - pre-populate with user LanID, Allow user to edit. If edited, the system should track the original LanID and the change to LanID. Note: If this function is not possible, do not allow the user to edit.
21 | YES | YES | YES | N/A | Asset Details | Other names assigned to task | <Open Text Box> | Not Required | Text field
22 | YES | YES | YES | YES, HOST ONLY | Access | Are you able to Access the Structure? | Yes / No | Required | single select button | **This is a new business requirments and is not commited to the 2/17 release**If No, Require the ability to create 1 or more LC's and end inspection as CGI. If No is selected, display "Guidance: Structure is in the field but the location is not accessible. (i.e. flooded, locked gate, excessive vegetation, terrain, permitting)"
23 | YES | YES | YES | NO | Access |  | Yes / No | Required | single select button | If Yes, Continue the Checklist. If No, display "This selection will create a Map Correction notification". If No, Require FIeld Comments <text box> and Attach Field Photos (3): map screenshot, structure, structure number.
24 | YES | YES | YES | NO | Access | Is this asset approved for inspection? (i.e. asset exists and should not be a street light only, comms only, or customer owned) | Yes / No | Required | single select button | If no is selected, display "Asset not approved for inspection options"
25 | YES | YES | YES | NO | Access | Select one | Structure does not exist in the field. | Required | single selection list | If selected, display "This selection will create a Map Correction notification". Select one - pill box - end inspection form as complete. Require Comments <text box> and Attach Field Photos (3): map screenshot, two field photos.
26 | YES | YES | YES | NO | Access | Select one | Structure is in the field; Structure is Customer-Owned. It is inspected by the Customer. | Required | single selection list | If selected, display "This selection will create a Map Correction notification". Select one - pill box - end inspection form as complete. Require Comments <text box> and Attach Field Photos (3): map screenshot, two field photos.
27 | YES | YES | YES | YES, HOST ONLY | Access | Did you perform a visual 360-degree Inspection of this Structure? | Yes / No | Required | single select button | If no, create CGI tag - end inspection form as CGI
28 | YES | YES | YES | NO | Access | Did you perform a visual Inspection of all host and guest(s) circuits present? | Yes, all hosts and guest(s) present inspected | Required | single select button | If "Yes, all hosts and guest(s) present inspected is selected, ask Conductor - Guest and Insulator
29 | YES | YES | YES | NO | Access | Did you perform a visual Inspection of all host and guest(s) circuits present? | Yes, asset inspected, no guest present | Required | single select button | If "Yes, asset inspected, no guest present" is selected, do not ask about Conductor - Guest and Insulator
30 | YES | YES | YES | YES | Access | Did you perform a visual Inspection of all host and guest(s) circuits present? | No | Required | single select button | If no, create CGI tag - end inspection form as CGI
31 | YES | YES | YES | YES, HOST ONLY | Access | Does the Structure have missing, illegible, or incorrect numbering signage on poles or tower legs? Guidance: If Yes, Create an LC and continue the checklist. If No, Continue the Checklist. The Structure’s numbering signage must match the numbering shown on the Inspect ET map. | Yes / No | Required | single select button | If Yes, Create an LC and continue the checklist. If No, Continue the Checklist.
32 | YES | YES | YES | NO | Access | Is this asset a Distribution-only Structure? | Yes / No | Required | single select button | If No, Continue Checklist. If yes is selected, display "This selection will create a Map Correction notification".When selecting yes, display "Guidance: You are required to perform the inspection". If Yes, continue the checklist and require Field Comments <text box> and Attach Field Photos (3): map screenshot, two field photos.
33 | YES | YES | YES | YES, HOST ONLY | Vegetation | Vegetation issues | Vegetation covering anchor / guy | Required | exclusive multi select
34 | YES | YES | YES | YES, HOST ONLY | Vegetation | Vegetation issues | Significant vegetation or poison ivy/oak around base of structure or impacting climbing | Required | exclusive multi select
35 | YES | YES | YES | YES, HOST & GUEST | Vegetation | Vegetation issues | Vegetation removal required within 4' of conductor for 60 or 70kV, 10' of conductor up to 230 kV and 15' for 500 kV | Required | exclusive multi select
36 | YES | YES | YES | YES, HOST ONLY | Vegetation | Vegetation issues | Vegetation growing through switch platform | Required | exclusive multi select
37 | YES | YES | YES | YES, HOST ONLY | Vegetation | Vegetation issues | Vegetation removal required at structure / energized components (vegetation within 12") | Required | exclusive multi select
38 | YES | YES | YES | YES, HOST ONLY | Vegetation | Vegetation issues | No Vegetation issues or compelling abnormal conditions to report | Required | exclusive multi select
39 | YES | YES | YES | NO | Vegetation | Comments for Vegetation Issues (Optional) | <open text box> |  | open text box
40 | YES | YES | YES | NO | Minor Work | Did you perform Minor Work at this location? | Yes / No | Required | single select button | If yes is selected, Show comments box
41 | YES | YES | YES | NO | Anchors & Guys | Does this structure have a guy? | Yes / No | Required | single select button | If yes is selected, show checkboxes
42 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Guy Issues | Guy or guy hardware loose, missing or in poor condition | Required | exclusive multi select
43 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Guy Issues | Guy clearance inadequate from energized conductors |  | exclusive multi select
44 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Guy Issues | Guy insulator (fiberglass or porcelain) is missing or in poor condition | Required | exclusive multi select
45 | NO | NO | YES | YES, HOST ONLY | Anchors & Guys | Guy Issues | Guy hardware bonding is missing or in poor condition | Required | exclusive multi select
46 | NO | NO | YES | YES, HOST ONLY | Anchors & Guys | Guy Issues | Cattle guards broken or missing on down guys | Required | exclusive multi select
47 | NO | NO | YES | YES, HOST ONLY | Anchors & Guys | Guy Issues | Guy Insulator/Rod not attached directly at Wood Pole | Required | exclusive multi select
48 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Guy Issues | Turnbuckle(s) bottomed out / out of thread / pinged | Required | exclusive multi select
49 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Guy Issues | Preform guy grip is loose, out of position or in poor condition | Required | exclusive multi select
50 | NO | YES | NO | YES, HOST ONLY | Anchors & Guys | Guy Issues | Cross ties are loose, missing or in poor condition | Required | exclusive multi select
51 | NO | YES | NO | YES, HOST ONLY | Anchors & Guys | Guy Issues | Guy cable and hardware not per design Standard (drawing 046181 for types HVL, 2HVL, and 3 HVL; drawing 212866 for types HVC) | Required | exclusive multi select
52 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Guy Issues | No Guys issues or compelling abnormal conditions to report | Required | exclusive multi select
53 | YES | YES | YES | NO | Anchors & Guys | Comments for Guy Issues (Optional) | <Open Text Box> | Not Required | open text box
54 | YES | YES | YES | NO | Anchors & Guys | Condition of Guy System | 1 - No Visible Damage | Required | single selection list
55 | YES | YES | YES | NO | Anchors & Guys | Condition of Guy System | 2 - Light Damage | Required | single selection list
56 | YES | YES | YES | NO | Anchors & Guys | Condition of Guy System | 3 - Moderate Damage | Required | single selection list
57 | YES | YES | YES | NO | Anchors & Guys | Condition of Guy System | 4 - Heavy Damage | Required | single selection list
58 | YES | YES | YES | NO | Anchors & Guys | Condition of Guy System | 5 - Heavy Damage with Safety Concerns | Required | single selection list
61 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Anchor Rod Issues | Anchor(s) out of position or in poor condition | Required | exclusive multi select
62 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Anchor Rod Issues | Anchor is missing | Required | exclusive multi select
63 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Anchor Rod Issues | Anchor head is buried | Required | exclusive multi select
64 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Anchor Rod Issues | Earth around anchors eroded, soil movement, slide | Required | exclusive multi select
65 | YES | YES | YES | YES, HOST ONLY | Anchors & Guys | Anchor Rod Issues | Anchor(s) concrete in poor condition | Required | exclusive multi select
66 | YES | YES | YES | NO | Anchors & Guys | Anchor Rod Issues | No Anchor Rod issues or compelling abnormal conditions to report | Required | exclusive multi select
67 | YES | YES | YES | NO | Anchors & Guys | Comments for Anchor Rod Issues (Optional) | <Open Text Box> | Not Required | open text box
68 | YES | YES | YES | NO | Anchors & Guys | Condition of Anchor | 1 - No Visible Damage | Required | single selection list | Need condition scale 1-5
69 | YES | YES | YES | NO | Anchors & Guys | Condition of Anchor | 2 - Light Damage | Required | single selection list | Need condition scale 1-5
70 | YES | YES | YES | NO | Anchors & Guys | Condition of Anchor | 3 - Moderate Damage | Required | single selection list | Need condition scale 1-5
71 | YES | YES | YES | NO | Anchors & Guys | Condition of Anchor | 4 - Heavy Damage | Required | single selection list | Need condition scale 1-5
72 | YES | YES | YES | NO | Anchors & Guys | Condition of Anchor | 5 - Heavy Damage with Safety Concerns | Required | single selection list | Need condition scale 1-5
73 | NO | YES | NO | NO | 500kV / Internal Guying | Does this structure have internal guying? | Yes/No | Required | single select button
74 | NO | YES | NO | NO | 500kV / Internal Guying | Does this structure have cross-ties? | Yes/No | Required | single select button
75 | NO | YES | NO | NO | 500kV / Internal Guying | Were guy tensions adjusted and results measured? | Yes, guy tension adjusted and measured | Required | single selection list | Requires new question "Select type of tower"
76 | NO | YES | NO | NO | 500kV / Internal Guying | Were guy tensions adjusted and results measured? | No, guy tension does not need adjustment | Required | single selection list | Nothing happens
77 | NO | YES | NO | YES, HOST ONLY | 500kV / Internal Guying | Were guy tensions adjusted and results measured? | No, guy tension needs adjustment | Required | single selection list | Requires an LC
78 | NO | YES | NO | NO | 500kV / Internal Guying | Select type of tower | HVL, 2HVL, 3HVL, 4HVL, 5HVL, HVR, 2HVR, HVS, 2HVS, HVM, 2HVM | Required | single selection list | This question is only shown if "Yes, guy tensions were adjusted and measured" was selected. If this tower type is selected, show link that directs to a new screen which allows inspector to fill out the appropriate guy tensions for this tower type.
79 | NO | YES | NO | NO | 500kV / Internal Guying | Select type of tower | HVA | Required | single selection list | This question is only shown if "Yes, guy tensions were adjusted and measured" was selected. If this tower type is selected, show link that directs to a new screen which allows inspector to fill out the appropriate guy tensions for this tower type.
80 | NO | YES | NO | NO | 500kV / Internal Guying | Select type of tower | HVD, HVT | Required | single selection list | This question is only shown if "Yes, guy tensions were adjusted and measured" was selected. If this tower type is selected, show link that directs to a new screen which allows inspector to fill out the appropriate guy tensions for this tower type.
81 | NO | YES | NO | NO | 500kV / Internal Guying | Is this structure a double decker? | Yes | Required | single select button
82 | NO | YES | NO | NO | 500kV / Internal Guying | Is this structure a double decker? | No | Required | single select button
83 | NO | YES | NO | NO | 500kV / Internal Guying | Photos |  |  | attach photos | This will be required if "Is this structure a double decker" = YES
84 | YES | YES | NO | NO | Steel Structure Foundation | Foundation Type | Concrete | Required | single selection list | Select one of the foundation type - pill option
85 | YES | YES | NO | NO | Steel Structure Foundation | Foundation Type | Direct buried | Required | single selection list | Select one of the foundation type - pill option
86 | YES | YES | NO | NO | Steel Structure Foundation | Foundation Type | Piles | Required | single selection list | Select one of the foundation type - pill option
87 | YES | YES | NO | NO | Steel Structure Foundation | Foundation Type | Unable to identify | Required | single selection list | Provide text box as follow up if selected
88 | YES | NO | NO | YES, HOST ONLY | Steel Structure Foundation | Steel Structure Foundation Issues | Steel structure anchor bolts in poor condition | Required | exclusive multi select
89 | YES | NO | NO | YES, HOST ONLY | Steel Structure Foundation | Steel Structure Foundation Issues | Grout damaged or in poor condition | Required | exclusive multi select
90 | YES | YES | NO | YES, HOST ONLY | Steel Structure Foundation | Steel Structure Foundation Issues | Foundation is earth-covered or buried | Required | exclusive multi select
91 | YES | YES | NO | YES, HOST ONLY | Steel Structure Foundation | Steel Structure Foundation Issues | Concrete damaged, cracking, or in poor condition | Required | exclusive multi select
92 | YES | YES | NO | YES, HOST ONLY | Steel Structure Foundation | Steel Structure Foundation Issues | Exposed rebar, unintentional or by design | Required | exclusive multi select
93 | YES | YES | NO | YES, HOST ONLY | Steel Structure Foundation | Steel Structure Foundation Issues | Ground wire in poor condition (e.g. corroded, flashed, broken, missing) | Required | exclusive multi select
94 | YES | YES | NO | YES, HOST ONLY | Steel Structure Foundation | Steel Structure Foundation Issues | Mastic sealant missing or in poor condition | Required | exclusive multi select
95 | YES | YES | NO | YES, HOST ONLY | Steel Structure Foundation | Steel Structure Foundation Issues | Earth around structure eroded, soil movement, slide | Required | exclusive multi select
96 | YES | YES | NO | YES, HOST ONLY | Steel Structure Foundation | Steel Structure Foundation Issues | Piles exposed, rotted, or deteriorated | Required | exclusive multi select
97 | YES | YES | NO | YES, HOST ONLY | Steel Structure Foundation | Steel Structure Foundation Issues | Foundation fully submerged or direct buried in standing water | Required | exclusive multi select
100 | YES | YES | NO | NO | Steel Structure Foundation | Steel Structure Foundation Issues | No Steel Structure Foundation issues or compelling abnormal conditions to report | Required | exclusive multi select
101 | YES | YES | NO | NO | Steel Structure Foundation | Comments for Steel Structure Foundation Issues (Optional) | <Open Text Box> | Not Required | open text box
102 | YES | YES | NO | NO | Steel Structure Foundation | Condition of Steel Structure Foundation | 1 - No Visible Damage | Required | single selection list | Need condition scale 1-5
103 | YES | YES | NO | NO | Steel Structure Foundation | Condition of Steel Structure Foundation | 2 - Light Damage | Required | single selection list | Need condition scale 1-5
104 | YES | YES | NO | NO | Steel Structure Foundation | Condition of Steel Structure Foundation | 3 - Moderate Damage | Required | single selection list | Need condition scale 1-5
105 | YES | YES | NO | NO | Steel Structure Foundation | Condition of Steel Structure Foundation | 4 - Heavy Damage | Required | single selection list | Need condition scale 1-5
106 | YES | YES | NO | NO | Steel Structure Foundation | Condition of Steel Structure Foundation | 5 - Heavy Damage with Safety Concerns | Required | single selection list | Need condition scale 1-5
107 | YES | YES | NO | YES, HOST ONLY | Steel Structure Foundation | Stub/Splice Plate Issues | Stub or stub angle damaged or in poor condition | Required | exclusive multi select
108 | YES | YES | NO | NO | Steel Structure Foundation | Stub/Splice Plate Issues | No Stub/Splice Plate issues or compelling abnormal conditions to report | Required | exclusive multi select
109 | YES | YES | NO | NO | Steel Structure Foundation | Comments for Stub/Splice Plate Issues | <Open Text Box> | Not Required | open text box
110 | YES | YES | NO | NO | Steel Structure Foundation | Condition of Stub/Splice Plate | 1 - No Visible Damage | Required | single selection list
111 | YES | YES | NO | NO | Steel Structure Foundation | Condition of Stub/Splice Plate | 2 - Light Damage | Required | single selection list
112 | YES | YES | NO | NO | Steel Structure Foundation | Condition of Stub/Splice Plate | 3 - Moderate Damage | Required | single selection list
113 | YES | YES | NO | NO | Steel Structure Foundation | Condition of Stub/Splice Plate | 4 - Heavy Damage | Required | single selection list
114 | YES | YES | NO | NO | Steel Structure Foundation | Condition of Stub/Splice Plate | 5 - Heavy Damage with Safety Concerns | Required | single selection list
115 | YES | YES | YES | NO | Steel Structures or Non-Steel Structures | Birds Nest present? | Yes / No | Required | single select button | Show questions for Steel structure foundation right when expanded. If yes, display bird issues. If no, steel structure issues will already be visible. If no, only display Steel Structure Issues (no change from Inspect QA app logic)
116 | YES | YES | YES | YES, HOST & GUEST | Steel Structures or Non-Steel Structures | Bird Nest Issues | Bird nest above or too close to conductor or insulator | Required | exclusive multi select
117 | YES | YES | YES | YES, HOST & GUEST | Steel Structures or Non-Steel Structures | Bird Nest Issues | Bird nest(s) affecting climbing access | Required | exclusive multi select
118 | YES | YES | YES | NO | Steel Structures or Non-Steel Structures | Bird Nest Issues | No Bird Nest issues or compelling abnormal conditions to report | Required | exclusive multi select
119 | YES | YES | YES | YES, HOST & GUEST | Steel Structures or Non-Steel Structures | Are Bird Guards in poor condition? | Yes/No/Not Applicable | Required | single selection list | LC required only if "Yes" is selected
120 | YES | YES | YES | NO | Steel Structures or Non-Steel Structures | Comments for Bird Nest and Guard Issues (Optional) | <Open Text Box> | Not Required | open text box | Show if either birds nest is present of if bird gaurd is in poor condition.
121 | NO | NO | YES | NO | Steel Structures or Non-Steel Structures | Is there woodpecker damage? | Yes/No | Required | single selection list
122 | NO | NO | YES | YES, HOST & GUEST | Steel Structures or Non-Steel Structures | Is the damage severe or within 1 inch of any hardware? | Yes/No | Required | single selection list | Shown only if "yes" is selected for "Is there woodpecker damage?". LC is required
123 | YES | YES | NO | YES, HOST & GUEST | Steel Structures | Steel Structure Issues | Arm / crossarm / framing is damaged or in poor condition | Required | exclusive multi select
124 | YES | YES | NO | YES, HOST ONLY | Steel Structures | Steel Structure Issues | Corrosion present with greater than 30% material loss on steel members and/or hardware | Required | exclusive multi select
125 | YES | YES | NO | YES, HOST ONLY | Steel Structures | Steel Structure Issues | Structure is leaning, twisted, rotated, or out of circuit alignment | Required | exclusive multi select
126 | YES | YES | NO | YES, HOST ONLY | Steel Structures | Steel Structure Issues | Primary members are missing or in poor condition (excluding corrosion) | Required | exclusive multi select
127 | YES | YES | NO | YES, HOST ONLY | Steel Structures | Steel Structure Issues | Secondary members are missing or in poor condition (excluding corrosion) | Required | exclusive multi select
128 | YES | YES | NO | YES, HOST ONLY | Steel Structures | Steel Structure Issues | Splice plate damaged or in poor conditon | Required | exclusive multi select
129 | YES | YES | NO | YES, HOST & GUEST | Steel Structures | Steel Structure Issues | Insulator hanger (eye) plate in poor condition | Required | exclusive multi select
130 | YES | YES | NO | YES, HOST ONLY | Steel Structures | Steel Structure Issues | Steel structure (e.g. TSP, LDSP) is in poor condition (excluding corrosion) | Required | exclusive multi select
131 | YES | YES | NO | YES, HOST ONLY | Steel Structures | Steel Structure Issues | Steel structure hardware loose, missing, or in poor condition | Required | exclusive multi select
132 | YES | YES | NO | YES, HOST ONLY | Steel Structures | Steel Structure Issues | Tower paint/galvanizing finish in poor condition | Required | exclusive multi select
133 | YES | YES | NO | NO | Steel Structures | Steel Structure Issues | No Steel Structure issues or compelling abnormal conditions to report | Required | exclusive multi select
134 | YES | YES | NO | NO | Steel Structures | Comments for Steel Structure Issues (Optional) | <Open Text Box> | Not Required | open text box
135 | YES | YES | NO | NO | Steel Structures | Condition of Steel Structure | 1 - No Visible Damage | Required | single selection list | Need condition scale 1-5
136 | YES | YES | NO | NO | Steel Structures | Condition of Steel Structure | 2 - Light Damage | Required | single selection list | Need condition scale 1-5
137 | YES | YES | NO | NO | Steel Structures | Condition of Steel Structure | 3 - Moderate Damage | Required | single selection list | Need condition scale 1-5
138 | YES | YES | NO | NO | Steel Structures | Condition of Steel Structure | 4 - Heavy Damage | Required | single selection list | Need condition scale 1-5
139 | YES | YES | NO | NO | Steel Structures | Condition of Steel Structure | 5 - Heavy Damage with Safety Concerns | Required | single selection list | Need condition scale 1-5
140 | NO | NO | YES | YES, HOST ONLY | Non-Steel Structures | Non-Steel Structure Issues | Wood pole failed the hammer test | Required | exclusive multi select
141 | NO | NO | YES | YES, HOST ONLY | Non-Steel Structures | Non-Steel Structure Issues | Structure has vehicular or mechanical damage | Required | exclusive multi select
142 | NO | NO | YES | YES, HOST ONLY | Non-Steel Structures | Non-Steel Structure Issues | Structure has breaks, cracks, or splits | Required | exclusive multi select
143 | NO | NO | YES | YES, HOST ONLY | Non-Steel Structures | Non-Steel Structure Issues | Structure is rotten or decayed | Required | exclusive multi select
144 | NO | NO | YES | YES, HOST ONLY | Non-Steel Structures | Non-Steel Structure Issues | Structure is burnt | Required | exclusive multi select
145 | NO | NO | YES | YES, HOST ONLY | Non-Steel Structures | Non-Steel Structure Issues | Pole-top has damage or split-top | Required | exclusive multi select
146 | NO | NO | YES | YES, HOST ONLY | Non-Steel Structures | Non-Steel Structure Issues | Pole is out-of-plumb, leaning / deflection (e.g. > 3') | Required | exclusive multi select
147 | NO | NO | YES | YES, HOST ONLY | Non-Steel Structures | Non-Steel Structure Issues | Earth around structure eroded, soil movement, slide | Required | exclusive multi select
148 | NO | NO | YES | YES, HOST ONLY | Non-Steel Structures | Non-Steel Structure Issues | Standing water around base (not including seasonal conditions) | Required | exclusive multi select
149 | NO | NO | YES | YES, HOST ONLY | Non-Steel Structures | Non-Steel Structure Issues | Structure has greater than 20% material loss | Required | exclusive multi select
150 | NO | NO | YES | NO | Non-Steel Structures | Non-Steel Structure Issues | No Non-Steel Structures issues or compelling abnormal conditions to report | Required | exclusive multi select
151 | NO | NO | YES | NO | Non-Steel Structures | Comments for Non-Steel Structure Issues (Optional) | <Open Text Box> | Not Required | open text box
152 | NO | NO | YES | NO | Non-Steel Structures | Condition of Non-Steel Structure | 1 - No Visible Damage | Required | single selection list
153 | NO | NO | YES | NO | Non-Steel Structures | Condition of Non-Steel Structure | 2 - Light Damage | Required | single selection list
154 | NO | NO | YES | NO | Non-Steel Structures | Condition of Non-Steel Structure | 3 - Moderate Damage | Required | single selection list
155 | NO | NO | YES | NO | Non-Steel Structures | Condition of Non-Steel Structure | 4 - Heavy Damage | Required | single selection list
156 | NO | NO | YES | NO | Non-Steel Structures | Condition of Non-Steel Structure | 5 - Heavy Damage with Safety Concerns | Required | single selection list
157 | NO | NO | YES | YES, HOST & GUEST | Non Steel Framing | Is there a Crossarm present? | Yes / No | Required | single select button | If Yes is selected, show checkboxes (Line 166/167) and open text box (optional)
158 | NO | NO | YES | YES, HOST & GUEST | Non Steel Framing | Crossarm Issues | Crossarm / Framing assembly (e.g. bracing) is damaged or poor condition | Required | exclusive multi select
159 | NO | NO | YES | NO | Non Steel Framing | Crossarm Issues | No Crossarm / Framing assembly issues or compelling abnormal conditions to report | Required | exclusive multi select
160 | NO | NO | YES | NO | Non Steel Framing | Comments for Crossarm Issues (Optional) | <Open Text Box> | Not Required | open text box
161 | NO | NO | YES | YES, HOST & GUEST | Non Steel Framing | Non-Steel Framing Issues | Ground wire/molding loose, missing or in poor condition | Required | exclusive multi select
162 | NO | NO | YES | YES, HOST & GUEST | Non Steel Framing | Non-Steel Framing Issues | Insulator hanger (eye) plate in poor condition | Required | exclusive multi select
163 | NO | NO | YES | YES, HOST & GUEST | Non Steel Framing | Non-Steel Framing Issues | Bonding broken/missing | Required | exclusive multi select
164 | NO | NO | YES | YES, HOST & GUEST | Non Steel Framing | Non-Steel Framing Issues | Hardware (e.g. bolts, nuts, staples) loose, missing or in poor condition | Required | exclusive multi select
165 | NO | NO | YES | NO | Non Steel Framing | Non-Steel Framing Issues | No Non-Steel Framing issues or compelling abnormal conditions to report | Required | exclusive multi select
166 | NO | NO | YES | NO | Non Steel Framing | Comments for Non-Steel Framing Issues (Optional) | <Open Text Box> | Not Required | open text box
167 | NO | NO | YES | NO | Non Steel Framing | Condition of Non-Steel Framing | 1 - No Visible Damage | Required | single selection list | Need condition scale 1-5
168 | NO | NO | YES | NO | Non Steel Framing | Condition of Non-Steel Framing | 2 - Light Damage | Required | single selection list | Need condition scale 1-5
169 | NO | NO | YES | NO | Non Steel Framing | Condition of Non-Steel Framing | 3 - Moderate Damage | Required | single selection list | Need condition scale 1-5
170 | NO | NO | YES | NO | Non Steel Framing | Condition of Non-Steel Framing | 4 - Heavy Damage | Required | single selection list | Need condition scale 1-5
171 | NO | NO | YES | NO | Non Steel Framing | Condition of Non-Steel Framing | 5 - Heavy Damage with Safety Concerns | Required | single selection list | Need condition scale 1-5
172 | YES | YES | YES | NO | Conductor | Is there a Conductor present? | Yes / No | Required | single select button | If yes is selected, show checkboxes
173 | YES | YES | YES | YES, HOST & GUEST | Conductor | Conductor Issues | Conductor damaged (e.g. gunshot, broken strands, arcing, twisted bundle, significant bird caging) or in poor condition | Required | exclusive multi select
174 | YES | YES | YES | YES, HOST & GUEST | Conductor | Conductor Issues | Conductor kinked / pinched at clamps/shoes or connectors |  | exclusive multi select
175 | YES | YES | YES | YES, HOST & GUEST | Conductor | Conductor Issues | Conductor clearance, uneven sag, tension, or snowloading issue | Required | exclusive multi select
176 | YES | YES | YES | YES, HOST & GUEST | Conductor | Conductor Issues | Connectors damaged or in poor condition |  | exclusive multi select
177 | YES | YES | YES | YES, HOST & GUEST | Conductor | Conductor Issues | Armor rod damaged, missing, or in poor condition | Required | exclusive multi select
178 | YES | YES | YES | YES, HOST & GUEST | Conductor | Conductor Issues | Spacers damaged, missing, or in poor condition | Required | exclusive multi select
179 | YES | YES | YES | YES, HOST & GUEST | Conductor | Conductor Issues | Dampers out of position, missing, or in poor condition | Required | exclusive multi select
180 | YES | YES | YES | YES, HOST & GUEST | Conductor | Conductor Issues | Splices in poor condition | Required | exclusive multi select
181 | YES | YES | YES | YES, HOST & GUEST | Conductor | Conductor Issues | Non-automatic splice(s) within 10’ of clamp/shoe not mitigated by a damper | Required | exclusive multi select | If Yes, Create LC Tag - issue B tag (Level 1 Priority)
182 | YES | YES | YES | YES, HOST & GUEST | Conductor | Conductor Issues | Automatic splice(s) present | Required | exclusive multi select
183 | YES | YES | YES | NO | Conductor | Conductor Issues | No Conductor issues or compelling abnormal conditions to report | Required | exclusive multi select
184 | YES | YES | YES | NO | Conductor | Comments for Conductor Issues (Optional) | <Open Text Box> | Not Required | open text box
185 | YES | YES | YES | NO | Conductor | Is there a jumper(s) present? | Yes / No | Required | single select button | If yes is selected, show checkboxes
186 | YES | YES | YES | YES, HOST & GUEST | Conductor | Jumper Issues | Jumper(s) in poor condition | Required | exclusive multi select
187 | YES | YES | YES | YES, HOST & GUEST | Conductor | Jumper Issues | Jumper clearance issue | Required | exclusive multi select
188 | YES | YES | YES | NO | Conductor | Jumper Issues | No Jumper issues or compelling abnormal conditions to report | Required | exclusive multi select
189 | YES | YES | YES | NO | Conductor | Comments for Jumper Issues (Optional) | <Open Text Box> | Not Required | open text box
190 | YES | YES | YES | NO | Conductor | Is there an open jumper(s) present? | Yes / No | Required | single select button | If yes is selected, show checkboxes
191 | YES | YES | YES | YES, HOST & GUEST | Conductor | Open Jumper Issues | Open jumper tail is too long for the field condition and conductor size (Requirements: less than 4/0 = 2’, 4/0-2300kcmil = 3’) | Required | exclusive multi select | If selected, Create LC Tag - issue A or B tag (Level 1 Priority)
192 | YES | YES | YES | NO | Conductor | Open Jumper Issues | No Open Jumper issues or compelling abnormal conditions to report | Required | exclusive multi select
193 | YES | YES | YES | NO | Conductor | Comments for Open Jumper Issues (Optional) | <Open Text Box> | Not Required | open text box
194 | YES | YES | YES | NO | Conductor | Condition of Conductor | 1 - No Visible Damage | Required | single selection list | Needs 1-5 condition scale, show if either conductor, jumper or open jumper is present
195 | YES | YES | YES | NO | Conductor | Condition of Conductor | 2 - Light Damage | Required | single selection list | Needs 1-5 condition scale, show if either conductor, jumper or open jumper is present
196 | YES | YES | YES | NO | Conductor | Condition of Conductor | 3 - Moderate Damage | Required | single selection list | Needs 1-5 condition scale, show if either conductor, jumper or open jumper is present
197 | YES | YES | YES | NO | Conductor | Condition of Conductor | 4 - Heavy Damage | Required | single selection list | Needs 1-5 condition scale, show if either conductor, jumper or open jumper is present
198 | YES | YES | YES | NO | Conductor | Condition of Conductor | 5 - Heavy Damage with Safety Concerns | Required | single selection list | Needs 1-5 condition scale, show if either conductor, jumper or open jumper is present
199 | YES | YES | YES | NO | Conductor | Is there Shield Wire/Fiber present? | Yes / No | Required | single select button | If yes is selected, show checkboxes
200 | YES | YES | YES | YES, HOST & GUEST | Conductor | Shield Wire/ Fiber Issues | Shield wire / Fiber in poor condition (i.e. broken strands at the connectors or in the span) | Required | exclusive multi select
201 | YES | YES | YES | YES, HOST & GUEST | Conductor | Shield Wire/ Fiber Issues | Shield wire / Fiber plate in poor condition | Required | exclusive multi select
202 | YES | YES | YES | YES, HOST & GUEST | Conductor | Shield Wire/ Fiber Issues | Shield wire / Fiber dampers in poor condition | Required | exclusive multi select
203 | YES | YES | YES | NO | Conductor | Shield Wire/ Fiber Issues | No Shield Wire/Fiber issues or compelling abnormal conditions to report | Required | exclusive multi select
204 | YES | YES | YES | NO | Conductor | Comments for Shield Wire/ Fiber Issues (Optional) | <Open Text Box> | Not Required | open text box
205 | YES | YES | YES | NO | Insulators | Is there an insulator present? | Yes / No | Required | single select button | if yes, show all other elements of the Insulator Section, Lines 216-238.
206 | YES | YES | YES | NO | Insulators | Cold end Hardware type: | C-Hook | Required | multi selection | only show if insulator present is yes
207 | YES | YES | YES | NO | Insulators | Cold end Hardware type: | Shackles | Required | multi selection | only show if insulator present is yes
208 | YES | YES | YES | NO | Insulators | Cold end Hardware type: | Clevis | Required | multi selection | only show if insulator present is yes
209 | YES | YES | YES | NO | Insulators | Cold end Hardware type: | Other | Required | multi selection | If selected, show open text box (required and should be on the same char id)
210 | YES | YES | YES | NO | Insulators | Do any of the insulator strings have mixed bell color and/or materials | Yes / No | Required | single selection button
211 | YES | YES | YES | NO | Insulators | Are Grading/Corona rings present? | Yes / No | Required | single selection button
212 | YES | YES | YES | YES, HOST & GUEST | Insulators | Insulator Issues | Cold-end hardware is in poor condition (e.g. c-hook, clevis) | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
213 | YES | YES | YES | YES, HOST & GUEST | Insulators | Insulator Issues | Cold-end hardware shows significant wear | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
214 | YES | YES | YES | YES, HOST & GUEST | Insulators | Insulator Issues | Corona rings missing on 500KV | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
215 | YES | YES | YES | No | Insulators | Insulator Issues | Grading / Corona rings missing on 115KV/230KV polymer insulators | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
216 | YES | YES | YES | YES, HOST & GUEST | Insulators | Insulator Issues | Insulator cap(s) show signs of corrosion | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
217 | YES | YES | YES | YES, HOST & GUEST | Insulators | Insulator Issues | Insulators are damaged, contaminated, arcing/tracking, or in poor condition | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
218 | YES | YES | YES | YES, HOST & GUEST | Insulators | Insulator Issues | Cotter key missing, out of place, or in poor condition | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
219 | YES | YES | YES | YES, HOST & GUEST | Insulators | Insulator Issues | Insulators are out-of-plumb (>2 bells out-of-plumb or > 6 inches for post) | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
220 | YES | YES | YES | YES, HOST & GUEST | Insulators | Insulator Issues | Grading / Corona rings in poor condition | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
221 | YES | YES | YES | YES, HOST & GUEST | Insulators | Insulator Issues | Hot-end hardware is in poor condition (e.g shoe or clamp assembly) | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
222 | YES | YES | YES | YES, HOST & GUEST | Insulators | Insulator Issues | Tie Wire in poor condition | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
223 | YES | YES | YES | NO | Insulators | Insulator Issues | No Insulator issues or compelling abnormal conditions to report | Required | exclusive multi select | Only Displayed when Inspector answers "Yes" to Line 239
224 | YES | YES | YES | NO | Insulators | Comments for Insulator Issues (Optional) | <Open Text Box> | Not Required | open text box | Only Displayed when Inspector answers "Yes" to Line 239
225 | YES | YES | YES | NO | Insulators | Condition of Insulators | 1 - No Visible Damage | Required | single selection list | Need condition scale 1-5
226 | YES | YES | YES | NO | Insulators | Condition of Insulators | 2 - Light Damage | Required | single selection list | Need condition scale 1-5
227 | YES | YES | YES | NO | Insulators | Condition of Insulators | 3 - Moderate Damage | Required | single selection list | Need condition scale 1-5
228 | YES | YES | YES | NO | Insulators | Condition of Insulators | 4 - Heavy Damage | Required | single selection list | Need condition scale 1-5
229 | YES | YES | YES | NO | Insulators | Condition of Insulators | 5 - Heavy Damage with Safety Concerns | Required | single selection list | Need condition scale 1-5
230 | YES | YES | YES | NO | Insulators | Is there a switch present? | Yes / No | Required | single select button | If yes is selected, show checkboxes
231 | YES | YES | YES | YES, HOST & GUEST | Insulators | Switch Issues | Switch has visible signs of rust, corrosion, cracking, arcing, open/unlocked, tracking, contamination, damaged components | Required | exclusive multi select
232 | YES | YES | YES | NO | Insulators | Switch Issues | No Switch issues or compelling abnormal conditions to report | Required | exclusive multi select
233 | YES | YES | YES | NO | Insulators | Comments for Switch Issues (Optional) | <Open Text Box> | Not Required | open text box
234 | YES | YES | NO | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Anti-climbing damaged or needed per E.D. 022168 | Required | exclusive multi select | If selected, show "structure location options" (Rows 280-285) as multi-selection
235 | YES | YES | NO | NO | Other Non-Conformances Requiring Corrective Action | Structure location options | Urban area and structure within 600 feet of a school | Required | exclusive multi select | Only shows if Anti-Climbing guard issue is selected. Add check box for stucture location options
236 | YES | YES | NO | NO | Other Non-Conformances Requiring Corrective Action | Structure location options | Urban area and less than 5 ft of horizontal distance from the conductor to the steel surface | Required | exclusive multi select | Only shows if Anti-Climbing guard issue is selected. Add check box for stucture location options
237 | YES | YES | NO | NO | Other Non-Conformances Requiring Corrective Action | Structure location options | Rural area and within 600 feet of a dwelling or camp | Required | exclusive multi select | Only shows if Anti-Climbing guard issue is selected. Add check box for stucture location options
238 | YES | YES | NO | NO | Other Non-Conformances Requiring Corrective Action | Structure location options | Rural area and the structure in an orchard | Required | exclusive multi select | Only shows if Anti-Climbing guard issue is selected. Add check box for stucture location options
239 | YES | YES | NO | NO | Other Non-Conformances Requiring Corrective Action | Structure location options | Rural area and structure within 600 ft of a frequently traveled road/trail | Required | exclusive multi select | Only shows if Anti-Climbing guard issue is selected. Add check box for stucture location options
240 | YES | YES | NO | NO | Other Non-Conformances Requiring Corrective Action | Structure location options | None of the above structure location options apply | Required | exclusive multi select | Only shows if Anti-Climbing guard issue is selected. Add check box for stucture location options
241 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Marker balls in poor condition | Required | exclusive multi select
242 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Markers (high voltage, visibility strips) missing, damaged, or installed incorrectly | Required | exclusive multi select
243 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Evidence of unauthorized climbing of the structure | Required | exclusive multi select
244 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Climbing steps installed incorrectly or in poor condition | Required | exclusive multi select
245 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Tower/FAA lighting damaged or in poor condition | Required | exclusive multi select
246 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Guy marker missing (GO 95 infraction) | Required | exclusive multi select
247 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Third-Party Utility Infraction | Required | exclusive multi select
248 | YES | YES | YES | YES, HOST & GUEST | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Idle facility | Required | exclusive multi select
249 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Distribution issue on a Transmission structure with Distribution underbuild | Required | exclusive multi select
250 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Concrete barrier post (bollard) is damaged or missing | Required | exclusive multi select
251 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Unauthorized non-utility attachments present | Required | exclusive multi select | If selected, require an LC
252 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | PG&E debris | Required | exclusive multi select | If selected, require an LC
253 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Foreign Objects/Debris (e.g., balloons, kites) present on the line? | Required | exclusive multi select | If selected, require an LC
254 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Road Issues | Required | exclusive multi select | If selected, require an LC
255 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | ROW/Encroachment Issues | Required | exclusive multi select | If selected, require an LC
256 | YES | YES | YES | YES, HOST ONLY | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | Fence Issues | Required | exclusive multi select | If selected, require an LC
257 | YES | YES | YES | NO | Other Non-Conformances Requiring Corrective Action | Other Non-Conformances Requiring Corrective Action | No other non-conformances requiring corrective action to report | Required | exclusive multi select
258 | YES | YES | YES | NO | Other Non-Conformances Requiring Corrective Action | Comments for other Non-Conformances Requiring Corrective Action(Optional) | <Open Text Box> | Not Required | open text box
259 | YES | YES | YES | NO | Other Required Data | Other Required Data | Structure located in water (e.g. bay, wetland, pond, etc.) | Required | exclusive multi select
260 | YES | YES | YES | NO | Other Required Data | Other Required Data | Cell antennas and/or telephone/cable attachments | Required | exclusive multi select
261 | YES | YES | YES | NO | Other Required Data | Other Required Data | Automatic guy splice present | Required | exclusive multi select
262 | YES | YES | YES | NO | Other Required Data | Other Required Data | 2 or more splices present in any one phase per span | Required | exclusive multi select | If selected, require comments and minimum 2 field photos. (Note - bug identified 03/01/21 in QA/SAP - data captured in iOS, but does not populate in SAP. Per Asset Strategy, this is NOT Business Critical or Out-of-compliance, leave as-is in current Sprint and revisit this bug issue in next sprint to resolve)
263 | YES | YES | YES | NO | Other Required Data | Other Required Data | Number of splices across all phases to midspan forward and backward | Required | open text box | Only shown if "2 or more splices present in any one phase per span" is checked". Minimum of 2, Maximum of 45.
264 | YES | YES | YES | NO | Other Required Data | Other Required Data | Shield wire grounded | Required | exclusive multi select
265 | YES | YES | YES | NO | Other Required Data | Other Required Data | Mid-span bells (aka flying bells) present | Required | exclusive multi select | If selected, require comments and minimum 2 field photos. (Note - bug identified 03/01/21 in QA/SAP - data captured in iOS, but does not populate in SAP. Per Asset Strategy, this is NOT Business Critical or Out-of-compliance, leave as-is in current Sprint and revisit this bug issue in next sprint to resolve)
266 | YES | YES | YES | NO | Other Required Data | Other Required Data | Dampers present | Required | exclusive multi select
267 | YES | YES | YES | NO | Other Required Data | Other Required Data | Distibution underbuild present | Required | exclusive multi select
268 | YES | YES | YES | NO | Other Required Data | Other Required Data | FAA lighting present | Required | exclusive multi select
269 | YES | YES | YES | NO | Other Required Data | Other Required Data | External ground wire present | Required | exclusive multi select | if yes, require a photo
270 | YES | YES | YES | NO | Other Required Data | Other Required Data | Structure is in the field; near corrosive environment/agriculture/industrial | Required | exclusive multi select
271 | YES | YES | YES | NO | Other Required Data | Other Required Data | Span over canyon/valley | Required | exclusive multi select
272 | YES | YES | YES | NO | Other Required Data | Other Required Data | Anchor consists of loops | Required | exclusive multi select
273 | YES | YES | YES | NO | Other Required Data | Other Required Data | Anchor consists of rods | Required | exclusive multi select
274 | YES | YES | YES | NO | Other Required Data | Other Required Data | No Other Required Data items to report | Required | exclusive multi select
275 | YES | YES | YES | NO | Other Required Data | Is there a Splice Present? | Yes / No | Required | single selection button
276 | YES | YES | YES | NO | Other Required Data | Type of Splice | Compression | Required | multi selection
277 | YES | YES | YES | NO | Other Required Data | Type of Splice | Automatic | Required | multi selection
278 | YES | YES | YES | NO | Other Required Data | Type of Splice | Twist | Required | multi selection
279 | YES | YES | YES | NO | Other Required Data | Type of Splice | Union | Required | multi selection
280 | YES | YES | YES | NO | Other Required Data | Type of Splice | Shunt | Required | multi selection
281 | YES | YES | NO | NO | Other Required Data | Tower Finish Type | Painted | Required | single selection list
282 | YES | YES | NO | NO | Other Required Data | Tower Finish Type | Galvanized | Required | single selection list
283 | YES | YES | NO | NO | Other Required Data | Tower Finish Type | Weathered | Required | single selection list
284 | YES | YES | NO | NO | Other Required Data | Tower Finish Type | Aluminum | Required | single selection list
285 | YES | YES | NO | NO | Other Required Data | Tower Finish Type | Unable to identify | Required | single selection list | If selected, show open text box (not required)
286 | YES | YES | YES | N/A | Attach Photos | Photo of structure number (as visible) |  | Required | attach photos
288 | NO | NO | YES | N/A | Attach Photos | Photos of first 30 feet of the pole from the ground up. Minimum two photos from different positions. |  | Required | attach photos | Consolidate into single question and ask for pictures of all 4 legs (Upload in order A,B,C,D)
289 | YES | YES | YES | N/A | Attach Photos | Photos of Top and Bottom half of Structure (Upload in order top to bottom) |  | Required | attach photos
290 | YES | YES | NO | N/A | Attach Photos | Photos of first 30 feet of all 4 legs from the ground up (Upload in order A,B,C,D) |  | Required | attach photos | Consolidate into single question and ask for pictures of all 4 legs (Upload in order A,B,C,D)
292 | YES | YES | YES | N/A | Attach Photos | View of clamp/shoe (hot end) two photos per string (both sides of shoe/clamp) | Attach photos | Required | attach photos | minimum of two photos per string
293 | YES | YES | YES | N/A | Attach Photos | View of point of attachment hardware (cold end) two photos per string (both sides of shoe/clamp) | Attach photos | Required | attach photos | minimum of two photos per string
294 | YES | YES | YES | N/A | Attach Photos | View of clamp/shoe (hot end) (two photos per string (both sides of clamp/shoe) | Attach photos | Required | attach photos | minimum of two photos per string
295 | YES | YES | YES | N/A | Attach Photos | View of point of attachment hardware (cold end) two photos per strong (both sides of clamp/shoe) | Attach photos | Required | attach photos | Just need to require minimum 1 photo, not one photo per string
296 | YES | YES | YES | N/A | Asset Details | Initiated Latitude | <Metadata/Autopopulated> | Required | Hidden - Payload only | Record the lat/long of where the user first started the inspection form
297 | YES | YES | YES | N/A | Asset Details | Initiated Longitude | <Metadata/Autopopulated> | Required | Hidden - Payload only | Record the lat/long of where the user first started the inspection form
298 | YES | YES | YES | N/A | Asset Details | Submitted Latitude | <Metadata/Autopopulated> | Required | Hidden - Payload only | Record the lat/long of where the user clicked 'Submit' for the inspection
299 | YES | YES | YES | N/A | Asset Details | Submitted Longitude | <Metadata/Autopopulated> | Required | Hidden - Payload only | Record the lat/long of where the user clicked 'Submit' for the inspection
300 | YES | YES | NO | NO | Steel Structure Foundation | Indicate number of legs that have a condition of 3 or above. | 1 | Required | single selection list | Need number between 1-4
301 | YES | YES | NO | NO | Steel Structure Foundation | Indicate number of legs that have a condition of 3 or above. | 2 | Required | single selection list | Need number between 1-4
302 | YES | YES | NO | NO | Steel Structure Foundation | Indicate number of legs that have a condition of 3 or above. | 3 | Required | single selection list | Need number between 1-4
303 | YES | YES | NO | NO | Steel Structure Foundation | Indicate number of legs that have a condition of 3 or above. | 4 | Required | single selection list | Need number between 1-4
304 | YES | YES | YES | N/A | Attach Photos | Number of Strings of Bells | 0-45 | Required | attach photos | Add number with +/- controls - If "0" Strings selected - hide line 299 and 300
305 | YES | YES | YES | N/A | Attach Photos | Number of Post Insulators | 0-45 | Required | attach photos | minimum of two photos per string