## LOGIC
CAN'T INSPECT DROPDOWN:
INCORRECT ASSET TYPE | LAN ID AND PHOTO REQUIRED. FLAG FOR SAP UPDATE & REQUIRE CHECKBOX WITH FOLLOWING STATEMENT: MISCELLANEOUS INSPECTION FORM TO BE COMPLETED WITH CORRECT INFORMATION.
REMOVED | FLAG FOR SAP UPDATE & REQUIRE COMMENT AND PHOTO OF PHYSICAL VOID/SLD SHOWING EQUIPMENT REMOVED
ENCLOSED | REQUIRE COMMENT & PHOTO OF ENCLOSED EQUIPMENT WITH EQUIPMENT NAME
CLEARANCE REQUIRED | REQUIRE COMMENT & PHOTO OF CLEARANCE REQUIRED TO ENTER SIGN
OTHER | PHOTO REQUIRED, COMMENTS REQUIRED
CONDITION CODE LEVELS:
1 - ROUTINE | PHOTO OPTIONAL, COMMENTS VISIBLE | Keep as it is what we have Pronto
2 - ELEVATED | PHOTO OPTIONAL, COMMENTS VISIBLE
3 - SERIOUS | FLAG, PHOTO, & COMMENTS REQUIRED
4 - SEVERE | FLAG, PHOTO, & COMMENTS REQUIRED
5 - CRITICAL | FLAG, PHOTO, & COMMENTS REQUIRED
GENERAL LOGIC
1. PHOTO OF NAMEPLATE REQUIRED ON ALL ASSETS.
2. 8 PHOTOS OF ASSET PERIMETER REQUIRED ON ALL ASSETS
3. ADDITIONAL PHOTOS AND COMMENT ONLY REQUIRED ON A FLAG
4. PIC NUMBER REQUIRED WHEN NO FLAG IS CREATED
5. IRS REJECTION CAPABILITY WITH COMMENTS AVAILABLE FOR COACHING PURPOSES.
6. RENAME MISSING ASSET FORM TO "MISCELLANEOUS INSPECTION FORM"
ELIMINATION CRITERIA
ADEQUATE FINDINGS (100%) IN APM
NOT DIRECTLY RELATED TO WILDFIRE IGNITION
NO SAFETY RISK
FUTURE ANALYSIS TO DETERMINE IF OVERLAP NECESSARY

## ARSW GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
AIR SWITCH and FUSED DISCONNECT SWITCH
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS THIS A METAL CLAD ARSW? YES-NO IF YES NEST ARSW METAL CLAD FORM. IF NO, CONTINUE TO NEXT QUESTION
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET, INCLUDING IDENTIFICATION NUMBER
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
LIVE PARTS IN POOR CONDITION? (E.G. MALE-FEMALE AND/OR MAKE-BREAK CONNECTIONS/WHIPS/ARCING HORNS/ATTACHMENTS) YES-NO FLAG ON YES
SWITCH/DISCONNECT NOT FULLY SEATED OR FULLY OPEN/MISALIGNED? YES-NO FLAG ON YES
OPERATING LINKAGE IN POOR CONDITION? YES-NO-N/A FLAG ON YES
MISSING, DAMAGED, OR IMPROPER SWITCH LOCKS? YES-NO-N/A FLAG ON YES
MISSING OR DAMAGED FUSES? YES-NO-N/A FLAG ON YES
INSULATORS OUT-OF-PLUMB OR LEANING? YES-NO FLAG ON YES & COMMENT
DESCRIBE AND GIVE LOCATION(S)
DO INSULATORS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/OTHER(ENTER TEXT)
INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
BIRDS NEST(S) PRESENT? YES-NO FLAG ON YES & COMMENT WITH LOCATION
GIVE LOCATION
SELECT ONE: TRANSMISSION VOLTAGE/DISTRIBUTION VOLTAGE IF DISTRIBUTION, NEST ANIMAL ABATEMENT QUESTIONS
IS ANIMAL ABATEMENT PRESENT? YES-NO FLAG ON YES | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO, KEEP NESTED ? “IS ANIMAL ABATEMENT DAMAGED”
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT) IF YES, NEST SELECTION DROPDOWN AND COMMENTS
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DROPDOWN AND COMMENTS
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5 AND NEST DROPDOWN
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES AND NEST DROPDOWN
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
SWITCHING PLATFORM IN POOR CONDITION? (VEGETATION/DEBRIS UNDER PLATFORM, PLATFORM BONDING) YES-NO-N/A FLAG ON YES & NEST COMMENTS
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## ARSW AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
AIR SWITCH and FUSED DISCONNECT SWITCH
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | Remove asset removed and Obstaructive view
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | on answring no ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES | on answring no ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
LIVE PARTS IN POOR CONDITION? (E.G. MALE-FEMALE AND/OR MAKE-BREAK CONNECTIONS) YES-NO FLAG ON YES
SWITCH/DISCONNECT NOT FULLY SEATED OR FULLY OPEN/MISALIGNED? YES-NO FLAG ON YES
OPERATING LINKAGE IN POOR CONDITION? YES-NO-N/A FLAG ON YES | No pic number on NA
MISSING OR DAMAGED FUSES? YES-NO-N/A FLAG ON YES | No pic number on NA
INSULATORS OUT-OF-PLUMB OR LEANING? YES-NO FLAG ON YES & COMMENT
DESCRIBE AND GIVE LOCATION(S)
DO INSULATORS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED | Update to Pronto
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
BIRDS NEST(S) PRESENT? YES-NO FLAG ON YES & COMMENT WITH LOCATION
GIVE LOCATION
SELECT ONE: TRANSMISSION VOLTAGE/DISTRIBUTION VOLTAGE IF DISTRIBUTION, NEST ANIMAL ABATEMENT QUESTIONS
IS ANIMAL ABATEMENT PRESENT? YES-NO FLAG ON YES | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO, KEEP NESTED ? “IS ANIMAL ABATEMENT DAMAGED”
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES | Flag on Yes | Present and damage on no
DESCRIBE AND GIVE LOCATION(S)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT) | Remove all assets
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/OTHER(ENTER TEXT) | Remove all assets
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES | REMOVE THIS QUESTION
ARE THERE CABLE RISERS/POTHEADS ASSOCIATED WITH THIS ASSET? YES-NO IF YES NEST CABLE RISER/POTHEAD QUESTIONS
ARE CABLE RISER/POTHEAD CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES
DO CABLE RISER/POTHEAD BUSHINGS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED | remove flag and dropdown
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
CABLE RISER/POTHEAD BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
DOES CABLE RISER/POTHEAD HAVE ANIMAL ABATEMENT PRESENT? YES-NO IF YES NEST ANIMAL ABATEMENT QUESTIONS | present - on seletection yes damaged . Selection no should needed
IS ANIMAL ABATEMENT ON CABLE RISER/POTHEAD DAMAGED? YES-NO FLAG ON YES
IS ANIMAL ABATEMENT NEEDED ON CABLE RISER/POTHEAD? YES-NO FLAG ON YES AND NEST COMMENT
DESCRIBE AND GIVE LOCATION(S)
IS CABLE RISER/POTHEAD STRUCTURE OUT-OF-PLUMB/TWISTED OR LEANING? YES-NO FLAG ON YES | REMOVE NESTED QUESTIONS | Check whether it is removed
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST COMMENTS
DESCRIBE AND GIVE LOCATION(S)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## BATT
Header
Station:
Tier Level: | To be prepopulated from ESS list
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
BATTERIES AND RACKS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT
PROVIDE CLEAR PHOTOS OF ASSET, INCLUDING IDENTIFICATION NUMBER
ARE THERE ANY ALARMS ON THE BATTERY CHARGER OR ANNUNCIATOR? (E.G. GROUND INDICATION) YES-NO FLAG IF YES AND NEST NEXT 4 LINES | If YES, replace "comment" with "Describe Alarms" make required on YES (don't need 2 entry lines)
DESCRIBE ALARMS
NOTIFY YOUR PG&E LEAD, OR THE CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
IS THE BATTERY RACK IN POOR CONDITION? YES-NO FLAG ON YES
ARE BATTERIES LEAKING/DAMAGED? YES-NO FLAG ON YES AND NEST COMMENTS
ELECTROLYTE LEVEL ABNORMAL? YES-NO FLAG ON YES AND COMMENT WHICH CELL(S)
DESCRIBE WHICH CELL NUMBER(S)
ANY VENT CAPS DAMAGED? YES-NO FLAG ON YES AND COMMENT WHICH CELL(S)
DESCRIBE WHICH CELL NUMBER(S)
BATTERY CONTAMINATION/DAMAGE/CORROSION LEVEL 1-2-3-4-5. FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5. | Comment should only be required on 3-4-5
BATTERY POSTS & LINKS CONTAMINATION/DAMAGE/CORROSION LEVEL 1-2-3-4-5. FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5. | Comment should only be required on 3-4-5
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## BRKR GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
CIRCUIT BREAKERS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS THIS A METAL CLAD BRKR? YES-NO IF YES NEST BRKR METAL CLAD FORM. IF NO, CONTINUE TO NEXT QUESTION
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET, INCLUDING IDENTIFICATION NUMBER & NAMEPLATE
ARE THERE ANY ALARMS ON THE LOCAL ANNUNCIATOR? YES-NO FLAG IF YES AND NEST NEXT 4 LINES
DESCRIBE ALARMS
NOTIFY YOUR PG&E LEAD, OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
BREAKER TYPE: OIL-AIR/VAC -RECLOSER-SF6 (SELECT ONE)
IF OIL OIL LEVEL ABNORMAL? YES-NO FLAG ON YES
IF OIL ANY SIGN OF LEAKS? YES-NO FLAG ON YES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS
IF OIL SELECT ALL THAT APPLY (LEAKING, WEEPING, DRIPPING, SEEPING)
IF OIL LEAK CONTAINMENT MISSING/LACKING? FLAG ON YES
IF OIL BUSHING LEVEL ABNORMAL? YES-NO FLAG ON YES
IF RECLOSER IS BATTERY IN POOR CONDITION? YES-NO FLAG ON YES
IF SF6 IS SF6 PRESSURE ABNORMAL? YES-NO FLAG ON YES AND NEST COMMENT
IF SF6 DESCRIBE HOW MANY POUNDS FROM ALARM
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
DO BUSHINGS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES & SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
IS THIS A DISTRIBUTION VOLTAGE BREAKER? IF YES, NEST ANIMAL ABATEMENT QUESTIONS
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO, KEEP NESTED QUESTION
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
CABINET DOORS DO NOT CLOSE PROPERLY/WARPED LATCHES/SEAL IN POOR CONDITION? YES/NO FLAG ON YES
IMPROPERLY SEALED UNDERGROUND CONDUITS? YES-NO FLAG ON YES
CONTROL WIRE TERMINATIONS LOOSE OR DAMAGED? YES-NO FLAG ON YES AND NEST COMMENT & PHOTO
MECHANICAL POSITION INDICATOR IN CORRECT POSITION? YES-NO FLAG ON YES
MISSING, NON-FUNCTIONING, DAMAGED, OR IMPROPER INDICATING LIGHTS? YES-NO IF YES FLAG & NEST NEXT QUESTION
IS THE RED LIGHT NON-FUNCTIONING? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
BREAKER MECHANISM INDICATOR SHOWING DISCHARGED? YES-NO-N/A FLAG ON YES & NEST NEXT PHOTO AND 3 LINES
NOTIFY YOUR PG&E LEAD, OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
OPERATING MECHANISM IN POOR CONDITION? YES-NO IF YES FLAG AND NEST DROPDOWN SELECTION BOX
SELECT ALL THAT APPLY (MECH IS GUMMY, DRY OR HAS POOR LUBRICATION, OTHER_
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
BREAKER IMPROPERLY MOUNTED TO PAD E.G. ANCHORS/WELDS/BOLTS YES-NO FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## BRKR AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
CIRCUIT BREAKERS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW" | Conflict with Logic tab
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
BREAKER TYPE: OIL-AIR/VAC -RECLOSER-SF6 (SELECT ONE)
IF OIL ANY SIGN OF LEAKS? YES-NO FLAG ON YES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS
IF OIL SELECT ALL THAT APPLY (LEAKING, WEEPING, DRIPPING, SEEPING)
IF OIL LEAK CONTAINMENT MISSING/LACKING? FLAG ON YES | Remove this question
IF RECLOSER IS BATTERY IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
DO BUSHINGS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES & SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED | remove pic & comment
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
IS THIS A DISTRIBUTION VOLTAGE BREAKER? IF YES, NEST ANIMAL ABATEMENT QUESTIONS
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO, KEEP NESTED QUESTION | remove photo and pic number
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## BUSS GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
BUSS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET, INCLUDING IDENTIFICATION NUMBER
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
ARE EXTERNAL BUS DAMPERS IN POOR CONDITION/MISSING? YES-NO-N/A IF YES FLAG & COMMENT
ARE THERE MISSING/DAMAGED CAPS ON ANY ENDS OF BUS TUBING? (CAPS ARE REQUIRED ON ALL ENDS OF BUS TUBING OVER 2" IN DIAMETER) YES-NO-N/A FLAG ON YES & COMMENT
ARE BUS SUPPORT CAPS/SADDLES IN POOR CONDITION? YES-NO FLAG ON YES & COMMENT
INSULATORS OUT-OF-PLUMB OR LEANING? YES-NO FLAG ON YES & COMMENT
DO INSULATORS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/OTHER(ENTER TEXT)
INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
ARE CORONA RINGS PRESENT? YES-NO IF YES NEST NEXT QUESTION
ARE ANY CORONA RINGS MISSING OR IN POOR CONDITION? YES-NO FLAG ON YES & COMMENT
IMPROPER OR MISSING SIGNAGE? YES-NO FLAG YES & COMMENT
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO, KEEP NESTED QUESTION
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES | MOVE UP 2 LINES. ON YES, NEST LINE 37, 38.
BIRDS NEST(S) PRESENT? YES-NO FLAG ON YES & COMMENT
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & NEST DROPDOWN
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DROPDOWN
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/HANGER(EYE)PLATE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5 AND NEST DROPDOWN
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## BUSS AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
BUSS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
ARE EXTERNAL BUS DAMPERS IN POOR CONDITION/MISSING? YES-NO-N/A IF YES FLAG & COMMENT
ARE THERE MISSING/DAMAGED CAPS ON ANY ENDS OF BUS TUBING? (CAPS ARE REQUIRED ON ALL ENDS OF BUS TUBING OVER 2" IN DIAMETER) YES-NO-N/A FLAG ON YES & COMMENT
ARE BUS SUPPORT CAPS/SADDLES IN POOR CONDITION? YES-NO FLAG ON YES & COMMENT
INSULATORS OUT-OF-PLUMB OR LEANING? YES-NO FLAG ON YES & COMMENT
DO INSULATORS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/OTHER(ENTER TEXT)
INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
ARE CORONA RINGS PRESENT? YES-NO IF YES NEST NEXT QUESTION
ARE CORONA RINGS MISSING OR IN POOR CONDITION? YES-NO FLAG ON YES
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO, KEEP NESTED QUESTION | These question are not on 2022 form for buss | Add it to 2023
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES | MOVE UP 2 LINES. ON YES, NEST LINE 35, 36. | 37 main que. 35 under 37 and 36 under 35 - 35 flag on No. 36 flag on yes. No flag on 37
IMPROPER OR MISSING SIGNAGE? YES-NO FLAG YES & COMMENT
BIRDS NEST(S) PRESENT? YES-NO FLAG ON YES & COMMENT
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/HANGER(EYE)PLATE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## CAP BK GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
CAPACITOR BANKS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET, INCLUDING IDENTIFICATION NUMBER
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
BLOWN FUSES? YES-NO IF YES FLAG AND NEST COMMENT
DEFORMED OR LEAKING CAPACITOR? YES-NO FLAG ON YES & NEST COMMENT
BUSHINGS HAVE DAMAGE/CONTAMINATION/CORROSION OR LEAKS? YES-NO FLAG ON YES & NEST SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED / REMOVE PIC NUMBER FROM "NOT VISIBLE" / REMOVE PIC NUMBER FROM "N/A"
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
BARRIERS OR FENCE IN POOR CONDITION OR IN NEED OF REPAIR? YES-NO FLAG ON YES AND NEST COMMENT
FENCE/GATE GROUND WIRE OR BONDING IN NEED OF REPAIR? (E.G. CORRODED, BROKEN, MISSING) YES-NO-N/A FLAG ON YES & NEST COMMENT
IMPROPER OR MISSING SIGNAGE? YES-NO FLAG ON YES & NEST COMMENT
HAVE DEFENSIBLE SPACE REQUIREMENTS BEEN MET? YES-NO FLAG ON NO & NEST COMMENT
BIRDS NEST(S) PRESENT? YES-NO FLAG ON YES & COMMENT WITH LOCATION
GIVE LOCATION
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
PLATFORM/STRUCTURE INSULATORS HAVE DAMAGE/CONTAMINATION/CORROSION OR LEAKS? YES-NO FLAG ON YES & NEST SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
PLATFORM/STRUCTURE INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
ARE THERE LIGHTNING ARRESTORS ASSOCIATED WITH THIS ASSET? YES-NO IF YES NEST LIGHTNING ARRESTOR QUESTIONS
LIGHTNING ARRESTOR CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES
ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED? YES-NO FLAG ON YES
IS THERE A LIGHTNING ARRESTOR COUNTER? YES-NO IF YES NEST NEXT QUESTION, IF NO NEST FOLLOWING QUESTION
IS COUNTER DAMAGED OR ILLEGIBLE? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
HAS COUNTER BEEN REMOVED IMPROPERLY? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
DO LIGHTNING ARRESTORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES AND NEST DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
LIGHTNING ARRESTOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
LIGHTNING ARRESTOR GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## CAP BK AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
CAPACITOR BANKS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
BLOWN FUSES? YES-NO IF YES FLAG AND NEST COMMENT
DEFORMED OR LEAKING CAPACITOR? YES-NO FLAG ON YES & NEST COMMENT
BUSHINGS HAVE DAMAGE/CONTAMINATION/CORROSION OR LEAKS? YES-NO FLAG ON YES & NEST SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED / REMOVE PIC NUMBER FROM "NOT VISIBLE" / REMOVE PIC NUMBER FROM "N/A" | REMOVE PIC NUMBER FROM "N/A"
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
BARRIERS OR FENCE IN POOR CONDITION OR IN NEED OF REPAIR? YES-NO FLAG ON YES AND NEST COMMENT
IMPROPER OR MISSING SIGNAGE? YES-NO FLAG ON YES & NEST COMMENT
HAVE DEFENSIBLE SPACE REQUIREMENTS BEEN MET? YES-NO FLAG ON NO & NEST COMMENT
BIRDS NEST(S) PRESENT? YES-NO FLAG ON YES & COMMENT WITH LOCATION
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
PLATFORM/STRUCTURE INSULATORS HAVE DAMAGE/CONTAMINATION/CORROSION OR LEAKS? YES-NO FLAG ON YES & NEST SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
PLATFORM/STRUCTURE INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
ARE THERE LIGHTNING ARRESTORS ASSOCIATED WITH THIS ASSET? YES-NO IF YES NEST LIGHTNING ARRESTOR QUESTIONS
LIGHTNING ARRESTOR CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES
ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED? YES-NO FLAG ON YES
DO LIGHTNING ARRESTORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES AND NEST DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
LIGHTNING ARRESTOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
LIGHTNING ARRESTOR GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES | MOVE THIS QUESTION UNDER QUESTION "ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED"
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## SVC
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
SVC
thyrister module area capacitors/metering/
cooling system-fans/noise/leaks/pressure gauge/fluid level/ leaks temp/ containment/ filtration /alarms
Active alarms in SVC building (water pressure/flow/temp and stuff
Valve hall cooling components damaged/abnormal?
Air conditioning condition in building
any other issues with the SVC

## CKSW GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
CIRCUIT SWITCHERS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET, INCLUDING IDENTIFICATION NUMBER & NAMEPLATE
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
LIVE PARTS IN POOR CONDITION? (E.G. MALE-FEMALE AND/OR MAKE-BREAK CONNECTIONS/WHIPS/ARCHING HORNS/ATTACHMENTS) YES-NO FLAG ON YES
SWITCH/DISCONNECT NOT FULLY SEATED OR FULLY OPEN/MISALLIGNED? YES-NO FLAG ON YES
OPERATING LINKAGE IN POOR CONDITION? YES-NO FLAG ON YES
MISSING, DAMAGED, OR IMPROPER SWITCH LOCKS? YES-NO FLAG ON YES
INSULATORS OUT-OF-PLUMB OR LEANING? YES-NO FLAG ON YES & COMMENT
DESCRIBE AND GIVE LOCATION(S)
DO INSULATORS HAVE ANY DAMAGE OR CONTAMINATION? YES-NO FLAG ON YES | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
MECHANICAL POSITION INDICATOR IN CORRECT POSITION? YES-NO FLAG ON YES
MISSING, NON-FUNCTIONING, DAMAGED, OR IMPROPER INDICATING LIGHTS? YES-NO IF YES FLAG & NEST NEXT QUESTION
IS THE RED LIGHT NON-FUNCTIONING? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
OPERATING MECHANISM IN POOR CONDITION? YES-NO IF YES FLAG AND NEST DROPDOWN SELECTION BOX
SELECT ALL THAT APPLY (MECH IS GUMMY, DRY OR HAS POOR LUBRICATION, OTHER(ENTER TEXT)
BIRDS NEST(S) PRESENT? YES-NO FLAG ON YES & COMMENT WITH LOCATION
GIVE LOCATION
SF6 GAS PRESSURE ABNORMAL? (E.G. RED/GREEN/SILVER-GO/NO-GO) YES-NO FLAG ON YES
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DROPDOWN
SELECT FROM DUPLEX DROPDOWN - (ISSUE) BROKEN, BENT, CORRODED, OTHER -(PART)CROSS MEMBERS, SHOES, C-HOOKS, COTTER PINS/KEYS, SHACKLES, STRING BELL, OTHER
DESCRIBE AND GIVE LOCATION(S)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5 AND NEST DROPDOWN
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES AND NEST DROPDOWN
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
SWITCHING PLATFORM IN POOR CONDITION? (VEGETATION/DEBRIS UNDER PLATFORM, PLATFORM BONDING) YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## CKSW AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
CIRCUIT SWITCHERS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
LIVE PARTS IN POOR CONDITION? (E.G. MALE-FEMALE AND/OR MAKE-BREAK CONNECTIONS/ FULLY OPEN/ FULLY CLOSED/MISALIGNED) YES-NO FLAG ON YES
SWITCH/DISCONNECT NOT FULLY SEATED OR FULLY OPEN/MISALIGNED? YES-NO-NOT VISIBLE FLAG ON YES
OPERATING LINKAGE IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES
INSULATORS OUT-OF-PLUMB OR LEANING? YES-NO FLAG ON YES & COMMENT
DESCRIBE AND GIVE LOCATION(S)
DO INSULATORS HAVE ANY DAMAGE OR CONTAMINATION? YES-NO FLAG ON YES | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
BIRDS NEST(S) PRESENT? YES-NO FLAG ON YES & COMMENT WITH LOCATION
GIVE LOCATION
SF6 GAS PRESSURE ABNORMAL? (E.G. RED/GREEN/SILVER-GO/NO-GO) YES-NO FLAG ON YES
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DROPDOWN
SELECT FROM DUPLEX DROPDOWN - (ISSUE) BROKEN, BENT, CORRODED, OTHER -(PART)CROSS MEMBERS, SHOES, C-HOOKS, COTTER PINS/KEYS, SHACKLES, STRING BELL, OTHER
DESCRIBE AND GIVE LOCATION(S)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## CT-PT-CCVT GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
EACH CT/PT/CCTV
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET & NAMEPLATE
CONDUCTOR IN POOR CONDITION? YES-NO-FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONDUCTOR IN POOR CONDITION? YES-NO-FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
BUSHINGS HAVE DAMAGE/CONTAMINATION OR LEAKS? YES-NO FLAG ON YES | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVELS 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
NOTICEABLE DEFORMATION OF THE TANK? (E.G. BULGING) YES-NO FLAG ON YES
OIL LEVEL ABNORMAL? YES-NO-N/A FLAG ON YES
ANY SIGN OF LEAKS? YES-NO FLAG ON YES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS
SELECT ALL THAT APPLY (LEAKING, WEEPING, DRIPPING, SEEPING)
LEAK CONTAINMENT MISSING? YES-NO FLAG ON YES
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO, KEEP NESTED ? “IS ANIMAL ABATEMENT DAMAGED”
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DROPDOWN
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## CT-PT-CCVT AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
EACH CT/PT/CCTV
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
CONDUCTOR IN POOR CONDITION? YES-NO-FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONDUCTOR IN POOR CONDITION? YES-NO-FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
BUSHINGS HAVE DAMAGE/CONTAMINATION OR LEAKS? YES-NO FLAG ON YES | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVELS 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
NOTICEABLE DEFORMATION OF THE TANK? (E.G. BULGING) YES-NO FLAG ON YES
ANY SIGN OF LEAKS? YES-NO FLAG ON YES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS | remove Leak containment missing? Remove both 31 and 32
SELECT ALL THAT APPLY (LEAKING, WEEPING, DRIPPING, SEEPING)
LEAK CONTAINMENT MISSING? YES-NO FLAG ON YES
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO, KEEP NESTED ? “IS ANIMAL ABATEMENT DAMAGED” | remove both pic and pic number questions or make those optional
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DROPDOWN
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## LTC GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
LTC
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET & NAMEPLATE
LTC OIL TEMP. (DEGREES C) (ENTER TEXT)
IS LTC OIL TEMP HOTTER THAN MAIN TANK TEMP YES-NO-NON-FUNCTIONING GAUGE FLAG ON YES & NON-FUNCTIONING GAUGE
IS OIL LEVEL ABNORMAL? YES-NO FLAG ON YES
ANY SIGNS OF LEAKS? YES-NO FLAG ON YES AND NEST NEXT 3 LINES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS
PLEASE SELECT ALL THAT APPLY (LEAKING, DRIPPING, WEEPING, SEEPING)
LEAK CONTAINMENT MISSING/LACKING? YES-NO FLAG ON YES
OIL PRESERVATION SYSTEM - IS DESICANT COLOR WHITE? (SHOWING NEEDING TO BE REPLACED) YES-NO-N/A FLAG ON YES
OIL PRESERVATION SYSTEM - VENTED SYSTEM. IS VENT BLOCKED/OBSTRUCTED? YES-NO-N/A FLAG ON YES
OIL PRESERVATION SYSTEM - CONSERVERTOR TANK HAVE LOW OIL? YES-NO-N/A FLAG ON YES
IS THERE AN ONLINE OIL FILTRATION SYSTEM? YES-NO IF YES, NEST NEXT 2 LINES
IS FILTRATION SYSTEM IN POOR CONDITION? (E.G. HIGH PRESSURE OR TRIPPED OFFLINE) YES-NO FLAG ON YES AND NEST NEXT 3 LINES
ABNORMAL NOISES/ODORS? YES-NO FLAG YES AND NEST COMMENT
DESCRIBE
DOES LTC HAVE A PRD? YES-NO (IF YES, SKIP NEXT QUESTION-NO FLAG, INFORMATIONAL ONLY)
DOES LTC HAVE AN XPRD? YES-NO (NO FLAG, INFORMATIONAL ONLY)
IS DISCHARGE PIPE ROUTED OVER ANY CONTROL CABINETS & DRAIN VALVES? YES-NO IF YES FLAG
IS THERE INDICATION OF PRESSURE RELIEF DEVICE ACTIVATION? YES-NO-N/A IF YES FLAG
IS PRESSURE RELIEF DEVICE ACTUATION FLAG DAMAGED? YES-NO-N/A IF YES FLAG
ANY LOCAL FEATURE C/OUT SWITCHES IN ABNORMAL STATUS? YES-NO-N/A FLAG ON YES & NEST NEXT 3 LINES
DESCRIBE
NOTIFY YOUR PG&E LEAD OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
LTC CONTROL POWER OFF? YES-NO-N/A FLAG ON YES & NEST NEXT 2 LINES
NOTIFY YOUR PG&E LEAD OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
DRIVE MOTOR & MECANISM IN POOR CONDITION? YES/NO-NOT VISIBLE FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## LTC AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
LTC
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
| IS OIL LEVEL ABNORMAL? YES-NO FLAG ON YES (PLEASE ADD THIS QUESTION TO AIR + PRONTO) | replace "is asset description incorrect"?
NOTE CORRECT ASSET DESCRIPTION
ANY SIGNS OF LEAKS? YES-NO FLAG ON YES AND NEST NEXT 3 LINES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS | remove row 27?
PLEASE SELECT ALL THAT APPLY (LEAKING, DRIPPING, WEEPING, SEEPING)
LEAK CONTAINMENT MISSING/LACKING? YES-NO FLAG ON YES
DOES LTC HAVE A PRD? YES-NO (IF YES, SKIP NEXT QUESTION-NO FLAG, INFORMATIONAL ONLY)
DOES LTC HAVE AN XPRD? YES-NO (NO FLAG, INFORMATIONAL ONLY)
IS DISCHARGE PIPE ROUTED OVER ANY CONTROL CABINETS & DRAIN VALVES? YES-NO IF YES FLAG | THIS QUESTION SHOULD ONLY POPULATE WHEN ANSWERING YES TO QUESTION "DOES TRANSFORMER HAVE AN XPRD"
IS THERE INDICATION OF PRESSURE RELIEF DEVICE ACTIVATION? YES-NO-N/A IF YES FLAG
IS PRESSURE RELIEF DEVICE ACTUATION FLAG DAMAGED? YES-NO-N/A IF YES FLAG
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count

## MOAS GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
MOAS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET & NAMEPLATE
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
LIVE PARTS IN POOR CONDITION? (E.G. MALE-FEMALE AND/OR MAKE-BREAK CONNECTIONS/WHIPS/ARCHING HORNS/ATTACHMENTS) YES-NO FLAG ON YES
SWITCH/DISCONNECT NOT FULLY SEATED OR FULLY OPEN/MISALIGNED? YES-NO FLAG ON YES
OPERATING LINKAGE IN POOR CONDITION? YES-NO FLAG ON YES
MISSING, DAMAGED, OR IMPROPER SWITCH LOCKS? YES-NO FLAG ON YES
INSULATORS OUT-OF-PLUMB OR LEANING? YES-NO FLAG ON YES & COMMENT
DO INSULATORS HAVE ANY DAMAGE OR CONTAMINATION? YES-NO FLAG ON YES | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
MECHANICAL POSITION INDICATOR IN CORRECT POSITION? YES-NO FLAG ON YES
MISSING, NON-FUNCTIONING, DAMAGED, OR IMPROPER INDICATING LIGHTS? YES-NO IF YES FLAG & NEST NEXT QUESTION
IS THE RED LIGHT NON-FUNCTIONING? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
OPERATING MECHANISM IN POOR CONDITION? YES-NO IF YES FLAG AND NEST DROPDOWN SELECTION BOX
SELECT ALL THAT APPLY (MECH IS GUMMY, DRY OR HAS POOR LUBRICATION, OTHER(ENTER TEXT)
BIRDS NEST(S) PRESENT? YES-NO FLAG ON YES & COMMENT WITH LOCATION
GIVE LOCATION
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS
SELECT FROM DUPLEX DROPDOWN - (ISSUE) BROKEN, BENT, CORRODED, OTHER -(PART)CROSS MEMBERS, SHOES, C-HOOKS, COTTER PINS/KEYS, SHACKLES, STRING BELL, OTHER
DESCRIBE AND GIVE LOCATION(S)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## MOAS AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
MOAS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT
NOTE CORRECT ASSET DESCRIPTION
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE (PIC NUMBER:*/COMMENT)
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE (PIC NUMBER:*/COMMENT)
LIVE PARTS IN POOR CONDITION? (E.G. MALE-FEMALE AND/OR MAKE-BREAK CONNECTIONS/ FULLY OPEN/ FULLY CLOSED/MISALIGNED) YES-NO FLAG ON YES
SWITCH/DISCONNECT NOT FULLY SEATED OR FULLY OPEN/MISALIGNED? YES-NO FLAG ON YES
OPERATING LINKAGE IN POOR CONDITION? YES-NO FLAG ON YES
INSULATORS OUT-OF-PLUMB OR LEANING? YES-NO FLAG ON YES & COMMENT
DO INSULATORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES & SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PHOTO REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT) | REMOVE THIS NESTED QUESTION
INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
BIRDS NEST(S) PRESENT? YES-NO FLAG ON YES & COMMENT WITH LOCATION
GIVE LOCATION
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS
SELECT FROM DUPLEX DROPDOWN - (ISSUE) BROKEN, BENT, CORRODED, OTHER -(PART)CROSS MEMBERS, SHOES, C-HOOKS, COTTER PINS/KEYS, SHACKLES, STRING BELL, OTHER
DESCRIBE AND GIVE LOCATION(S)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count

## SHRE-SERE GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
REACTORS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN | REPLACE SLD CORRECTION WITH "OBSTRUCTED VIEW"
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET & NAMEPLATE
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
WINDINGS HAVE DAMAGE/CONTAMINATION? YES-NO-NOT VISIBLE FLAG ON YES & NEST SELECTION DROPDOWN
SELECT ISSUE(S): DAMAGE/CONTAMINATION/FLASHED/BROKEN/CRACKED/VISUAL SIGN OF HEATING/OTHER(ENTER TEXT)
SUPPORT INSULATORS HAVE DAMAGE/CONTAMINATION? YES-NO-N/A FLAG ON YES
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/OTHER(ENTER TEXT)
SUPPORT INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES REMOVE THE N/A FROM THIS QUESTION | REMOVE THE N/A FROM THIS QUESTION
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
IS REACTOR OIL FILLED? YES-NO IF YES, ANSWER BELOW IF OIL QUESTIONS. IF NO, SKIP TO STEEL STRUCTURE QUESTIONS
IF OIL BUSHING LEVEL ABNORMAL? YES-NO-N/A FLAG ON YES
IF OIL DO BUSHINGS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES & SELECTION DROPDOWN
IF OIL SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
IF OIL BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
IF OIL IS OIL LEVEL ABNORMAL? YES-NO FLAG ON YES
IF OIL ANY SIGN OF LEAKSYES-NO IF YES FLAG AND NEST NEXT 4 LINES | IF OIL ANY SIGN OF LEAKS AND OR CONTAINMENT MISSING/LACKING?? YES-NO IF YES FLAG AND NEST NEXT 4 LINES
IF OIL SELECT ALL THAT APPLY - (LEAKING, WEEPING, DRIPPING, SEEPING) REMOVE
IF OIL LEAK CONTAINMENT MISSING/LACKING? YES-NO FLAG ON YES REMOVE
IF OIL RADIATORS/PUMPS IN POOR CONDITION OR FANS IN POOR CONDITION/MISSING? YES-NO FLAG ON YES
IF OIL DOES REACTOR HAVE A PRD? YES-NO (IF YES, SKIP NEXT QUESTION-NO FLAG, INFORMATIONAL ONLY) WHN ANSWER NO REMOVE PIC # | WHN ANSWER NO REMOVE PIC #
IF OIL DOES REACTOR HAVE AN XPRD? YES-NO (NO FLAG, INFORMATIONAL ONLY) WHN ANSWER NO REMOVE PIC # | WHN ANSWER NO REMOVE PIC #
IF OIL IS DISCHARGE PIPE ROUTED OVER ANY CONTROL CABINETS & DRAIN VALVES? YES-NO IF YES FLAG SHOULD BE NESTED UNDER XPRD WHN ANSWER IS YES | SHOULD BE NESTED UNDER XPRD WHN ANSWER IS YES
IF OIL IS THERE INDICATION OF PRESSURE RELIEF DEVICE ACTIVATION? YES-NO-N/A IF YES FLAG
IF OIL IS PRESSURE RELIEF DEVICE ACTUATION FLAG DAMAGED? YES-NO-N/A IF YES FLAG
ARE THERE LIGHTNING ARRESTORS ASSOCIATED WITH THIS ASSET? YES-NO IF YES NEST LIGHTNING ARRESTOR QUESTIONS
LIGHTNING ARRESTOR CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | LIGHTNING ARRESTOR CONNECTIONS IN POOR CONDITION (E.G. CORRODED, FLASHED, BROKEN, MISSING)? YES-NO FLAG ON YES
ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED? YES-NO FLAG ON YES
IS THERE A LIGHTNING ARRESTOR COUNTER? YES-NO IF YES NEST NEXT QUESTION, IF NO NEST FOLLOWING QUESTION
IS COUNTER DAMAGED OR ILLEGIBLE? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
HAS COUNTER BEEN REMOVED IMPROPERLY? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
DO LIGHTNING ARRESTORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES AND NEST DROPDOWN
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
LIGHTNING ARRESTOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
LIGHTNING ARRESTOR GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED | REMOVE NESTED. FOR YES ANSWER, WILL ANSWER IN COMMENTS
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS | REMOVE NESTED. FOR YES ANSWER, WILL ANSWER IN COMMENTS
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
REACTOR TANK IMPROPERLY MOUNTED TO PAD E.G. ANCHORS/WELDS/BOLTS YES-NO-N/A FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## SHRE-SERE AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
REACTORS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET, INCLUDING IDENTIFICATION NUMBER & NAMEPLATE
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
WINDINGS HAVE DAMAGE/CONTAMINATION? YES-NO-NOT VISIBLE FLAG ON YES & NEST SELECTION DROPDOWN | REMOVE NESTED QUESTIONS
SELECT ISSUE(S): DAMAGE/CONTAMINATION/FLASHED/BROKEN/CRACKED/VISUAL SIGN OF HEATING/OTHER(ENTER TEXT)
SUPPORT INSULATORS HAVE DAMAGE/CONTAMINATION? YES-NO-N/A FLAG ON YES | NO FLAG ON YES, KEEP "DESCRIBE ISSUE", REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/OTHER(ENTER TEXT)
SUPPORT INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO, KEEP NESTED QUESTION
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
IS REACTOR OIL FILLED? YES-NO IF YES, ANSWER BELOW IF OIL QUESTIONS. IF NO, SKIP TO STEEL STRUCTURE QUESTIONS
IF OIL BUSHING LEVEL ABNORMAL? YES-NO-N/A FLAG ON YES
IF OIL DO BUSHINGS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES & SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
IF OIL SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
IF OIL BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
IF OIL ANY SIGN OF LEAKS YES-NO IF YES FLAG AND NEST NEXT 4 LINES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS | even remove line 43 question?
IF OIL SELECT ALL THAT APPLY - (LEAKING, WEEPING, DRIPPING, SEEPING)
IF OIL LEAK CONTAINMENT MISSING/LACKING? YES-NO FLAG ON YES
IF OIL RADIATORS/PUMPS IN POOR CONDITION OR FANS IN POOR CONDITION/MISSING? YES-NO FLAG ON YES
IF OIL DOES REACTOR HAVE A PRD? YES-NO (IF YES, SKIP NEXT QUESTION-NO FLAG, INFORMATIONAL ONLY)
IF OIL DOES REACTOR HAVE AN XPRD? YES-NO (NO FLAG, INFORMATIONAL ONLY)
IF OIL IS DISCHARGE PIPE ROUTED OVER ANY CONTROL CABINETS & DRAIN VALVES? YES-NO IF YES FLAG | THIS QUESTION SHOULD ONLY POPULATE WHEN ANSWERING YES TO QUESTION "DOES TRANSFORMER HAVE AN XPRD"
IF OIL IS THERE INDICATION OF PRESSURE RELIEF DEVICE ACTIVATION? YES-NO-N/A IF YES FLAG
IF OIL IS PRESSURE RELIEF DEVICE ACTUATION FLAG DAMAGED? YES-NO-N/A IF YES FLAG
ARE THERE LIGHTNING ARRESTORS ASSOCIATED WITH THIS ASSET? YES-NO IF YES NEST LIGHTNING ARRESTOR QUESTIONS
ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED? YES-NO FLAG ON YES
IS THERE A LIGHTNING ARRESTOR COUNTER? YES-NO IF YES NEST NEXT QUESTION, IF NO NEST FOLLOWING QUESTION
IS COUNTER DAMAGED OR ILLEGIBLE? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
HAS COUNTER BEEN REMOVED IMPROPERLY? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
DO LIGHTNING ARRESTORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES AND NEST DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
LIGHTNING ARRESTOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
LIGHTNING ARRESTOR GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES | MOVE THIS QUESTION UNDER QUESTION "ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED"
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.

## REGR GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
REGULATOR
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET & NAMEPLATE
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
DO BUSHINGS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES & SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
REG/LTC OIL TEMP. (DEGREES C)
IS LTC OIL TEMP HOTTER THAN MAIN TANK TEMP YES-NO-NON-FUNCTIONING GAUGE FLAG ON YES & NON-FUNCTIONING GAUGE
IS OIL LEVEL ABNORMAL? YES-NO FLAG ON YES
ANY SIGNS OF LEAKS YES-NO FLAG ON YES AND NEST NEXT 3 LINES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS
PLEASE SELECT ALL THAT APPLY (LEAKING, DRIPPING, WEEPING, SEEPING)
LEAK CONTAINMENT MISSING/LACKING? YES-NO FLAG ON YES
OIL PRESERVATION SYSTEM - IS DESICANT COLOR WHITE? (SHOWING NEEDING TO BE REPLACED) YES-NO-N/A FLAG ON YES
OIL PRESERVATION SYSTEM - VENTED SYSTEM. IS VENT BLOCKED/OBSTRUCTED? YES-NO-N/A FLAG ON YES
OIL PRESERVATION SYSTEM - CONSERVERTOR TANK HAVE LOW OIL? YES-NO-N/A FLAG ON YES
IS THERE AN ONLINE OIL FILTRATION SYSTEM? YES-NO IF YES, NEST NEXT 2 LINES
IS FILTRATION SYSTEM IN POOR CONDITION? (E.G. HIGH PRESSURE OR TRIPPED OFFLINE) YES-NO FLAG ON YES AND NEST NEXT 3 LINES
ANY SIGNS OF LEAKS? YES-NO FLAG ON YES AND NEST NEXT 3 LINES
PLEASE SELECT ALL THAT APPLY (LEAKING, DRIPPING, WEEPING, SEEPING)
LEAK CONTAINMENT MISSING/LACKING? YES-NO FLAG ON YES
ABNORMAL NOISES/ODORS? YES-NO FLAG YES AND NEST COMMENT
DESCRIBE
DOES REG HAVE A PRD? YES-NO (IF YES, SKIP NEXT QUESTION-NO FLAG, INFORMATIONAL ONLY)
DOES REG HAVE AN XPRD? YES-NO (NO FLAG, INFORMATIONAL ONLY)
IS DISCHARGE PIPE ROUTED OVER ANY CONTROL CABINETS & DRAIN VALVES? YES-NO IF YES FLAG
IS THERE INDICATION OF PRESSURE RELIEF DEVICE ACTIVATION? YES-NO-N/A IF YES FLAG
IS PRESSURE RELIEF DEVICE ACTUATION FLAG DAMAGED? YES-NO-N/A IF YES FLAG
ANY LOCAL FEATURE C/OUT SWITCHES IN ABNORMAL STATUS? YES-NO-N/A FLAG ON YES & NEST NEXT 4 LINES
DESCRIBE
NOTIFY YOUR PG&E LEAD OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
REG CONTROL POWER OFF? YES-NO FLAG ON YES
NOTIFY YOUR PG&E LEAD OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
DRIVE MOTOR & MECHANISM IN POOR CONDITION? YES/NO-NOT VISIBLE FLAG ON YES
IS ANIMAL ABATEMENT PRESENT? REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO / KEEP NESTED ? "IS ANIMAL ABATEMENT DAMAGED” | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO / KEEP NESTED ? "IS ANIMAL ABATEMENT DAMAGED”
IS ANIMAL ABATEMENT DAMAGED? YES-NO-N/A FLAG ON YES
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
RADIATORS/PUMPS IN POOR CONDITION OR FANS IN POOR CONDITION/MISSING? YES-NO FLAG ON YES
ARE THERE LIGHTNING ARRESTORS ASSOCIATED WITH THIS ASSET? YES-NO IF YES NEST LIGHTNING ARRESTOR QUESTIONS
LIGHTNING ARRESTOR CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES
ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED? YES-NO FLAG ON YES
IS THERE A LIGHTNING ARRESTOR COUNTER? YES-NO IF YES NEST NEXT QUESTION, IF NO NEST FOLLOWING QUESTION
IS COUNTER DAMAGED OR ILLEGIBLE? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
HAS COUNTER BEEN REMOVED IMPROPERLY? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
DO LIGHTNING ARRESTORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES AND NEST DROPDOWN NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED | DO LIGHTNING ARRESTORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES AND NEST DROPDOWN NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
LIGHTNING ARRESTOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
LIGHTNING ARRESTOR GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES MOVE THIS QUESTION UNDER QUESTION "ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED" | LIGHTNING ARRESTOR GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES MOVE THIS QUESTION UNDER QUESTION "ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED"
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
REGULATOR TANK IMPROPERLY MOUNTED TO PAD E.G. ANCHORS/WELDS/BOLTS YES-NO-N/A FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## REGR AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
REGULATOR
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
CONDUCTOR IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
DO BUSHINGS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES & SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
ANY SIGNS OF LEAKS YES-NO FLAG ON YES AND NEST NEXT 3 LINES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS
PLEASE SELECT ALL THAT APPLY (LEAKING, DRIPPING, WEEPING, SEEPING)
LEAK CONTAINMENT MISSING/LACKING? YES-NO FLAG ON YES
DOES REG HAVE A PRD? YES-NO
DOES REG HAVE AN XPRD? YES-NO
IS DISCHARGE PIPE ROUTED OVER ANY CONTROL CABINETS & DRAIN VALVES? YES-NO IF YES FLAG | THIS QUESTION SHOULD ONLY POPULATE WHEN ANSWERING YES TO QUESTION "DOES TRANSFORMER HAVE AN XPRD"
IS THERE INDICATION OF PRESSURE RELIEF DEVICE ACTIVATION? YES-NO-N/A IF YES FLAG
IS PRESSURE RELIEF DEVICE ACTUATION FLAG DAMAGED? YES-NO-N/A IF YES FLAG
IS ANIMAL ABATEMENT PRESENT? | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO / KEEP NESTED ? "IS ANIMAL ABATEMENT DAMAGED”
IS ANIMAL ABATEMENT DAMAGED YES-NO-N/A FLAG ON YES
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
RADIATORS/PUMPS IN POOR CONDITION OR FANS IN POOR CONDITION/MISSING? YES-NO FLAG ON YES
ARE THERE LIGHTNING ARRESTORS ASSOCIATED WITH THIS ASSET? YES-NO IF YES NEST LIGHTNING ARRESTOR QUESTIONS
LIGHTNING ARRESTOR CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES
ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED? YES-NO FLAG ON YES
DO LIGHTNING ARRESTORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES AND NEST DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
LIGHTNING ARRESTOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
LIGHTNING ARRESTOR GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES | MOVE THIS QUESTION UNDER QUESTION "ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED"
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES & COMMENTS REQUIRED
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DUPLEX DROPDOWN AND COMMENTS
SELECT ISSUE(S): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/SHOES/C-HOOKS/COTTER PINS-KEYS/SHACKLES/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## STSB GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
STATION SERVICE TRANSFORMER
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET & NAMEPLATE
CONDUCTOR IN POOR CONDITION? YES-NO-FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO-FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER*/COMMENT
BUSHINGS HAVE DAMAGE/CONTAMINATION/CORROSION OR LEAKS? YES-NO FLAG ON YES & SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTION AND PIC REQUIRED
Select issue(s): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVELS 1-2-3-4-5 FLAG ON 4-5, COMMENTS REQUIRED ON 3-4-5.
NOTICEABLE DEFORMATION OF THE TANK? (E.G. BULGING) YES-NO FLAG ON YES
OIL LEVEL ABNORMAL? YES-NO-NOT VISIBLE FLAG ON YES
ANY SIGN OF LEAKS YES-NO FLAG ON YES | THIS QUESTIION SHOULD READ "ANY SIGN OF LEAKS?/ AND OR CONTAINMENT MISSING/LACKING, REMOVE NESTED QUESTIONS
SELECT ALL THAT APPLY (LEAKING, WEEPING, DRIPPING, SEEPING)
LEAK CONTAINMENT MISSING? YES-NO FLAG ON YES
IS THIS SF6 FILLED EQUIPMENT? YES-NO IF YES, NEST NEXT SF6 QUESTIONS
IF SF6 IS SF6 PRESSURE ABNORMAL? YES-NO FLAG ON YES
IF SF6 DESCRIBE HOW MANY POUNDS FROM ALARM (ENTER TEXT)
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWIRING NO
IS ANIMAL ABATEMENT DAMAGED? YES-NO-N/A FLAG ON YES
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DROPDOWN
Select issue(s): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
Select issue(s):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
Select issue(s):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## STSB AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
STATION SERVICE TRANSFORMER
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
CONDUCTOR IN POOR CONDITION? YES-NO-FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO-FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER*/COMMENT
BUSHINGS HAVE DAMAGE/CONTAMINATION/CORROSION OR LEAKS? YES-NO FLAG ON YES & SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTION AND PIC REQUIRED
Select issue(s): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVELS 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
NOTICEABLE DEFORMATION OF THE TANK? (E.G. BULGING) YES-NO FLAG ON YES
ANY SIGN OF LEAKS YES-NO FLAG ON YES | THIS QUESTIION SHOULD READ "ANY SIGN OF LEAKS?/ AND OR CONTAINMENT MISSING/LACKING, REMOVE NESTED QUESTIONS
SELECT ALL THAT APPLY (LEAKING, WEEPING, DRIPPING, SEEPING)
LEAK CONTAINMENT MISSING? YES-NO FLAG ON YES
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWIRING NO
IS ANIMAL ABATEMENT DAMAGED? YES-NO-N/A FLAG ON YES
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
STRUCTURE IS OUT-OF-PLUMB, TWISTED OR LEANING? YES-NO FLAG ON YES
SELECT ISSUE(S): OUT OF PLUMB/TWISTED/LEANING/OTHER(ENTER TEXT)
DAMAGED, LOOSE OR MISSING STEEL MEMBERS OR HARDWARE? YES-NO IF YES NEST DROPDOWN
Select issue(s): DAMAGED/LOOSE/MISSING/CROSS MEMBERS/HARDWARE/OTHER(ENTER TEXT)
GALVANIZED OR PAINT FINISH IN POOR CONDITION? YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## TXFR GROUND
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
TRANSFORMER
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS THIS A UNIT SUBSTATION? YES-NO IF YES, NEST UNIT SUB TXFR FORM. IF NO, CONTINUE TO NEXT QUESTION.
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET & NAMEPLATE
ANY ALARMS ON LOCAL ANNUNCIATOR/TRANSFORMER? YES-NO FLAG ON YES. IF YES, NEST NEXT QUESTION AND PHOTO
DESCRIBE ALARMS
NOTIFY YOUR PG&E LEAD OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
CONDUCTOR IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
BUSHING OIL LEVEL ABNORMAL? YES-NO-N/A FLAG ON YES
DO BUSHINGS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES & SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO
IS ANIMAL ABATEMENT DAMAGED? YES-NO-N/A FLAG ON YES
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
ARE THERE LIGHTNING ARRESTORS ASSOCIATED WITH THIS ASSET? YES-NO IF YES NEST LIGHTNING ARRESTOR QUESTIONS
LIGHTNING ARRESTOR CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES
ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED? YES-NO FLAG ON YES
IS THERE A LIGHTNING ARRESTOR COUNTER? YES-NO IF YES NEST NEXT QUESTION, IF NO NEST FOLLOWING QUESTION
IS COUNTER DAMAGED OR ILLEGIBLE? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
HAS COUNTER BEEN REMOVED IMPROPERLY? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
DO LIGHTNING ARRESTORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES AND NEST DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
LIGHTNING ARRESTOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
LIGHTNING ARRESTOR GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
IS THE HIGHSIDE NEUTRAL (H0) GROUNDED? YES-NO (NO FLAG, INFORMATIONAL ONLY) IF THESE 3 HIGHLIGHTED QUESTIONS ARE ANSWERED LIKE IN BLUE, CREATE A FLAG NO
IS THE TRANSFORMER HIGHSIDE FUSED? YES-NO (NO FLAG, INFORMATIONAL ONLY) IF THESE 3 HIGHLIGHTED QUESTIONS ARE ANSWERED LIKE IN BLUE, CREATE A FLAG YES
IS THE H0 BUSHING OF A LOWER CLASS VOLTAGE THAN THE H BUSHINGS YES-NO (NO FLAG, INFORMATIONAL ONLY) IF THESE 3 HIGHLIGHTED QUESTIONS ARE ANSWERED LIKE IN BLUE, CREATE A FLAG YES
ANY LOCAL FEATURE C/OUT SWITCHES IN ABNORMAL STATUS? YES-NO-N/A FLAG ON YES & NEST NEXT 4 LINES
DESCRIBE ALARMS
NOTIFY YOUR PG&E LEAD OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
OIL TEMP. (DEGREES C)
WINDING TEMP. (DEGREES C)
IS OIL LEVEL ABNORMAL? YES-NO FLAG ON YES
ANY SIGNS OF LEAKS YES-NO FLAG ON YES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS
PLEASE SELECT ALL THAT APPLY (LEAKING, DRIPPING, WEEPING, SEEPING)
LEAK CONTAINMENT MISSING/LACKING? YES-NO FLAG ON YES
IF OIL RADIATORS/PUMPS IN POOR CONDITION OR FANS IN POOR CONDITION/MISSING? YES-NO FLAG ON YES | THIS QUESTION SHOULD STAND ALONE NOT NESTED
DOES TRANSFORMER HAVE A PRD? YES-NO (IF YES, SKIP NEXT QUESTION-NO FLAG, INFORMATIONAL ONLY)
DOES TRANSFORMER HAVE AN XPRD? YES-NO (NO FLAG, INFORMATIONAL ONLY)
IS DISCHARGE PIPE ROUTED OVER ANY CONTROL CABINETS/DRAIN VALVE? YES-NO IF YES FLAG
IS THERE INDICATION OF PRESSURE RELIEF DEVICE ACTIVATION? YES-NO-N/A IF YES FLAG
IS PRESSURE RELIEF DEVICE ACTUATION FLAG DAMAGED? YES-NO-N/A IF YES FLAG
IS THERE NOTICEABLE DEFORMATION OF THE TANK? (BULGING) YES-NO FLAG ON YES
ABNORMAL NOISES/ODORS? YES-NO FLAG YES AND NEST COMMENT
DESCRIBE
CABINET DOORS DO NOT CLOSE PROPERLY/WARPED LATCHES/SEAL IN POOR CONDITION? YES/NO FLAG ON YES
IMPROPERLY SEALED UNDERGROUND CONDUITS? YES-NO FLAG ON YES
CONTROL WIRE TERMINATIONS LOOSE OR DAMAGED? YES-NO FLAG ON YES AND NEST COMMENT & PHOTO
NITROGEN CYLINDER PRESSURE AT OR BELOW 200PSI (ENTER TEXT) YES-NO-N/A FLAG ON YES
NITROGEN BLANKET PRESSURE AT OR BELOW 0 (ENTER TEXT) YES-NO-N/A FLAG ON YES
IS NLTC PHYSICALLY LOCKED? YES-N0-N/A FOR INFORMATIONAL PURPOSES ONLY, NO FLAG
FIRE WALL/BARRIER DAMAGE YES-NO-N/A FLAG ON YES
TRANSFORMER TANK IMPROPERLY MOUNTED TO PAD E.G. ANCHORS/WELDS/BOLTS YES-NO FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## TXFR AIR+
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
TRANSFORMER
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
CONDUCTOR IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
CONNECTIONS IN POOR CONDITION? YES-NO-NOT VISIBLE FLAG ON YES | ADD THE WORD COMMENT EXAMPLE PIC NUMBER:*/COMMENT
BUSHING OIL LEVEL ABNORMAL? YES-NO-NOT VISIBLE FLAG ON YES
DO BUSHINGS HAVE ANY DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES & SELECTION DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
BUSHING CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
IS ANIMAL ABATEMENT PRESENT? IF YES, NEST NEXT QUESTION | REMOVE PHOTO REQUIRED WHEN ANSWERING YES, REMOVE PIC NUMBER WHEN ANSWERING NO
IS ANIMAL ABATEMENT DAMAGED? YES-NO-N/A FLAG ON YES
IS ANIMAL ABATEMENT NEEDED? YES-NO FLAG ON YES
DESCRIBE AND GIVE LOCATION(S)
ARE THERE LIGHTNING ARRESTORS ASSOCIATED WITH THIS ASSET? YES-NO IF YES NEST LIGHTNING ARRESTOR QUESTIONS
LIGHTNING ARRESTOR CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES
ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED? YES-NO FLAG ON YES
IS THERE A LIGHTNING ARRESTOR COUNTER? YES-NO IF YES NEST NEXT QUESTION, IF NO NEST FOLLOWING QUESTION
IS COUNTER DAMAGED OR ILLEGIBLE? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
HAS COUNTER BEEN REMOVED IMPROPERLY? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
DO LIGHTNING ARRESTORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES AND NEST DROPDOWN | NO FLAG ON YES, KEEP THE WORD COMMENT, REMOVE NESTED QUESTIONS AND PIC REQUIRED
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
LIGHTNING ARRESTOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
LIGHTNING ARRESTOR GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES | MOVE THIS QUESTION UNDER QUESTION "ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED"
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
IS THE HIGHSIDE NEUTRAL (H0) GROUNDED? YES-NO | WHEN ANSWERING NO REMOVE PHOTO IS REQIURED / ADD PIC NUMBER INSTEAD
IS THE TRANSFORMER HIGHSIDE FUSED? YES-NO | WHEN ANSWERING YES REMOVE PHOTO IS REQUIRED AND ADD PIC NUMBER INSTEAD / REMOVE PIC NUMBER WHEN ANSWERING NO
IS THE H0 BUSHING OF A LOWER CLASS VOLTAGE THAN THE H BUSHINGS YES-NO | REMOVE PIC NUMBER WHEN ANSWERING NO
IS OIL LEVEL ABNORMAL ? YES-NO-NOT VISIBLE FLAG ON YES
ANY SIGNS OF LEAKS YES-NO FLAG ON YES | THIS QUESTION SHOULD READ "ANY SIGN OF LEAKS?"/AND OR CONTAINMENT MISSING/LACKING" / REMOVE NESTED QUESTIONS
PLEASE SELECT ALL THAT APPLY (LEAKING, DRIPPING, WEEPING, SEEPING)
LEAK CONTAINMENT MISSING/LACKING? YES-NO FLAG ON YES
IF OIL RADIATORS/PUMPS IN POOR CONDITION OR FANS IN POOR CONDITION/MISSING? YES-NO FLAG ON YES | THIS QUESTION SHOULD STAND ALONE NOT NESTED
DOES TRANSFORMER HAVE A PRD? YES-NO (IF YES, SKIP NEXT QUESTION-NO FLAG, INFORMATIONAL ONLY)
DOES TRANSFORMER HAVE AN XPRD? YES-NO (NO FLAG, INFORMATIONAL ONLY)
IS DISCHARGE PIPE ROUTED OVER ANY CONTROL CABINETS/DRAIN VALVE? YES-NO IF YES FLAG | THIS QUESTION SHOULD ONLY POPULATE WHEN ANSWERING YES TO QUESTION "DOES TRANSFORMER HAVE AN XPRD"
IS THERE INDICATION OF PRESSURE RELIEF DEVICE ACTIVATION? YES-NO-N/A IF YES FLAG
IS PRESSURE RELIEF DEVICE ACTUATION FLAG DAMAGED? YES-NO-N/A IF YES FLAG
IS THERE NOTICEABLE DEFORMATION OF THE TANK? (BULGING) YES-NO FLAG ON YES
IS NLTC PHYSICALLY LOCKED? YES-NO-N/A FOR INFORMATIONAL PURPOSES ONLY, NO FLAG
FIRE WALL/BARRIER DAMAGE YES-NO-N/A FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## MTL CLD ARSW
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
METAL CLAD AIR SWITCH
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET, INCLUDING IDENTIFICATION NUMBER
CONDUCTOR IN POOR CONDITION? YES-NO FLAG ON YES
CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES
LIVE PARTS IN POOR CONDITION? (E.G. MALE-FEMALE AND/OR MAKE-BREAK CONNECTIONS/WHIPS/ARCING HORNS/ATTACHMENTS) YES-NO FLAG ON YES
SWITCH/DISCONNECT NOT FULLY SEATED OR FULLY OPEN? YES-NO FLAG ON YES
OPERATING LINKAGE IN POOR CONDITION? YES-NO-N/A FLAG ON YES
MISSING, DAMAGED, OR IMPROPER SWITCH LOCKS? YES-NO-N/A FLAG ON YES
MISSING OR DAMAGED FUSES? YES-NO-N/A FLAG ON YES
INSULATORS OUT-OF-PLUMB OR LEANING? YES-NO FLAG ON YES & COMMENT
DESCRIBE AND GIVE LOCATION(S)
DO INSULATORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES & SELECTION DROPDOWN
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
INSULATOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## MTL CLD BRKR
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
METAL CLAD CIRCUIT BREAKERS
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET, INCLUDING IDENTIFICATION NUMBER & NAMEPLATE
ANY ALARMS ON LOCAL ANNUNCIATOR/BREAKER? YES-NO FLAG ON YES. IF YES, NEST NEXT QUESTION AND PHOTO
DESCRIBE ALARMS? (ENTER TEXT)
NOTIFY YOUR PG&E LEAD OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
BREAKER TYPE: OIL/AIR/VAC (SELECT ONE)
IF OIL OIL LEVEL ABNORMAL? YES/NO/NOT VISIBLE FLAG ON YES
IF OIL ANY SIGN OF LEAKS? YES/NO FLAG ON YES AND NEST NEXT 2 QUESTIONS
IF OIL SELECT ALL THAT APPLY (LEAKING, WEEPING, DRIPPING, SEEPING)
IF OIL LEAK CONTAINMENT MISSING/LACKING? FLAG ON YES
CABINET DOORS DO NOT CLOSE PROPERLY/WARPED LATCHES/SEAL IN POOR CONDITION? YES/NO FLAG ON YES
CELL OR CABINET CONTAINS DUST/ DEBRIS? YES/NO FLAG ON YES
CONTROL WIRE TERMINATIONS LOOSE OR DAMAGED? YES-NO FLAG ON YES AND NEST COMMENT & PHOTO
MECHANICAL POSITION INDICATOR IN CORRECT POSITION? YES-NO FLAG ON YES
MISSING, NON-FUNCTIONING, DAMAGED, OR IMPROPER INDICATING LIGHTS? YES-NO IF YES FLAG & NEST NEXT QUESTION
IS THE RED LIGHT NON-FUNCTIONING? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
OPERATING MECHANISM IN POOR CONDITION? YES-NO IF YES FLAG AND NEST DROPDOWN SELECTION BOX
SELECT ALL THAT APPLY (MECH IS GUMMY, DRY OR HAS POOR LUBRICATION, OTHER(ENTER TEXT)
BREAKER MECHANISM INDICATOR SHOWING DISCHARGED? YES-NO FLAG ON YES & NEST NEXT PHOTO AND 2 QUESTIONS
NOTIFY YOUR PG&E LEAD OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
FLASH MARKS VISIBLE? YES-NO FLAG ON YES
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO-N/A FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count

## UNIT SUB TXFR
Header
Station:
Tier Level:
Head Quarter:
Longitude:
Latitude:
Date Inspected:
Inspected By:
User
Final Approver
Approved?
Approved? Comments
Asset
Asset Type
Description
Equipment
Functional Location
Manufacturer:
Manufacturer Serial #
UNIT SUB TRANSFORMER
ARE YOU ABLE TO INSPECT THIS ASSET? YES-NO IF NO, NEST SELECTION DROPDOWN
IS ASSET DESCRIPTION INCORRECT? IF YES, FLAG & COMMENT WITH CORRECT ASSET DESCRIPTION
NOTE CORRECT ASSET DESCRIPTION
PROVIDE CLEAR PHOTOS OF ASSET, INCLUDING IDENTIFICATION NUMBER & NAMEPLATE
ANY ALARMS ON LOCAL ANNUNCIATOR/TRANSFORMER? YES-NO FLAG ON YES. IF YES, NEST NEXT QUESTION
WHAT ALARMS?
NOTIFY YOUR PG&E LEAD OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
IS THE HIGHSIDE BUSHING (HO) GROUNDED? YES-NO (NO) IF THE 3 HIGHLIGHTED QUESTIONS ARE ANSWERED LIKE IN RED, CREATE FLAG
TRANSFORMER HIGHSIDE FUSED? YES-NO IF YES, NEST NEXT QUESTION AND PHOTO (YES)
IS THE H0 BUSHING OF A LOWER CLASS THAN THE H BUSHING? YES-NO-NOT VISIBLE (YES)
ANY LOCAL FEATURE C/OUT SWITCHES IN AN ABNORMAL POSITION? (E.G. RED/GREEN/BLACK LAMICOIDS) YES-NO FLAG ON YES & NEST NEXT PHOTO & 2 QUESTIONS
NOTIFY YOUR PG&E LEAD OR CONTROL CENTER HAVING JURISDICTION OVER STATION
WHO DID YOU NOTIFY?
OIL TEMP (DEGREES IN C)
WINDING TEMP (DEGREES IN C)
TRANSFORMER OIL LEVEL ABNORMAL? YES-NO FLAG ON YES ANSWER
ANY SIGN OF LEAKS? YES-NO FLAG ON YES ANSWER AND NEST NEXT 4 QUESTIONS
SELECT ALL THAT APPLY (LEAKING, WEEPING, DRIPPING, SEEPING)
LEAK CONTAINMENT MISSING/LACKING? YES-NO FLAG ON YES
RADIATORS/PUMPS IN POOR CONDITION OR FANS IN POOR CONDITION/MISSING? YES-NO FLAG ON YES
DOES THE TRANSFORMER HAVE A PRD? YES-NO (NO FLAG, INFORMATIONAL ONLY)
DOES THE TRANSFORMER HAVE AN XPRD? YES-NO (NO FLAG, INFORMATIONAL ONLY)
IS DISCHARGE PIPE ROUTED OVER ANY CONTROL CABINETS & DRAIN VALVES? YES-NO IF YES FLAG
ANY INDICATION OF PRESSURE RELIEF DEVICE ACTIVATION? YES-NO-N/A FLAG ON YES
IS PRESSURE RELIEF DEVICE ACTUATION FLAG DAMAGED? YES-NO-N/A FLAG ON YES
CABINET DOORS DO NOT CLOSE PROPERLY/WARPED LATCHES/SEAL IN POOR CONDITION? YES/NO FLAG ON YES
CONTROL WIRE TERMINATIONS LOOSE OR DAMAGED? YES-NO IF YES FLAG, COMMENT & PHOTO
IMPROPERLY SEALED UNDERGROUND CONDUITS? YES-NO IF YES FLAG, COMMENT & PHOTO
NITROGEN CYLINDER PRESSURE AT OR BELOW 200PSI? (ENTER TEXT) YES-NO-N/A IF YES NEST NEXT QUESTION FLAG, COMMENT & PHOTO
NITROGEN BLANKET PRESSURE AT OR BELOW ZERO? (ENTER TEXT) YES-NO-N/A FLAG ON YES
IS NLTC PHYSICALLY LOCKED? INFORMATIONAL ONLY, NO FLAG
ANY NOTICEABLE DEFORMATION/BULGING OF THE TANK? YES-NO FLAG ON YES
ANY ABNORMAL NOISES OR ODORS? YES-NO IF YES, COMMENT & PHOTO
ARE THERE LIGHTNING ARRESTORS ASSOCIATED WITH THIS ASSET? YES-NO IF YES NEST LIGHTNING ARRESTOR QUESTIONS
LIGHTNING ARRESTOR CONNECTIONS IN POOR CONDITION? YES-NO FLAG ON YES
ARE LIGHTNING ARRESTORS IMPROPERLY GROUNDED? YES-NO FLAG ON YES
IS THERE A LIGHTNING ARRESTOR COUNTER? YES-NO IF YES NEST NEXT QUESTION, IF NO NEST FOLLOWING QUESTION
IS COUNTER DAMAGED OR ILLEGIBLE? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
HAS COUNTER BEEN REMOVED IMPROPERLY? (IF YES, CONTACT PG&E LEAD IMMEDIATELY) YES-NO FLAG ON YES
DO LIGHTNING ARRESTORS HAVE DAMAGE/CONTAMINATION/CORROSION? YES-NO FLAG ON YES AND NEST DROPDOWN
SELECT ISSUE(S): DAMAGE/CONTAMINATION/CORROSION/FLASHED/BROKEN/CRACKED/LEAKING/OTHER(ENTER TEXT)
LIGHTNING ARRESTOR CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
LIGHTNING ARRESTOR GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO FLAG ON YES
SELECT ISSUE(S):CORRODED/FLASHED/BROKEN/MISSING/OTHER(ENTER TEXT)
TRANSFORMER TANK IMPROPERLY MOUNTED TO PAD E.G. ANCHORS/WELDS/BOLTS YES-NO FLAG ON YES
FOUNDATION CONDITION LEVEL 1-2-3-4-5 FLAG ON 3-4-5, COMMENTS REQUIRED ON 3-4-5.
SELECT ISSUE(S):FOUNDATION SUBSIDENCE/CRACKED/DETERIORATED/SOIL MOVEMENT/EXPOSED REBAR/ERODED EARTH/OTHER(ENTER TEXT)
GROUND WIRE(S) IN POOR CONDITION? (E.G. CORRODED, FLASHED, BROKEN, MISSING) YES-NO-N/A FLAG ON YES
WERE THERE ANY OTHER FINDINGS FOR THIS ASSET? YES-NO IF YES, FLAG AND NEST COMMENT & PHOTO. IF NO, END FORM.
Flag Count
Flag Count