## Read Me
In the subsequent tab, the following is provided to understand the information presented
Column A lists the "Facility" when referring to an FDA
Column B lists the specific "Damage" found in the field
Column C lists the "Action" to be taken based on the nonconformance in the field
Column D is how the information appears in SAP and in common vernacular
Column E represents the associated wildfire risk submodel that a particular non-conformance is mapped to. If an item is "out of scope" that means it does not map to a wildfire risk model, and is therefore not an ignition risk.
Note: Several FDAs have been added to the scope of the inspection checklists this year. Additionally, refined guidance has been developed and implemented for our inspection checklists.
These changes necessitate a review of our list of FDAs for changes or addition of ignition risk categories. This review is in progress and expected to be completed at the end of Q3 2023.

## fda_model_map
object_code_text | damage_code_text | activity_code_text | primary_key | model
high sign | missing | install | high sign-missing-install | out_of_scope
pole | decayed/rotten | replace | pole-decayed/rotten-replace | support_structure_equipment_cause
connector | incorrectly installed | replace | connector-incorrectly installed-replace | conductor_composite
pole | broken/damaged | replace | pole-broken/damaged-replace | support_structure_equipment_cause
guy | overgrown | trim | guy-overgrown-trim | out_of_scope
tree/vine | overgrown | trim | tree/vine-overgrown-trim | vegetation_branch
pole | woodpecker damage | assessment | pole-woodpecker damage-assessment | support_structure_equipment_cause
crossarm | decayed/rotten | replace | crossarm-decayed/rotten-replace | support_structure_equipment_cause
pole | overloaded | test | pole-overloaded-test | support_structure_equipment_cause
anchor | soil/eroded/graded | replace | anchor-soil/eroded/graded-replace | support_structure_equipment_cause
marking | broken/damaged | replace | marking-broken/damaged-replace | out_of_scope
guy | loose | adjust | guy-loose-adjust | support_structure_equipment_cause
marking | missing | install | marking-missing-install | out_of_scope
ground | exposed | repair | ground-exposed-repair | out_of_scope
crossarm | broken/damaged | replace | crossarm-broken/damaged-replace | support_structure_equipment_cause
pole step | clearance impaired | remove | pole step-clearance impaired-remove | out_of_scope
oh facility | idle facilities | remove | oh facility-idle facilities-remove | out_of_scope
tree/vine | clearance impaired | trim | tree/vine-clearance impaired-trim | vegetation_composite
anchor | soil/eroded/graded | adjust | anchor-soil/eroded/graded-adjust | support_structure_equipment_cause
conductor | improper connection | adjust | conductor-improper connection-adjust | conductor_composite
conductor | broken/damaged | replace | conductor-broken/damaged-replace | conductor_composite
molding | broken/damaged | replace | molding-broken/damaged-replace | out_of_scope
pole | idle facilities | remove | pole-idle facilities-remove | out_of_scope
transformer | idle facilities | remove | transformer-idle facilities-remove | out_of_scope
conductor | broken/damaged | repair | conductor-broken/damaged-repair | conductor_composite
guy marker | missing | install | guy marker-missing-install | out_of_scope
pole | leaning | adjust | pole-leaning-adjust | support_structure_equipment_cause
tree/vine | overgrown | remove | tree/vine-overgrown-remove | vegetation_composite
conductor | sag/clearance | adjust | conductor-sag/clearance-adjust | conductor_composite
lapp insulator | broken/damaged | replace | lapp insulator-broken/damaged-replace | conductor_composite
molding | loose | adjust | molding-loose-adjust | conductor_composite
transformer | corroded | replace | transformer-corroded-replace | out_of_scope
pole | leaning | replace | pole-leaning-replace | support_structure_equipment_cause
conductor | clearance impaired | adjust | conductor-clearance impaired-adjust | conductor_composite
hardware/framing | loose | adjust | hardware/framing-loose-adjust | out_of_scope
insulator | broken/damaged | replace | insulator-broken/damaged-replace | support_structure_equipment_cause
conductor | idle facilities | remove | conductor-idle facilities-remove | conductor_composite
anchor | missing | install | anchor-missing-install | support_structure_equipment_cause
under | arm bus | broken/damaged | under-arm bus-broken/damaged | out_of_scope
pole | broken/damaged | repair | pole-broken/damaged-repair | out_of_scope
molding | broken/damaged | repair | molding-broken/damaged-repair | out_of_scope
cutout | broken/damaged | replace | cutout-broken/damaged-replace | conductor_composite
insulator | primary squatter | replace | insulator-primary squatter-replace | support_structure_equipment_cause
guy marker | missing | replace | guy marker-missing-replace | out_of_scope
guy | clearance impaired | adjust | guy-clearance impaired-adjust | out_of_scope
anchor | broken/damaged | replace | anchor-broken/damaged-replace | support_structure_equipment_cause
guy | broken/damaged | replace | guy-broken/damaged-replace | support_structure_equipment_cause
tree/vine | decayed/rotten | install cl pole | tree/vine-decayed/rotten-install cl pole | support_structure_equipment_cause
pole | overloaded | replace | pole-overloaded-replace | support_structure_equipment_cause
tree/vine | tree connect | install cl pole | tree/vine-tree connect-install cl pole | support_structure_equipment_cause
hardware/framing | broken/damaged | replace | hardware/framing-broken/damaged-replace | support_structure_equipment_cause
pole | decayed/rotten | pole top repair | pole-decayed/rotten-pole top repair | support_structure_equipment_cause
conductor | clearance impaired | install cl pole | conductor-clearance impaired-install cl pole | conductor_composite
pole | burnt | replace | pole-burnt-replace | support_structure_equipment_cause
bird protection | bird protection | replace | bird protection-bird protection-replace | animal_bird
molding | missing | install | molding-missing-install | out_of_scope
transformer | leaks/seeps/weeps | replace | transformer-leaks/seeps/weeps-replace | transformer_equipment_cause
guy | corroded | replace | guy-corroded-replace | support_structure_equipment_cause
hardware/framing | missing | install | hardware/framing-missing-install | support_structure_equipment_cause
climbing space | obstructed | adjust | climbing space-obstructed-adjust | out_of_scope
tie wire | broken/damaged | replace | tie wire-broken/damaged-replace | support_structure_equipment_cause
tree/vine | clearance impaired | remove | tree/vine-clearance impaired-remove | vegetation_composite
guy | strain/abrasion | adjust | guy-strain/abrasion-adjust | support_structure_equipment_cause
insulator | secondary squatter | replace | insulator-secondary squatter-replace | support_structure_equipment_cause
guy | missing | install | guy-missing-install | support_structure_equipment_cause
anchor | corroded | replace | anchor-corroded-replace | support_structure_equipment_cause
crossarm | broken/damaged | repair | crossarm-broken/damaged-repair | support_structure_equipment_cause
guy | broken/damaged | repair | guy-broken/damaged-repair | support_structure_equipment_cause
oh facility | idle facilities | de | oh facility-idle facilities-de | support_structure_equipment_cause
lightning arrester | broken/damaged | replace | lightning arrester-broken/damaged-replace | conductor_composite
tie wire | loose | replace | tie wire-loose-replace | support_structure_equipment_cause
trans_dist pole | bonding broken | repair | trans_dist pole-bonding broken-repair | support_structure_equipment_cause
guy | strain/abrasion | remove | guy-strain/abrasion-remove | support_structure_equipment_cause
animal mitigation | broken/damaged | replace | animal mitigation-broken/damaged-replace | animal_composite
animal mitigation | mitigation missing | install | animal mitigation-mitigation missing-install | animal_composite
conductor | sag/clearance | install spreader bracket | conductor-sag/clearance-install spreader bracket | conductor_composite
insulator | primary squatter | repair | insulator-primary squatter-repair | support_structure_equipment_cause
connector | corroded | replace | connector-corroded-replace | conductor_composite
transformer | broken/damaged | replace | transformer-broken/damaged-replace | transformer_equipment_cause
hardware/framing | broken/damaged | repair | hardware/framing-broken/damaged-repair | support_structure_equipment_cause
crossarm | burnt | replace | crossarm-burnt-replace | support_structure_equipment_cause
pole | clearance impaired | replace | pole-clearance impaired-replace | support_structure_equipment_cause
insulator | flashed | replace | insulator-flashed-replace | support_structure_equipment_cause
conductor | sag/clearance | replace | conductor-sag/clearance-replace | conductor_composite
connector | corroded | repair | connector-corroded-repair | conductor_composite
ground | missing | install | ground-missing-install | out_of_scope
jumper | clearance impaired | adjust | jumper-clearance impaired-adjust | conductor_composite
pole | decayed/rotten | repair | pole-decayed/rotten-repair | support_structure_equipment_cause
pole | broken/damaged | re | pole-broken/damaged-re | support_structure_equipment_cause
transformer | parallel | replace | transformer-parallel-replace | transformer_equipment_cause
insulator | secondary squatter | repair | insulator-secondary squatter-repair | support_structure_equipment_cause
transformer | flashed | replace | transformer-flashed-replace | transformer_equipment_cause
trans_dist pole | bonding missing | install | trans_dist pole-bonding missing-install | support_structure_equipment_cause
streetlight | broken/damaged | repair | streetlight-broken/damaged-repair | out_of_scope
cutout | broken/damaged | repair | cutout-broken/damaged-repair | conductor_composite
oh facility | obstructed | remove | oh facility-obstructed-remove | out_of_scope
connector | burnt | replace | connector-burnt-replace | conductor_composite
switch | broken/damaged | replace | switch-broken/damaged-replace | conductor_composite
conductor | clearance impaired | raychem | conductor-clearance impaired-raychem | conductor_composite
conductor | burnt | repair | conductor-burnt-repair | conductor_composite
connector | temp differential | replace | connector-temp differential-replace | conductor_composite
crossarm | decayed/rotten | repair | crossarm-decayed/rotten-repair | support_structure_equipment_cause
streetlight | broken/damaged | replace | streetlight-broken/damaged-replace | out_of_scope
cutout | flashed | replace | cutout-flashed-replace | conductor_composite
oh facility | bird prot required | install | oh facility-bird prot required-install | animal_bird
conductor | burnt | replace | conductor-burnt-replace | conductor_composite
ground | broken/damaged | repair | ground-broken/damaged-repair | out_of_scope
jumper | burnt | replace | jumper-burnt-replace | conductor_composite
anchor | broken/damaged | repair | anchor-broken/damaged-repair | support_structure_equipment_cause
pole | burnt | repair | pole-burnt-repair | support_structure_equipment_cause
lightning arrester | flashed | replace | lightning arrester-flashed-replace | conductor_composite
guy | corroded | repair | guy-corroded-repair | support_structure_equipment_cause
jumper | clearance impaired | replace | jumper-clearance impaired-replace | conductor_composite
switch | broken/damaged | repair | switch-broken/damaged-repair | conductor_composite
transformer | broken/damaged | repair | transformer-broken/damaged-repair | transformer_equipment_cause
cutout | clearance impaired | adjust | cutout-clearance impaired-adjust | conductor_composite
transformer | overloaded | test | transformer-overloaded-test | transformer_equipment_cause
pole | clearance impaired | repair | pole-clearance impaired-repair | support_structure_equipment_cause
pole | broken/damaged | pole stub | pole-broken/damaged-pole stub | out_of_scope
pole | woodpecker damage | replace | pole-woodpecker damage-replace | support_structure_equipment_cause
conductor | floater | repair | conductor-floater-repair | conductor_composite
riser/pothead | broken/damaged | replace | riser/pothead-broken/damaged-replace | conductor_composite
transformer | leaks/seeps/weeps | repair | transformer-leaks/seeps/weeps-repair | transformer_equipment_cause
hardware/framing | bird prot required | install | hardware/framing-bird prot required-install | animal_bird
oh facility | idle facilities | transfer | oh facility-idle facilities-transfer | out_of_scope
crossarm | burnt | repair | crossarm-burnt-repair | support_structure_equipment_cause
ground | broken/damaged | replace | ground-broken/damaged-replace | out_of_scope
tree/vine | tree connect | assessment | tree/vine-tree connect-assessment | vegetation_trunk
riser/pothead | broken/damaged | repair | riser/pothead-broken/damaged-repair | conductor_composite
oh facility | limited access | remove | oh facility-limited access-remove | out_of_scope
pole | decayed/rotten | pole stub | pole-decayed/rotten-pole stub | support_structure_equipment_cause
anchor | corroded | repair | anchor-corroded-repair | support_structure_equipment_cause
capacitor | broken/damaged | replace | capacitor-broken/damaged-replace | out_of_scope
riser/pothead | flashed | replace | riser/pothead-flashed-replace | conductor_composite
streetlight | missing | install | streetlight-missing-install | out_of_scope
lightning arrester | broken/damaged | repair | lightning arrester-broken/damaged-repair | conductor_composite
transformer | flashed | repair | transformer-flashed-repair | transformer_equipment_cause
recloser/sectionalizer | leaks/seeps/weeps | replace | recloser/sectionalizer-leaks/seeps/weeps-replace | conductor_composite
conductor | overloaded | test | conductor-overloaded-test | conductor_composite
recloser/sectionalizer | broken/damaged | replace | recloser/sectionalizer-broken/damaged-replace | conductor_composite
riser/pothead | installed in error | relocate | riser/pothead-installed in error-relocate | out_of_scope
capacitor | broken/damaged | repair | capacitor-broken/damaged-repair | out_of_scope
decorative streetlight | broken/damaged | replace | decorative streetlight-broken/damaged-replace | out_of_scope
pole | burnt | pole stub | pole-burnt-pole stub | support_structure_equipment_cause
transformer | leaks/seeps/weeps | clean | transformer-leaks/seeps/weeps-clean | transformer_equipment_cause
fault indicators | broken/damaged | replace | fault indicators-broken/damaged-replace | out_of_scope
oh facility | transmission issue | create lc | oh facility-transmission issue-create lc | other_equipment_type
capacitor | leaks/seeps/weeps | replace | capacitor-leaks/seeps/weeps-replace | voltage_control_equipment_type
booster/regulator | broken/damaged | replace | booster/regulator-broken/damaged-replace | out_of_scope
steel lattice tower | broken/damaged | replace | steel lattice tower-broken/damaged-replace | support_structure_equipment_cause
rtvi | interference | repair | rtvi-interference-repair | out_of_scope
hardware/framing | birdcage | install | hardware/framing-birdcage-install | conductor_composite
steel lattice pole | guarding missing | install | steel lattice pole-guarding missing-install | out_of_scope
recloser/sectionalizer | broken/damaged | repair | recloser/sectionalizer-broken/damaged-repair | out_of_scope
oh facility | graffiti | paint | oh facility-graffiti-paint | out_of_scope
transformer | no common neutral | relocate | transformer-no common neutral-relocate | out_of_scope
cutout | flashed | repair | cutout-flashed-repair | conductor_composite
capacitor | burnt | repair | capacitor-burnt-repair | out_of_scope
booster/regulator | leaks/seeps/weeps | replace | booster/regulator-leaks/seeps/weeps-replace | out_of_scope
trip saver | broken/damaged | repair | trip saver-broken/damaged-repair | out_of_scope
booster/regulator | broken/damaged | repair | booster/regulator-broken/damaged-repair | out_of_scope
recloser/sectionalizer | flashed | replace | recloser/sectionalizer-flashed-replace | out_of_scope
riser/pothead | flashed | repair | riser/pothead-flashed-repair | conductor_composite
cb pole | decayed/rotten | replace | cb pole-decayed/rotten-replace | support_structure_equipment_cause
decorative streetlight | missing | install | decorative streetlight-missing-install | out_of_scope
rtvi | interference | replace | rtvi-interference-replace | out_of_scope
booster/regulator | burnt | repair | booster/regulator-burnt-repair | out_of_scope
trip saver | broken/damaged | replace | trip saver-broken/damaged-replace | out_of_scope
capacitor | leaks/seeps/weeps | repair | capacitor-leaks/seeps/weeps-repair | out_of_scope
deadend cover | broken/damaged | replace | deadend cover-broken/damaged-replace | animal_bird
under | arm bus | broken/damaged | under-arm bus-broken/damaged | out_of_scope
recloser/sectionalizer | leaks/seeps/weeps | repair | recloser/sectionalizer-leaks/seeps/weeps-repair | out_of_scope
tree/vine | decayed/rotten | remove | tree/vine-decayed/rotten-remove | vegetation_trunk
recloser/sectionalizer | flashed | repair | recloser/sectionalizer-flashed-repair | out_of_scope
cb pole | broken/damaged | replace | cb pole-broken/damaged-replace | support_structure_equipment_cause
oh facility | obstructed | replace | oh facility-obstructed-replace | out_of_scope
oh facility | limited access | inspect | oh facility-limited access-inspect | out_of_scope
booster/regulator | leaks/seeps/weeps | repair | booster/regulator-leaks/seeps/weeps-repair | out_of_scope
tree/vine | overgrown |  | tree/vine-overgrown- | vegetation_branch
anchor | soil/eroded/graded |  | anchor-soil/eroded/graded- | support_structure_equipment_cause
conductor | strain/abrasion | remove | conductor-strain/abrasion-remove | conductor_composite
climbing space | obstructed | trim | climbing space-obstructed-trim | out_of_scope
anchor | soil/eroded/graded | install | anchor-soil/eroded/graded-install | support_structure_equipment_cause
conductor | clearance impaired | replace | conductor-clearance impaired-replace | conductor_composite
transformer | padmount | idle facilities | transformer-padmount-idle facilities | out_of_scope
scada/pdac | leaks/seeps/weeps | test | scada/pdac-leaks/seeps/weeps-test | out_of_scope
tree/vine | broken/damaged | install cl pole | tree/vine-broken/damaged-install cl pole | vegetation_trunk
pole | clearance impaired | install | pole-clearance impaired-install | support_structure_equipment_cause
tree/vine | clearance impaired |  | tree/vine-clearance impaired- | vegetation_composite
bird protection | birdcage | replace | bird protection-birdcage-replace | animal_bird
capacitor | burnt | replace | capacitor-burnt-replace | out_of_scope
cb pole | burnt | replace | cb pole-burnt-replace | support_structure_equipment_cause
scada/pdac | broken/damaged | repair | scada/pdac-broken/damaged-repair | out_of_scope
pole | woodpecker damage | repair | pole-woodpecker damage-repair | out_of_scope
tree/vine | decayed/rotten | install | tree/vine-decayed/rotten-install | vegetation_trunk
anchor | soil/eroded/graded | repair | anchor-soil/eroded/graded-repair | support_structure_equipment_cause
scada/pdac | leaks/seeps/weeps | repair | scada/pdac-leaks/seeps/weeps-repair | out_of_scope