## Fixes List 2022
Station Issues (Communications/Sensors) - These can be visited, prioritize OFFLINE & BLUE Stations, 2nd priority ORANGE stations if in the area
Date Added | Serial Number | MesoWest ID | Date Installed | Station Status | Collection Interval | N/A | Station Name | Circuit Name | Lat | Longitude | Elev (ft) | Service Center (District) | Pole Structure # | Issue Status | Issue Notes | Solution | Additional Comments
2022-12-19 | SCE-2352 | SE403 | 2019-07-31 | OFFLINE | 10 |  | SCE Bridgeport | STROSNIDER | 38.2583 | -119.2261 | 6460 | Bishop | 1618078E | Hardware - Battery & Datalogger | Station lost comms suspected due to corrupted program from brown out power conditions | Confirm CR1000X is dead and Repalce datalogger. Most likely battery when there is access to station
2022-12-12 | SCE-2700 | SE731 | 2020-05-05 | Online | 10 |  | SCE Tanager Ln | TRAIL | 37.2489 | -119.1931 | 7075 | Shaver Lake | 4278906E | Hardware - Sensor | Wind Monitor has started to give bad reads. Suspected bad bearings or broken propellor | Check for damge and loose wiring. Replace bearings, propellor, and/or sensor to fix
2022-12-12 | SCE-2701 | SE727 | 2020-05-05 | Online | 10 |  | SCE Huntington Lake Rd | RANCHERIA | 37.2532 | -119.1655 | 6968 | Shaver Lake | 1031019E | Hardware - Sensor | Wind Monitor has started to give bad reads. Suspected bad bearings or broken propellor | Check for damge and loose wiring. Replace bearings, propellor, and/or sensor to fix
2022-12-08 | SCE-2795 | SE807 | 2020-05-26 | Online | 10 |  | SCE Kaiser Ridge | MT. GIVENS | 37.2692 | -119.1242 | 8276 | Shaver Lake | 1807072E | Hardware - Sensor | Temp/rh sensor has failed and is giving bad readings | Check for obvious damage; replace sensor
2022-12-09 | SCE-3648 | 638SE | 2022-11-02 | OFFLINE | 10 |  | SCE Horsethief Mtn | ANTELOPE-MAGUNDEN NO. 1 | 35.1028 | -118.7195 | 2636 | Kernville | 7014854 | Hardware - Satellite Modem | Lost comms 12/7/22; no sign of power issue | Power-cycle; update OS/program if needed. Check for damage and/or wiring errors. Test all satellite equipment; log into sat interface and check RSSI and online status
2022-12-08 | SCE-3768 | 628SE | 2022-10-03 | Online | 10 |  | SCE Woody Road | MAGUNDEN-SPRINGVILLE NO. 2 | 35.5846 | -118.9197 | 1232 | Tulare | 7019176 | Software - CH200 | CH200 does not have the battery capacity set to 52, causing erroneous readings | Connect to CH200 charger interface and confirm the battery family, capacity, and type.
Resolved Station Incidents
Date Added | Serial Number | MesoWest ID | Date Installed | Station Status | Collection Interval | N/A | Station Name | Circuit Name | Lat | Longitude | Elev (ft) | Service Center (District) | Pole Structure # | Issue Status | Issue Notes | Solution | Resolution Comments | Tech Visited | Date Resolved
2022-12-08 | SCE-3066 | 045SE | 2020-09-23 | Online | 10 |  | SCE Raywood Flat Rd | GUNSITE | 34.0381 | -116.8317 | 7162 | Redlands | 1609854E | Hardware - Sensor | Temp/rh sensor has failed and is giving bad readings | Check for obvious damage; replace sensor | Replaced cable and sensor | Davis | 2022-12-23
2022-09-26 | SCE-3486 |  | 2021-10-15 | Online | 60 |  | SCE Graveyard Tktr | VERDUGO | 34.2866 | -118.2912 | 1465 | Monrovia | 478820E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Power cycled. O.S updated. Rediscovered. Moved back to Websocket collection (10 min interval). Remapped. Cell service present for Dual Comm addition. | Colligan | 2022-12-21
2022-12-08 | SCE-2634 | SE631 | 2020-04-03 | Online | 10 |  | SCE Oak Grove Dr | DEVILS GATE | 34.1919 | -118.1762 | 1042 | Monrovia | 4548848E | Hardware - Sensor | Wind monitor is going in and out of giving good readings; suspected bad bearings | Confirm no damge or loose/incorrect wiring. Suspected bad bearings, replace bearings or wind monitor sensor | Propeller had a broken blade so a new propeller was put on. | Colligan | 2022-12-21
2022-12-08 | SCE-2099 | SE121 | 2018-10-31 | Online | 10 |  | SCE Olinda Village | VERA CRUZ | 33.9329 | -117.7952 | 675 | Fullerton | 2325728E | Hardware - Sensor | Wind monitor is going in and out of giving good readings; suspected loose wiring or failed sensor | Confirm no damge or loose/incorrect wiring. Replace sensor if all else checked out. | David found that the main cylinder was loose (area behind prop) and re-tightened. Performed 4 point test and 30 degree test and sensor passed. | Colligan | 2022-12-20
2022-12-08 | SCE-3353 | 377SE | 2021-08-30 | Online | 10 |  | SCE Montara Rd | LOTTO | 34.4382 | -117.5837 | 4012 | Victorville | 4069297E | Hardware - Sensor | Temp/rh sensor has failed and is giving bad readings | Check for obvious damage; replace sensor | Steve mentioned someone had been shootong the temp housing with a BBgun and damaged the cable. Replaced cable and reading was correct. | Smith | 2022-12-20
2022-10-14 | SCE-2307 | SE472 | 2019-10-17 | Online | 10 |  | SCE Yellow Hill | GALAHAD | 34.0775 | -118.9415 | 1504 | Thousand Oaks | 2241500E | Hardware - Sensor | SolarRad died 7/10/22 | Replace or remove SolarRad | Sensor and cables were replaced. | Colligan | 2022-12-20
2022-09-26 | SCE-2678 |  | 2020-04-17 | Online | 60 |  | SCE Mustang Springs Rd | ATENTO | 33.7527 | -117.6341 | 1462 | Saddleback | 1269552E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Power-cycled; restored to always powered | Colligan | 2022-12-19
2022-12-08 | SCE-2266 | SE151 | 2019-03-20 | OFFLINE | 10 |  | SCE East Fork City Creek | CRAM | 34.1864 | -117.1796 | 2646 | Redlands | 721226E | Hardware - Cell Modem | Lost comms 11/29/22; no signs on power issue | Power-cycle, call WWG to troubleshoot further and deduce what issue may be | Power Cycled, no problems found. OS and program were up to date, calibrated recently. Signal was full bars 4G at time of repair call. | 2022-12-15 | 2022-12-19
2022-12-08 | SCE-2926B | 114SE | 2021-06-08 | OFFLINE | 10 |  | SCE Haul Rd | TAIWAN | 33.7675 | -117.7105 | 854 | Santa Ana | 2095959E | Hardware - Cell & Satellite Modem | Lost comms 12/6/22; no sign of power issue | Power-cycle, check for damage, reupload OS/program call WWG to troubleshoot further and deduce what issue may be | Power-cycled, updated OS and Program, replaced ch200 sdi-12 cable | Colligan | 2022-12-19
2022-11-23 | SCE-2377B | 099SE | 2021-06-04 | OFFLINE | 10 |  | SCE Barley Flats Rd | RED BOX | 34.273 | -118.0453 | 4611 | Monrovia | 735908E | Hardware - Modem | Lost comms 11/11/22; no signs on power issue | Power-cycle; update OS/program if needed. Check for damage and/or wiring errors. Test all satellite equipment; log into sat interface and check RSSI and online status | Updated OS/program, replaced sat power cable | Davis | 2022-12-15
2022-09-26 | SCE-3337 |  | 2021-08-25 | Online | 60 |  | SCE Green Earth | SHEFFIELD | 34.4172 | -119.5236 | 185 | Santa Barbara | 2024119E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Needs Dualcomms upgrade (Cell modem) | No issues present, possibly self resolved. Added cell modem. | Smith | 2022-12-06
2022-11-22 | SCE-2108 | SE097 | 2018-09-26 | OFFLINE | 10 |  | SCE Baker Canyon | ATENTO | 33.7673 | -117.6616 | 1480 | Saddleback | 4349530E | Hardware - Modem | Lost comms 11/13/22; no signs on power issue | Power-cycle, access satellite interface to confirm online, 5 bars, RSSI value; Potentially swap out sat equipment. | Power cycled and added Default program | Spinowitz | 2022-11-29
2022-11-16 | SCE-2283 | SE441 | 2019-09-06 | Online | 10 |  | SCE Pipeline Rd | GAMBLER | 34.3941 | -117.5819 | 4599 | Victorville | 4099929E | Hardware - Sensor + Satellite | Satellite, Temp/RH, SolarRad started failing all on 11/10/22 | Check for station damage, recalibrate bad sensors and swap out if needed; confirm access to satellite interface with 'Online' status and RSSI value; potentially swap out bad satellite equipment | Replaced satellite equipment, Temp/rh, solarrad, and datalogger | Smith | 2022-11-29
2022-10-26 | SCE-3220 | 224SE | 2021-07-08 | Online | 10 |  | SCE Rocky Mountain | CANET | 34.3533 | -119.3012 | 361 | Ventura | 681632E | Hardware - Datalogger | Suspected failed ethernet port; dualcomms, no satellite access | Bring spare datalogger to potentially replace; Bring satellite equipment just in case of issue with modem itself | Replaced sat power cable, re-aligned terminal, sent frequency file. Updated Program/OS | Spinowitz | 2022-11-22
2022-11-22 | SCE-2947 | 027SE | 2020-09-18 | Online | 10 |  | SCE Mesa Grande Rd | SAND CANYON | 34.4579 | -118.3003 | 2536 | Valencia | 820434H | Hardware - Sensor | Wind monitor goes in and out giving good readings then bad all day; suspected loose or damged wires | Check for wiring issues and damage. Perform a pull test on each wire. Re-seat wires on main terminal block, check wiring behind terminal block to datalogger, and check wind sensor junction box wiring. If issue persists, replace sensor and re-calibrate. | Replaced wind sensor + cable and Temp/RH cable | Spinowitz | 2022-11-22
2022-10-26 | 3194 | 201SE | 2021-07-08 | Online | 10 |  | SCE Brents Junction | MILO | 34.1486 | -118.6969 | 804 | Thousand Oaks | 1638608E | Hardware - Datalogger | Suspected failed ethernet port; dualcomms, no satellite access | Bring spare datalogger to potentially replace; Bring satellite equipment just in case of issue with modem itself | Dan found that the sat terminal had failed. replaced with TI# 4802 and connection now good | Spinowitz | 2022-11-21
2022-11-08 | 2143 | SE212 | 2019-04-19 | Online | 10 |  | SCE Meiners Oaks | TICO | 34.4506 | -119.2854 | 746 | Ventura | 4510527E | Hardware - Modem | Cell modem pings, but does not connect with the datalogger; 11/4/22 | Power-cycle to attempt to restore comms. Double check wiring. Check if OS/program are still there and current. Potentially replace cell modem itself or datalogger. | Power cycle station, update program, and update modem template. | Colligan | 2022-11-18
2022-10-26 | 2203 | SE214 | 2019-04-20 | Online | 10 |  | SCE Red Mountain | RED MOUNTAIN | 34.3489 | -119.3379 | 2033 | Ventura | 4407799E | Hardware - Modem | Cell modem pings, but does not connect with the datalogger | Power-cycle to attempt to restore comms. Double check wiring. Check if OS/program are still there and current. Potentially replace cell modem itself or datalogger. | Power cycle station, update program, and update modem template. | Colligan | 2022-11-18
2022-11-01 | 3546 | 539SE | 2022-04-14 | Online | 10 |  | SCE Greencourt Dr | SAND CANYON | 34.4492 | -118.388 | 1789 | Valencia | 4104422E | Hardware - Battery | Battery is dying rapidly, suspected bad weather, or damage to solar panel | Check voltage on everything, confirm no damage or loose wiring. Replace battery and/or solar panel. | Replaced solar panel. | Colligan | 2022-11-18
2022-11-17 | SCE-3356 | 338SE | 2021-08-23 | Online | 10 |  | SCE The Old Rd | TAMBOURINE | 34.4935 | -118.6228 | 1194 | Valencia | 4398379E | Hardware - Sensor + Solar Panel | Wind is giving erroneous readings; Sensor could be damged/loose or bearings going bad. Has two small solar panels that were never wired correctly; tech never returned to fix issue 8/23/22 Needs to be wired in 'parallel' and NOT in 'series' | Check for damge to station/sensors. Fix solar panel wiring (wire in parallel); recalibrate wind sensor and replace if bad values persist | Replaced wind monitor | Colligan | 2022-11-18
2022-11-01 | 2257 | SE196 | 2019-04-13 | OFFLINE | 10 |  | SCE Corriganville Park | BIG ROCK | 34.2652 | -118.6516 | 1119 | Thousand Oaks | 4557327E | Hardware - Modem | Cell modem pings, but does not connect with the datalogger | Power-cycle to attempt to restore comms. Double check wiring. Check if OS/program are still there and current. Potentially replace cell modem itself or datalogger. | Power-cycled, updated OS and Program | Spinowitz | 2022-11-17
2022-11-17 | SCE-2947 | 027SE | 2020-09-18 | Online | 10 |  | SCE Mesa Grande Rd | SAND CANYON | 34.4579 | -118.3003 | 2536 | Valencia | 820434H | Hardware - Sensor | Wind is giving erroneous readings; Sensor could be damged/loose or bearings going bad | Check for damge to station/sensors. Recalibrate wind sensor and replace if bad values persist | Recalibrated wind monitor | Colligan | 2022-11-17
2022-08-29 | 3017 | SE914 | 2020-07-24 | Online | 10 |  | SCE Black Walnut Dr | CHARLTON | 33.7596 | -116.9333 | 1654 | Menifee | 2133993E | Hardware - Satellite | Return to add replacement satellite terminal | Replace terminal and call WWG to confirm. | Replaced satellite terminal | Davis | 2022-11-15
2022-11-08 | 2813 | SE812 | 2020-05-29 | Online | 10 |  | SCE Carter St | STONEWOOD | 34.0628 | -117.0213 | 3011 | Redlands | 721064E | Hardware - Battery | Battery is dying rapidly, suspected bad weather, or damage to solar panel | Check voltage on everything, confirm no damage or loose wiring. Replace battery and/or solar panel. | Ben moved station 1 span east, replaced battery | Davis | 2022-11-15
2022-10-26 | 3216 | 229SE | 2021-07-15 | Online | 10 |  | SCE Pepsico | CARDIFF-GREENSPOT-SANTA ANA 3 | 34.0853 | -117.2524 | 1060 | Redlands | 4329238E | Hardware - Datalogger | Suspected failed ethernet port; dualcomms, no satellite access | Bring spare datalogger to potentially replace; Bring satellite equipment just in case of issue with modem itself | Updated OS/program. Confirmed good datalogger | Davis | 2022-11-15
2022-10-31 | 3051 | 061SE | 2020-10-06 | Online | 10 |  | SCE San Bernardino Mountain | PENSTOCK | 34.3258 | -117.2718 | 3161 | Victorville | 1533996E | Hardware - Battery | Battery drops to 11.5 volts throughout the year but does not ever go fully down. | Confirm that there are shading/siting issues causing battery problems; replace or recharge battery | Station seemed to have fixed its self. | Davis | 2022-11-15
2022-09-26 | 2714 |  | 2020-04-24 | Online | 60 |  | SCE Boosey Rd | PYLE | 34.3791 | -119.0279 | 457 | Ventura | 4628633E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Power-cycled to comms; updated OS/program and added cell modem to make it dualcomms | Davis | 2022-11-03
2022-10-19 | 3624 | 605SE | 2022-06-30 | Online | 10 |  | SCE Shell Station | CASA DIABLO-RUSH CREEK | 37.8116 | -119.0525 | 7707 | Bishop | 2177642E | Hardware - Modem | Station secondary comms (satellite) failed. | Bad Satellite terminal hardware confirmed. Needs Replacement. Original one is being sent back to WWG. Solution: Run 6_4_DualComm program. Install new satellie terminal, check online status, # of bars, RSSI; Check station LED's once secondary comms is powered on (PoE, 10/100 ethernet port). Call WWG to assist further. | Replaced satellite terminal. | Davis | 2022-11-01
2022-10-21 | 2534 | SE528 | 2020-02-25 | Online | 10 |  | SCE Mountain View Rd | INYO LUMBER | 37.3611 | -118.4454 | 4349 | Bishop | 1735727E | Hardware - Sensor | Single scan of bad temp/rh readings rarely occurs, affecting daily data; Sensor working otherwise | Check Temp/RH wiring to main terminal block; Check CSI Pre-wiring behind terminal block to datalogger ports; Check datalogger green terminal rows for tightness; Perform pull test to confirm wiring is good; inspect Temp/RH sensorhead connection to cable; Power cycle station; Replace EE-181 temp/rh sensor if necessary | Replaced temp/rh probe and resecured wiring. Updated logger OS and program | Smith | 2022-10-31
2022-10-26 | 3301 | 315SE | 2021-08-11 | Online | 10 |  | SCE Lancer Way | TALLEY | 34.2132 | -118.8708 | 788 | Thousand Oaks | 1383635E | Hardware - Datalogger | Suspected failed ethernet port; dualcomms, no satellite access | Bring spare datalogger to potentially replace; Bring satellite equipment just in case of issue with modem itself | Power-cycled and updated OS/Program. | Spinowitz | 2022-10-27
2022-09-26 | 2313 |  | 2019-05-04 | Online | 60 |  | SCE Big Sycamore Canyon | RAMAC | 34.1244 | -118.9971 | 278 | Ventura | 4376299E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Power cycled and updated OS 6.0 | Spinowitz | 2022-10-27
2022-09-26 | 2992 |  | 2020-08-21 | Online | 10 |  | SCE Coyote Canyon Dr | KRUEGER | 33.6287 | -117.8395 | 215 | Huntington Beach | 4009169E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Reset sat terminal, checked power, calibration station. Converted to DualComms using SCE-10009-96 | Spinowitz | 2022-10-26
2022-10-14 | 3572 | 631SE | 2022-10-04 | OFFLINE | 10 |  | SCE Rock Hill Lane | Big Creek 4-Springville | 37.0508 | -119.4935 | 1877 | Shaver Lake | 7015113 | Hardware - Modem | Station secondary comms (satellite) is failing, while primary comms (cellular) is marginal | Double check satellite terminal hardware is functioning properly. Determine satellie terminal online status, # of bars, RSSI; Check station LED's once secondary comms is powered on (PoE, 10/100 ethernet port). Call WWG to assist further, replace malfunctioning hardware | Reset cell modem, replaced satellite terminal with TI-6807 | Wright | 2022-10-26
2022-10-14 | 3048 |  |  | Test | 10 |  | Santa Ana Test Station | N/A | 33.7317 | -117.849 | 99 | Santa Ana | N/A | Hardware - Sensor | Bad Temp/RH Readings | Check Temp/RH wiring to main terminal block; Check CSI Pre-wiring behind terminal block to datalogger ports; Check datalogger green terminal rows for tightness; Perform pull test to confirm wiring is good; inspect Temp/RH sensorhead connection to cable; Power cycle station; Replace EE-181 temp/rh sensor if necessary | Replaced temp/rh | Spinowitz | 2022-10-25
2022-10-14 | 2330 | SE221 | 2019-04-24 | Online | 10 |  | SCE Temescal Wash | PORPHYRY | 33.8524 | -117.52 | 698 | Ontario | 4854901E | Hardware - Sensor | Bad Temp/RH Readings; Bad SolarRad | Check Temp/RH wiring to main terminal block; Check CSI Pre-wiring behind terminal block to datalogger ports; Check datalogger green terminal rows for tightness; Perform pull test to confirm wiring is good; inspect Temp/RH sensorhead connection to cable; Power cycle station; Replace EE-181 temp/rh sensor if necessary; Calibrate and replace SolarRad sensorhead if necessary | Powercycled station which seemed to fix EE-181 issues. | Smith | 2022-10-24
2022-10-21 | 2086 | SE069 | 2018-09-06 | OFFLINE | 10 |  | SCE Sage | WINERY | 33.5739 | -116.9633 | 1925 | Wildomar | 2225226E | Hardware - Modem | Cellular modem rarely communicates since 10/12/22 | Power cycle station first, then call WWG to troubleshoot, potentially swap out modem equipment; Bring an external cellular antenna if possible. | Replaced cell modem, upgraded antenna | Davis | 2022-10-24
2022-10-14 | 2232 | SE163 | 2019-03-29 | OFFLINE | 10 |  | SCE Chino Creek | VENGEANCE | 33.9494 | -117.6647 | 539 | Ontario | 1868846E | Power - Battery | Battery drained, left unplugged, station works during the day but not at night | Replace the battery, power cycle station, confirm with WWG all comms restored | Replaced with 60W solar panel and lithium battery | Davis | 2022-10-24
2022-10-14 | 2660 | SE683 | 2020-04-23 | Online | 10 |  | SCE Whitaker Ridge Rd | CLARINET | 34.5844 | -118.7237 | 3749 | Valencia | 4556642E | Hardware - Modem | Sat modem down 10/12/22 | Power-cycle station first, then call WWG to troubleshoot, poitentially swap out modem equipment | Replaced datalogger due to failed ethenet port. The 10/100 was bad, orange light was blinking steadily and both lights stayed on when etherent cable was unplugged. Station also converted to dual comms. 6_4_DualComms program added. | Spinowitz | 2022-10-24
2022-10-14 | 3066 | 045SE | 2020-09-23 | Online | 10 |  | SCE Raywood Flat Rd | GUNSITE | 34.0381 | -116.8317 | 7162 | Redlands | 1609854E | Hardware - Sensor | Bad Temp/RH Readings | Check Temp/RH wiring to main terminal block; Check CSI Pre-wiring behind terminal block to datalogger ports; Check datalogger green terminal rows for tightness; Perform pull test to confirm wiring is good; inspect Temp/RH sensorhead connection to cable; Power cycle station; Replace EE-181 temp/rh sensor if necessary | Sensor reading 406 degrees. Checked wiring, checked the probe, then power cycled station. Station started reading correct values
2022-10-14 | 2585 | SE550 | 2020-03-06 | Online | 10 |  | SCE Ocean View Dr | ALPINE | 34.2274 | -117.2576 | 5246 | Arrowhead | 1301995E | Hardware - Sensor | Bad Temp/RH Readings | Check Temp/RH wiring to main terminal block; Check CSI Pre-wiring behind terminal block to datalogger ports; Check datalogger green terminal rows for tightness; Perform pull test to confirm wiring is good; inspect Temp/RH sensorhead connection to cable; Power cycle station; Replace EE-181 temp/rh sensor if necessary | Power-cycled to fix temp/rh | Smith | 2022-10-24
2022-10-14 | 2724 | SE726 | 2020-05-04 | Online | 10 |  | SCE Glen Helen Rd | CHEVELLE | 34.2257 | -117.424 | 2184 | Redlands | 1706097E | Hardware - Sensor | Bad Temp/RH Readings | Power-cycle first, if does not fix then call WWG to troubleshoot and potentially replace sensor | Powercycled station which seemed to fix EE-181 bad data readings. | Davis | 2022-10-21
2022-09-26 | 3304 |  | 2021-08-26 | Online | 60 |  | SCE Ojai Grant | THACHER | 34.4217 | -119.1263 | 2416 | Ventura | 4204576E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Station was powercycled. Updated OS and Program, rediscovered and remapped. | Spinowitz | 2022-10-12
2022-09-26 | 3337 |  | 2021-08-25 | Online | 60 |  | SCE Green Earth | SHEFFIELD | 34.4172 | -119.5236 | 185 | Santa Barbara | 2024119E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Power cycled to restore sat comms. Historical data collected. 10 min interval set up. | Colligan | 2022-10-12
2022-09-26 | 3364 |  | 2021-08-25 | Online | 60 |  | SCE Barger Canyon Rd | HURST | 34.4634 | -119.7474 | 491 | Santa Barbara | 4779299E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Power cycled to restore sat comms. Dual comm needed (weak sat signal) but did not have modem in spare inventory. | Colligan | 2022-10-12
2022-09-26 | 3288 |  | 2021-08-26 | Online | 60 |  | SCE Fordyce Rd | THACHER | 34.4576 | -119.2149 | 854 | Ventura | 1425263E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Potential Power Issue Present | Spinowitz | 2022-10-12
2022-09-26 | 3344 |  | 2021-08-26 | Online | 60 |  | SCE Clark Ranch Rd | THACHER | 34.4076 | -119.2641 | 1106 | Ventura | 4651806E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Power cycled to restore sat comms. Dual comm added. | Spinowitz | 2022-10-12
2022-09-26 | 3076 | 006SE | 2020-09-15 | Online | 10 |  | SCE Cuesta Verde | TECOLOTE | 34.4594 | -119.8305 | 204 | Santa Barbara | 1339948E | Hardware - Satellite | Comms down since 9/14/22; no power issue | Power-cycle, Call WWG to troubleshoot | Power cycled to restore cellular comms. Dual comm added. | Colligan | 2022-10-12
2022-09-26 | 2177 | SE233 | 2019-04-30 | Online | 10 |  | SCE Sycamore Dr | RIVA | 34.3636 | -119.3079 | 278 | Ventura | 1203835E | Hardware - Cell modem | Comms lost 9/11/22 | Power-cycle, Call WWG to troubleshoot | Power cycled to restore cellular comms. Historical data collected. | Spinowitz | 2022-10-12
2022-09-26 | 2378 |  | 2019-05-20 | Online | 60 |  | SCE Little Tujunga Canyon Rd | LOPEZ | 34.3298 | -118.3435 | 1889 | Valencia | 1945996E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Power cycled to restore cellular comms, replaced Temp/RH sensor | colligan | 2022-10-11
2022-09-26 | 2152 | SE207 | 2019-04-18 | Online | 10 |  | SCE Las Posas Hills | DONLON | 34.2507 | -118.9792 | 692 | Ventura | 2096785E | Hardware - Cell modem | Comms lost 9/21/22 | Power-cycle, Call WWG to troubleshoot | Comms restored with power cycle and template update. Replaced temp/rh sensor | Spinowitz | 2022-10-11
2022-04-12 | 2944 | SE973 | 2020-08-31 | Online | 10 |  | SCE Espuella Dr | CHARIOT | 34.4295 | -118.5286 | 1206 | Valencia | 1580140E | Frequently Missed Comm | Station communications drop in and out throughout the day, occasionally out for few hours at a time; Needs Dualcomms upgrade (Cell modem) | Needs Dualcomms upgrade (Cell modem) | Fixed with cell modem addition and OS/program update | Colligan | 2022-10-11
2022-05-09 | 2987 | SE937 | 2020-08-11 | Online | AP |  | SCE Starbuck Cir | FULLBACK | 33.5818 | -117.2421 | 1188 | Wildomar |  | Frequently Missed Comm | Ben visited and tried cell modem 9/26/22; Replaced satellite cable; WWG continuing to monitor | self resolved | Comms improved after power cycle visit and WWG monitoring | N/A Self Resolved | 2022-10-07
2022-08-01 | 2218 | SE199 | 2019-04-16 | Online | 10 |  | SCE Kanan Rd | MULHOLLAND | 34.1098 | -118.8046 | 1431 | Thousand Oaks |  | Frequently Missed Comm | Comms improived after recent power-cycle fix visit; WWG continuing to monitor | self resolved | Comms improved after power cycle visit and WWG monitoring | N/A Self Resolved | 2022-10-07
2022-09-19 | 2041 | SE087 | 2018-09-20 | Online | 10 |  | SCE Weldon | CANEBRAKE | 35.6363 | -118.2496 | 2800 | Kernville |  | Frequently Missed Comm | External Omni Antenna installed 8/1/22 - No improvement - Needs Dualcomms upgrade (Satellite, 65W panel, Lithium battery) - Waiting on Quote + Order; Comms improved after recent power-cycle fix visit; WWG continuing to monitor | self resolved | Comms improved after power cycle visit and WWG monitoring | N/A Self Resolved | 2022-10-07
2022-09-26 | 3323 |  | 2021-08-16 | Online | 60 |  | SCE Enchanted Hills Rd | BOOTLEGGER | 34.4681 | -118.14 | 3380 | Antelope Valley | 1634614E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Resolved after standard calibration visit 9/30/22 | Davis | 2022-09-30
2022-09-26 | 2541 |  | 2020-02-27 | Online | 60 |  | SCE Citrus Ave E | NICKLIN | 34.1639 | -117.4524 | 1772 | Foothill | 1329356E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Power-Cycled. O.S 6.00 updated. Dual comm added. Program version 6_4DualComm uploaded. | Smith | 2022-09-28
2022-09-26 | 2888 |  | 2020-06-23 | Online | 60 |  | SCE Pine Bench Rd | OAK GLEN | 34.0383 | -116.9108 | 5514 | Redlands | 1733493E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Station was powercycled. Updated OS and Program, rediscovered and remapped. | Smith | 2022-09-28
2022-09-26 | 3086 |  | 2020-09-23 | Online | 60 |  | SCE Burnt Mill Creek | COTTAGE GROVE | 34.2453 | -117.1932 | 5345 | Arrowhead | 1346445E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Station was powercycled. Added cell, updated OS and Program, rediscovered and remapped. | Smith | 2022-09-28
2022-09-26 | 2650 |  | 2020-04-14 | Online | 60 |  | SCE Deerick Sta Ballfield | GREEN BEAR | 34.2029 | -117.0905 | 6019 | Arrowhead | 4421533E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Station was powercycled. Added cell, updated OS and Program, rediscovered and remapped. | Smith | 2022-09-28
2022-09-26 | 2664 |  | 2020-04-14 | Online | 60 |  | SCE Hilltop Blvd | LURING | 34.207 | -117.1123 | 6149 | Arrowhead | 1403121E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present; Data may not be up to date | Power-cycle, call WWG to collect all historical data needed. After WWG gives OK, fully update station OS/program/check for dual comms; Potentially replace battery or solar panel in case power issue is discovered; Calibrate if necessary | Station was powercycled. Added cell, updated OS and Program, rediscovered and remapped. | Smith | 2022-09-28
2022-09-19 | 2041 | SE087 | 2018-09-20 | Online | 10 |  | SCE Weldon | Canebrake | 35.6363 | -118.2496 | 2800 | Kernville | 2275350E | Hardware - Cell modem | Comms down since 9/14/22 | Needs Power-cycle | Power-cycled | Brad | 2022-09-27
2022-09-26 | 3064 |  | 2020-09-15 | Online | 60 |  | SCE Webster Ave | HAMMOCK | 33.7937 | -117.2438 | 1571 | Menifee | 4413115E | 60-min power-cycling | Station stuck on hourly power-cycling mode - Power issue may be present | Power-cycle, potentially replace battery or solar panel in case power issue is discovered | Steve fixed and added Modem | Steve | 2022-09-27
2022-05-09 | 2987 | SE937 | 2020-08-11 | Online | 10 |  | SCE Starbuck Cir | FULLBACK | 33.5818 | -117.2421 | 1188 | Wildomar | 4169716E | Frequently Missed Comm | Station communications drop in and out throughout the day, occasionally out for few hours at a time; Needs Dualcomms upgrade (Cell modem) | Needs Dualcomms upgrade (Cell modem) | Cell modem tested for dual comms but had to bad of a signal. Satellite power cable was bad so was replaced which seemed to help improve comms. | Davis | 2022-09-26
2022-09-20 | 3525 | 527SE | 2022-04-07 | Online | 10 |  | SCE Ray St | NATIONS | 33.7776 | -117.1541 | 1550 | Menifee | 4358064E | Hardware - Satellite | Comms down since 9/19/22 | Power-cycle, swap to, or install cell modem; Call WWG to troubleshoot | Power cycled to restore communications - added cell modem for dual redundancy | Davis | 2022-09-26
2022-09-21 | 2848 | SE838 | 2020-06-13 | OFFLINE | 10 |  | OAKDALE | 33.7233 | -117.2355 | 1787 | Menifee | 4528935E | Hardware - Satellite | Comms down since 9/12/22; no power issue | Power-cycle, Call WWG to troubleshoot | Pings, no comms with logger | Power-cycled, added cell modem | Davis | 2022-09-26
2022-09-20 | 3409 | 428SE | 2021-09-15 | Online | AP |  | SCE Carl Lake | SODA SPRINGS | 36.2402 | -118.7433 | 4430 | Tulare | 2105026E | Hardware - Satellite | Comms down since 9/18/22 | Power-cycle, Call WWG to troubleshoot | Replaced satellite terminal | Wright | 2022-09-23
2022-09-21 | 3021 | SE276 | 2020-07-14 | Online | AP |  | SCE Lady Linda | ORION | 34.486 | -118.5443 | 1296 | Valencia | 949069E | Hardware - Satellite | Comms down since 9/19/22 | Power-cycle, Call WWG to troubleshoot | Added cell modem to improve coms. | Colligan | 2022-09-22
2022-09-21 | 2218 | SE199 | 2019-04-16 | Online | 10 |  | SCE Kanan Rd | MULHOLLAND | 34.1098 | -118.8046 | 1431 | Thousand Oaks | 2240093E | Hardware - Cell modem | Comms down since 9/12/22 | Power-cycle, Call WWG to troubleshoot | Power-cycled to fix comms | Spinowitz | 2022-09-22
2022-08-25 | 3002 | SE887 | 2020-07-13 | Online | AP |  | SCE S Spring Meadow Dr | BOBBY | 34.0546 | -117.8815 | 665 | Covina | 1528406E | Hardware - Satellite | Lost comms 8/17 | Power-cycle, Call WWG to troubleshoot. Potentially swap sat equipment | Power-cycled, added cell modem | Colligan | 2022-09-20
2022-09-06 | 2080 | SE048 | 2018-08-05 | Online | 10 |  | SCE Balcom Canyon | BALCOM | 34.3545 | -118.9897 | 345 | Ventura | 4335115E | Hardware - Communications | Lost comms 8/26/22 | Power cycle and call WWG to troubleshoot. | Resolved with a power cycle to restore comms - troubleshoot extended but no other issues found | Spinowitz | 2022-09-19
2022-08-10 | 2031 | SE044 | 2018-08-05 | Online | AP |  | SCE South Mountain | BALCOM | 34.3346 | -119.0099 | 1980 | Ventura | 4551912E | Hardware - Wiring | Temp/RH and SolarRad sensors stopped working since visited on 8/10/22 for calibration. | Bring the calibration kit and wire the temp/rh on it's datalogger to confirm sensor is good. Then Check if Temp/RH & Solar Rad power wires (red) are located in the 12 V port. Check for loose wires. Check for loose green terminals in the datalogger. By-pass "terminal block" and wire sensors straight in the datalogger. | Self resolved; No new issues seen since 9/1 | N/A Self Resolved | 2022-09-19
2022-08-29 | 3278 | 293SE | 2021-08-05 | Online | AP |  | SCE Javon Peak | RED MOUNTAIN | 34.3425 | -119.3994 | 781 | Ventura | 1138752E | Hardware - Communications | Lost comms 8/15/22 | Power cycle and call WWG to troubleshoot. | Resolved with a power cycle to restore comms - troubleshoot extended but no other issues found | Spinowitz | 2022-09-19
2022-09-08 | 3295 | 289SE | 2021-08-04 | Online | AP |  | SCE Gold Canyon Access Rd | DEVERS-BANNING-WINDPARK | 33.9494 | -116.6709 | 2193 | Palm Springs | 2312565E | Hardware - Communications | Lost Comms 9/6/22, pings but no connection | Power cycle and call WWG to troubleshoot. | Replaced sat power cable | Colligan | 2022-09-14
2022-04-12 | 2998 | SE935 | 2020-08-10 | Online | AP |  | SCE Camino Estribo | CRUZ | 33.4815 | -117.1454 | 1024 | Wildomar | 2352462E | Freqently Missed Collections | Station communications drop in and out throughout the day, occasionally out for few hours at a time | Replaced satellite power cable, added cellular modem for redundancy | Replaced satellite power cable, added cellular modem for redundancy | Davis | 2022-09-09
2022-09-08 | 2965 | 014SE | 2020-09-16 | Online | AP |  | SCE Esterina Way | PANCAKE | 33.9976 | -118.3837 | 209 | Santa Monica | 4501131E | Hardware - Communications | Lost Comms 9/3/22, no pings or connection | Power cycle and call WWG to troubleshoot. | Power-cycled station which seemed to fix the problem. | Spinowitz | 2022-09-09
2022-09-06 | 2066 | SE066 | 2018-07-09 | Online | 10 |  | SCE Cerro Villa Heights | HANDY | 33.8288 | -117.8014 | 550 | Santa Ana | 1535502E | Hardware - Communications | Lost comms 8/27/22 | Power cycle and call WWG to troubleshoot. | Template re-uploaded to cell modem and station power-cycled which seemed to fix the problem. | Spinowitz | 2022-09-09
2022-09-06 |  | 440SE | 2021-09-16 | Online | AP |  | SCE Sequoia NF | MAHOGANY | Tulare | 4601355E | Hardware - Communications |  |  | Hardware - Satellite | Lost comms 8/28/22 | Power cycle and call WWG to troubleshoot. | Adjusted modem for better RSSI, power-cycled. | Wright | 2022-09-09
2022-09-08 | 2273 | SE161 | 2019-03-27 | Online | 10 |  | SCE Polly Butte | CORSAIR | 33.6918 | -116.9432 | 4990 | Menifee | 1996779E | Hardware - Communications | Lost Comms 9/8/22, pings but no connection | Power cycle and call WWG to troubleshoot. | Power-cycled, updated OS | Davis | 2022-09-09
2022-09-06 | 2874 | SE961 | 2020-08-25 | Online | AP |  | SCE Murrieta Rd | DEACON | 33.7559 | -117.2065 | 1411 | Menifee | 4535207E | Hardware - Satellite | Cannot connect with satellite | check port forwarding, replace sat equipment, confirm wiring | Reseated SIM card, Power cycled satellite terminal, confirmed connection; May have failing 10/100 ethernet port if issues persist | Smith | 2022-09-07
2022-08-26 | 3067 | SE968 | 2020-08-27 | Online | AP |  | SCE Park Ave | KIRBY | 33.759 | -116.9504 | 1644 | Menifee | 4552476E | Hardware - Satellite | Lost comms | Power cycle and call WWG to troubleshoot. | Swapped out satellite power cable and datalogger to resolve frequently missed collections | Davis | 2022-09-07
2022-08-29 | 3184 | 227SE | 2021-07-15 | Online | AP |  | SCE Montgomery Creek | SADDLEBACK | 33.9088 | -116.8768 | 2200 | Redlands | 256839S | Hardware - Battery/Comms | Lost comms 8/10/22 due to dying battery | Power cycle to restore comms. Address potential poor siting/location. Find out if there is a shading issue. Potentially replace battery | Replaced solar panel, sat cable and battery which seemed to fix the issue. | Smith | 2022-09-07
2022-08-09 | 3583 | 558SE | 2022-05-05 | Online | AP |  | SCE Chalon Rd | Chalon | 33.8252 | -117.3715 | 1645 | Menifee | 1668611E | Hardware - Temp/RH | Station is reading bad RH values. | Return with a new cable for EE181 (temp/RH) sensor. | Ben found that there was a loose wire so he tightened it up which fixed the problem. | Davis | 2022-08-29
2022-08-09 | 2029 | SE064 | 2018-07-19 | Online | 10 |  | BLUE CUT / VERDEMONT | Foothill | 4611612E | Hardware - Battery | Station is giving bad values since it died and came back. |  |  | Hardware - Battery | Station is giving bad values since it died and came back. | Return with a new lead alkaline battery and battery charger cable. | Replaced battery and leads | Davis | 2022-08-29
2022-08-17 | 2157 | SE213 | 2019-04-19 | Online | 10 |  | SCE Copper Canyon | TICO | 34.4355 | -119.3305 | 860 | Ventura | 2068425E | Hardware - modem | Modem and datalogger aren't communicating even though modem is working. | Power-cycle. Call WWG to troubleshoot | Tech powercycled station and station is consistently on and reachable, although it is inconsistent on collections. Tech did not have an external but it is recommended. Also worth noting it as a potential dual comms station. | Spinowitz | 2022-08-25
2022-08-10 | 2031 | SE044 | 2018-08-05 | Online | AP |  | SCE South Mountain | BALCOM | 34.3346 | -119.0099 | 1980 | Ventura | 4551912E | Hardware - Wiring | Temp/RH and SolarRad sensors stopped working since visited on 8/10/22 for calibration. | Bring the calibration kit and wire the temp/rh on it's datalogger to confirm sensor is good. Then Check if Temp/RH & Solar Rad power wires (red) are located in the 12 V port. Check for loose wires. Check for loose green terminals in the datalogger. By-pass "terminal block" and wire sensors straight in the datalogger. | fixed wiring issue | Spinowitz | 2022-08-24
2022-08-09 | 2440 | SE344 | 2019-06-24 | Offline | AP |  | SCE Big Morongo Canyon Rd | MORONGO | 34.0813 | -116.5973 | 3523 | Yucca Valley | 342690S | Hardware - Battery | Battery died 8/4/22 | Power-cycle to fix bad data, check if battery is charged back up, potentially replace - Call WWG. Bad CH200 (9018) confirmed.CH200 is being sent to WWG. Battery discharged confirmed. Batt (RB52DU260067) will be charged and used as spare. | CH200 (11174) replaced. Battery (RB52DQ140069) replaced. | Smith | 2022-08-19
2022-08-09 | 2375 | SE348 | 43642 | Online | AP |  | SCE Little Morongo Rd | KICKAPOO TRAIL | 34.1033 | -116.53 | 3040 | Yucca Valley | 2154154E | Hardware - CH200 / Battery | Station is giving bad EE181 values since batt spiked low (9.9 V) on 8/9/22 and came back. | Return with a volt meter to check battery voltage. Unplug solar pannel power wire and call WWG to check batt voltage. Check output CH200 12 v to confrim CH200 is working ok. | 1st visit 8/16/22. Temp values was fixed by O.S update. Station was found OFFline (7.8 V batt). 2nd visit 8/19/22 Baterry replaced. | Smith | 2022-08-19
2022-07-18 | 2716 | SE695 | 2020-04-25 | Online | AP |  | SCE Orchard-2 Rd | LOCKNER | 33.8134 | -116.9613 | 1512 | Menifee | 2302417E | Hardware - Satellite Terminal, Solar Panel | Solar panel is cracked, working but may not be fully efficient. Satellite terminal failed, removed, Currently running cellular only. | Replace satellite terminal and solar panel | Replaced solar panel and satellite modem | Smith | 2022-08-18
2022-08-08 | 2866 | SE866 | 2020-06-23 | Online | AP |  | SCE Cajon Wash | ROI-TAN | 34.1362 | -117.3527 | 1297 | Redlands | 1826240E | Hardware - Satellite Terminal | Comms did not recover after Satellite outage; no signs of power issue | Power-cycle first, then further troubleshoot with WWG to determine if satellite equipment needs to be replaced. | 1st visited 8/16/22. Partial fixed: Installed Cell modem SCE-10009-60 (Station is temporarly running cell only), bad POE detected. 2nd visited 8/17/22 POE replaced. Set to Dual Comm. | Smith | 2022-08-17
2022-08-08 | 2799 | SE770 | 2020-05-13 | Online | AP |  | SCE Point Vicente | AMBERSKY | 33.7428 | -118.4099 | 152 | South Bay | 482833E | Hardware - Satellite Terminal | Comms did not recover after Satellite outage; no signs of power issue | Power-cycle first, then further troubleshoot with WWG to determine if satellite equipment needs to be replaced. | Fixed Temp issue - rewiring; Fixed cell / sat connection issue - power cycle | Spinowitz | 2022-08-15
2022-08-08 | 2752 | SE762 | 2020-05-12 | Online | AP |  | SCE McLaughlin Rd | ROS | 33.7357 | -117.1306 | 1540 | Menifee | 312520S | Hardware - Satellite Terminal | Comms did not recover after Satellite outage; no signs of power issue | Power-cycle first, then further troubleshoot with WWG to determine if satellite equipment needs to be replaced. | Station was powercycled which seemed to fix the problem. | Davis | 2022-08-12
2022-08-09 | 3625 | 611SE | 2022-07-14 | Online | AP |  | SCE Ballona Creek | LA CIENEGA-EL NIDO-TAHITI | 33.9659 | -118.4413 | 7 | Santa Monica | 12778663E | Hardware - Temp/RH Sensor + Wind Monitor | Station has given bad temp/RH values since 3 days after installed. | Bring a EE181 Temp/RH Sensor spare. Power-cycle to attempt to fix bad sensor values. Call WWG. Replace sensor if needed. | Replaced EE181, fixed the problem. | Spinowitz | 2022-08-11
2022-08-08 | 3614 | 594SE | 2022-06-27 | Online | AP |  | SCE Thornton Ranch Rd | NEWBURY-THOUSAND OAKS | 34.1599 | -118.8985 | 1122 | Thousand Oaks | 4743415E | Hardware - Satellite Terminal | Comms did not recover after Satellite outage; no signs of power issue | Power-cycle first, then further troubleshoot with WWG to determine if satellite equipment needs to be replaced. | Powercycled station which seemed to fix the problem. | Spinowitz | 2022-08-10
2022-08-08 | 2920 | SE857 | 2020-06-18 | Online | AP |  | SCE Corte Castillo | PARCO | 33.9886 | -117.4563 | 911 | Foothill | 1707005E | Hardware - Satellite Terminal | Comms did not recover after Satellite outage; no signs of power issue | Power-cycle first, then further troubleshoot with WWG to determine if satellite equipment needs to be replaced. | Station was powercycled which seemed to fix the problem. | Davis | 2022-08-10
2022-08-09 | 2140 | SE291 | 2019-05-30 | Online | 10 |  | SCE West Woolsey Canyon | BIG ROCK | 34.2417 | -118.6752 | 2090 | Thousand Oaks | 2107060E | Hardware - Cell modem | Comms failed and have not been able to communicate with the datalogger since 7/26/22 | Power-cycle, check wiring, call WWG to troubleshoot | Power-cycled | Spinowitz | 2022-08-10
2022-07-13 | 2974 | SE930 | 2020-08-06 | OFFLINE | AP |  | SCE Ely Mountain Rd | ROSEBUD | 37.1655 | -119.2891 | 5761 | Shaver Lake | 1771718E | Power Issue - Battery Discharged, Station Offline | Battery fully discharged in late 2021; Need to identify alternate location with no shading issues, or install AC power to station. Need up update datalogger and confirm comms with WWG | Station died in late 2021 due to winter weather conditions, did not self recover; Confirm station location is shaded or power issue present, relocate if alternate locatin is identified; Install AC power into station CH200, confirm data with WWG | Station was calibrated, OS updated, battery confirmed charge. Likely died from winter weather/low solar resource + AQ sensor additional power draw. AQ sensor was showing errors, pulled and sending to WWG | Spinowitz | 2022-08-03
2022-07-11 | 3601 | 595SE | 2022-06-28 | Online | AP |  | SCE Camarillo St | Camgen-Colonia | 34.175 | -119.0432 | 57 | Ventura | 4032153E | Hardware - Battery | Station has died due to low battery | Recharge or replace battery, Call WWG to confirm | Fixed internal solar panel wiring and replaced battery. | Colligan | 2022-08-03
2022-07-21 | 3459 | 498SE | 2022-03-23 | OFFLINE | AP |  | SCE WW School | CUTHBERT | 34.0236 | -118.7883 | 105 | Thousand Oaks | 4844502 | Hardware - Satellite Terminal or Datalogger | Station lost communications 7/14/22, no power issue before stopping. Satellite terminal appears to be offline | Check station LED's to see if station is powered up and running program. Check datalogger 10/100 ethernet port and PoE LED. Try to connect to satellite terminal to verify status, # bars, RSSI. Power cycle. Replace terminal if necessary | SAT terminal replaced (Original SCE-3598) | Wright | 2022-08-02
2022-07-27 | 2105 | SE096 | 2018-09-26 | Online | 10 |  | SCE Santiago Canyon | ATENTO | 33.7271 | -117.6495 | 1140 | Saddleback | 2257518E | Communications - Cellular Signal | Station communications drop in and out throughout the day, occasionally out for few hours at a time | Record or call WWG to record current cellular metrics; Replace internal paddle antenna with external omni antenna; Reboot station and record new cellular metrics after 5 minutes of online time; If signal does not improve, may need to convert to satellite only station | External antenna was added to the station which boosted the signal enough to be able to connect and see data. | Spinowitz | 2022-08-01
2022-07-13 | 3163 | 283SE | 2021-08-03 | OFFLINE | AP |  | SCE Portal Forebay | MT. GIVENS | 37.3186 | -119.0662 | 7201 | Shaver Lake | No Pole Tag # | Power Issue - Battery Discharged, Station Offline | Battery fully discharged in late 2021; Need to identify alternate location with no shading issues, or install AC power to station. Need up update datalogger and confirm comms with WWG | Station died in late 2021 due to winter weather conditions, did not self recover; Confirm station location is shaded or power issue present, relocate if alternate locatin is identified; Install AC power into station CH200, confirm data with WWG | Replaced satellite | Colligan | 2022-07-29
2022-04-20 | 2024 | SE024 | 2018-05-02 | Online | 10 |  | SCE Laguna Beach 4 | ACRES | 33.5343 | -117.7542 | 900 | Saddleback | 1220779E | Hardware - Pyranometer | Solar Rad reading 0 | Replace Solar Rad sensor or remove and update program for no solar rad | Replaced bad SolarRad cable | Spinowitz | 2022-07-20
2022-07-11 | 2896 | SE848 | 2020-06-17 | Online | AP |  | SCE Myrl Dr | JUBILEE | 33.9433 | -116.9842 | 2598 | Redlands | 4494709E | Hardware - Satellite Terminal or Datalogger Ethernet Port | Datalogger calibration issues. Failed ethernet port. | Replace datalogger. | Datalogger replaced. | Smith | 2022-07-18
2022-04-12 | 3497 | 459SE | 2021-10-06 | Online | AP |  | SCE Europa Village | PAUBA-TRITON | 33.522 | -117.0874 | 1283 | Wildomar | 4130677E | Station communications drop in and out throughout the day, occasionally out for few hours at a time |  |  | Self Resolved | Smith | 2022-07-18
2022-04-12 | 2304 | SE189 | 2019-04-10 | Online | AP |  | SCE Johnstone Peak | BRYDON | 34.1536 | -117.7979 | 2726 | Covina | 4491472E | Station communications drop in and out throughout the day, occasionally out for few hours at a time |  |  | Self Resolved | Spinowitz | 2022-07-15
2022-01-21 | 2634 | SE631 | 2020-04-03 | Online | AP |  | SCE Oak Grove Dr | DEVILS GATE | 34.1919 | -118.1762 | 1042 | Monrovia | 4548848E | Hardware - Wind Monitor | Wind Speed reading 0 at all times | Bring spare wind monitor to station; Inspect wind monitor and check wiring. Calibrate or replace sensor if necessary. Call WWG to confirm issue | Replaced Wind Monitor | Davis | 2022-07-14
2022-05-19 | 3012 | SE900 | 2020-07-17 | Online | AP |  | SCE E Francisquito Ave | ANN | 34.0503 | -117.9138 | 455 | Covina | 1243311E | Hardware - Satellite | Station lost communication 5/17/22; No signs of battery/power issue | Power-cycle, check modem interface to confirm online, 5 bars, RSSI, port-forwarding; Call WWG to confirm | X2n reboot unsuccessful, last RSSI: 114; SC47055 | Colligan | 2022-07-14
2021-12-14 | 3152 | 208SE | 2021-07-12 | OFFLINE | AP |  | SCE Lake George | AUTUMN | 37.604 | -119.0127 | 9090 | Bishop | 4464188E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Self resolved - late enough in year to power | N/A Self Resolved | 2022-07-13
2022-05-19 | 3490 | 482SE | 2021-10-15 | OFFLINE | AP |  | SCE Lopez Canyon Rd | LOPEZ | 34.3087 | -118.3931 | 1560 | Valencia | 2023678E | Hardware - Satellite | Station lost communication 5/16/22; No signs of battery/power issue | Power-cycle, check modem interface to confirm online, 5 bars, RSSI, port-forwarding; Call WWG to confirm | Replaced satellite terminal with spare SCE-S10026-2. Replaced PoE, sat power cable, temp/rh, temp/rh wiring, temp/rh radiation shield. | Smith | 2022-07-13
2022-04-12 | 2211 | SE147 | 2019-02-27 | OFFLINE | 10 |  | SCE Sleepy Valley | DAVENPORT | 34.5035 | -118.3759 | 2143 | Valencia | 4308811E | Hardware - Cell modem | Lost comms 4/11/22, no signs of power issue | Power-cycle, Call WWG to confirm, check modem interface, possibly replace | Relocated ~5 spans West | N/A Self Resolved | 2022-07-12
2021-12-14 | 2374 | SE389 | 2019-07-18 | OFFLINE | AP |  | SCE Nelson Creek | MAHOGANY | 36.156 | -118.6238 | 5955 | San Joaquin Valley | 4289793E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | DO NOT VISIT UNTIL AC POWER OR RELOCATION IS CONFIRMED. Call WWG to troubleshoot. | Station was moved to nearby location ~ 1 mile north. Same circuit, station high on pole to avoid any shading or line of sight issue | N/A Self Resolved | 2022-07-12
2021-12-14 | 2494 | SE481 | 2019-11-19 | Online | 10 |  | SCE Krbt Station Rd | HI LINE | 33.3598 | -118.376 | 1465 | Catalina | 4733693E | Hardware - Datalogger, Pyranometer | Datalogger calibration errors - randomly loses connection, wont send data, or bad temp/rh, batt volt values. Bad Solarrad, needs to be replaced | Update datalogger OS to version 5.01, confirm connectivity and errors cleared from datalogger with WWG. Replace Solarrad | Replaced bad SolarRad, Updated logger to 5.01, power retrofitted to new lithium battery, updated CH200 settings | Smith | 2022-07-12
2021-12-28 | 2664 | SE648 | 2020-04-14 | OFFLINE | AP |  | SCE Hilltop Blvd | LURING | 34.207 | -117.1123 | 6149 | Arrowhead | 1403121E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Reuploaded lost logger program from weather-related dead battery. Updated OS. | N/A Self Resolved | 2022-07-12
2022-03-14 | 2735 | SE705 | 2020-04-29 | Online | AP |  | SCE Wolcott Way | GUITAR | 34.4267 | -118.6379 | 968 | Valencia | 4244921E | Hardware - Satellite terminal | Satellite comms failed 3/5/22. No signs of battery issue. | Power-cycle, Call WWG to confirm and further troubleshoot | Power-cycled, restored comms | N/A Self Resolved | 2022-07-12
2022-03-14 | 3058 | 032SE | 2020-09-21 | Online | AP |  | SCE W Country Line Rd | CALIMESA | 34.0039 | -117.0836 | 2171 | Redlands | 2311716E | Hardware - Satellite terminal | Satellite comms failed 2/19/22. No signs of battery issue. | Power-cycle, Call WWG to confirm and further troubleshoot | Power-cycled, restored comms | N/A Self Resolved | 2022-07-12
2022-06-03 | 3288 | 362SE | 2021-08-26 | Online | AP |  | SCE Fordyce Rd | THACHER | 34.4576 | -119.2149 | 854 | Ventura | 1425263E | High Qloss / Battery nearing fully discharged | Station qloss is rising to the point the station may go offline due to low battery volatage. Station may go online/offline cycle if battery cannot gain enough charge over time | Check for location or shading issue causing low solar resource. Check Solar panel wiring, CH200 wiring and programming. Clean solar panel, move station for better sunlight if necessary. | Self Resolved | N/A Self Resolved | 2022-07-12
2022-05-25 | 3301 | 315SE | 2021-08-11 | Online | AP |  | SCE Lancer Way | TALLEY | 34.2132 | -118.8708 | 788 | Thousand Oaks | 1383635E | Hardware - Satellite | Station lost communication 5/14 | Power-cycle, check modem interface to confirm online, 5 bars, RSSI, port-forwarding; Call WWG to confirm | Power-cycled. Installed cellmodem (SCE-1009-156) , 6_3DualComm updated, Good CELL signal (5 bars, RSRP -80, RSRQ -15) | N/A Self Resolved | 2022-07-12
2022-03-29 | 3460 | 501SE | 2022-03-23 | Online | AP |  |  | HELICOPTER | 33.8011 | -117.184 | 1452 | Menifee | 77058S | Drained Battery / Low Solar Resource | Lost comms 3/28/22, low battery readings | Check wirings, check voltage to and from solar, power-cycle, call WWG to troubleshoot | Fixed wiring error | N/A Self Resolved | 2022-07-12
2022-07-13 | 3337 | 358SE | 2021-08-25 | Online | AP |  | SCE Green Earth | SHEFFIELD | 34.4172 | -119.5236 | 185 | Santa Barbara | 2024119E | Power Issue - Battery Discharged, Station on Hourly Mode | Battery near fully discharged late May 2022; Possibly a shading issue or local power issue (solar panel/battery related) | Need to determine why station lost power in May 2022; Check location for shading issues, resolve by adjusting solar panel or moving station if necessary; check battery and solar panel voltage and wiring. Update datalogger if necessary, confirm comms with WWG | Self Resolved - WWG Monitoring for power issue | Colligan | 2022-07-05
2022-06-21 | 2802 | SE801 | 2020-05-22 | Online | AP |  | SCE Summit Valley | BUCKTHORN | 34.3666 | -117.3212 | 3332 | Victorville | 4265933E | Hardware - Satellite | No communication with station as of 6/13/22 | Power-cycle, call WWG, check cable, PoE | Replaced satellite power cable | Smith | 2022-06-23
2022-04-12 | 2178 | SE230 | 2019-04-29 | Online | 10 |  | SCE Sexton Canyon | SEXTON | 34.2945 | -119.2312 | 559 | Ventura | 1795600E | Station communications drop in and out throughout the day, occasionally out for few hours at a time |  |  | Self Resolved | Steve Smith | 2022-06-17
2022-07-15 | 3558 | 547E | 2022-04-27 | OFFLINE | AP |  | SCE Wolfie | MIRA LOMA-VINCENT | 34.4329 | -118.0982 | 3972 | Antelope Valley | 7028374 | Hardware - Cell modem, wiring | Cell modem switches on and off like there is some sort of wiring error | Check wiring. Potentially replace power relay | Satellite terminal replaced, removed cellular modem | Steve Smith | 2022-06-17
2022-01-17 | 3441 | 425SE | 2021-09-14 | OFFLINE | AP |  | SCE San Bern NF | JOB | 34.2615 | -117.3576 | 4508 | Arrowhead | 4526778E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Replaced Satellite terminal with spare SCE-S10026-7 | Davis | 2022-06-06
2021-12-17 | 3445 | 407SE | 2021-09-09 | OFFLINE | AP |  | SCE Chestnut Ct | TENNECO | 34.8374 | -119.1452 | 6218 | Antelope Valley | 2038166E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Recharged drained battery, swapped for new battery at station. Cleaned solar panel, checked satellite RSSI. Resent OS/Program. No shading issues, power was weather related | Smith | 2022-06-06
2022-04-21 | 2069 | SE031 | 2018-06-24 | Online | 10 |  | SCE Topanga Oaks | SYLVIA | 34.0972 | -118.5994 | 847 | Thousand Oaks | 340149E | Hardware - Temp/RH Sensor + Wind Monitor | Temp/RH sensor readings bad since 4/2/22, Wind speed stuck at 0 since 4/6/22 | Power-cycle station, double-check wirings, Call WWG to troubleshoot over phone; Replace both sensors | EE181 Cable, Wind monitor sensor + cable replaced. Due to Rodent damage | Colligan | 2022-06-03
2022-06-02 | 2788 | SE756 | 2020-05-11 | Online | AP |  | SCE College Canyons | TIPS | 34.3994 | -118.5735 | 1337 | Valencia | 4450298E | Hardware - Satellite | Station lost communication 6/1/22; No signs of battery/power issue | Power-cycle, check modem interface to confirm online, 5 bars, RSSI, port-forwarding; Call WWG to confirm | Rewired loose Relay terminal 2 | Colligan | 2022-06-03
2022-05-19 | 2878 | 047SE | 2020-09-24 | OFFLINE | AP |  | SCE Palisades Point | KUFFEL | 34.2583 | -117.1759 | 5270 | Arrowhead | 452954E | Hardware - Satellite | Station lost communication 5/15/22; No signs of battery/power issue | Power-cycle, check modem interface to confirm online, 5 bars, RSSI, port-forwarding; Call WWG to confirm | Power cycled station | Smith | 2022-06-03
2022-01-17 | 3445 | 407SE | 2021-09-09 | OFFLINE | AP |  | SCE Chestnut Ct | TENNECO | 34.8374 | -119.1452 | 6218 | Antelope Valley | 2038166E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Swapped battery and reuploaded lost datalogger program | Colligan | 2022-06-03
2022-03-31 | 3067 | SE968 | 2020-08-27 | Online | AP |  | SCE Park Ave | KIRBY | 33.759 | -116.9504 | 1644 | Menifee | 4552476E | Hardware - Satellite | Lost comms 3/30/22, no signs of battery/power issue | Power-cycle, call WWG to confirm and further troubleshoot | Might be related to the ViaSat maintenance on 3/30/22; SC46690 | Spinowitz | 2022-06-01
2022-05-25 | 3477 | 464SE | 2021-10-12 | OFFLINE | AP |  | SCE Joshua Rd | DEVERS-SAN BERNARDINO | 33.9302 | -116.6897 | 1470 | Palm Springs | 4503012E | Hardware - Satellite | Station lost communication 5/22 | Power-cycle, check modem interface to confirm online, 5 bars, RSSI, port-forwarding; Call WWG to confirm | Power-cycled to fix satellite, installed cell modem, updated to dualcomms station | Spinowitz | 2022-06-01
2022-07-11 | 3558 | 547E | 2022-04-27 | OFFLINE | AP |  | SCE Wolfie | MIRA LOMA-VINCENT | 34.4329 | -118.0982 | 3972 | Antelope Valley | 7028374 | Hardware - Satellite Terminal or Datalogger Ethernet Port | Communication lost 6/30/22 | Power-cyvcle, check RSSI, terminal status, call WWG to troubleshoot | Switched to cell modem set up | Spinowitz | 2022-06-01
2021-12-28 | 2701 | SE727 | 2020-05-05 | OFFLINE | AP |  | SCE Huntington Lake Rd | RANCHERIA | 37.2532 | -119.1655 | 6968 | Shaver Lake | 1031019E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Replaced battery | Colligan | 2022-05-26
2022-02-16 | 2711 | SE721 | 2020-05-01 | Online | AP |  | SCE Old Mammoth Rd | CRAWFORD | 37.6287 | -118.9887 | 8004 | Bishop | 4551559E | Hardware - Temp/RH Sensor | Temp/RH sensor giving bad values due to station dying | Power-cycle, Call WWG to confirm | Replaced Temp/RH sensor | Spinowitz | 2022-05-26
2022-01-05 | 2795 | SE807 | 2020-05-26 | OFFLINE | AP |  | SCE Kaiser Ridge | MT. GIVENS | 37.2692 | -119.1242 | 8276 | Shaver Lake | 1807072E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Calibrated, confirmed best location, updated OS /PRogram | Colligan | 2022-05-26
2022-03-31 | 2998 | SE935 | 2020-08-10 | Online | AP |  | SCE Camino Estribo | CRUZ | 33.4815 | -117.1454 | 1024 | Wildomar | 2352462E | Hardware - Satellite | Lost comms 3/30/22, no signs of battery/power issue | Power-cycle, call WWG to confirm and further troubleshoot | Might be related to the ViaSat maintenance on 3/30/22; SC46691 | N/A Self Resolved | 2022-05-25
2022-05-25 | 3464 | 499SE | 2022-03-23 | OFFLINE | AP |  | SCE Orange Ave | HELICOPTER | 33.8157 | -117.1825 | 1538 | Menifee | 4697049E | Hardware - Satellite | Station lost communication 5/24 | Power-cycle, check modem interface to confirm online, 5 bars, RSSI, port-forwarding; Call WWG to confirm | Power-cycled, replaced satellite power cable | Spinowitz | 2022-05-17
2022-05-25 | 3536 | 548SE | 2022-04-28 | OFFLINE | AP |  | SCE Backbone Trail | HORNTOAD | 34.0814 | -118.6452 | 2372 | Thousand Oaks | 4733764E | Hardware - Satellite | Station lost communication 5/19 | Power-cycle, check modem interface to confirm online, 5 bars, RSSI, port-forwarding; Call WWG to confirm | Replaced sat terminal with spare SCE-S10026-1; Sending old terminal to WWG for warranty replacement | Spinowitz | 2022-05-17
2022-05-05 | 2866 | SE866 | 2020-06-23 | OFFLINE | AP |  | SCE Cajon Wash | ROI-TAN | 34.1362 | -117.3527 | 1297 | Redlands | 1826240E | Hardware - Satellite Terminal | Comms stopped 4/25/22 5PM; Battery good | WWG waiting for ViaSat Response; Call WWG on site to review troubleshooting; Power-cycle station, check Ethernet port LEDS, check terminal connection, # bars, RSSI, status | Steve rebooted, resent OS/Program. Satellite came online after. RSSI ~90 | Smith | 2022-05-09
2022-04-21 | 3301 | 315SE | 2021-08-11 | Online | AP |  | SCE Lancer Way | TALLEY | 34.2132 | -118.8708 | 788 | Thousand Oaks | 1383635E | Hardware - Satellite | Satellite comms lost 4/20/22, no signs of power/battery issue, terminal pings, but no comms with station, last RSSI: 100 | Power-cycle, Call WWG to confirm/troubleshoot, possibly replace sat modem, cable, and/or PoE | Self Resolved - Comms came back on their own. Rebooted on-site | Colligan | 2022-05-02
2022-05-25 | 2061 | SE042 | 2018-07-08 | OFFLINE | 10 |  | SCE Oak Spring Canyon | PYTHON | 34.4234 | -118.4153 | 1575 | Valencia | 4466687E | Hardware - Cellular Modem | Station Modem is reachable, cannot connect to datalogger or collect data | Check modem LED's, wiring, connection to datalogger. Check datalogger program and OS. Power cycle station. Troubleshoot with WWG | Manually updated modem firmware and template; power cycled station | Colligan | 2022-04-29
2022-02-08 | 2086 | SE069 | 2018-09-06 | Online | 10 |  | SCE Sage | WINERY | 33.5739 | -116.9633 | 1925 | Wildomar | 2225226E | Hardware - Pyranometer | Solar rad reading ~50% low, needs replacement | Replace solar rad sensor, call WWG to confirm or recalibrate | swapped out bad pyranometer | Spinowitz | 2022-04-25
2021-12-20 | 2745 | SE707 | 2020-04-29 | Online | AP |  | SCE Dalbo St | SPINKS | 34.1467 | -117.9511 | 629 | Monrovia | 791585E | Hardware - Wind Monitor | Bad wind direction | Replace sensor | Replaced missing screw in wind monitor, g2g | N/A Self Resolved | 2022-04-25
2021-12-28 | 3125 | 152SE | 2021-06-18 | Online | AP |  | SCE Bel Air | HILTON | 34.0831 | -118.4227 | 414 | Santa Monica | 4467155E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Replaced battery; Re-sent datalogger program that was lost; Re-wired loose power wire. | Spinowitz | 2022-04-25
2022-05-25 | 2285 | SE464 | 2019-10-01 | Online | AP |  | SCE Caliente Spring | VIENTO | 35.2998 | -118.5943 | 1446 | Tehachapi | 678636E | Hardware - Charging regulator | CH200 bad readings | Check out sensor wiring, cable, sensorhead connection. Determine if sensor needs to be replaced; power cycle station | Uploaded unique program to run CH200 off of C1 port instead of failed C3. | Colligan | 2022-04-21
2022-04-12 | 2788 | SE756 | 2020-05-11 | OFFLINE | AP |  | SCE College Canyons | TIPS | 34.3994 | -118.5735 | 1337 | Valencia | 4450298E | Hardware - Satellite terminal | Lost comms 4/2/22, no signs of power issue | Power-cycle, Call WWG to confirm, check modem interface, possibly replace | Sagehorn visit 4/20 - Replaced PoE Injector to power sat terminal | Sagehorn | 2022-04-20
2022-06-03 | 2714 | SE692 | 2020-04-24 | Online | AP |  | SCE Boosey Rd | PYLE | 34.3791 | -119.0279 | 457 | Ventura | 4628633E | High Qloss / Battery nearing fully discharged | Station qloss is rising to the point the station may go offline due to low battery volatage. Station may go online/offline cycle if battery cannot gain enough charge over time | Check for location or shading issue causing low solar resource. Check Solar panel wiring, CH200 wiring and programming. Clean solar panel, move station for better sunlight if necessary. | Self Resolved | Spinowitz | 2022-04-15
2021-12-14 | 2381 | SE361 | 2019-07-02 | OFFLINE | AP |  | SCE Tramway Rd | TRAM | 33.8429 | -116.6073 | 2200 | Palm Springs | 4507505E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | DO NOT VISIT UNTIL AC POWER OR RELOCATION IS CONFIRMED. Call WWG to troubleshoot. | Swapped bad CH200 | N/A Self Resolved | 2022-04-13
2022-04-12 | 2875 | 031SE | 2020-09-21 | OFFLINE | AP |  | SCE Terrace View Dr | DOMIC | 34.0383 | -117.3386 | 1045 | Redlands | 1239999E | Hardware - Satellite terminal | Lost comms 4/11/22, no signs of power issue | Power-cycle, Call WWG to confirm, check modem interface, possibly replace | Swapped out bad datalogger due to bad Ethernet port | Smith | 2022-04-13
2022-07-11 | 3045 | 069SE | 2020-10-26 | OFFLINE | AP |  | SCE Gould Canyon | HASKELL | 34.208 | -118.1886 | 1301 | Monrovia | 4452547E | Hardware - Satellite Terminal or Datalogger Ethernet Port | Communication lost 7/5/22 | Power-cyvcle, check RSSI, terminal status, call WWG to troubleshoot | Power-cycled, updated datalogger OS | N/A Self Resolved | 2022-04-12
2022-03-31 | 2987 | SE937 | 2020-08-11 | Online | AP |  | SCE Starbuck Cir | FULLBACK | 33.5818 | -117.2421 | 1188 | Wildomar | 4169716E | Hardware - Satellite | Lost comms 3/30/22, no signs of battery/power issue | Power-cycle, call WWG to confirm and further troubleshoot | Might be related to the ViaSat maintenance on 3/30/22; SC46692 | N/A Self Resolved | 2022-04-06
2022-06-03 | 3351 | 365SE | 2021-08-26 | Online | AP |  | SCE Boiling Point | SHOVEL | 34.5232 | -118.2535 | 3332 | Antelope Valley | 4373702E | High Qloss / Battery nearing fully discharged | Station qloss is rising to the point the station may go offline due to low battery volatage. Station may go online/offline cycle if battery cannot gain enough charge over time | Check for location or shading issue causing low solar resource. Check Solar panel wiring, CH200 wiring and programming. Clean solar panel, move station for better sunlight if necessary. | Self Resolved | Spinowitz | 2022-04-06
2022-07-01 | 2483 | SE357 | 2019-06-30 | Online | AP |  | SCE Rim of the World | CEDAR GLEN | 34.2327 | -117.1713 | 5694 | Arrowhead | 4835813E | Hardware - Satellite Terminal or Datalogger Ethernet Port | Cannot connect to secondary satellite IP. Station failing secondarycomms local test; Likely bad satellite hardware or failed datalogger 10/100 ethernet port | Call WWG on site for troubleshooting specifics; Determine if you can reach the terminal interface, check RSSI, state, # of bars. Determine if 10/100 ethernet port LED's are behaving normally | Plugged black power cable back into POE | Sagehorn | 2022-04-01
2022-01-05 | 2569 | SE559 | 2020-03-09 | OFFLINE | AP |  | SCE Fredalba Rd | ROWCO | 34.2037 | -117.1423 | 5392 | Arrowhead | 1354143E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Swapped bad sat terminal (TI-5303) with spare SCE-S10026-4 (TI-6858) | Colligan | 2022-03-30
2022-03-14 | 3440 | 418SE | 2021-09-13 | Online | AP |  | SCE Gorman Post Rd | RIDGE | 34.7903 | -118.8275 | 3602 | Antelope Valley | 1433698E | Hardware - Satellite terminal | Satellite comms failed 3/11/22. No signs of battery issue. | Power-cycle, Call WWG to confirm and further troubleshoot | Power-cycled to restore comms | Davis | 2022-03-30
2022-05-05 | 3536 | 548SE | 2022-04-28 | OFFLINE | AP |  | SCE Backbone Trail | HORNTOAD | 34.0814 | -118.6452 | 2372 | Thousand Oaks | 4733764E | Hardware - Satellite Terminal | Comms stopped 5/4/22 1PM; Battery good | WWG waiting for ViaSat Response; Call WWG on site to review troubleshooting; Power-cycle station, check Ethernet port LEDS, check terminal connection, # bars, RSSI, status | Power Cycled station | Davis | 2022-03-30
2022-03-02 | 2964 | SE922 | 2020-07-30 | Online | 60 |  | SCE Bold Ventura Dr | TANAGER | 35.076 | -118.6242 | 3893 | Tehachapi | 1983869E | Hardware - Satellite terminal | Satellite comms failed 2/26/22. No signs of battery issue. | Power-cycle, Call WWG to confirm | Power-cycled, rewired PoE/Relay, restored comms | Sagehorn | 2022-03-23
2021-12-14 | 2744 | SE758 | 2020-05-12 | OFFLINE | AP |  | SCE Gold Arrow CP | TOLLHOUSE | 37.2344 | -119.1619 | 7060 | Shaver Lake | 4694302E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | DO NOT VISIT UNTIL AC POWER OR RELOCATION IS CONFIRMED. Call WWG to troubleshoot. | Sagehorn visit 11-19-21 - Installed 20W panel facing east for morning sun. Battery not replaced at the time; Self Recovered - Late enough in year to power on | Colligan | 2022-03-21
2022-03-16 | 2869 | SE879 | 2020-06-25 | Online | AP |  | SCE Island View Dr | CISCO | 34.2833 | -119.2513 | 397 | Ventura | 1748888E | Hardware - Satellite terminal | Satellite comms failed 3/15/22. No signs of battery issue. | Power-cycle, Call WWG to confirm and further troubleshoot | Power-cycled to restore comms | Spinowitz | 2022-03-18
2022-04-21 | 3356 | 338SE | 2021-08-23 | Online | AP |  | SCE The Old Rd | TAMBOURINE | 34.4935 | -118.6228 | 1194 | Valencia | 4398379E | Hardware - Wind Monitor | Wind speed reading 0 for 30 days | Power-cycle station, double-check wirings, Call WWG to troubleshoot over phone; Replace both sensors | Resent OS/Program. Power Cycled, data corrected itself | Davis | 2022-03-16
2022-01-21 | 3031 | 089SE | 2021-04-19 | Online | AP |  | SCE Pendleton Rd | OAK GLEN | 34.0402 | -117.0194 | 3041 | Redlands | 4512235E | Hardware - Cellular Modem | Cellular modem communications stopped 12-29-21; Power Okay. Station continuing to communicate via secondary (Satellite) comms | Check all station LED's including cellular modem power, signal, network lights. Check cellular antenna tightness and wire connections. Check station power. Compare station cellular coverage on technicians phone. Power cycle station. Call WWG to troubleshoot further | Cell coveage self recovered after being down for 20+ days | Smith | 2022-03-15
2022-03-07 | 2815 | SE799 | 2020-05-22 | Online | AP |  | SCE Loma Vista Pl | MCKEVETT | 34.3605 | -119.0692 | 469 | Ventura | 120210E | Hardware - Satellite terminal | Satellite comms failed 3/2/22. No signs of battery issue. | Power-cycle, Call WWG to confirm | Updated logger program/OS. Power-cycled. | Spinowitz | 2022-03-07
2022-01-21 | 2107 | SE112 | 2018-10-11 | OFFLINE | 10 |  | SCE San Antonio Canyon 2 | FERRARA | 34.1835 | -117.6774 | 2754 | Ontario | 4526556E | Hardware - Cellular Modem | Bad cell signal | Install satellite terminal and convert to dualcomms or satellite only station. | Retrofitted to satellite | Smith | 2022-03-03
2022-01-21 | 2109 | SE114 | 2018-10-25 | Online | 10 |  | SCE Mias Canyon | STUBBY | 33.9516 | -116.8821 | 2760 | Redlands | 78153S | Hardware - Pyranometer | SolarRad reading 0 at all times | Bring spare pyranometer; Inspect pyranometer and check wiring. Calibrate or replace sensor if necessary. Call WWG to confirm issue | Pyranometer replaced | Davis | 2022-03-02
2022-04-12 | 2714 | SE692 | 2020-04-24 | OFFLINE | AP |  | SCE Boosey Rd | PYLE | 34.3791 | -119.0279 | 457 | Ventura | 4628633E | Hardware - Satellite terminal | Lost Comms 4/3/22, no signs of power issue | Power-cycle, Call WWG to confirm, check modem interface, possibly replace | Swapped bad satellite terminal for TI-6833 originally going to uninstalled SCE-3536. Old TI-5456 is bad. | Sagehorn | 2022-02-17
2022-06-16 | 2172 | SE251 | 2019-05-08 | Online |  |  | SCE Wright Mountain Rd | CIRCLE | 34.3579 | -117.6086 | 5614 | Victorville | 1341642E | Hardware - Station Burned | Station getting replaced | Replacement equipment is ready | Replaced with SCE-3641, dualcomm added | Smith | 2022-02-02
2021-12-14 | 2708 | SE732 | 2020-05-05 | OFFLINE | AP |  | SCE Tollhouse Rd | CHINA PEAK | 37.2506 | -119.1592 | 7050 | Shaver Lake | 4662994E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | DO NOT VISIT UNTIL AC POWER OR RELOCATION IS CONFIRMED. Call WWG to troubleshoot. | Moved station, power cycled, updated OS/program | Sagehorn | 2022-01-28
2022-06-03 | 3364 | 351SE | 2021-08-25 | Online | AP |  | SCE Barger Canyon Rd | HURST | 34.4634 | -119.7474 | 491 | Santa Barbara | 4779299E | High Qloss / Battery nearing fully discharged | Station qloss is rising to the point the station may go offline due to low battery volatage. Station may go online/offline cycle if battery cannot gain enough charge over time | Check for location or shading issue causing low solar resource. Check Solar panel wiring, CH200 wiring and programming. Clean solar panel, move station for better sunlight if necessary. | Self Resolved | Davis | 2022-01-28
2022-07-11 | 2617 | SE646 | 2020-04-14 | OFFLINE | AP |  | SCE Tuckerway Ranch-W Ave U | BOOTLEGGER | 34.5244 | -118.1434 | 3900 | Antelope Valley | 4267398E | Hardware - Satellite Terminal or Datalogger Ethernet Port | Communication lost 6/22/22 | Power-cyvcle, check RSSI, terminal status, call WWG to troubleshoot | Swapped out bad datalogger | Davis | 2022-01-27
2022-01-17 | 2804 | SE809 | 2020-05-27 | OFFLINE | AP |  | SCE Badger Canyon Rd | CALSTATE | 34.1896 | -117.327 | 1602 | Redlands | 4450234E | Hardware - Sat Terminal | Communications stopped on 1/5/22; Power looks okay | Call WWG prior to visiting site to review station solution. Check all station LEDs, connect to Sat terminal to check Status, # of bars, RSSI. Check datalogger running program; Power cycle station | Replaced bad PoE | Smith | 2022-01-27
2022-05-25 | 3394 | 435SE | 2021-09-16 | Online | AP |  | SCE Campbell Creek Dr | ELSTER | 36.1297 | -118.8604 | 851 | Tulare | 4477451E | Hardware - Temp/RH Sensor | Temp/RH sensor stuck at bad values | Check out sensor wiring, cable, sensorhead connection. Determine if sensor needs to be replaced; power cycle station | Replaced Temp/RH sensor | Sagehorn | 2022-01-26
2021-12-14 | 2680 | SE691 | 2020-04-24 | Online | AP |  | SCE Williams Canyon Rd | MIDDLE ROAD | 34.3111 | -119.1742 | 603 | Ventura | 2359260E | Communications - Sat Terminal | Station lost comms 12/13/21; Cannot connect or collect data | Check all station LED's and power. Connect to satellite terminal to check the Status, # of Bars, GPS, RSSI, Port forwarding. Connect to datalogger to confirm running program. Power cycle station. Call WWG to troubleshoot | Power cycled station upon arrival. Afterwards, connection restored. RSSI 66 w/ optimal pointing. Did not send frequency file. Station was calibrated after resolving incident | Davis | 2022-01-25
2021-12-28 | 2705 | SE717 | 2020-05-01 | OFFLINE | AP |  | SCE Round Valley | BIRCHIM | 37.4001 | -118.6565 | 6190 | Bishop | 1830541E | Hardware - Sat Terminal | Communications stopped on 12/25/21; Power looks okay | Call WWG prior to visiting site to review station solution. Check all station LEDs, connect to Sat terminal to check Status, # of bars, RSSI. Check datalogger running program; Power cycle station | Swapped bad PoE. Swapped battery. | Sagehorn | 2022-01-25
2022-03-30 | 3012 | SE900 | 2020-07-17 | Online | AP |  | SCE E Francisquito Ave | ANN | 34.0503 | -117.9138 | 455 | Covina | 1243311E | Hardware - Satellite | Lost comms 3/29/22, no signs of battery/power issue | Power-cycle, call WWG to confirm and further troubleshoot | X2n case number SC46686 | Smith | 2022-01-25
2022-01-17 | 2589 | SE555 | 2020-03-06 | OFFLINE | AP |  | SCE Cliff Dr | CEDAR PINES | 34.252 | -117.3303 | 4804 | Arrowhead | 2315410E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Reuploaded lost logger program from weather-related dead battery | Smith | 2022-01-24
2022-04-12 | 2645 | SE602 | 2020-03-20 | Online | AP |  | SCE Rangeview Dr | SIAM | 33.7781 | -117.7651 | 588 | Santa Ana | 4024500E | Station communications drop in and out throughout the day, occasionally out for few hours at a time |  |  | Self Resolved | Spinowitz | 2022-01-24
2022-03-30 | 2752 | SE762 | 2020-05-12 | Online | AP |  | SCE McLaughlin Rd | ROS | 33.7357 | -117.1306 | 1540 | Menifee | 312520S | Hardware - Satellite | Lost comms 3/29/22, no signs of battery/power issue | Power-cycle, call WWG to confirm and further troubleshoot | X2n case number SC46687 | Smith | 2022-01-24
2022-02-16 | 2700 | SE731 | 2020-05-05 | OFFLINE | AP |  | SCE Tanager Ln | TRAIL | 37.2489 | -119.1931 | 7075 | Shaver Lake | 4278906E | Hardware - Temp/RH Sensor | Temp/RH sensor giving bad values due to station dying | Power-cycle, Call WWG to confirm | Power cycled station | Spinowitz | 2022-01-18
2022-01-17 | 2865 | SE877 | 2020-06-25 | OFFLINE | AP |  | SCE Arroyo Verde | PEARCE | 34.2844 | -119.2283 | 391 | Ventura | 2096808E | Hardware - Sat Terminal | Communications stopped on 1/1/22; Power looks okay | Call WWG prior to visiting site to review station solution. Check all station LEDs, connect to Sat terminal to check Status, # of bars, RSSI. Check datalogger running program; Power cycle station | Replaced faulty PoE Injector | Spinowitz | 2022-01-18
2022-01-05 | 2748 | SE744 | 2020-05-07 | OFFLINE | AP |  | SCE Wilderness Rd Park | ROWCO | 34.2161 | -117.1117 | 6198 | Arrowhead | 4559409E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Reuploaded lost logger program from weather-related dead battery | Spinowitz | 2022-01-03
2021-12-28 | 2914 | SE916 | 2020-07-28 | OFFLINE | AP |  | SCE Walnut Creek | EGMONT | 34.0911 | -117.8341 | 680 | Covina | 332021E | Hardware - Sat Terminal | Communications stopped on 12/23/21; Power looks okay | Call WWG prior to visiting site to review station solution. Check all station LEDs, connect to Sat terminal to check Status, # of bars, RSSI. Check datalogger running program; Power cycle station | Station lost datalogger program, perhaps power related. program was re-sent and station calibrated. Replaced Temp/RH sensor after calibration. | colligan | 2021-12-31
2022-01-21 | 3031 | 089SE | 2021-04-19 | Online | AP |  | SCE Pendleton Rd | OAK GLEN | 34.0402 | -117.0194 | 3041 | Redlands | 4512235E | Hardware - Cellular Modem | Cellular modem communications stopped 12-29-21; Power Okay. Station continuing to communicate via secondary (Satellite) comms | Check all station LED's including cellular modem power, signal, network lights. Check cellular antenna tightness and wire connections. Check station power. Compare station cellular coverage on technicians phone. Power cycle station. Call WWG to troubleshoot further | Cell modem recovered comms after calibration visit. | colligan | 2021-12-29
2022-03-29 | 3428 | 410SE | 2021-09-10 | Online | AP |  | SCE Wheeler Canyon Rd | MIDDLE ROAD | 34.395 | -119.1391 | 954 | Ventura | 4770893E | Hardware - Satellite | Lost comms 3/22/22, no signs of battery/power issue | Power-cycle, call WWG to confirm and further troubleshoot | Satellite terminal failed - Replaced with spare terminal SCE-S10026-10 (TI-6864). Old terminal TI-6525 under warranty, shipping to WWG | Sagehorn | 2021-12-28
2021-12-14 | 2784 | SE818 | 2020-08-06 | AQI - OFFLINE | 60 |  | SCE Powerhouse 2 | MUSICK | 37.1994 | -119.3065 | 2986 | Shaver Lake | 1921442E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | DO NOT VISIT UNTIL AC POWER OR RELOCATION IS CONFIRMED. Call WWG to troubleshoot. | Station was not relocated or set up w/ AC power. Battery recharged; Station needs OS/Program update 12/20/21; Battery recharged again, removed AQI sensor in attempt to save battery power 12/22/21 | Sagehorn | 2021-12-22
2021-12-14 | 2458 | SE339 | 2019-06-20 | Online | AP |  | SCE Horn Mountain | PAWLEY | 36.3822 | -118.8463 | 2254 | San Joaquin Valley | 4242837E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | DO NOT VISIT UNTIL AC POWER OR RELOCATION IS CONFIRMED. Call WWG to troubleshoot. | Station moved 7ft up pole, solar panel alignment optimized. Supposed to take care of shading issues | Davis | 2021-12-17
2022-03-16 | 2374 | SE389 | 2019-07-18 | OFFLINE | 60 |  | SCE Nelson Creek | MAHOGANY | 36.156 | -118.6238 | 5955 | Tulare | 4289793E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Swap/recharge battery | Self resolved - late enough in year to power | Sagehorn | 2021-12-16
2022-03-31 | 2458 | SE339 | 2019-06-20 | Online | AP |  | SCE Horn Mountain | PAWLEY | 36.3822 | -118.8463 | 2254 | Tulare | 4242837E | Hardware - Satellite | Lost comms 3/29/22, no signs of battery/power issue | Power-cycle, call WWG to confirm and further troubleshoot | Power-cycled, rebooted modem | Sagehorn | 2021-12-15
2022-01-17 | 2680 | SE691 | 2020-04-24 | OFFLINE | AP |  | SCE Williams Canyon Rd | MIDDLE ROAD | 34.3111 | -119.1742 | 603 | Ventura | 2359260E | Hardware - Sat Terminal | Communications stopped on 1/16/22; Power looks okay | Call WWG prior to visiting site to review station solution. Check all station LEDs, connect to Sat terminal to check Status, # of bars, RSSI. Check datalogger running program; Power cycle station | Unplugged/Replugged Ethernet cable into datalogger without power cycling restored comms. Power cycled before leaving | Spinowitz | 2021-12-15
7/27/2022 | 2067 | SE030 | 6/24/2018 | Online | 10 |  | SCE Greenleaf Canyon | SYLVIA | 34.1008334 | -118.604999 | 947 | Thousand Oaks | 769491E | Communications - Cellular Signal | Station communications drop in and out throughout the day, occasionally out for few hours at a time | Record or call WWG to record current cellular metrics; Replace internal paddle antenna with external omni antenna; Reboot station and record new cellular metrics after 5 minutes of online time; If signal does not improve, may need to convert to satellite | External antenna added, WWG monitoring for comms improvement

## Fixes List 2021
Station Issues (Communications/Sensors)
Date Added | Serial Number | MesoWest ID | Date Installed | Station Status | Collection Interval | N/A | Station Name | Circuit Name | Lat | Longitude | Elev (ft) | Service Center (District) | Pole Structure # | Issue Status | Issue Notes | Solution | Additional Comments
2021-12-14 | 2494 | SE481 | 2019-11-19 | Online | 10 |  | SCE Krbt Station Rd | HI LINE | 33.3598 | -118.376 | 1465 | Catalina | 4733693E | Hardware - Datalogger, Pyranometer | Datalogger calibration errors - randomly loses connection, wont send data, or bad temp/rh, batt volt values. Bad Solarrad, needs to be replaced | Update datalogger OS to version 5.01, confirm connectivity and errors cleared from datalogger with WWG. Replace Solarrad
Resolved Station Incidents
Date Added | Serial Number | MesoWest ID | Date Installed | Station Status | Collection Interval | N/A | Station Name | Circuit Name | Lat | Longitude | Elev (ft) | Service Center (District) | Pole Structure # | Issue Status | Issue Notes | Solution | Resolution Comments | Tech Visited | Date Resolved
2022-01-21 | 3031 | 089SE | 2021-04-19 | Online | AP |  | SCE Pendleton Rd | OAK GLEN | 34.0402 | -117.0194 | 3041 | Redlands | 4512235E | Hardware - Cellular Modem | Cellular modem communications stopped 12-29-21; Power Okay. Station continuing to communicate via secondary (Satellite) comms | Check all station LED's including cellular modem power, signal, network lights. Check cellular antenna tightness and wire connections. Check station power. Compare station cellular coverage on technicians phone. Power cycle station. Call WWG to troubleshoot further | Cell coveage self recovered after being down for 20+ days | Smith | 2022-01-25
2022-01-17 | 2865 | SE877 | 2020-06-25 | OFFLINE | AP |  | SCE Arroyo Verde | PEARCE | 34.2844 | -119.2283 | 391 | Ventura | 2096808E | Hardware - Sat Terminal | Communications stopped on 1/1/22; Power looks okay | Call WWG prior to visiting site to review station solution. Check all station LEDs, connect to Sat terminal to check Status, # of bars, RSSI. Check datalogger running program; Power cycle station | Replaced faulty PoE Injector | Spinowitz | 2022-01-18
2022-01-17 | 2680 | SE691 | 2020-04-24 | OFFLINE | AP |  | SCE Williams Canyon Rd | MIDDLE ROAD | 34.3111 | -119.1742 | 603 | Ventura | 2359260E | Hardware - Sat Terminal | Communications stopped on 1/16/22; Power looks okay | Call WWG prior to visiting site to review station solution. Check all station LEDs, connect to Sat terminal to check Status, # of bars, RSSI. Check datalogger running program; Power cycle station | Unplugged/Replugged Ethernet cable into datalogger without power cycling restored comms. Power cycled before leaving | Spinowitz | 2022-01-18
2021-12-28 | 2914 | SE916 | 2020-07-28 | OFFLINE | AP |  | SCE Walnut Creek | EGMONT | 34.0911 | -117.8341 | 680 | Covina | 332021E | Hardware - Sat Terminal | Communications stopped on 12/23/21; Power looks okay | Call WWG prior to visiting site to review station solution. Check all station LEDs, connect to Sat terminal to check Status, # of bars, RSSI. Check datalogger running program; Power cycle station | Station lost datalogger program, perhaps power related. program was re-sent and station calibrated. Replaced Temp/RH sensor after calibration. | Colligan | 2021-12-31
2021-12-28 | 3125 | 152SE | 2021-06-18 | Online | AP |  | SCE Bel Air | HILTON | 34.0831 | -118.4227 | 414 | Santa Monica | 4467155E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Replaced battery; Re-sent datalogger program that was lost; Re-wired loose power wire. | Colligan | 2021-12-29
2021-12-20 | 2745 | SE707 | 2020-04-29 | Online | AP |  | SCE Dalbo St | SPINKS | 34.1467 | -117.9511 | 629 | Monrovia | 791585E | Hardware - Wind Monitor | Bad wind direction | Replace sensor | Replaced missing screw in wind monitor, g2g | Spinowitz | 2022-01-03
2022-01-17 | 3441 | 425SE | 2021-09-14 | OFFLINE | AP |  | SCE San Bern NF | JOB | 34.2615 | -117.3576 | 4508 | Arrowhead | 4526778E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Replaced Satellite terminal with spare SCE-S10026-7 | Davis | 2022-01-28
2022-01-21 | 2109 | SE114 | 2018-10-25 | Online | 10 |  | SCE Mias Canyon | STUBBY | 33.9516 | -116.8821 | 2760 | Redlands | 78153S | Hardware - Pyranometer | SolarRad reading 0 at all times | Bring spare pyranometer; Inspect pyranometer and check wiring. Calibrate or replace sensor if necessary. Call WWG to confirm issue | Pyranometer replaced | Smith | 2022-02-02
2021-12-28 | 2705 | SE717 | 2020-05-01 | OFFLINE | AP |  | SCE Round Valley | BIRCHIM | 37.4001 | -118.6565 | 6190 | Bishop | 1830541E | Hardware - Sat Terminal | Communications stopped on 12/25/21; Power looks okay | Call WWG prior to visiting site to review station solution. Check all station LEDs, connect to Sat terminal to check Status, # of bars, RSSI. Check datalogger running program; Power cycle station | Swapped bad PoE. Swapped battery. | Sagehorn | 2022-01-28
2022-01-17 | 2804 | SE809 | 2020-05-27 | OFFLINE | AP |  | SCE Badger Canyon Rd | CALSTATE | 34.1896 | -117.327 | 1602 | Redlands | 4450234E | Hardware - Sat Terminal | Communications stopped on 1/5/22; Power looks okay | Call WWG prior to visiting site to review station solution. Check all station LEDs, connect to Sat terminal to check Status, # of bars, RSSI. Check datalogger running program; Power cycle station | Replaced bad PoE | Smith | 2022-01-27
2022-01-21 | 3031 | 089SE | 2021-04-19 | Online | AP |  | SCE Pendleton Rd | OAK GLEN | 34.0402 | -117.0194 | 3041 | Redlands | 4512235E | Hardware - Cellular Modem | Cellular modem communications stopped 12-29-21; Power Okay. Station continuing to communicate via secondary (Satellite) comms | Check all station LED's including cellular modem power, signal, network lights. Check cellular antenna tightness and wire connections. Check station power. Compare station cellular coverage on technicians phone. Power cycle station. Call WWG to troubleshoot further | Cell modem recovered comms after calibration visit. | Smith | 2022-01-25
2021-12-17 | 3445 | 407SE | 2021-09-09 | OFFLINE | AP |  | SCE Chestnut Ct | TENNECO | 34.8374 | -119.1452 | 6218 | Antelope Valley | 2038166E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Recharged drained battery, swapped for new battery at station. Cleaned solar panel, checked satellite RSSI. Resent OS/Program. No shading issues, power was weather related | Sagehorn | 2021-12-28
2022-01-05 | 2569 | SE559 | 2020-03-09 | OFFLINE | AP |  | SCE Fredalba Rd | ROWCO | 34.2037 | -117.1423 | 5392 | Arrowhead | 1354143E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Swapped bad sat terminal (TI-5303) with spare SCE-S10026-4 (TI-6858) | Smith | 2022-01-24
2022-01-05 | 2748 | SE744 | 2020-05-07 | OFFLINE | AP |  | SCE Wilderness Rd Park | ROWCO | 34.2161 | -117.1117 | 6198 | Arrowhead | 4559409E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Reuploaded lost logger program from weather-related dead battery | Smith | 2022-01-24
2022-01-17 | 2589 | SE555 | 2020-03-06 | OFFLINE | AP |  | SCE Cliff Dr | CEDAR PINES | 34.252 | -117.3303 | 4804 | Arrowhead | 2315410E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Reuploaded lost logger program from weather-related dead battery | Davis | 2022-01-27
2021-12-28 | 2664 | SE648 | 2020-04-14 | OFFLINE | AP |  | SCE Hilltop Blvd | LURING | 34.207 | -117.1123 | 6149 | Arrowhead | 1403121E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Reuploaded lost logger program from weather-related dead battery. Updated OS. | Davis | 2022-01-25
2022-01-17 | 3445 | 407SE | 2021-09-09 | OFFLINE | AP |  | SCE Chestnut Ct | TENNECO | 34.8374 | -119.1452 | 6218 | Antelope Valley | 2038166E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Swapped battery and reuploaded lost datalogger program | Sagehorn | 2022-01-26
2022-01-21 | 2634 | SE631 | 2020-04-03 | Online | AP |  | SCE Oak Grove Dr | DEVILS GATE | 34.1919 | -118.1762 | 1042 | Monrovia | 4548848E | Hardware - Wind Monitor | Wind Speed reading 0 at all times | Bring spare wind monitor to station; Inspect wind monitor and check wiring. Calibrate or replace sensor if necessary. Call WWG to confirm issue | Replaced Wind Monitor | Spinowitz | 2022-01-24
2021-12-28 | 2701 | SE727 | 2020-05-05 | OFFLINE | AP |  | SCE Huntington Lake Rd | RANCHERIA | 37.2532 | -119.1655 | 6968 | Shaver Lake | 1031019E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | Weather/Snow likely affecting solar panel voltage and battery charge. Wait for solar resource to improve, possible self recovery. Call WWG to graph power data before visiting. May need to replace battery and recharge old battery for future re-use. AC Power or Relocation also viable. | Replaced battery | Sagehorn | 2022-01-25
2021-12-14 | 2784 | SE818 | 2020-08-06 | AQI - OFFLINE | 60 |  | SCE Powerhouse 2 | MUSICK | 37.1994 | -119.3065 | 2986 | Shaver Lake | 1921442E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | DO NOT VISIT UNTIL AC POWER OR RELOCATION IS CONFIRMED. Call WWG to troubleshoot. | Station was not relocated or set up w/ AC power. Battery recharged; Station needs OS/Program update 12/20/21; Battery recharged again, removed AQI sensor in attempt to save battery power 12/22/21 | Sagehorn | 12/20/2021 & again on 12/22/21
2021-12-14 | 2381 | SE361 | 2019-07-02 | OFFLINE | AP |  | SCE Tramway Rd | TRAM | 33.8429 | -116.6073 | 2200 | Palm Springs | 4507505E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | DO NOT VISIT UNTIL AC POWER OR RELOCATION IS CONFIRMED. Call WWG to troubleshoot. | Swapped bad CH200 | Davis | 2021-12-17
2021-12-14 | 2374 | SE389 | 2019-07-18 | OFFLINE | AP |  | SCE Nelson Creek | MAHOGANY | 36.156 | -118.6238 | 5955 | San Joaquin Valley | 4289793E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | DO NOT VISIT UNTIL AC POWER OR RELOCATION IS CONFIRMED. Call WWG to troubleshoot. | Station was moved to nearby location ~ 1 mile north. Same circuit, station high on pole to avoid any shading or line of sight issue | Sagehorn | 2021-12-16
2021-12-14 | 2458 | SE339 | 2019-06-20 | Online | AP |  | SCE Horn Mountain | PAWLEY | 36.3822 | -118.8463 | 2254 | San Joaquin Valley | 4242837E | Drained Battery / Low Solar Resource | Battery is nearly/completely discharged due to power issue (weather/shading on solar panel); Station may come online during the day, but will likely die at night due to power loss or stay offline | DO NOT VISIT UNTIL AC POWER OR RELOCATION IS CONFIRMED. Call WWG to troubleshoot. | Station moved 7ft up pole, solar panel alignment optimized. Supposed to take care of shading issues | Sagehorn | 2021-12-15
2021-12-14 | 2680 | SE691 | 2020-04-24 | Online | AP |  | SCE Williams Canyon Rd | MIDDLE ROAD | 34.3111 | -119.1742 | 603 | Ventura | 2359260E | Communications - Sat Terminal | Station lost comms 12/13/21; Cannot connect or collect data | Check all station LED's and power. Connect to satellite terminal to check the Status, # of Bars, GPS, RSSI, Port forwarding. Connect to datalogger to confirm running program. Power cycle station. Call WWG to troubleshoot | Power cycled station upon arrival. Afterwards, connection restored. RSSI 66 w/ optimal pointing. Did not send frequency file. Station was calibrated after resolving incident | Spinowitz | 2021-12-15

## Fixes - 2020
Circuit | District | Station Name | In Service Date (WWG) | Comm Solution (WWG) | Station Number (ex. SCE-2127) (WWG) | Installed Structure (WWG) | Installed Latitude (WWG) | Installed Longitude (WWG) | Station Status | Issue Status | Issue Code | Issue Notes | Solution | Additional Comments | Crew
HI LINE | Catalina | SCE Krbt Station Rd | 2019-11-19 | Satellite | SCE-2494 | 4733693E | 33.3598 | -118.376 | Online | Hardware Issue - Datalogger | 3 | Datalogger calibration errors - randomly loses connection, wont send data, or bad temp/rh, batt volt values | Replace datalogger, call WWG to confirm all settings and data. |  | DS
QUIXOTE | Tehachapi | SCE Tehachapi WIllowSpring Rd | 2020-02-22 | Satellite | SCE-2547 | 2300906E | 35.0273 | -118.3524 | Online | Hardware Issue - Datalogger | 3 | Datalogger calibration errors (2nd time) - randomly loses connection, wont send data, or bad temp/rh, batt volt values | Determine why 2nd datalogger started getting calibration errors. Ground weather statoin. Replace datalogger, call WWG to confirm all settings and data. | First datalogger calibration errors swap 12-2-20