## Inspections
Question ID | Additional Wildfire Driver
0.008 | Y
0.009 | Y
0.016
0.022
0.024
0.027 | Y
0.028 | Y
0.029
1.002
1.004
1.007
1.009 | Y
2.008 | Y
2.009 | Y
2.010 | Y
3.001
3.002
3.003
3.004
3.005 | Y
4.001
4.002
4.003
4.004 | Y
5.001
5.003
5.005
5.006 | Y
6.001 | Y
6.002
6.003
6.005 | Y
6.006 | Y
7.006 | Y
7.007 | Y
8.001
8.006 | Y
8.008 | Y
8.009 | Y
8.010
8.011 | Y
8.012 | Y
8.013 | Y
8.014 | Y
8.015 | Y
8.016 | Y
8.017 | Y
8.018 | Y
8.019 | Y
8.02
9.003
9.004
9.005 | Y
9.006 | Y
9.008 | Y
9.009 | Y
9.010 | Y
9.011 | Y
9.012 | Y
10.004
10.006
10.007 | Y
10.008 | Y
11.002
11.003
11.004 | Y
11.005 | Y
12.001
12.002
12.003
12.004 | Y
13.002
13.004 | Y
13.006 | Y
13.007 | Y
13.008 | Y
13.009 | Y
13.010 | Y
13.011 | Y
13.012 | Y
13.013 | Y
13.014 | Y
14.002
14.003
14.004 | Y
15.001 | Y
15.004
16.001 | Y
17.001 | Y
17.002 | Y
17.003 | Y
17.004 | Y
18.001 | Y
18.002 | Y
18.003 | Y
0.005A
0.005B | Y
0.014A | Y
0.014B | Y
0.014C | Y
0.014D | Y
0.014E | Y
0.014F | Y
0.014G | Y
0.014H | Y
0.014I | Y
0.014J | Y
0.014K | Y
0.014L | Y
0.014M | Y
0.014N | Y
0.014O | Y
0.020B
0.021A | Y
0.021B | Y
0.021C | Y
0.021D | Y
0.021E | Y
0.026A | Y
0.026B | Y
13.001A
13.001B
2.003A
2.003B
2.003C | Y
2.003D | Y
2.004A
2.005B
2.006A
2.006B
7.002A
7.002B
7.004A
8.002A
8.002B
8.007A | Y
8.007B | Y
9.007A | Y
9.007B | Y
MAT_COMM | Y
MAT_PRI | Y
MAT_PUB | Y
MAT_SEC | Y
MAT_TRAN | Y
SV001 | Y
SV002 | Y
SV002A | Y
SV003 | Y
SV004 | Y
SV005 | Y
SV006 | Y
SV007 | Y
SV008 | Y
SV009 | Y
SV010 | Y
T001 | Y
T002 | Y
T003 | Y

## InspectApp Q&A (hidden)
Fields | QC_Worded_Question | Inspect_App_Question_Name | Level | Question_Sequence | Sort | New_Fields | Final_Question | AssetKind | ValidTo | FIeld_ID | Notif Matrix | Question Types
|  | IS THE CIRCULAR POLE MEDALLION PRESENT? | PUBLIC-LEVEL | 0 | 4032 | Pub_Pole_Medallion | IS THE CIRCULAR POLE MEDALLION PRESENT? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.008 | N | Data Capture
|  | IS THE POLE BRAND VISIBLE? | PUBLIC-LEVEL | 0 | 4018 | Pub_Pole_Brand | IS THE POLE BRAND VISIBLE? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.009 | N | Data Capture
|  | WHAT IS THE CLEARANCE BETWEEN TREES/FOLIAGE AND PRIMARY CONDUCTORS? | PRIMARY-LEVEL | 0 | 1042 | Pri_Conductor_Tree_Cleareance | WHAT IS THE CLEARANCE BETWEEN TREES/FOLIAGE AND PRIMARY CONDUCTORS? | CONDUCTORS - PRIMARY | 2958465 | 0.016 | Y | Health/Condition | Both
|  | IS THERE AT LEAST 6 FEET OF CLEARANCE BETWEEN TREES/FOLIAGE AND CONDUCTORS? | PRIMARY-LEVEL | 0 | 1042 | Pri_Conductor_Tree_Cleareance_1 | WHAT IS THE CLEARANCE BETWEEN TREES/FOLIAGE AND PRIMARY CONDUCTORS? | CONDUCTORS - PRIMARY | 2958465 | 0.016 | Y | Health/Condition
|  | WILL 6 FEET OF CLEARANCE BETWEEN CONDUCTORS AND TREES REMAIN DURING WIND EVENTS? | PRIMARY-LEVEL | 0 | 1015 | Pri_Conductor_6ft_wind_1 | WILL 6 FEET OF CLEARANCE BETWEEN CONDUCTORS AND TREES REMAIN DURING WIND EVENTS? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.017 | N
|  | WILL 6 FEET OF CLEARANCE BETWEEN STRUCTURE AND TREES REMAIN DURING WIND EVENTS? | PRIMARY-LEVEL | 0 | 1015 | Pri_Conductor_6ft_wind_2 | WILL 6 FEET OF CLEARANCE BETWEEN CONDUCTORS AND TREES REMAIN DURING WIND EVENTS? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.017 | N
|  | Will 6 feet of clearance between conductors and trees remain during wind events? | PRIMARY-LEVEL | 0 | 1015 | Pri_Conductor_6ft_wind_3 | Will 6 feet of clearance between conductors and trees remain during wind events? | CONDUCTORS - PRIMARY | 2958465 | 0.017 | N
|  |  | PRIMARY-LEVEL | 0 | 1015 | Pri_Conductor_6ft_wind_4 | Will 6 feet of clearance between structure and trees remain during wind events? | CONDUCTORS - PRIMARY | 2958465 | 0.017 | N
|  |  | PRIMARY-LEVEL | 0 | 1015 | Pri_Conductor_6ft_wind_5 | Will 6 feet of clearance between structure and trees remain during wind events? | CONDUCTORS - PRIMARY | 2958465 | 0.017 | N
|  | WILL 6 FEET OF CLEARANCE BETWEEN CONDUCTORS AND TREES REMAIN DURING WIND EVENTS? | SECONDARY-LEVEL | 0 | 2033 | Sec_Pole_6Feet_Clearance | WILL 6 FEET OF CLEARANCE BETWEEN CONDUCTORS AND TREES REMAIN DURING WIND EVENTS? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.017 | N | Health/Condition
|  | WILL 6 FEET OF CLEARANCE BETWEEN STRUCTURE AND TREES REMAIN DURING WIND EVENTS? | SECONDARY-LEVEL | 0 | 2033 | Sec_Pole_6Feet_Clearance_1 | WILL 6 FEET OF CLEARANCE BETWEEN CONDUCTORS AND TREES REMAIN DURING WIND EVENTS? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.017 | N | Health/Condition
|  | Will 6 feet of clearance between conductors and trees remain during wind events? | SECONDARY-LEVEL | 0 | 2033 | Sec_Pole_6Feet_Clearance_2 | Will 6 feet of clearance between conductors and trees remain during wind events? | CONDUCTORS - SECONDARY | 2958465 | 0.017 | N | Health/Condition
|  | Will 6 feet of clearance between conductors and trees remain during wind events? | SECONDARY-LEVEL | 0 | 2033 | Sec_Pole_6Feet_Clearance_3 | Will 6 feet of clearance between structure and trees remain during wind events? | CONDUCTORS - SECONDARY | 2958465 | 0.017 | N | Health/Condition
|  | IF NON-EXEMPT MATERIAL IS PRESENT ON THE POLE, IS THERE AT LEAST 10 FEET OF CLEARANCE BETWEEN VEGETATION AND THE BASE OF THE POLE, UP TO 8 FEET HIGH? | PUBLIC-LEVEL | 0 | 4033 | Pub_Pole_NonExempt_Clearance_10Feet | IF NON-EXEMPT MATERIAL IS PRESENT ON THE POLE, IS THERE AT LEAST 10 FEET OF CLEARANCE BETWEEN VEGETATION AND THE BASE OF THE POLE, UP TO 8 FEET HIGH? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.022 | N | Health/Condition
|  | INDICATE WHICH OF THE FOLLOWING DEFECTS ARE PRESENT ON OR AROUND THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4030 | Pub_Pole_Defects | INDICATE WHICH OF THE FOLLOWING DEFECTS ARE PRESENT ON OR AROUND THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.024 | Y | Health/Condition
|  | ARE THERE COMMUNICATIONS LINES INSTALLED ON THIS STRUCTURE? | COMMUNICATION-LEVEL | 0 | 3004 | Comm_Pole_Line | ARE THERE COMMUNICATIONS LINES INSTALLED ON THIS STRUCTURE? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.025 | N | Data Capture
|  | Are there communications lines installed on this structure? | COMMUNICATION-LEVEL | 0 | 3004 | Comm_Pole_Line_1 | Are there communications lines installed on this structure? | COMMUNICATION LINES AND EQUIPMENT | 2958465 | 0.025 | N | Data Capture
|  | WHICH OF THE FOLLOWING GENERALLY DESCRIBES THE AREA SURROUNDING THE POLE WITHIN 100 FEET? | PUBLIC-LEVEL | 0 | 4017 | Pub_Pole_Area_100Feet | WHICH OF THE FOLLOWING GENERALLY DESCRIBES THE AREA SURROUNDING THE POLE WITHIN 100 FEET? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.027 | N | Health/Condition
|  | IF A BUDDY POLE EXISTS, WHAT IS ATTACHED TO THE BUDDY POLE? | COMMUNICATION-LEVEL | 0 | 3007 | Comm_Buddy_Pole | IF A BUDDY POLE EXISTS, WHAT IS ATTACHED TO THE BUDDY POLE? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.028 | N | Data Capture
|  | If a Buddy Pole exists, what is attached to the Buddy Pole? | COMMUNICATION-LEVEL | 0 | 3007 | Comm_Buddy_Pole_1 | If a Buddy Pole exists, what is attached to the Buddy Pole? | BUDDY POLE | 2958465 | 0.028 | N | Data Capture
|  | If a Buddy Pole exists, what is attached to the Buddy Pole? | COMMUNICATION-LEVEL | 0 | 3007 | Comm_Buddy_Pole_2 | What is attached to the Buddy Pole? | BUDDY POLE | 2958465 | 0.028 | N | Data Capture
|  | INDICATE IF ANY OF THE FOLLOWING COMMUNICATION EQUIPMENT CONDITIONS ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | COMMUNICATION-LEVEL | 0 | 3008 | Comm_Equip_Condition | INDICATE IF ANY OF THE FOLLOWING COMMUNICATION EQUIPMENT CONDITIONS ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.029 | Y | Health/Condition
|  | Indicate if any of the following communication equipment conditions are observed. Select all that apply or select “No abnormal conditions”. | COMMUNICATION-LEVEL | 0 | 3008 | Comm_Equip_Condition_2 | Indicate if any of the following communication equipment conditions are observed. Select all that apply or select “No abnormal conditions”. | COMMUNICATION LINES AND EQUIPMENT | 2958465 | 0.029 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | COMMUNICATION-LEVEL | 0 | 3003 | Comm_Pole_Comp_Structure_Failure | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 1.002 | Y | Health/Condition
abnormal_com | Indicate if any of the following types of structural failure are observed on pole. | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | COMMUNICATION-LEVEL | 113 | 3005 | Comm_Pole_Structure_Failure | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 1.002 | Y | Health/Condition
|  | (AERIAL/GROUND) Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | COMMUNICATION-LEVEL | 0 | 3005 | Comm_Pole_Wood_Structure_Failure_1 | (AERIAL/GROUND) Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.002 | Y | Health/Condition
|  | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | COMMUNICATION-LEVEL | 0 | 3005 | Comm_Pole_Wood_Structure_Failure_2 | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.002 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1059 | Pri_Pole_Comp_Structure_Failure | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 1.002 | Y | Health/Condition
|  | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1061 | Pri_Pole_Wood_Structure_Failure_1 | (AERIAL/GROUND) Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.002 | Y | Health/Condition
|  | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1061 | Pri_Pole_Wood_Structure_Failure_2 | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.002 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4040 | Pub_Pole_Structure_Failure | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 1.002 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED ON POLE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4040 | Pub_Pole_Structure_Failure_1 | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 1.002 | Y | Health/Condition
|  | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4046 | Pub_Pole_Wood_Structure_Failure_2 | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.002 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2034 | Sec_Pole_Comp_Structure_Failure | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 1.002 | Y | Health/Condition
|  | (AERIAL/GROUND) Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2034 | Sec_Pole_Wood_Structure_Failure_1 | (AERIAL/GROUND) Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.002 | Y | Health/Condition
|  | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2034 | Sec_Pole_Wood_Structure_Failure_2 | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.002 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF CONSTRUCTION FAULTS ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4029 | Pub_Pole_Construction_Fault | INDICATE IF ANY OF THE FOLLOWING TYPES OF CONSTRUCTION FAULTS ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 1.004 | Y | Health/Condition
|  | Indicate if any of the following types of construction faults are observed. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4029 | Pub_Pole_Construction_Fault_1 | Indicate if any of the following types of construction faults are observed. Select all that apply or select “No abnormal conditions”. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.004 | Y | Health/Condition
|  | Indicate if any of the following types of construction faults are observed. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4029 | Pub_Pole_Construction_Fault_2 | Indicate if there are any of the following types of construction faults. Select all that apply. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.004 | Y | Health/Condition
|  | INDICATE IF THE POLE IS SHOWING ANY OF THE FOLLOWING SIGNS OF POLE LEAN. OTHERWISE, SELECT “POLE NOT LEANING". | PUBLIC-LEVEL | 0 | 4031 | Pub_Pole_Lean | INDICATE IF THE POLE IS SHOWING ANY OF THE FOLLOWING SIGNS OF POLE LEAN. OTHERWISE, SELECT “POLE NOT LEANING". | POLES - WOOD, POLES - COMPOSITE | 2958465 | 1.007 | Y | Health/Condition
|  | Indicate if the pole is showing any of the following signs of pole lean. | PUBLIC-LEVEL | 0 | 4031 | Pub_Pole_Lean_1 | Indicate if the pole is showing any of the following signs of pole lean. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.007 | Y | Health/Condition
|  | INDICATE IF THERE ARE ANIMAL NESTS ON ANY OF THE FOLLOWING EQUIPMENT ON THE STRUCTURE? SELECT ALL THAT APPLY OR SELECT “NO ANIMAL NESTS OBSERVED” | PUBLIC-LEVEL | 0 | 4999 | NULL | NULL | NULL | 2958465 | 1.008 | Y | Health/Condition
|  | INDICATE IF THERE ARE ANIMAL NESTS ON ANY OF THE FOLLOWING EQUIPMENT ON THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ANIMAL NESTS OBSERVED” | PUBLIC-LEVEL | 0 | 4016 | Pub_Pole_Animal_Nest | INDICATE IF THERE ARE ANIMAL NESTS ON ANY OF THE FOLLOWING EQUIPMENT ON THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ANIMAL NESTS OBSERVED” | POLES - WOOD, POLES - COMPOSITE | 2958465 | 1.008 | Y | Health/Condition
|  | Indicate if there are animal nests on any of the following equipment on the structure? Select all that apply or select “No animal nests observed” | PUBLIC-LEVEL | 0 | 4016 | Pub_Pole_Animal_Nest_1 | Indicate if there are animal nests on any of the following equipment on the structure. Select all that apply. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 1.008 | Y | Health/Condition
|  | Are any of the following structure conditions observed? Select all that apply. | PUBLIC-LEVEL | 0 | 4020 | Pub_Pole_Comp_Conditions | Are any of the following structure conditions observed? Select all that apply. | POLES - COMPOSITE | 2958465 | 1.009 | Y | Health/Condition
|  | Are any of the following structure conditions observed? Select all that apply. | PUBLIC-LEVEL | 0 | 4022 | Pub_Pole_Comp_Conditions_2 | Are any of the following structure conditions observed? Select all that apply. | POLES - COMPOSITE | 2958465 | 1.009 | Y | Health/Condition
|  | Are any of the following structure conditions observed? Select all that apply. | PUBLIC-LEVEL | 0 | 4045 | Pub_Pole_Wood_Conditions | Are any of the following structure conditions observed? Select all that apply. | POLES - WOOD | 2958465 | 1.009 | Y | Health/Condition
|  | Are any of the following structure conditions observed? Select all that apply. | PUBLIC-LEVEL | 0 | 4045 | Pub_Pole_Wood_Conditions_1 | Are any of the following structure conditions observed? Select all that apply. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.009 | Y | Health/Condition
|  | Indicate if any of the following types of structural failure are observed at this level. Select all that apply. | PUBLIC-LEVEL | 0 | 4047 | Pub_Pole_Wood_Structure_Failure_3 | Indicate if any of the following types of structural failure are observed at this level. Select all that apply. | POLES - WOOD | 2958465 | 1.012 | Y | Health/Condition
|  | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. copy | PUBLIC-LEVEL | 0 | 4048 | Pub_Pole_Wood_Structure_Failure_4 | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. copy | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.012 | Y | Health/Condition
|  | Indicate if any of the following types of structural failure are observed at this level. Select all that apply or select “No abnormal conditions”. copy | PUBLIC-LEVEL | 0 | 4048 | Pub_Pole_Wood_Structure_Failure_5 | Indicate if any of the following types of structural failure are observed at this level. Select all that apply. | POLES - WOOD, STREETLIGHT ONLY POLE - WOOD | 2958465 | 1.012 | Y | Health/Condition
|  | Are any of the following primary wood crossarm conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1097 | Pri_XARM_Wood_Conditions | (AERIAL/GROUND) Are any of the following primary wood crossarm conditions observed? Select all that apply. | CROSSARMS - WOOD | 2958465 | 2.008 | Y | Health/Condition
|  | Are any of the following wood crossarm conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1097 | Pri_XARM_Wood_Conditions_1 | Are any of the following primary wood crossarm conditions observed? Select all that apply. | CROSSARMS - WOOD | 2958465 | 2.008 | Y | Health/Condition
|  | Are any of the following wood crossarm conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1097 | Pri_XARM_Wood_Conditions_2 | Are any of the following wood crossarm conditions observed? Select all that apply. | CROSSARMS - WOOD | 2958465 | 2.008 | Y | Health/Condition
|  | Are any of the following steel crossarm conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1082 | Pri_XARM_Steel_Conditions | (AERIAL/GROUND) Are any of the following steel crossarm conditions observed? Select all that apply. | CROSSARMS - STEEL | 2958465 | 2.009 | N | Health/Condition
|  | Are any of the following steel crossarm conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1082 | Pri_XARM_Steel_Conditions_1 | Are any of the following steel crossarm conditions observed? Select all that apply. | CROSSARMS - STEEL | 2958465 | 2.009 | N | Health/Condition
|  | (AERIAL/GROUND) Are any of the following steel crossarm conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2055 | Sec_XARM_Steel_Conditions | (AERIAL/GROUND) Are any of the following steel crossarm conditions observed? Select all that apply. | CROSSARMS - STEEL | 2958465 | 2.009 | N | Health/Condition
|  | Are any of the following steel crossarm conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2055 | Sec_XARM_Steel_Conditions_1 | Are any of the following steel crossarm conditions observed? Select all that apply. | CROSSARMS - STEEL | 2958465 | 2.009 | N | Health/Condition
|  | Are any of the following wood crossarm conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2068 | Sec_XARM_Wood_Conditions | Are any of the following wood crossarm conditions observed? Select all that apply. | CROSSARMS - WOOD | 2958465 | 2.01 | N | Health/Condition
|  | Are any of the following secondary wood crossarm conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2068 | Sec_XARM_Wood_Conditions_1 | (AERIAL/GROUND) Are any of the following secondary wood crossarm conditions observed? Select all that apply. | CROSSARMS - WOOD | 2958465 | 2.01 | N | Health/Condition
|  | Are any of the following wood crossarm conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2068 | Sec_XARM_Wood_Conditions_2 | Are any of the following secondary wood crossarm conditions observed? Select all that apply. | CROSSARMS - WOOD | 2958465 | 2.01 | N | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING SIGNS OF TRANSFORMER OIL LEAKAGE OR WEEPAGE ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1109 | Pri_XFMR_Oil_Leak | INDICATE IF ANY OF THE FOLLOWING SIGNS OF TRANSFORMER OIL LEAKAGE OR WEEPAGE ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD TRANSFORMERS | 2958465 | 3.001 | Y | Health/Condition
|  | Indicate if any of the following signs of transformer oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1109 | Pri_XFMR_Oil_Leak_1 | Indicate if any of the following signs of transformer oil leakage or weepage are observed. Select all that apply. | OVERHEAD TRANSFORMERS | 2958465 | 3.001 | Y | Health/Condition
|  | (AERIAL/GROUND) Indicate if any of the following signs of transformer oil leakage or weepage are observed. Select all that apply. | PRIMARY-LEVEL | 0 | 1109 | Pri_XFMR_Oil_Leak_2 | (AERIAL/GROUND) Indicate if any of the following signs of transformer oil leakage or weepage are observed. Select all that apply. | OVERHEAD TRANSFORMERS | 2958465 | 3.001 | Y | Health/Condition
|  | Indicate if any of the following signs of transformer oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1109 | Pri_XFMR_Oil_Leak_3 | Indicate if any of the following signs of transformer oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | OVERHEAD TRANSFORMERS | 2958465 | 3.001 | Y | Health/Condition
|  | INDICATE IF TRANSFORMER HAS ANY OF THE FOLLOWING CONDITIONS AT THE TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1108 | Pri_XFMR_Damage_Operational_Issue | INDICATE IF TRANSFORMER HAS ANY OF THE FOLLOWING CONDITIONS AT THE TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD TRANSFORMERS | 2958465 | 3.002 | Y | Health/Condition
|  | INDICATE IF ANY TRANSFORMERS SHOW SIGNS OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1108 | Pri_XFMR_Damage_Operational_Issue_1 | INDICATE IF TRANSFORMER HAS ANY OF THE FOLLOWING CONDITIONS AT THE TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD TRANSFORMERS | 2958465 | 3.002 | Y | Health/Condition
|  | INDICATE IF TRANSFORMER SHOWS SIGNS OF ANY OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1108 | Pri_XFMR_Damage_Operational_Issue_2 | INDICATE IF TRANSFORMER HAS ANY OF THE FOLLOWING CONDITIONS AT THE TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD TRANSFORMERS | 2958465 | 3.002 | Y | Health/Condition
|  | Indicate if any transformers show signs of the following conditions. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1108 | Pri_XFMR_Damage_Operational_Issue_4 | Indicate if transformer has any of the following conditions at the time of inspection. Select all that apply. | OVERHEAD TRANSFORMERS | 2958465 | 3.002 | Y | Health/Condition
|  | Indicate if transformer has any of the following conditions at the time of inspection. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1108 | Pri_XFMR_Damage_Operational_Issue_5 | Indicate if transformer shows signs of any of the following conditions. Select all that apply or select “No abnormal conditions”. | OVERHEAD TRANSFORMERS | 2958465 | 3.002 | Y | Health/Condition
|  | (AERIAL/GROUND) Indicate if transformer has any of the following conditions at the time of inspection. Select all that apply. | PRIMARY-LEVEL | 0 | 1108 | Pri_XFMR_Damage_Operational_Issue_6 | (AERIAL/GROUND) Indicate if transformer has any of the following conditions at the time of inspection. Select all that apply. | OVERHEAD TRANSFORMERS | 2958465 | 3.002 | Y | Health/Condition
pri_trans | NULL | INDICATE IF TRANSFORMER HAS ANY OF THE FOLLOWING CONDITIONS AT THE TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 141 | 1108 | Pri_XFMR_Damage_Operational_Issue_7 | INDICATE IF TRANSFORMER HAS ANY OF THE FOLLOWING CONDITIONS AT THE TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD TRANSFORMERS | 2958465 | 3.002 | Y | Health/Condition
transformer_conditions | Do transformer shows signs of any of the following conditions? | INDICATE IF ANY TRANSFORMERS SHOW SIGNS OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 15 | 1108 | Pri_XFMR_Damage_Operational_Issue_8 | INDICATE IF TRANSFORMER HAS ANY OF THE FOLLOWING CONDITIONS AT THE TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD TRANSFORMERS | 43846 | 3.002 | Y | Health/Condition
transformer_conditions_2 | Do transformer shows signs of any of the following conditions? | INDICATE IF TRANSFORMER SHOWS SIGNS OF ANY OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 15 | 1108 | Pri_XFMR_Damage_Operational_Issue_9 | INDICATE IF TRANSFORMER HAS ANY OF THE FOLLOWING CONDITIONS AT THE TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD TRANSFORMERS | 43978 | 3.002 | Y | Health/Condition
|  | IS THE TRANSFORMER SHOWING ANY OF THE FOLLOWING SIGNS OF RUST OR CORROSION? | PRIMARY-LEVEL | 0 | 1111 | Pri_XFMR_Rust | IS THE TRANSFORMER SHOWING ANY OF THE FOLLOWING SIGNS OF RUST OR CORROSION? | OVERHEAD TRANSFORMERS | 2958465 | 3.003 | Y | Health/Condition
|  | ARE ANY TRANSFORMERS EXTREMELY RUSTED OR CORRODED? | PRIMARY-LEVEL | 0 | 1111 | Pri_XFMR_Rust_1 | IS THE TRANSFORMER SHOWING ANY OF THE FOLLOWING SIGNS OF RUST OR CORROSION? | OVERHEAD TRANSFORMERS | 2958465 | 3.003 | Y | Health/Condition
|  | Is the transformer showing any of the following signs of rust or corrosion? | PRIMARY-LEVEL | 0 | 1111 | Pri_XFMR_Rust_2 | Is the transformer showing any of the following signs of rust or corrosion? | OVERHEAD TRANSFORMERS | 2958465 | 3.003 | Y | Health/Condition
|  | Is the transformer showing any of the following signs of rust or corrosion? | PRIMARY-LEVEL | 0 | 1111 | Pri_XFMR_Rust_3 | Are any transformers extremely rusted or corroded? | OVERHEAD TRANSFORMERS | 2958465 | 3.003 | Y | Health/Condition
|  | ARE ANIMAL GUARDS INSTALLED, INTACT, AND ADEQUATELY COVERING THE TRANSFORMER? | PRIMARY-LEVEL | 0 | 1106 | Pri_XFMR_Animal_Guard | ARE ANIMAL GUARDS INSTALLED, INTACT, AND ADEQUATELY COVERING THE TRANSFORMER? | OVERHEAD TRANSFORMERS | 2958465 | 3.004 | N | Health/Condition
|  | ARE ANIMAL GUARDS INSTALLED, INTACT, AND ADEQUATELY COVERING ALL TRANSFORMERS? | PRIMARY-LEVEL | 0 | 1106 | Pri_XFMR_Animal_Guard_1 | ARE ANIMAL GUARDS INSTALLED, INTACT, AND ADEQUATELY COVERING THE TRANSFORMER? | OVERHEAD TRANSFORMERS | 2958465 | 3.004 | N | Health/Condition
|  | Are animal guards installed, intact, and adequately covering the transformer? | PRIMARY-LEVEL | 0 | 1106 | Pri_XFMR_Animal_Guard_2 | (AERIAL/GROUND) Are animal guards installed, intact, and adequately covering the transformer? | OVERHEAD TRANSFORMERS | 2958465 | 3.004 | N | Health/Condition
|  | Are animal guards installed, intact, and adequately covering all transformers? | PRIMARY-LEVEL | 0 | 1106 | Pri_XFMR_Animal_Guard_3 | Are animal guards installed, intact, and adequately covering all transformers? | OVERHEAD TRANSFORMERS | 2958465 | 3.004 | N | Health/Condition
|  | Are any of the following transformer conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1107 | Pri_XFMR_Conditions | (AERIAL/GROUND) Are any of the following transformer conditions observed? Select all that apply. | OVERHEAD TRANSFORMERS | 2958465 | 3.005 | N | Health/Condition
|  | Are any of the following transformer conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1107 | Pri_XFMR_Conditions_1 | Are any of the following transformer conditions observed? Select all that apply. | OVERHEAD TRANSFORMERS | 2958465 | 3.005 | N | Health/Condition
|  | INDICATE IF ANY CAPACITOR BANK, OR ASSOCIATED EQUIPMENT, SHOWS ANY OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1011 | Pri_CAP_BANK_Dmg-Op_Issue | INDICATE IF ANY CAPACITOR BANK, OR ASSOCIATED EQUIPMENT, SHOWS ANY OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD CAPACITORS | 2958465 | 4.001 | N | Health/Condition
|  | INDICATE IF ANY CAPACITOR OR ASSOCIATED EQUIPMENT SHOWS SIGNS OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1011 | Pri_CAP_BANK_Dmg-Op_Issue_1 | INDICATE IF ANY CAPACITOR BANK, OR ASSOCIATED EQUIPMENT, SHOWS ANY OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD CAPACITORS | 2958465 | 4.001 | N | Health/Condition
|  | Indicate if any capacitor bank, or associated equipment, shows any of the following conditions. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1011 | Pri_CAP_BANK_Dmg-Op_Issue_2 | Indicate if any capacitor bank, or associated equipment, shows any of the following conditions. Select all that apply. | OVERHEAD CAPACITORS | 2958465 | 4.001 | N | Health/Condition
|  | Indicate if any capacitor or associated equipment shows signs of the following conditions. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1011 | Pri_CAP_BANK_Dmg-Op_Issue_3 | Indicate if any capacitor or associated equipment shows signs of the following conditions. Select all that apply or select “No abnormal conditions”. | OVERHEAD CAPACITORS | 2958465 | 4.001 | N | Health/Condition
|  | (AERIAL/GROUND) Indicate if any capacitor bank, or associated equipment, shows any of the following conditions. Select all that apply. | PRIMARY-LEVEL | 0 | 1011 | Pri_CAP_BANK_Dmg-Op_Issue_4 | (AERIAL/GROUND) Indicate if any capacitor bank, or associated equipment, shows any of the following conditions. Select all that apply. | OVERHEAD CAPACITORS | 2958465 | 4.001 | N | Health/Condition
|  | Indicate if any capacitor bank, or associated equipment, shows any of the following conditions. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1011 | Pri_CAP_BANK_Dmg-Op_Issue_5 | Indicate if any capacitor bank, or associated equipment, shows any of the following conditions. Select all that apply or select “No abnormal conditions”. | OVERHEAD CAPACITORS | 2958465 | 4.001 | N | Health/Condition
capacitor_conditions | Are capacitor(s) or associated equipment shows signs of the following conditions? | INDICATE IF ANY CAPACITOR BANK, OR ASSOCIATED EQUIPMENT, SHOWS ANY OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 19 | 1011 | Pri_CAP_BANK_Dmg-Op_Issue_6 | INDICATE IF ANY CAPACITOR BANK, OR ASSOCIATED EQUIPMENT, SHOWS ANY OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD CAPACITORS | 2958465 | 4.001 | N | Health/Condition
capacitor_conditions | Are capacitor(s) or associated equipment shows signs of the following conditions? | INDICATE IF ANY CAPACITOR OR ASSOCIATED EQUIPMENT SHOWS SIGNS OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 19 | 1011 | Pri_CAP_BANK_Dmg-Op_Issue_7 | INDICATE IF ANY CAPACITOR BANK, OR ASSOCIATED EQUIPMENT, SHOWS ANY OF THE FOLLOWING CONDITIONS. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD CAPACITORS | 44286 | 4.001 | N | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF CAPACITOR BANK OIL LEAKAGE OR WEEPAGE ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1012 | Pri_CAP_BANK_Oil_Leak | INDICATE IF ANY OF THE FOLLOWING TYPES OF CAPACITOR BANK OIL LEAKAGE OR WEEPAGE ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD CAPACITORS | 2958465 | 4.002 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF CAPACITOR OIL LEAKAGE OR WEEPAGE ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1012 | Pri_CAP_BANK_Oil_Leak_1 | INDICATE IF ANY OF THE FOLLOWING TYPES OF CAPACITOR BANK OIL LEAKAGE OR WEEPAGE ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | OVERHEAD CAPACITORS | 2958465 | 4.002 | Y | Health/Condition
|  | Indicate if any of the following types of capacitor oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1012 | Pri_CAP_BANK_Oil_Leak_2 | Indicate if any of the following types of capacitor oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | OVERHEAD CAPACITORS | 2958465 | 4.002 | Y | Health/Condition
|  | Indicate if any of the following types of capacitor bank oil leakage or weepage are observed. Select all that apply. | PRIMARY-LEVEL | 0 | 1012 | Pri_CAP_BANK_Oil_Leak_3 | Indicate if any of the following types of capacitor bank oil leakage or weepage are observed. Select all that apply. | OVERHEAD CAPACITORS | 2958465 | 4.002 | Y | Health/Condition
|  | Indicate if any of the following types of capacitor bank oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1012 | Pri_CAP_BANK_Oil_Leak_4 | Indicate if any of the following types of capacitor bank oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | OVERHEAD CAPACITORS | 2958465 | 4.002 | Y | Health/Condition
|  | HAS THE CAPACITOR EQUIPMENT (I.E. FUSES) BROKEN DOWN TO A SINGLE PHASE CONDITION WITH BANK STILL ENERGIZED? | PRIMARY-LEVEL | 0 | 1009 | Pri_CAP_1_Phase | HAS THE CAPACITOR EQUIPMENT (I.E. FUSES) BROKEN DOWN TO A SINGLE PHASE CONDITION WITH BANK STILL ENERGIZED? | OVERHEAD CAPACITORS | 2958465 | 4.003 | Y | Health/Condition
|  | Has the capacitor equipment (i.e. fuses) broken down to a single phase condition with bank still energized? | PRIMARY-LEVEL | 0 | 1009 | Pri_CAP_1_Phase_1 | Has the capacitor equipment (i.e. fuses) broken down to a single phase condition with bank still energized? | OVERHEAD CAPACITORS | 2958465 | 4.003 | Y | Health/Condition
capacitor_phase | Has the capacitor equipment (i.e. fuses) broken down to a single phase condition with bank still energized? | HAS THE CAPACITOR EQUIPMENT (I.E. FUSES) BROKEN DOWN TO A SINGLE PHASE CONDITION WITH BANK STILL ENERGIZED? | PRIMARY-LEVEL | 21 | 1009 | Pri_CAP_1_Phase_2 | HAS THE CAPACITOR EQUIPMENT (I.E. FUSES) BROKEN DOWN TO A SINGLE PHASE CONDITION WITH BANK STILL ENERGIZED? | OVERHEAD CAPACITORS | 2958465 | 4.003 | Y | Health/Condition
|  | Are any of the following capacitor conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1010 | Pri_CAP_BANK_Conditions | (AERIAL/GROUND) Are any of the following capacitor conditions observed? Select all that apply. | OVERHEAD CAPACITORS | 2958465 | 4.004 | N | Health/Condition
|  | Are any of the following capacitor conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1010 | Pri_CAP_BANK_Conditions_1 | Are any of the following capacitor conditions observed? Select all that apply. | OVERHEAD CAPACITORS | 2958465 | 4.004 | N | Health/Condition
|  | Indicate if any of the following types of structural damage are observed on the pole. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4025 | Pub_Pole_Comp_Structural_Damage | Indicate if any of the following types of structural damage are observed on the pole. Select all that apply or select “No abnormal conditions”. | POLES - COMPOSITE | 2958465 | 5.001 | Y | Health/Condition
|  | Indicate if any of the following types of structural failure are observed on pole. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4025 | Pub_Pole_Comp_Structural_Damage_1 | Indicate if any of the following types of structural damage are observed on the pole. Select all that apply. | POLES - COMPOSITE | 2958465 | 5.001 | Y | Health/Condition
|  | Indicate if any of the following types of structural damage are observed on the pole. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4025 | Pub_Pole_Comp_Structural_Damage_2 | Indicate if any of the following types of structural failure are observed on pole. Select all that apply or select “No abnormal conditions”. | POLES - COMPOSITE | 2958465 | 5.001 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL DAMAGE ARE OBSERVED ON THE POLE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4039 | Pub_Pole_Structural_Damage | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL DAMAGE ARE OBSERVED ON THE POLE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 5.001 | Y | Health/Condition
|  | Indicate if any of the following signs of overloading are observed on the pole. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4024 | Pub_Pole_Comp_Overloading | Indicate if any of the following signs of overloading are observed on the pole. Select all that apply or select “No abnormal conditions”. | POLES - COMPOSITE | 2958465 | 5.003 | Y | Health/Condition
|  | Indicate if any of the following signs of overloading are observed on the pole. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4024 | Pub_Pole_Comp_Overloading_1 | Indicate if any of the following signs of overloading are observed on the pole. Select all that apply. | POLES - COMPOSITE | 2958465 | 5.003 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING SIGNS OF OVERLOADING ARE OBSERVED ON THE POLE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4034 | Pub_Pole_Overloading | INDICATE IF ANY OF THE FOLLOWING SIGNS OF OVERLOADING ARE OBSERVED ON THE POLE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 5.003 | Y | Health/Condition
|  | Indicate if there are animal nests on any of the following equipment on the structure? Select all that apply. | PUBLIC-LEVEL | 0 | 4023 | Pub_Pole_Comp_Nest | Indicate if there are animal nests on any of the following equipment on the structure? Select all that apply. | POLES - COMPOSITE | 2958465 | 5.005 | Y | Health/Condition
|  | Are any of the following structure conditions observed? Select all that apply. | PUBLIC-LEVEL | 0 | 4021 | Pub_Pole_Comp_Conditions_1 | Are any of the following structure conditions observed? Select all that apply. | POLES - COMPOSITE | 2958465 | 5.006 | Y | Health/Condition
|  | WHAT TYPES OF INSULATORS ARE INSTALLED AT THIS LEVEL? SELECT ALL THAT APPLY. | PRIMARY-LEVEL | 0 | 1057 | Pri_Insulator_Type | WHAT TYPES OF INSULATORS ARE INSTALLED AT THIS LEVEL? SELECT ALL THAT APPLY. | INSULATORS | 2958465 | 6.001 | N | Data Capture
|  | WHAT TYPES OF INSULATORS ARE INSTALLED AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1057 | Pri_Insulator_Type_1 | WHAT TYPES OF INSULATORS ARE INSTALLED AT THIS LEVEL? SELECT ALL THAT APPLY. | INSULATORS | 2958465 | 6.001 | N | Data Capture
|  | What types of insulators are installed at this level? | PRIMARY-LEVEL | 0 | 1057 | Pri_Insulator_Type_2 | What types of insulators are installed at this level? | INSULATORS | 2958465 | 6.001 | N | Data Capture
|  | WHAT TYPES OF INSULATORS ARE INSTALLED AT THIS LEVEL? SELECT ALL THAT APPLY. | SECONDARY-LEVEL | 0 | 2032 | Sec_Insulator_Type | WHAT TYPES OF INSULATORS ARE INSTALLED AT THIS LEVEL? SELECT ALL THAT APPLY. | INSULATORS | 2958465 | 6.001 | N | Data Capture
|  | WHAT TYPES OF INSULATORS ARE INSTALLED AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2032 | Sec_Insulator_Type_1 | WHAT TYPES OF INSULATORS ARE INSTALLED AT THIS LEVEL? SELECT ALL THAT APPLY. | INSULATORS | 2958465 | 6.001 | N | Data Capture
|  | What types of insulators are installed at this level? | SECONDARY-LEVEL | 0 | 2032 | Sec_Insulator_Type_2 | What types of insulators are installed at this level? | INSULATORS | 2958465 | 6.001 | N | Data Capture
|  | ARE ANY INSULATORS AT THIS LEVEL MISSING PARTS (NUTS, BOLTS, ETC.)? | PRIMARY-LEVEL | 0 | 1054 | Pri_Insulator_Missing_Part | ARE ANY INSULATORS AT THIS LEVEL MISSING PARTS (NUTS, BOLTS, ETC.)? | INSULATORS | 2958465 | 6.002 | N | Health/Condition
|  | ARE ANY INSULATORS AT THIS LEVEL MISSING PARTS (NUTS, BOLTS, ETC.)? | SECONDARY-LEVEL | 0 | 2029 | Sec_Insulator_Missing_Part | ARE ANY INSULATORS AT THIS LEVEL MISSING PARTS (NUTS, BOLTS, ETC.)? | INSULATORS | 2958465 | 6.002 | N | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTION OF ANY INSULATOR, OR ITS ASSOCIATED HARDWARE, AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS.” | PRIMARY-LEVEL | 0 | 1052 | Pri_Insulator_Damage | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTION OF ANY INSULATOR, OR ITS ASSOCIATED HARDWARE, AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS.” | INSULATORS | 2958465 | 6.003 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTIONS OF THE INSULATOR OR ITS ASSOCIATED HARDWARE. SELECT ALL THAT APPLY, OR SELECT “NO ABNORMAL CONDITIONS.” | PRIMARY-LEVEL | 0 | 1052 | Pri_Insulator_Damage_1 | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTION OF ANY INSULATOR, OR ITS ASSOCIATED HARDWARE, AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS.” | INSULATORS | 2958465 | 6.003 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTIONS OF THE INSULATOR OR ITS ASSOCIATED HARDWARE. SELECT ALL THAT APPLY, OR SELECT “NO ABNORMAL CONDITIONS.” | PRIMARY-LEVEL | 0 | 1052 | Pri_Insulator_Damage_2 | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTION OF ANY INSULATOR, OR ITS ASSOCIATED HARDWARE, AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS.” | INSULATORS | 2958465 | 6.003 | Y | Health/Condition
|  | Indicate if any of the following types of damage are observed on any portion of any insulator, or its associated hardware, at this level. Select all that apply. | PRIMARY-LEVEL | 0 | 1052 | Pri_Insulator_Damage_3 | (AERIAL/GROUND) Indicate if any of the following types of damage are observed on any portion of any insulator, or its associated hardware, at this level. Select all that apply. | INSULATORS | 2958465 | 6.003 | Y | Health/Condition
|  | Indicate if any of the following types of damage are observed on any portion of any insulator, or its associated hardware, at this level. Select all that apply or select “No abnormal conditions.” | PRIMARY-LEVEL | 0 | 1052 | Pri_Insulator_Damage_4 | Indicate if any of the following types of damage are observed on any portion of any insulator, or its associated hardware, at this level. Select all that apply. | INSULATORS | 2958465 | 6.003 | Y | Health/Condition
|  | Indicate if any of the following types of damage are observed on any portions of the insulator or its associated hardware. Select all that apply, or select “No abnormal conditions.” | PRIMARY-LEVEL | 0 | 1052 | Pri_Insulator_Damage_5 | Indicate if any of the following types of damage are observed on any portions of the insulator or its associated hardware. Select all that apply, or select “No abnormal conditions.” | INSULATORS | 2958465 | 6.003 | Y | Health/Condition
|  | Indicate if any of the following types of damage are observed on any portions of the insulator or its associated hardware. Select all that apply, or select “No abnormal conditions.” | PRIMARY-LEVEL | 0 | 1052 | Pri_Insulator_Damage_6 | Indicate if any of the following types of damage are observed on any portions of the insulator or its associated hardware. Select all that apply, or select “No abnormal conditions.” | INSULATORS | 2958465 | 6.003 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTION OF ANY INSULATOR, OR ITS ASSOCIATED HARDWARE, AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS.” | SECONDARY-LEVEL | 0 | 2027 | Sec_Insulator_Damage | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTION OF ANY INSULATOR, OR ITS ASSOCIATED HARDWARE, AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS.” | INSULATORS | 2958465 | 6.003 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTIONS OF THE INSULATOR OR ITS ASSOCIATED HARDWARE. SELECT ALL THAT APPLY, OR SELECT “NO ABNORMAL CONDITIONS.” | SECONDARY-LEVEL | 0 | 2027 | Sec_Insulator_Damage_1 | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTION OF ANY INSULATOR, OR ITS ASSOCIATED HARDWARE, AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS.” | INSULATORS | 2958465 | 6.003 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTIONS OF THE INSULATOR OR ITS ASSOCIATED HARDWARE. SELECT ALL THAT APPLY, OR SELECT “NO ABNORMAL CONDITIONS.” | SECONDARY-LEVEL | 0 | 2027 | Sec_Insulator_Damage_2 | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE ARE OBSERVED ON ANY PORTION OF ANY INSULATOR, OR ITS ASSOCIATED HARDWARE, AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS.” | INSULATORS | 2958465 | 6.003 | Y | Health/Condition
|  | ARE ANY TOP/SIDE TIE INSULATORS AT THIS LEVEL TOUCHING A CROSSARM? | PRIMARY-LEVEL | 0 | 1056 | Pri_Insulator_TopSide_XARM | ARE ANY TOP/SIDE TIE INSULATORS AT THIS LEVEL TOUCHING A CROSSARM? | INSULATORS | 2958465 | 6.004 | N | Health/Condition
|  | ARE ANY SIDE TIE INSULATORS AT THIS LEVEL TOUCHING A CROSSARM? | PRIMARY-LEVEL | 0 | 1056 | Pri_Insulator_TopSide_XARM_1 | ARE ANY TOP/SIDE TIE INSULATORS AT THIS LEVEL TOUCHING A CROSSARM? | INSULATORS | 2958465 | 6.004 | N | Health/Condition
|  | Are any top/side tie insulators at this level touching a crossarm? | PRIMARY-LEVEL | 0 | 1056 | Pri_Insulator_TopSide_XARM_2 | Are any side tie insulators at this level touching a crossarm? | CROSSARMS - WOOD | 2958465 | 6.004 | N | Health/Condition
|  | Are any top/side tie insulators at this level touching a crossarm? | PRIMARY-LEVEL | 0 | 1056 | Pri_Insulator_TopSide_XARM_3 | Are any top/side tie insulators at this level touching a crossarm? | CROSSARMS - WOOD | 2958465 | 6.004 | N | Health/Condition
|  | ARE ANY TOP/SIDE TIE INSULATORS AT THIS LEVEL TOUCHING A CROSSARM? | SECONDARY-LEVEL | 0 | 2031 | Sec_Insulator_TopSide_XARM | ARE ANY TOP/SIDE TIE INSULATORS AT THIS LEVEL TOUCHING A CROSSARM? | INSULATORS | 2958465 | 6.004 | N | Health/Condition
|  | ARE ANY SIDE TIE INSULATORS AT THIS LEVEL TOUCHING A CROSSARM? | SECONDARY-LEVEL | 0 | 2031 | Sec_Insulator_TopSide_XARM_1 | ARE ANY TOP/SIDE TIE INSULATORS AT THIS LEVEL TOUCHING A CROSSARM? | INSULATORS | 2958465 | 6.004 | N | Health/Condition
|  | Are any side tie insulators at this level touching a crossarm? | SECONDARY-LEVEL | 0 | 2031 | Sec_Insulator_TopSide_XARM_2 | Are any side tie insulators at this level touching a crossarm? | CROSSARMS - WOOD | 2958465 | 6.004 | N | Health/Condition
|  | Are any top/side tie insulators at this level touching a crossarm? | SECONDARY-LEVEL | 0 | 2031 | Sec_Insulator_TopSide_XARM_3 | Are any top/side tie insulators at this level touching a crossarm? | CROSSARMS - WOOD | 2958465 | 6.004 | N | Health/Condition
|  | DO THE INSULATORS CONNECT TO THE STRUCTURE USING A C-HOOK? | PRIMARY-LEVEL | 0 | 1053 | Pri_Insulator_HOOK | DO THE INSULATORS CONNECT TO THE STRUCTURE USING A C-HOOK? | INSULATORS | 2958465 | 6.005 | Y | Health/Condition
|  | Do the insulators connect to the structure using a C-hook? | PRIMARY-LEVEL | 0 | 1053 | Pri_Insulator_HOOK_1 | Do the insulators connect to the structure using a hook? | INSULATORS | 2958465 | 6.005 | Y | Health/Condition
|  | Do the insulators connect to the structure using a C-hook? | PRIMARY-LEVEL | 0 | 1053 | Pri_Insulator_HOOK_2 | Do the insulators connect to the structure using a C-hook? | INSULATORS | 2958465 | 6.005 | Y | Health/Condition
Pri_Insulator_C-HOOK | DO THE INSULATORS CONNECT TO THE STRUCTURE USING A C-HOOK? | DO THE INSULATORS CONNECT TO THE STRUCTURE USING A C-HOOK? | PRIMARY-LEVEL | 99 | 1053 | Pri_Insulator_HOOK_3 | DO THE INSULATORS CONNECT TO THE STRUCTURE USING A C-HOOK? | INSULATORS | 2958465 | 6.005 | Y | Health/Condition
|  | Are any of the following insulator conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1051 | Pri_Insulator_Conditions | (AERIAL/GROUND) Are any of the following insulator conditions observed? Select all that apply. | INSULATORS | 2958465 | 6.006 | Y | Health/Condition
|  | Are any of the following insulator conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1051 | Pri_Insulator_Conditions_1 | Are any of the following insulator conditions observed? Select all that apply. | INSULATORS | 2958465 | 6.006 | Y | Health/Condition
|  | (AERIAL/GROUND) Are any of the following insulator conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2026 | Sec_Insulator_Conditions | (AERIAL/GROUND) Are any of the following insulator conditions observed? Select all that apply. | INSULATORS | 2958465 | 6.006 | Y | Health/Condition
|  | Are any of the following insulator conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2026 | Sec_Insulator_Conditions_1 | Are any of the following insulator conditions observed? Select all that apply. | INSULATORS | 2958465 | 6.006 | Y | Health/Condition
|  | Indicate if any of the following types of damage are observed on any portion of any insulator, or its associated hardware, at this level. Select all that apply or select “No abnormal conditions.” | SECONDARY-LEVEL | 0 | 2028 | Sec_Insulator_Damage_3 | Indicate if any of the following types of damage are observed on any portion of any insulator, or its associated hardware, at this level. Select all that apply. | INSULATORS | 2958465 | 6.008 | N | Health/Condition
|  | Indicate if any of the following types of damage are observed on any portions of the insulator or its associated hardware. Select all that apply, or select “No abnormal conditions.” | SECONDARY-LEVEL | 0 | 2028 | Sec_Insulator_Damage_4 | Indicate if any of the following types of damage are observed on any portions of the insulator or its associated hardware. Select all that apply, or select “No abnormal conditions.” | INSULATORS | 2958465 | 6.008 | N | Health/Condition
|  | Indicate if any of the following types of damage are observed on any portions of the insulator or its associated hardware. Select all that apply, or select “No abnormal conditions.” | SECONDARY-LEVEL | 0 | 2028 | Sec_Insulator_Damage_5 | Indicate if any of the following types of damage are observed on any portions of the insulator or its associated hardware. Select all that apply, or select “No abnormal conditions.” | INSULATORS | 2958465 | 6.008 | N | Health/Condition
|  | (AERIAL/GROUND) Indicate if any of the following types of damage are observed on any portion of any insulator, or its associated hardware, at this level. Select all that apply. | SECONDARY-LEVEL | 0 | 2028 | Sec_Insulator_Damage_6 | (AERIAL/GROUND) Indicate if any of the following types of damage are observed on any portion of any insulator, or its associated hardware, at this level. Select all that apply. | INSULATORS | 2958465 | 6.008 | N | Health/Condition
|  | Indicate if any of the following types of damage are observed on any portions of the insulator or its associated hardware. Select all that apply, or select “No abnormal conditions.” | SECONDARY-LEVEL | 0 | 2028 | Sec_Insulator_Damage_7 | Indicate if any of the following types of damage are observed on any portion of any insulator, or its associated hardware, at this level. Select all that apply or select “No abnormal conditions.” | INSULATORS | 2958465 | 6.008 | N | Health/Condition
|  | Are any of the following primary composite crossarm conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1072 | Pri_XARM_Composite_Conditions | (AERIAL/GROUND) Are any of the following primary composite crossarm conditions observed? Select all that apply. | CROSSARMS - COMPOSITE | 2958465 | 7.006 | Y | Health/Condition
|  | Are any of the following composite crossarm conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1072 | Pri_XARM_Composite_Conditions_1 | Are any of the following composite crossarm conditions observed? Select all that apply. | CROSSARMS - COMPOSITE | 2958465 | 7.006 | Y | Health/Condition
|  | Are any of the following composite crossarm conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1072 | Pri_XARM_Composite_Conditions_2 | Are any of the following primary composite crossarm conditions observed? Select all that apply. | CROSSARMS - COMPOSITE | 2958465 | 7.006 | Y | Health/Condition
|  | Are any of the following composite crossarm conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2046 | Sec_XARM_Composite_Conditions | Are any of the following composite crossarm conditions observed? Select all that apply. | CROSSARMS - COMPOSITE | 2958465 | 7.007 | N | Health/Condition
|  | Are any of the following secomdary composite crossarm conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2046 | Sec_XARM_Composite_Conditions_1 | (AERIAL/GROUND) Are any of the following secondary composite crossarm conditions observed? Select all that apply. | CROSSARMS - COMPOSITE | 2958465 | 7.007 | N | Health/Condition
|  | Are any of the following composite crossarm conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2046 | Sec_XARM_Composite_Conditions_2 | Are any of the following secomdary composite crossarm conditions observed? Select all that apply. | CROSSARMS - COMPOSITE | 2958465 | 7.007 | N | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF FOREIGN OBJECTS ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1029 | Pri_Conductor_Foreign_Object | INDICATE IF ANY OF THE FOLLOWING TYPES OF FOREIGN OBJECTS ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CONDUCTORS - PRIMARY | 2958465 | 8.001 | Y | Health/Condition
|  | Indicate if any of the following types of foreign objects are observed. Select all that apply. | PRIMARY-LEVEL | 0 | 1029 | Pri_Conductor_Foreign_Object_1 | (AERIAL/GROUND) Indicate if any of the following types of foreign objects are observed. Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.001 | Y | Health/Condition
|  | Indicate if any of the following types of foreign objects are observed. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1029 | Pri_Conductor_Foreign_Object_2 | Indicate if any of the following types of foreign objects are observed. Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.001 | Y | Health/Condition
|  | Is there any indication that there is imminent contact of primary conductor with other conductors or public? | PRIMARY-LEVEL | 0 | 1030 | Pri_Conductor_Imminent_Contact | Is there any indication that there is imminent contact of primary conductor, other conductors, guy wires – span or down guy wires, or public? | CONDUCTORS - PRIMARY | 2958465 | 8.003 | N | Health/Condition
|  | Is there any indication that there is imminent contact of primary conductor with other conductors or public? | PRIMARY-LEVEL | 0 | 1030 | Pri_Conductor_Imminent_Contact_1 | Is there any indication that there is imminent contact of primary conductor with other conductors or public? | CONDUCTORS - PRIMARY | 2958465 | 8.003 | N | Health/Condition
|  | DO ALL SPANS IN ALL DIRECTIONS HAVE THE SAME PRIMARY CONDUCTOR TYPES/SIZES? NOTE: DO NOT CONSIDER TAPS/JUMPERS AND/OR ADJACENT SPANS. | PRIMARY-LEVEL | 0 | 1036 | Pri_Conductor_Same_Type | DO ALL SPANS IN ALL DIRECTIONS HAVE THE SAME PRIMARY CONDUCTOR TYPES/SIZES? NOTE: DO NOT CONSIDER TAPS/JUMPERS AND/OR ADJACENT SPANS. | CONDUCTORS - PRIMARY | 2958465 | 8.005 | N | Data Capture
|  | DOES THE SPAN HAVE THE SAME PRIMARY CONDUCTOR TYPES? | PRIMARY-LEVEL | 0 | 1036 | Pri_Conductor_Same_Type_1 | DO ALL SPANS IN ALL DIRECTIONS HAVE THE SAME PRIMARY CONDUCTOR TYPES/SIZES? NOTE: DO NOT CONSIDER TAPS/JUMPERS AND/OR ADJACENT SPANS. | CONDUCTORS - PRIMARY | 2958465 | 8.005 | N | Data Capture
|  | Does the span have the same primary conductor types? | PRIMARY-LEVEL | 0 | 1036 | Pri_Conductor_Same_Type_2 | Does the span have the same primary conductor types? | CONDUCTORS - PRIMARY | 2958465 | 8.005 | N | Data Capture
|  | WHICH OF THE FOLLOWING ESTIMATED SIZES OF PRIMARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY. NOTE: ONLY SELECT PRIMARY CONDUCTOR/PHASE SIZES AND NOT TAPS/JUMPERS. | PRIMARY-LEVEL | 0 | 1037 | Pri_Conductor_Size_Span | WHICH OF THE FOLLOWING ESTIMATED SIZES OF PRIMARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY. NOTE: ONLY SELECT PRIMARY CONDUCTOR/PHASE SIZES AND NOT TAPS/JUMPERS. | CONDUCTORS - PRIMARY | 2958465 | 8.006 | N | Data Capture
|  | WHICH OF THE FOLLOWING SIZES OF PRIMARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY OR SELECT “NONE OF THE ABOVE”. | PRIMARY-LEVEL | 0 | 1037 | Pri_Conductor_Size_Span_1 | WHICH OF THE FOLLOWING ESTIMATED SIZES OF PRIMARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY. NOTE: ONLY SELECT PRIMARY CONDUCTOR/PHASE SIZES AND NOT TAPS/JUMPERS. | CONDUCTORS - PRIMARY | 2958465 | 8.006 | N | Data Capture
|  | WHICH OF THE FOLLOWING TYPES OF PRIMARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY OR SELECT “NONE OF THE ABOVE”. | PRIMARY-LEVEL | 0 | 1037 | Pri_Conductor_Size_Span_2 | WHICH OF THE FOLLOWING ESTIMATED SIZES OF PRIMARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY. NOTE: ONLY SELECT PRIMARY CONDUCTOR/PHASE SIZES AND NOT TAPS/JUMPERS. | CONDUCTORS - PRIMARY | 2958465 | 8.006 | N | Data Capture
|  | WHICH OF THE FOLLOWING ESTIMATED SIZES OF PRIMARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY OR SELECT “NONE OF THE ABOVE”. | PRIMARY-LEVEL | 0 | 1037 | Pri_Conductor_Size_Span_3 | WHICH OF THE FOLLOWING ESTIMATED SIZES OF PRIMARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY. NOTE: ONLY SELECT PRIMARY CONDUCTOR/PHASE SIZES AND NOT TAPS/JUMPERS. | CONDUCTORS - PRIMARY | 2958465 | 8.006 | N | Data Capture
|  | Which of the following estimated sizes of primary conductors are on the span? Select all that apply or select “None of the above”. | PRIMARY-LEVEL | 0 | 1037 | Pri_Conductor_Size_Span_4 | Which of the following estimated sizes of primary conductors are on the span? Select all that apply or select “None of the above”. | CONDUCTORS - PRIMARY | 2958465 | 8.006 | N | Data Capture
|  | Which of the following estimated sizes of primary conductors are on the span? Select all that apply or select “None of the above”. | PRIMARY-LEVEL | 0 | 1037 | Pri_Conductor_Size_Span_5 | Which of the following sizes of primary conductors are on the span? Select all that apply or select “None of the above”. | CONDUCTORS - PRIMARY | 2958465 | 8.006 | N | Data Capture
|  | FOR SLACK SPANS ONLY – DO ALL SLACK SPANS IN ALL DIRECTIONS HAVE PRIMARY CONDUCTOR SPACERS? NOTE: IF ONE SLACK SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “NO”. | PRIMARY-LEVEL | 0 | 1038 | Pri_Conductor_Slack_Spacers | FOR SLACK SPANS ONLY – DO ALL SLACK SPANS IN ALL DIRECTIONS HAVE PRIMARY CONDUCTOR SPACERS? NOTE: IF ONE SLACK SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “NO”. | CONDUCTORS - PRIMARY | 2958465 | 8.008 | N | Data Capture
|  | FOR SLACK SPANS ONLY – DOES THE SPAN HAVE PRIMARY CONDUCTOR SPACERS? | PRIMARY-LEVEL | 0 | 1038 | Pri_Conductor_Slack_Spacers_1 | FOR SLACK SPANS ONLY – DO ALL SLACK SPANS IN ALL DIRECTIONS HAVE PRIMARY CONDUCTOR SPACERS? NOTE: IF ONE SLACK SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “NO”. | CONDUCTORS - PRIMARY | 2958465 | 8.008 | N | Data Capture
|  | For slack spans only – Does the span have primary conductor spacers? | PRIMARY-LEVEL | 0 | 1038 | Pri_Conductor_Slack_Spacers_2 | For slack spans only – Does the span have primary conductor spacers? | CONDUCTORS - PRIMARY | 2958465 | 8.008 | N | Data Capture
|  | WHAT TYPE(S) OF PRIMARY CONDUCTORS ARE INSTALLED? SELECT ALL THAT APPLY. NOTE: ONLY SELECT PRIMARY CONDUCTOR SIZES AND NOT TAPS/JUMPERS. COVERED IS TREE WIRE. AERIAL CABLE IS BUNDLED CABLE. | PRIMARY-LEVEL | 0 | 1043 | Pri_Conductor_Type | WHAT TYPE(S) OF PRIMARY CONDUCTORS ARE INSTALLED? SELECT ALL THAT APPLY. NOTE: ONLY SELECT PRIMARY CONDUCTOR SIZES AND NOT TAPS/JUMPERS. COVERED IS TREE WIRE. AERIAL CABLE IS BUNDLED CABLE. | CONDUCTORS - PRIMARY | 2958465 | 8.009 | N | Data Capture
|  | WHAT TYPE(S) OF PRIMARY CONDUCTORS ARE INSTALLED? SELECT ALL THAT APPLY OR SELECT “NONE OF THE ABOVE”. | PRIMARY-LEVEL | 0 | 1043 | Pri_Conductor_Type_1 | WHAT TYPE(S) OF PRIMARY CONDUCTORS ARE INSTALLED? SELECT ALL THAT APPLY. NOTE: ONLY SELECT PRIMARY CONDUCTOR SIZES AND NOT TAPS/JUMPERS. COVERED IS TREE WIRE. AERIAL CABLE IS BUNDLED CABLE. | CONDUCTORS - PRIMARY | 2958465 | 8.009 | N | Data Capture
|  | What type(s) of primary conductors are installed? Select all that apply or select “None of the above”. | PRIMARY-LEVEL | 0 | 1043 | Pri_Conductor_Type_2 | What type(s) of primary conductors are installed? Select all that apply or select “None of the above”. | CONDUCTORS - PRIMARY | 2958465 | 8.009 | N | Data Capture
|  | What type(s) of primary conductors are installed? Select all that apply or select “None of the above”. | PRIMARY-LEVEL | 0 | 1043 | Pri_Conductor_Type_3 | Which of the following types of primary conductors are on the span? Select all that apply or select “None of the above”. | CONDUCTORS - PRIMARY | 2958465 | 8.009 | N | Data Capture
|  | IF COVERED CONDUCTOR IS INSTALLED, ARE THERE VISIBLE SIGNS OF TRACKING OR DAMAGE ON THE OUTER JACKET? | PRIMARY-LEVEL | 0 | 1027 | Pri_Conductor_Covered_Tracking | IF COVERED CONDUCTOR IS INSTALLED, ARE THERE VISIBLE SIGNS OF TRACKING OR DAMAGE ON THE OUTER JACKET? | CONDUCTORS - PRIMARY | 2958465 | 8.01 | Y | Health/Condition
|  | For covered conductor, are there visible signs of tracking or damage on the outer jacket? | PRIMARY-LEVEL | 0 | 1027 | Pri_Conductor_Covered_Tracking_1 | (AERIAL/GROUND) For covered conductor, are there visible signs of tracking or damage on the outer jacket? | CONDUCTORS - PRIMARY | 2958465 | 8.01 | Y | Health/Condition
|  | If covered conductor is installed, are there visible signs of tracking or damage on the outer jacket? | PRIMARY-LEVEL | 0 | 1027 | Pri_Conductor_Covered_Tracking_2 | For covered conductor, are there visible signs of tracking or damage on the outer jacket? | CONDUCTORS - PRIMARY | 2958465 | 8.01 | Y | Health/Condition
|  | HOW MANY AUTOMATIC (BUMP) SPLICES ARE IN THE PRIMARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | PRIMARY-LEVEL | 0 | 1018 | Pri_Conductor_Bump_Splice_Qty | HOW MANY AUTOMATIC (BUMP) SPLICES ARE IN THE PRIMARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - PRIMARY | 2958465 | 8.011 | N | Data Capture
|  | HOW MANY AUTOMATIC (BUMP) SPLICES ARE IN THE PRIMARY LEVEL? | PRIMARY-LEVEL | 0 | 1018 | Pri_Conductor_Bump_Splice_Qty_1 | HOW MANY AUTOMATIC (BUMP) SPLICES ARE IN THE PRIMARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - PRIMARY | 2958465 | 8.011 | N | Data Capture
|  | How many automatic (bump) splices are in the primary level? | PRIMARY-LEVEL | 0 | 1018 | Pri_Conductor_Bump_Splice_Qty_2 | How many automatic (bump) splices are in the primary level? | CONDUCTORS - PRIMARY | 2958465 | 8.011 | N | Data Capture
|  | HOW MANY PREFORM SPLICES ARE IN THE PRIMARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | PRIMARY-LEVEL | 0 | 1034 | Pri_Conductor_Preform_Splice_Qty | HOW MANY PREFORM SPLICES ARE IN THE PRIMARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - PRIMARY | 2958465 | 8.012 | N | Data Capture
|  | HOW MANY PREFORM SPLICES ARE IN THE PRIMARY LEVEL? | PRIMARY-LEVEL | 0 | 1034 | Pri_Conductor_Preform_Splice_Qty_1 | HOW MANY PREFORM SPLICES ARE IN THE PRIMARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - PRIMARY | 2958465 | 8.012 | N | Data Capture
|  | How many preform splices are in the primary level? | PRIMARY-LEVEL | 0 | 1034 | Pri_Conductor_Preform_Splice_Qty_2 | How many preform splices are in the primary level? | CONDUCTORS - PRIMARY | 2958465 | 8.012 | N | Data Capture
|  | HOW MANY COMPRESSION SPLICES ARE IN THE PRIMARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | PRIMARY-LEVEL | 0 | 1021 | Pri_Conductor_Compression_Splice_Qty | HOW MANY COMPRESSION SPLICES ARE IN THE PRIMARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - PRIMARY | 2958465 | 8.013 | N | Data Capture
|  | HOW MANY COMPRESSION SPLICES ARE IN THE PRIMARY LEVEL? | PRIMARY-LEVEL | 0 | 1021 | Pri_Conductor_Compression_Splice_Qty_1 | HOW MANY COMPRESSION SPLICES ARE IN THE PRIMARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - PRIMARY | 2958465 | 8.013 | N | Data Capture
|  | How many compression splices are in the primary level? | PRIMARY-LEVEL | 0 | 1021 | Pri_Conductor_Compression_Splice_Qty_2 | How many compression splices are in the primary level? | CONDUCTORS - PRIMARY | 2958465 | 8.013 | N | Data Capture
|  | FOR COVERED CONDUCTOR – SELECT ALL APPLICABLE DIRECTIONS COVERED CONDUCTOR IS INSTALLED. SELECT ALL THAT APPLY OR SELECT “NO PRIMARY COVERED CONDUCTORS INSTALLED”. | PRIMARY-LEVEL | 0 | 1025 | Pri_Conductor_Covered_Direction | FOR COVERED CONDUCTOR – SELECT ALL APPLICABLE DIRECTIONS COVERED CONDUCTOR IS INSTALLED. SELECT ALL THAT APPLY OR SELECT “NO PRIMARY COVERED CONDUCTORS INSTALLED”. | CONDUCTORS - PRIMARY | 2958465 | 8.014 | N | Data Capture
|  | FOR COVERED CONDUCTOR – SELECT ALL APPLICABLE DIRECTIONS COVERED CONDUCTOR IS INSTALLED. | PRIMARY-LEVEL | 0 | 1025 | Pri_Conductor_Covered_Direction_1 | FOR COVERED CONDUCTOR – SELECT ALL APPLICABLE DIRECTIONS COVERED CONDUCTOR IS INSTALLED. SELECT ALL THAT APPLY OR SELECT “NO PRIMARY COVERED CONDUCTORS INSTALLED”. | CONDUCTORS - PRIMARY | 2958465 | 8.014 | N | Data Capture
|  | For covered conductor – select all applicable directions covered conductor is installed. | PRIMARY-LEVEL | 0 | 1025 | Pri_Conductor_Covered_Direction_2 | For covered conductor – select all applicable directions covered conductor is installed. | CONDUCTORS - PRIMARY | 2958465 | 8.014 | N | Data Capture
|  | For covered conductor – select all applicable directions covered conductor is installed. Select all that apply or select “No primary covered conductors installed”. | PRIMARY-LEVEL | 0 | 1025 | Pri_Conductor_Covered_Direction_3 | For covered conductor – select all applicable directions covered conductor is installed. Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.014 | N | Data Capture
|  | FOR COVERED CONDUCTOR – INDICATE IF ANY OF THE FOLLOWING COVERED CONDUCTOR COVERS ARE MISSING. SELECT ALL THAT APPLY OR SELECT “NO MISSING COVERED CONDUCTOR COVERS” OR SELECT “NO PRIMARY COVERED CONDUCTOR INSTALLED”. | PRIMARY-LEVEL | 0 | 1026 | Pri_Conductor_Covered_Missing | FOR COVERED CONDUCTOR – INDICATE IF ANY OF THE FOLLOWING COVERED CONDUCTOR COVERS ARE MISSING. SELECT ALL THAT APPLY OR SELECT “NO MISSING COVERED CONDUCTOR COVERS” OR SELECT “NO PRIMARY COVERED CONDUCTOR INSTALLED”. | CONDUCTORS - PRIMARY | 2958465 | 8.015 | Y | Health/Condition
|  | FOR COVERED CONDUCTOR – INDICATE IF ANY OF THE FOLLOWING COVERED CONDUCTOR COVERS ARE MISSING | PRIMARY-LEVEL | 0 | 1026 | Pri_Conductor_Covered_Missing_1 | FOR COVERED CONDUCTOR – INDICATE IF ANY OF THE FOLLOWING COVERED CONDUCTOR COVERS ARE MISSING. SELECT ALL THAT APPLY OR SELECT “NO MISSING COVERED CONDUCTOR COVERS” OR SELECT “NO PRIMARY COVERED CONDUCTOR INSTALLED”. | CONDUCTORS - PRIMARY | 2958465 | 8.015 | Y | Health/Condition
|  | For covered conductor – indicate if any of the following covered conductor covers are missing | PRIMARY-LEVEL | 0 | 1026 | Pri_Conductor_Covered_Missing_2 | For covered conductor – indicate if any of the following covered conductor covers are missing | CONDUCTORS - PRIMARY | 2958465 | 8.015 | Y | Health/Condition
|  | For covered conductor – indicate if any of the following covered conductor covers are missing. Select all that apply or select “No missing covered conductor covers” or select “No primary covered conductor installed”. | PRIMARY-LEVEL | 0 | 1026 | Pri_Conductor_Covered_Missing_3 | For covered conductor – indicate if any of the following covered conductor covers are missing. Select all that apply or select “No missing covered conductor covers.” | CONDUCTORS - PRIMARY | 2958465 | 8.015 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF CONDUCTOR, SPAN, AND/OR GUY WIRE ISSUES IDENTIFIED ON THE POLE LIKELY TO CREATE CONDUCTOR CLASH. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS". | PRIMARY-LEVEL | 0 | 1019 | Pri_Conductor_Clash | INDICATE IF ANY OF THE FOLLOWING TYPES OF CONDUCTOR, SPAN, AND/OR GUY WIRE ISSUES IDENTIFIED ON THE POLE LIKELY TO CREATE CONDUCTOR CLASH. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS". | CONDUCTORS - PRIMARY | 2958465 | 8.016 | Y | Health/Condition
|  | IS THERE ANY INDICATION THAT THERE IS IMMINENT CONTACT OF PRIMARY CONDUCTOR, OTHER CONDUCTORS, GUY WIRES – SPAN OR DOWN GUY WIRES, OR PUBLIC? | PRIMARY-LEVEL | 0 | 1019 | Pri_Conductor_Clash_1 | INDICATE IF ANY OF THE FOLLOWING TYPES OF CONDUCTOR, SPAN, AND/OR GUY WIRE ISSUES IDENTIFIED ON THE POLE LIKELY TO CREATE CONDUCTOR CLASH. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS". | CONDUCTORS - PRIMARY | 2958465 | 8.016 | Y | Health/Condition
|  | IS THERE ANY INDICATION THAT THERE IS IMMINENT CONTACT OF PRIMARY CONDUCTOR WITH OTHER CONDUCTORS OR PUBLIC? | PRIMARY-LEVEL | 0 | 1019 | Pri_Conductor_Clash_2 | INDICATE IF ANY OF THE FOLLOWING TYPES OF CONDUCTOR, SPAN, AND/OR GUY WIRE ISSUES IDENTIFIED ON THE POLE LIKELY TO CREATE CONDUCTOR CLASH. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS". | CONDUCTORS - PRIMARY | 2958465 | 8.016 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF CONDUCTOR, SPAN, AND/OR GUY WIRE ISSUES IDENTIFIED ON THE POLE WILL CREATE CONDUCTOR CLASH. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS". | PRIMARY-LEVEL | 0 | 1019 | Pri_Conductor_Clash_3 | INDICATE IF ANY OF THE FOLLOWING TYPES OF CONDUCTOR, SPAN, AND/OR GUY WIRE ISSUES IDENTIFIED ON THE POLE LIKELY TO CREATE CONDUCTOR CLASH. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS". | CONDUCTORS - PRIMARY | 2958465 | 8.016 | Y | Health/Condition
|  | Indicate if any of the following types of conductor, span, and/or guy wire issues identified on the pole likely to create conductor clash. Select all that apply or select “No abnormal conditions". | PRIMARY-LEVEL | 0 | 1019 | Pri_Conductor_Clash_4 | Indicate if any of the following types of conductor, span, and/or guy wire issues identified on the pole may create conductor clash. Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.016 | Y | Health/Condition
|  | Indicate if any of the following types of conductor, span, and/or guy wire issues identified on the pole will create conductor clash. Select all that apply or select “No abnormal conditions". | PRIMARY-LEVEL | 0 | 1019 | Pri_Conductor_Clash_5 | Indicate if any of the following types of conductor, span, and/or guy wire issues identified on the pole will create conductor clash. Select all that apply or select “No abnormal conditions". | CONDUCTORS - PRIMARY | 2958465 | 8.016 | Y | Health/Condition
|  | (AERIAL/GROUND) Indicate if any of the following types of conductor, span, and/or guy wire issues identified on the pole may create conductor clash. Select all that apply. | PRIMARY-LEVEL | 0 | 1019 | Pri_Conductor_Clash_6 | (AERIAL/GROUND) Indicate if any of the following types of conductor, span, and/or guy wire issues identified on the pole may create conductor clash. Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.016 | Y | Health/Condition
|  | FOR COVERED CONDUCTOR – ARE LIGHTNING ARRESTERS INSTALLED ON STRUCTURES CONTAINING THE FOLLOWING EQUIPMENT: RAR, RSR, CAPACITORS, VOLTAGE REGULATORS, PTS ASSOCIATED WITH RSCS AND PE EQUIPMENT, TRANSFORMERS, BLFS, AND UG DIPS? | PRIMARY-LEVEL | 0 | 1017 | Pri_Conductor_Arrester | FOR COVERED CONDUCTOR – ARE LIGHTNING ARRESTERS INSTALLED ON STRUCTURES CONTAINING THE FOLLOWING EQUIPMENT: RAR, RSR, CAPACITORS, VOLTAGE REGULATORS, PTS ASSOCIATED WITH RSCS AND PE EQUIPMENT, TRANSFORMERS, BLFS, AND UG DIPS? | CONDUCTORS - PRIMARY | 2958465 | 8.017 | Y | Health/Condition | Both
|  | FOR COVERED CONDUCTOR – FOR LINE CONNECTIONS (EXCLUDES CONNECTIONS TO EQUIPMENT), WHAT JUMPER IS USED? | PRIMARY-LEVEL | 0 | 1023 | Pri_Conductor_Connection_Jumper | FOR COVERED CONDUCTOR – FOR LINE CONNECTIONS (EXCLUDES CONNECTIONS TO EQUIPMENT), WHAT JUMPER IS USED? | CONDUCTORS - PRIMARY | 2958465 | 8.018 | Y | Health/Condition | Both
|  | Are there any splices on the conductors? * NOTE: Check all conductors in all directions from pole to mid-span. | PRIMARY-LEVEL | 0 | 1039 | Pri_Conductor_Splices | Are there any splices on the conductors? * NOTE: Check all conductors in all directions from pole to mid-span. | CONDUCTORS - PRIMARY | 2958465 | 8.019 | N | Data Capture
|  | Are there any splices on the primary conductors? * NOTE: Check all conductors in all directions from pole to mid-span. | PRIMARY-LEVEL | 0 | 1039 | Pri_Conductor_Splices_1 | Are there any splices on the primary conductors? * NOTE: Check all conductors in all directions from pole to mid-span. | CONDUCTORS - PRIMARY | 2958465 | 8.019 | N | Data Capture
|  | Are any of the following conductor conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1022 | Pri_Conductor_Conditions | Are any of the following conductor conditions observed? Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.02 | N | Health/Condition
|  | Are any of the following conductor conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1022 | Pri_Conductor_Conditions_1 | (AERIAL/GROUND) Are any of the following conductor conditions observed? Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.02 | N | Health/Condition
|  | ARE THERE ANY FOREIGN MATERIALS IN THE LINES? | SECONDARY-LEVEL | 0 | 2011 | Sec_Conductor_Foreign_Material | ARE THERE ANY FOREIGN MATERIALS IN THE LINES? | CONDUCTORS - SECONDARY | 2958465 | 9.001 | N | Data Capture
|  | WHICH OF THE FOLLOWING INADEQUATE CLEARANCES ARE OBSERVED AT THIS LEVEL AT TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2007 | Sec_Conductor_Clearance_Observered | WHICH OF THE FOLLOWING INADEQUATE CLEARANCES ARE OBSERVED AT THIS LEVEL AT TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CONDUCTORS - SECONDARY | 2958465 | 9.003 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING SIGNS OF INADEQUATE CLEARANCE DISTANCES ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2007 | Sec_Conductor_Clearance_Observered_1 | WHICH OF THE FOLLOWING INADEQUATE CLEARANCES ARE OBSERVED AT THIS LEVEL AT TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CONDUCTORS - SECONDARY | 2958465 | 9.003 | Y | Health/Condition
|  | Which of the following inadequate clearances are observed at this level at time of inspection? Select all that apply. | SECONDARY-LEVEL | 0 | 2007 | Sec_Conductor_Clearance_Observered_2 | (AERIAL/GROUND) Which of the following inadequate clearances are observed at this level at time of inspection? Select all that apply. | CONDUCTORS - SECONDARY | 2958465 | 9.003 | Y | Health/Condition
|  | Indicate if any of the following inadequate clearances are observed at time of inspection. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2007 | Sec_Conductor_Clearance_Observered_3 | Indicate if any of the following inadequate clearances are observed at time of inspection. Select all that apply or select “No abnormal conditions”. | CONDUCTORS - SECONDARY | 2958465 | 9.003 | Y | Health/Condition
|  | Which of the following inadequate clearances are observed at this level at time of inspection. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2007 | Sec_Conductor_Clearance_Observered_4 | Indicate if any of the following signs of inadequate clearance distances are observed at this level. Select all that apply or select “No abnormal conditions”. | CONDUCTORS - SECONDARY | 2958465 | 9.003 | Y | Health/Condition
|  | Indicate if any of the following signs of inadequate clearance distances are observed. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2007 | Sec_Conductor_Clearance_Observered_5 | Indicate if any of the following signs of inadequate clearance distances are observed. Select all that apply or select “No abnormal conditions”. | CONDUCTORS - SECONDARY | 2958465 | 9.003 | Y | Health/Condition
|  | Indicate if any of the following signs of inadequate clearance distances are observed at this level. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2007 | Sec_Conductor_Clearance_Observered_6 | Which of the following inadequate clearances are observed at this level at time of inspection? Select all that apply or select “No abnormal conditions”. | CONDUCTORS - SECONDARY | 2958465 | 9.003 | Y | Health/Condition
|  | Which of the following inadequate clearances are observed at this level at time of inspection? Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2007 | Sec_Conductor_Clearance_Observered_7 | Which of the following inadequate clearances are observed at this level at time of inspection? Select all that apply. | CONDUCTORS - SECONDARY | 2958465 | 9.003 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF PART DAMAGE ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2015 | Sec_Conductor_Part_Damaged | INDICATE IF ANY OF THE FOLLOWING TYPES OF PART DAMAGE ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CONDUCTORS - SECONDARY | 2958465 | 9.004 | Y | Health/Condition
|  | Indicate if any of the following types of part damage are observed. Select all that apply. | SECONDARY-LEVEL | 0 | 2015 | Sec_Conductor_Part_Damaged_1 | (AERIAL/GROUND) Indicate if any of the following types of part damage are observed. Select all that apply. | CONDUCTORS - SECONDARY | 2958465 | 9.004 | Y | Health/Condition
|  | Indicate if any of the following types of part damage are observed. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2015 | Sec_Conductor_Part_Damaged_2 | Indicate if any of the following types of part damage are observed. Select all that apply. | CONDUCTORS - SECONDARY | 2958465 | 9.004 | Y | Health/Condition
|  | WHICH OF THE FOLLOWING SIZES OF SECONDARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY OR SELECT “ONE OR MORE CONDUCTORS ARE SIZES NOT LISTED” IF THE SIZE OF SECONDARY CONDUCTOR IS NOT LISTED. NOTE: ONLY COUNT SECONDARY CONDUCTOR/PHASES, NOT SERVICES. | SECONDARY-LEVEL | 0 | 2019 | Sec_Conductor_Size_Span | WHICH OF THE FOLLOWING SIZES OF SECONDARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY OR SELECT “ONE OR MORE CONDUCTORS ARE SIZES NOT LISTED” IF THE SIZE OF SECONDARY CONDUCTOR IS NOT LISTED. NOTE: ONLY COUNT SECONDARY CONDUCTOR/PHASES, NOT SERVICES. | CONDUCTORS - SECONDARY | 2958465 | 9.005 | N | Data Capture
|  | WHICH OF THE FOLLOWING TYPES OF SECONDARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY OR SELECT “NONE OF THE ABOVE”. | SECONDARY-LEVEL | 0 | 2019 | Sec_Conductor_Size_Span_1 | WHICH OF THE FOLLOWING SIZES OF SECONDARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY OR SELECT “ONE OR MORE CONDUCTORS ARE SIZES NOT LISTED” IF THE SIZE OF SECONDARY CONDUCTOR IS NOT LISTED. NOTE: ONLY COUNT SECONDARY CONDUCTOR/PHASES, NOT SERVICES. | CONDUCTORS - SECONDARY | 2958465 | 9.005 | N | Data Capture
|  | WHICH OF THE FOLLOWING SIZES OF SECONDARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY OR SELECT “NONE OF THE ABOVE”. | SECONDARY-LEVEL | 0 | 2019 | Sec_Conductor_Size_Span_2 | WHICH OF THE FOLLOWING SIZES OF SECONDARY CONDUCTORS ARE ON THE SPAN? SELECT ALL THAT APPLY OR SELECT “ONE OR MORE CONDUCTORS ARE SIZES NOT LISTED” IF THE SIZE OF SECONDARY CONDUCTOR IS NOT LISTED. NOTE: ONLY COUNT SECONDARY CONDUCTOR/PHASES, NOT SERVICES. | CONDUCTORS - SECONDARY | 2958465 | 9.005 | N | Data Capture
|  | Which of the following sizes of secondary conductors are on the span? Select all that apply or select “None of the above”. | SECONDARY-LEVEL | 0 | 2019 | Sec_Conductor_Size_Span_3 | Which of the following sizes of secondary conductors are on the span? Select all that apply or select “None of the above”. | CONDUCTORS - SECONDARY | 2958465 | 9.005 | N | Data Capture
|  | Which of the following sizes of secondary conductors are on the span? Select all that apply or select “One or more conductors are sizes not listed” if the size of secondary conductor is not listed. NOTE: Only count secondary conductor/phases, not services. | SECONDARY-LEVEL | 0 | 2019 | Sec_Conductor_Size_Span_4 | Which of the following sizes of secondary conductors are on the span? Select all that apply. NOTE: Only count secondary conductor/phases, not services. | CONDUCTORS - SECONDARY | 2958465 | 9.005 | N | Data Capture
|  | WHAT TYPE(S) OF SECONDARY CONDUCTORS ARE INSTALLED? SELECT ALL THAT APPLY. | SECONDARY-LEVEL | 0 | 2021 | Sec_Conductor_Type | WHAT TYPE(S) OF SECONDARY CONDUCTORS ARE INSTALLED? SELECT ALL THAT APPLY. | CONDUCTORS - SECONDARY | 2958465 | 9.006 | N | Data Capture
|  | WHAT TYPE(S) OF SECONDARY CONDUCTORS ARE INSTALLED? SELECT ALL THAT APPLY OR SELECT “NONE OF THE ABOVE”. | SECONDARY-LEVEL | 0 | 2021 | Sec_Conductor_Type_1 | WHAT TYPE(S) OF SECONDARY CONDUCTORS ARE INSTALLED? SELECT ALL THAT APPLY. | CONDUCTORS - SECONDARY | 2958465 | 9.006 | N | Data Capture
|  | What type(s) of secondary conductors are installed? Select all that apply or select “One or more conductors are types not listed”. | SECONDARY-LEVEL | 0 | 2021 | Sec_Conductor_Type_2 | (AERIAL/GROUND) What type(s) of secondary conductors are installed? Select all that apply. | CONDUCTORS - SECONDARY | 2958465 | 9.006 | N | Data Capture
|  | What type(s) of secondary conductors are installed? Select all that apply. | SECONDARY-LEVEL | 0 | 2021 | Sec_Conductor_Type_3 | What type(s) of secondary conductors are installed? Select all that apply or select “None of the above”. | CONDUCTORS - SECONDARY | 2958465 | 9.006 | N | Data Capture
|  | Which of the following types of secondary conductors are on the span? Select all that apply or select “None of the above”. | SECONDARY-LEVEL | 0 | 2021 | Sec_Conductor_Type_4 | What type(s) of secondary conductors are installed? Select all that apply or select “One or more conductors are types not listed”. | CONDUCTORS - SECONDARY | 2958465 | 9.006 | N | Data Capture
|  | What type(s) of secondary conductors are installed? Select all that apply or select “None of the above”. | SECONDARY-LEVEL | 0 | 2021 | Sec_Conductor_Type_5 | Which of the following types of secondary conductors are on the span? Select all that apply or select “None of the above”. | CONDUCTORS - SECONDARY | 2958465 | 9.006 | N | Data Capture
|  | What type(s) of secondary conductors are installed? Select all that apply. | SECONDARY-LEVEL | 0 | 2021 | Sec_Conductor_Type_6 | What type(s) of secondary conductors are installed? Select all that apply. | CONDUCTORS - SECONDARY | 2958465 | 9.006 | N | Data Capture
|  | HOW MANY AUTOMATIC (BUMP) SPLICES ARE IN THE SECONDARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | SECONDARY-LEVEL | 0 | 2006 | Sec_Conductor_Bump_Splice_Qty | HOW MANY AUTOMATIC (BUMP) SPLICES ARE IN THE SECONDARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - SECONDARY | 2958465 | 9.008 | N | Data Capture
|  | HOW MANY AUTOMATIC (BUMP) SPLICES ARE IN THE SECONDARY LEVEL? | SECONDARY-LEVEL | 0 | 2006 | Sec_Conductor_Bump_Splice_Qty_1 | HOW MANY AUTOMATIC (BUMP) SPLICES ARE IN THE SECONDARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - SECONDARY | 2958465 | 9.008 | N | Data Capture
|  | How many automatic (bump) splices are in the secondary level? | SECONDARY-LEVEL | 0 | 2006 | Sec_Conductor_Bump_Splice_Qty_2 | How many automatic (bump) splices are in the secondary level? | CONDUCTORS - SECONDARY | 2958465 | 9.008 | N | Data Capture
|  | HOW MANY PREFORM SPLICES ARE IN THE SECONDARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | SECONDARY-LEVEL | 0 | 2017 | Sec_Conductor_Preform_Splice_Qty | HOW MANY PREFORM SPLICES ARE IN THE SECONDARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - SECONDARY | 2958465 | 9.009 | N | Data Capture
|  | HOW MANY PREFORM SPLICES ARE IN THE SECONDARY LEVEL? | SECONDARY-LEVEL | 0 | 2017 | Sec_Conductor_Preform_Splice_Qty_1 | HOW MANY PREFORM SPLICES ARE IN THE SECONDARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - SECONDARY | 2958465 | 9.009 | N | Data Capture
|  | How many preform splices are in the secondary level? | SECONDARY-LEVEL | 0 | 2017 | Sec_Conductor_Preform_Splice_Qty_2 | How many preform splices are in the secondary level? | CONDUCTORS - SECONDARY | 2958465 | 9.009 | N | Data Capture
|  | HOW MANY COMPRESSION SPLICES ARE IN THE SECONDARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | SECONDARY-LEVEL | 0 | 2008 | Sec_Conductor_Compression_Splice_Qty | HOW MANY COMPRESSION SPLICES ARE IN THE SECONDARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - SECONDARY | 2958465 | 9.01 | N | Data Capture
|  | HOW MANY COMPRESSION SPLICES ARE IN THE SECONDARY LEVEL? | SECONDARY-LEVEL | 0 | 2008 | Sec_Conductor_Compression_Splice_Qty_1 | HOW MANY COMPRESSION SPLICES ARE IN THE SECONDARY LEVEL? NOTE: COUNT ALL SPLICES IN ALL DIRECTIONS FROM POLE TO MID-SPAN. | CONDUCTORS - SECONDARY | 2958465 | 9.01 | N | Data Capture
|  | How many compression splices are in the secondary level? | SECONDARY-LEVEL | 0 | 2008 | Sec_Conductor_Compression_Splice_Qty_2 | How many compression splices are in the secondary level? | CONDUCTORS - SECONDARY | 2958465 | 9.01 | N | Data Capture
|  | Are there any splices on the conductors? * NOTE: Check all conductors in all directions from pole to mid-span. | SECONDARY-LEVEL | 0 | 2020 | Sec_Conductor_Splices | Are there any splices on the conductors? * NOTE: Check all conductors in all directions from pole to mid-span. | CONDUCTORS - SECONDARY | 2958465 | 9.011 | N | Data Capture
|  | Are there any splices on the conductors? * NOTE: Check all conductors in all directions from pole to mid-span. | SECONDARY-LEVEL | 0 | 2020 | Sec_Conductor_Splices_1 | Are there any splices on the secondary conductors? * NOTE: Check all conductors in all directions from pole to mid-span. | CONDUCTORS - SECONDARY | 2958465 | 9.011 | N | Data Capture
|  | Are any of the following conductor conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2009 | Sec_Conductor_Conditions | (AERIAL/GROUND) Are any of the following conductor conditions observed? Select all that apply. | CONDUCTORS - SECONDARY | 2958465 | 9.012 | Y | Health/Condition
|  | Are any of the following conductor conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2009 | Sec_Conductor_Conditions_1 | Are any of the following conductor conditions observed? Select all that apply. | CONDUCTORS - SECONDARY | 2958465 | 9.012 | Y | Health/Condition
|  | INDICATE IF ANIMAL GUARDS ARE MISSING FROM ANY OF THE FOLLOWING TYPES OF APPARATUS EQUIPMENT. SELECT ALL THAT APPLY OR SELECT “NO ANIMAL GUARDS MISSING”. | PRIMARY-LEVEL | 0 | 1001 | Pri_Apparatus_Animal_Guard | INDICATE IF ANIMAL GUARDS ARE MISSING FROM ANY OF THE FOLLOWING TYPES OF APPARATUS EQUIPMENT. SELECT ALL THAT APPLY OR SELECT “NO ANIMAL GUARDS MISSING”. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.002 | N | Data Capture
|  | Indicate if animal guards are missing from any of the following types of apparatus equipment. Select all that apply or select “No animal guards missing”. | PRIMARY-LEVEL | 0 | 1001 | Pri_Apparatus_Animal_Guard_1 | Indicate if animal guards are missing from any of the following types of apparatus equipment. Select all that apply. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.002 | N | Data Capture
|  | Indicate if animal guards are missing from any of the following types of apparatus equipment. Select all that apply or select “No animal guards missing”. | SECONDARY-LEVEL | 0 | 2001 | Sec_Apparatus_Animal_Guard | Indicate if animal guards are missing from any of the following types of apparatus equipment. Select all that apply or select “No animal guards missing”. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.002 | N | Data Capture
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF OIL LEAKAGE OR WEEPAGE ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1004 | Pri_Apparatus_Oil_Leak | INDICATE IF ANY OF THE FOLLOWING TYPES OF OIL LEAKAGE OR WEEPAGE ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.004 | N | Health/Condition
|  | Indicate if any of the following types of oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1004 | Pri_Apparatus_Oil_Leak_1 | Indicate if any of the following types of oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.004 | N | Health/Condition
|  | Indicate if any of the following types of oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2003 | Sec_Apparatus_Oil_Leak | Indicate if any of the following types of oil leakage or weepage are observed. Select all that apply or select “No abnormal conditions”. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.004 | N | Health/Condition
|  | ARE TREES OR VEGETATION INTERFERING WITH OPERATION OF ANY RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, OR SWITCHES? | COMMUNICATION-LEVEL | 0 | 3006 | Comm_Apparatus_Tree_Interfering | ARE TREES OR VEGETATION INTERFERING WITH OPERATION OF ANY RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, OR SWITCHES? | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.006 | Y | Health/Condition
|  | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators, sectionalizers, or switches? | COMMUNICATION-LEVEL | 0 | 3006 | Comm_Apparatus_Tree_Interfering_1 | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators, sectionalizers, or switches? | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.006 | Y | Health/Condition
|  | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators, sectionalizers, or switches? | COMMUNICATION-LEVEL | 0 | 3006 | Comm_Apparatus_Tree_Interfering_2 | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators or switches? | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.006 | Y | Health/Condition
|  | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators or switches? | COMMUNICATION-LEVEL | 0 | 3006 | Comm_Apparatus_Tree_Interfering_3 | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators, or switches? | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.006 | Y | Health/Condition
|  | ARE TREES OR VEGETATION INTERFERING WITH OPERATION OF ANY RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, OR SWITCHES? | PRIMARY-LEVEL | 0 | 1005 | Pri_Apparatus_Tree_Interfering | ARE TREES OR VEGETATION INTERFERING WITH OPERATION OF ANY RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, OR SWITCHES? | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.006 | Y | Health/Condition
|  | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators or switches? | PRIMARY-LEVEL | 0 | 1005 | Pri_Apparatus_Tree_Interfering_1 | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators or switches? | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.006 | Y | Health/Condition
|  | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators, sectionalizers, or switches? | PRIMARY-LEVEL | 0 | 1005 | Pri_Apparatus_Tree_Interfering_2 | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators, sectionalizers, or switches? | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.006 | Y | Health/Condition
|  | ARE TREES OR VEGETATION INTERFERING WITH OPERATION OF ANY RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, OR SWITCHES? | SECONDARY-LEVEL | 0 | 2004 | Sec_Apparatus_Tree_Interfering | ARE TREES OR VEGETATION INTERFERING WITH OPERATION OF ANY RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, OR SWITCHES? | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.006 | Y | Health/Condition
|  | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators, sectionalizers, or switches? | SECONDARY-LEVEL | 0 | 2004 | Sec_Apparatus_Tree_Interfering_1 | Are trees or vegetation interfering with operation of any reclosers, PE gear, regulators, sectionalizers, or switches? | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.006 | Y | Health/Condition
|  | Are any of the following apparatus equipment conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1002 | Pri_Apparatus_Conditions | (AERIAL/GROUND) Are any of the following apparatus equipment conditions observed? Select all that apply. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.007 | Y | Health/Condition
|  | Are any of the following apparatus equipment conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1002 | Pri_Apparatus_Conditions_1 | Are any of the following apparatus equipment conditions observed? Select all that apply. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.007 | Y | Health/Condition
|  | (AERIAL/GROUND) Are any of the following apparatus equipment conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2002 | Sec_Apparatus_Conditions | (AERIAL/GROUND) Are any of the following apparatus equipment conditions observed? Select all that apply. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.007 | Y | Health/Condition
|  | Are any of the following apparatus equipment conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2002 | Sec_Apparatus_Conditions_1 | Are any of the following apparatus equipment conditions observed? Select all that apply. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.007 | Y | Health/Condition
|  | (AERIAL/GROUND) If the switch is in the closed position, are all switch blades fully engaged? | PRIMARY-LEVEL | 0 | 1001 | Pri_Apparatus_Switch_Blade_Engaged | (AERIAL/GROUND) If the switch is in the closed position, are all switch blades fully engaged? | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 10.008 | N | Health/Condition | Both
|  | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1050 | Pri_Hardware_Damage | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
|  | IS THERE ANY CORRODED, MISSING, OR BROKEN HARDWARE AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1050 | Pri_Hardware_Damage_1 | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
|  | IS THERE ANY CORRODED, MISSING, BROKEN , OR BENDING HARDWARE AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1050 | Pri_Hardware_Damage_2 | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
|  | Is there any corroded, missing, broken , or bending hardware at this level? | PRIMARY-LEVEL | 0 | 1050 | Pri_Hardware_Damage_3 | Is there any corroded, missing, broken , or bending hardware at this level? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
|  | Is there any corroded, missing, broken, or bending hardware at this level? | PRIMARY-LEVEL | 0 | 1050 | Pri_Hardware_Damage_4 | Is there any corroded, missing, broken, or bending hardware at this level? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
|  | Is there any corroded, missing, broken , or bending hardware at this level? | PRIMARY-LEVEL | 0 | 1050 | Pri_Hardware_Damage_5 | Is there any corroded, missing, or broken hardware at this level? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
hardward_pri | Is there any corroded, missing, or broken hardware at PRIMARY level? | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | PRIMARY-LEVEL | 60 | 1050 | Pri_Hardware_Damage_6 | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
hardward_pri_2 | Is there any corroded, missing, or broken hardware at PRIMARY level? | IS THERE ANY CORRODED, MISSING, OR BROKEN HARDWARE AT THIS LEVEL? | PRIMARY-LEVEL | 60 | 1050 | Pri_Hardware_Damage_7 | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 43952 | 11.001 | N | Health/Condition
hardward_pri | Is there any corroded, missing, or broken hardware at PRIMARY level? | IS THERE ANY CORRODED, MISSING, BROKEN , OR BENDING HARDWARE AT THIS LEVEL? | PRIMARY-LEVEL | 60 | 1050 | Pri_Hardware_Damage_8 | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 44286 | 11.001 | N | Health/Condition
|  | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2025 | Sec_Hardware_Damage | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
|  | IS THERE ANY CORRODED, MISSING, OR BROKEN HARDWARE AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2025 | Sec_Hardware_Damage_1 | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
|  | IS THERE ANY CORRODED, MISSING, BROKEN , OR BENDING HARDWARE AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2025 | Sec_Hardware_Damage_2 | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
|  | Is there any corroded, missing, broken , or bending hardware at this level? | SECONDARY-LEVEL | 0 | 2025 | Sec_Hardware_Damage_3 | Is there any corroded, missing, broken , or bending hardware at this level? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
|  | Is there any corroded, missing, or broken hardware at this level? | SECONDARY-LEVEL | 0 | 2025 | Sec_Hardware_Damage_4 | Is there any corroded, missing, broken, or bending hardware at this level? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
|  | Is there any corroded, missing, or broken hardware at this level? | SECONDARY-LEVEL | 0 | 2025 | Sec_Hardware_Damage_5 | Is there any corroded, missing, or broken hardware at this level? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
hardward_sec_2 | Is there any corroded, missing, or broken hardware at SECONDARY level? | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | SECONDARY-LEVEL | 98 | 2025 | Sec_Hardware_Damage_6 | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 2958465 | 11.001 | N | Health/Condition
hardward_sec | Is there any corroded, missing, or broken hardware at SECONDARY level? | IS THERE ANY CORRODED, MISSING, OR BROKEN HARDWARE AT THIS LEVEL? | SECONDARY-LEVEL | 98 | 2025 | Sec_Hardware_Damage_7 | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 43952 | 11.001 | N | Health/Condition
hardward_sec_2 | Is there any corroded, missing, or broken hardware at SECONDARY level? | IS THERE ANY CORRODED, MISSING, BROKEN , OR BENDING HARDWARE AT THIS LEVEL? | SECONDARY-LEVEL | 98 | 2025 | Sec_Hardware_Damage_8 | IS THERE ANY CORRODED, MISSING, BROKEN, OR BENDING HARDWARE AT THIS LEVEL? | HARDWARE/FRAMING | 44286 | 11.001 | N | Health/Condition
|  | ARE ANY FUSE HOLDERS BURNED OR TRACKING? | PRIMARY-LEVEL | 0 | 1047 | Pri_Fuse_Tracking | ARE ANY FUSE HOLDERS BURNED OR TRACKING? | HARDWARE/FRAMING | 2958465 | 11.002 | Y | Health/Condition
|  | Are any fuse holders burned or tracking? | PRIMARY-LEVEL | 0 | 1047 | Pri_Fuse_Tracking_1 | (AERIAL/GROUND) Are any fuse holders burned or tracking? | FUSES | 2958465 | 11.002 | Y | Health/Condition
|  | Are any fuse holders burned or tracking? | PRIMARY-LEVEL | 0 | 1047 | Pri_Fuse_Tracking_2 | Are any fuse holders burned or tracking? | FUSES | 2958465 | 11.002 | Y | Health/Condition
|  | ARE ANY EQUIPMENT BRACKETS OR BRACES DAMAGED AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1048 | Pri_Hardware_Brace_Damage | ARE ANY EQUIPMENT BRACKETS OR BRACES DAMAGED AT THIS LEVEL? | HARDWARE/FRAMING | 2958465 | 11.003 | N | Health/Condition
|  | ARE ANY EQUIPMENT BRACKETS OR BRACES DAMAGED AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2023 | Sec_Hardware_Brace_Damage | ARE ANY EQUIPMENT BRACKETS OR BRACES DAMAGED AT THIS LEVEL? | HARDWARE/FRAMING | 2958465 | 11.003 | N | Health/Condition
|  | Are any of the following hardware/framing conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1049 | Pri_Hardware_Conditions | (AERIAL/GROUND) Are any of the following hardware/framing conditions observed? Select all that apply. | HARDWARE/FRAMING | 2958465 | 11.004 | Y | Health/Condition
|  | Are any of the following hardware/framing conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1049 | Pri_Hardware_Conditions_1 | Are any of the following hardware/framing conditions observed? Select all that apply. | HARDWARE/FRAMING | 2958465 | 11.004 | Y | Health/Condition
|  | (AERIAL/GROUND) Are any of the following hardware/framing conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2024 | Sec_Hardware_Conditions | (AERIAL/GROUND) Are any of the following hardware/framing conditions observed? Select all that apply. | HARDWARE/FRAMING | 2958465 | 11.004 | Y | Health/Condition
|  | Are any of the following hardware/framing conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2024 | Sec_Hardware_Conditions_1 | Are any of the following hardware/framing conditions observed? Select all that apply. | HARDWARE/FRAMING | 2958465 | 11.004 | Y | Health/Condition
|  | Are any of the following streetlight conditions observed? | SECONDARY-LEVEL | 0 | 2043 | Sec_Streetlight_Conditions | Are any of the following streetlight conditions observed? | HARDWARE/FRAMING | 2958465 | 11.005 | Y | Health/Condition
|  | (AERIAL/GROUND) Are any of the following streetlight conditions observed? | SECONDARY-LEVEL | 0 | 2043 | Sec_Streetlight_Conditions_1 | (AERIAL/GROUND) Are any of the following streetlight conditions observed? | HARDWARE/FRAMING | 2958465 | 11.005 | Y | Health/Condition
|  | (AERIAL/GROUND) Are any of the following streetlight conditions observed? | SECONDARY-LEVEL | 0 | 2043 | Sec_Streetlight_Conditions_2 | (AERIAL/GROUND) Are any of the following streetlight conditions observed? | STREETLIGHT | 2958465 | 11.005 | Y | Health/Condition
|  | ARE ANY SPAN GUYS CRACKED, DAMAGED, DEFLECTED, FRAYED, OR LOOSE? | PRIMARY-LEVEL | 0 | 1067 | Pri_SpanGuy_Damaged | ARE ANY SPAN GUYS CRACKED, DAMAGED, DEFLECTED, FRAYED, OR LOOSE? | SPAN GUYS | 2958465 | 12.001 | N | Health/Condition
|  | ARE ANY SPAN GUYS CRACKED, DAMAGED, DEFLECTED, FRAYED, OR LOOSE? | SECONDARY-LEVEL | 0 | 2040 | Sec_SpanGuy_Damaged | ARE ANY SPAN GUYS CRACKED, DAMAGED, DEFLECTED, FRAYED, OR LOOSE? | SPAN GUYS | 2958465 | 12.001 | N | Health/Condition
|  | IS THERE INADEQUATE CLEARANCE BETWEEN SPAN GUY AND ANY OF THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1065 | Pri_SpanGuy_Clearance | IS THERE INADEQUATE CLEARANCE BETWEEN SPAN GUY AND ANY OF THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | ARE THERE SIGNS OF INADEQUATE CLEARANCE BETWEEN SPAN GUY AND ANY OF THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1065 | Pri_SpanGuy_Clearance_1 | IS THERE INADEQUATE CLEARANCE BETWEEN SPAN GUY AND ANY OF THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | IS THERE IMPROPER CLEARANCE BETWEEN THE SPAN GUY AND THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1065 | Pri_SpanGuy_Clearance_2 | IS THERE INADEQUATE CLEARANCE BETWEEN SPAN GUY AND ANY OF THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | Is there improper clearance between the span guy and the following. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1065 | Pri_SpanGuy_Clearance_3 | Is there inadequate clearance between span guy and any of the following? Select all that apply. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | Is there inadequate clearance between span guy and any of the following. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1065 | Pri_SpanGuy_Clearance_4 | Are there signs of inadequate clearance between span guy and any of the following. Select all that apply or select “No abnormal conditions”. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | Are there signs of inadequate clearance between span guy and any of the following. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1065 | Pri_SpanGuy_Clearance_5 | Is there improper clearance between the span guy and the following. Select all that apply or select “No abnormal conditions”. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | IS THERE INADEQUATE CLEARANCE BETWEEN SPAN GUY AND ANY OF THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2038 | Sec_SpanGuy_Clearance | IS THERE INADEQUATE CLEARANCE BETWEEN SPAN GUY AND ANY OF THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | IS THERE IMPROPER CLEARANCE BETWEEN THE SPAN GUY AND THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2038 | Sec_SpanGuy_Clearance_1 | IS THERE INADEQUATE CLEARANCE BETWEEN SPAN GUY AND ANY OF THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | ARE THERE SIGNS OF INADEQUATE CLEARANCE BETWEEN SPAN GUY AND ANY OF THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2038 | Sec_SpanGuy_Clearance_2 | IS THERE INADEQUATE CLEARANCE BETWEEN SPAN GUY AND ANY OF THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | Is there inadequate clearance between span guy and any of the following? Select all that apply. | SECONDARY-LEVEL | 0 | 2038 | Sec_SpanGuy_Clearance_3 | Is there inadequate clearance between span guy and any of the following? Select all that apply. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | Are there signs of inadequate clearance between span guy and any of the following. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2038 | Sec_SpanGuy_Clearance_4 | Are there signs of inadequate clearance between span guy and any of the following. Select all that apply or select “No abnormal conditions”. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | Is there improper clearance between the span guy and the following. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2038 | Sec_SpanGuy_Clearance_5 | Is there improper clearance between the span guy and the following. Select all that apply or select “No abnormal conditions”. | SPAN GUYS | 2958465 | 12.002 | Y | Health/Condition
|  | ARE ANY SPAN GUYS SAGGING OR EXTREMELY SLACK? | PRIMARY-LEVEL | 0 | 1069 | Pri_SpanGuy_Slack | ARE ANY SPAN GUYS SAGGING OR EXTREMELY SLACK? | SPAN GUYS | 2958465 | 12.003 | N | Health/Condition
|  | ARE ANY SPAN GUYS SAGGING OR EXTREMELY SLACK? | SECONDARY-LEVEL | 0 | 2042 | Sec_SpanGuy_Slack | ARE ANY SPAN GUYS SAGGING OR EXTREMELY SLACK? | SPAN GUYS | 2958465 | 12.003 | N | Health/Condition
|  | Are any of the following span guy conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1066 | Pri_SpanGuy_Conditions | Are any of the following span guy conditions observed? Select all that apply. | SPAN GUYS | 2958465 | 12.004 | Y | Health/Condition
|  | Are any of the following span guy conditions observed? Select all that apply. | SECONDARY-LEVEL | 0 | 2039 | Sec_SpanGuy_Conditions | Are any of the following span guy conditions observed? Select all that apply. | SPAN GUYS | 2958465 | 12.004 | Y | Health/Condition
|  | IS THERE INADEQUATE CLEARANCE BETWEEN DOWN GUY AND ANY OF THE FOLLOWING? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4011 | Pub_DownGuy_Clearance | IS THERE INADEQUATE CLEARANCE BETWEEN DOWN GUY AND ANY OF THE FOLLOWING? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | DOWN GUYS | 2958465 | 13.002 | Y | Health/Condition
|  | IS THERE IMPROPER CLEARANCE BETWEEN THE DOWN GUY AND THE FOLLOWING. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4011 | Pub_DownGuy_Clearance_1 | IS THERE INADEQUATE CLEARANCE BETWEEN DOWN GUY AND ANY OF THE FOLLOWING? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | DOWN GUYS | 2958465 | 13.002 | Y | Health/Condition
|  | ARE THERE SIGNS OF INADEQUATE CLEARANCE BETWEEN DOWN GUY AND ANY OF THE FOLLOWING? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4011 | Pub_DownGuy_Clearance_2 | IS THERE INADEQUATE CLEARANCE BETWEEN DOWN GUY AND ANY OF THE FOLLOWING? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | DOWN GUYS | 2958465 | 13.002 | Y | Health/Condition
|  | Is there inadequate clearance between down guy and any of the following? Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4011 | Pub_DownGuy_Clearance_3 | Are there signs of inadequate clearance between down guy and any of the following? Select all that apply or select “No abnormal conditions”. | DOWN GUYS | 2958465 | 13.002 | Y | Health/Condition
|  | Are there signs of inadequate clearance between down guy and any of the following? Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4011 | Pub_DownGuy_Clearance_4 | Is there improper clearance between the down guy and the following. Select all that apply or select “No abnormal conditions”. | DOWN GUYS | 2958465 | 13.002 | Y | Health/Condition
|  | Is there improper clearance between the down guy and the following. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4011 | Pub_DownGuy_Clearance_5 | Is there inadequate clearance between down guy and any of the following? Select all that apply. | DOWN GUYS | 2958465 | 13.002 | Y | Health/Condition
|  | ARE DOWN GUY WIRES SAGGING OR EXTREMELY SLACK? | PUBLIC-LEVEL | 0 | 4015 | Pub_DownGuy_Sagging | ARE DOWN GUY WIRES SAGGING OR EXTREMELY SLACK? | DOWN GUYS | 2958465 | 13.003 | N | Data Capture
|  | Are any of the following down guy conditions observed? Select all that apply. | PUBLIC-LEVEL | 0 | 4012 | Pub_DownGuy_Conditions | Are any of the following down guy conditions observed? Select all that apply. | DOWN GUYS | 2958465 | 13.004 | N | Health/Condition
|  | Which of the following SCE distribution down guy anchor types exist? Select all that apply. | PUBLIC-LEVEL | 0 | 4010 | Pub_DownGuy_Anchor_Type | Which of the following SCE distribution down guy anchor types exist? Select all that apply. | DOWN GUYS | 2958465 | 13.006 | Y | Health/Condition
|  | Quantity of 3 Eye anchors | PUBLIC-LEVEL | 0 | 4003 | Pub_DownGuy_Anchor_3Eye_Qty | Quantity of 3 Eye anchors | DOWN GUYS | 2958465 | 13.007 | N | Data Capture
|  | Indicate the type for all 3 Eye Anchors by identifying the stamp or construction configuration. Select all that apply. | PUBLIC-LEVEL | 0 | 4004 | Pub_DownGuy_Anchor_3Eye_Type | Indicate the type for all 3 Eye Anchors by identifying the stamp or construction configuration. Select all that apply. | DOWN GUYS | 2958465 | 13.008 | N | Data Capture
|  | Is there truck access to the PISA anchors at the time of inspection? | PUBLIC-LEVEL | 0 | 4009 | Pub_DownGuy_Anchor_PISA_Truck_Access | Is there truck access to the PISA anchors at the time of inspection? | DOWN GUYS | 2958465 | 13.009 | N | Data Capture
|  | Quantity of 2 Eye anchors | PUBLIC-LEVEL | 0 | 4002 | Pub_DownGuy_Anchor_2Eye_Type | Quantity of 2 Eye anchors | DOWN GUYS | 2958465 | 13.01 | N | Data Capture
|  | Quantity of 1 Eye anchors | PUBLIC-LEVEL | 0 | 4001 | Pub_DownGuy_Anchor_1Eye_Type | Quantity of 1 Eye anchors | DOWN GUYS | 2958465 | 13.011 | N | Data Capture
|  | Quantity of buried anchors | PUBLIC-LEVEL | 0 | 4005 | Pub_DownGuy_Anchor_Buried_Qty | Quantity of buried anchors | DOWN GUYS | 2958465 | 13.012 | N | Data Capture
|  | Quantity of anchor extension rods | PUBLIC-LEVEL | 0 | 4006 | Pub_DownGuy_Anchor_Ext_Qty | Quantity of anchor extension rods | DOWN GUYS | 2958465 | 13.013 | N | Data Capture
|  | Quantity of other anchors | PUBLIC-LEVEL | 0 | 4007 | Pub_DownGuy_Anchor_Other_Qty | Quantity of other anchors | DOWN GUYS | 2958465 | 13.014 | N | Data Capture
|  | ARE THERE ANY SIGNS OF DAMAGE SUCH AS DISCOLORATION ON THE RISER/POTHEAD? | PRIMARY-LEVEL | 0 | 1063 | Pri_Pothead_Riser_Discoloration | ARE THERE ANY SIGNS OF DAMAGE SUCH AS DISCOLORATION ON THE RISER/POTHEAD? | TERMINATIONS | 2958465 | 14.001 | Y | Health/Condition
|  | Are there any signs of damage such as discoloration on the Riser/Pothead? | PRIMARY-LEVEL | 0 | 1063 | Pri_Pothead_Riser_Discoloration_1 | Are there any signs of damage such as discoloration on the Riser/Pothead? | TERMINATIONS | 2958465 | 14.001 | Y | Health/Condition
pothead | NULL | INDICATE IF THE POTHEAD SHOWS SIGNS OF ANY OF THE FOLLOWING CONDITIONS IN THE PRIMARY LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 69 | 1062 | Pri_Pothead_Condition | INDICATE IF THE POTHEAD SHOWS SIGNS OF ANY OF THE FOLLOWING CONDITIONS IN THE PRIMARY LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | TERMINATIONS | 2958465 | 14.002 | Y | Health/Condition
|  | INDICATE IF THE POTHEAD SHOWS SIGNS OF ANY OF THE FOLLOWING CONDITIONS IN THE PRIMARY LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1062 | Pri_Pothead_Conditions | INDICATE IF THE POTHEAD SHOWS SIGNS OF ANY OF THE FOLLOWING CONDITIONS IN THE PRIMARY LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | TERMINATIONS | 2958465 | 14.002 | Y | Health/Condition
|  | Indicate if the Pothead shows signs of any of the following conditions in the primary level. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1062 | Pri_Pothead_Conditions_1 | Indicate if the Pothead shows signs of any of the following conditions in the primary level. Select all that apply. | TERMINATIONS | 2958465 | 14.002 | Y | Health/Condition
|  | (AERIAL/GROUND) Indicate if the Pothead shows signs of any of the following conditions in the primary level. Select all that apply. | PRIMARY-LEVEL | 0 | 1062 | Pri_Pothead_Conditions_2 | (AERIAL/GROUND) Indicate if the Pothead shows signs of any of the following conditions in the primary level. Select all that apply. | TERMINATIONS | 2958465 | 14.002 | Y | Health/Condition
|  | Indicate if the Pothead shows signs of any of the following conditions in the primary level. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1062 | Pri_Pothead_Conditions_3 | Indicate if the Pothead shows signs of any of the following conditions in the primary level. Select all that apply or select “No abnormal conditions”. | TERMINATIONS | 2958465 | 14.002 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING RISER CONDITIONS ARE OBSERVED ON THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4049 | Pub_Riser_Conditions | INDICATE IF ANY OF THE FOLLOWING RISER CONDITIONS ARE OBSERVED ON THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | TERMINATIONS | 2958465 | 14.003 | Y | Health/Condition
|  | Indicate if any of the following Riser conditions are observed on the structure. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4049 | Pub_Riser_Conditions_1 | (AERIAL/GROUND) Indicate if any of the following Riser conditions are observed on the structure. Select all that apply or select “No abnormal conditions”. | TERMINATIONS | 2958465 | 14.003 | Y | Health/Condition
|  | Indicate if any of the following Riser conditions are observed on the structure. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4049 | Pub_Riser_Conditions_2 | Indicate if any of the following Riser conditions are observed on the structure. Select all that apply or select “No abnormal conditions”. | TERMINATIONS | 2958465 | 14.003 | Y | Health/Condition
riser_pub | NULL | INDICATE IF ANY OF THE FOLLOWING RISER CONDITIONS ARE OBSERVED ON THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 133 | 4049 | Pub_Riser_Conditions_3 | INDICATE IF ANY OF THE FOLLOWING RISER CONDITIONS ARE OBSERVED ON THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | TERMINATIONS | 2958465 | 14.003 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING RISER CONDITIONS ARE OBSERVED ON THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2035 | Sec_Riser_Conditions | INDICATE IF ANY OF THE FOLLOWING RISER CONDITIONS ARE OBSERVED ON THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | TERMINATIONS | 2958465 | 14.003 | Y | Health/Condition
|  | (AERIAL/GROUND) Indicate if any of the following Riser conditions are observed on the structure. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2035 | Sec_Riser_Conditions_1 | (AERIAL/GROUND) Indicate if any of the following Riser conditions are observed on the structure. Select all that apply or select “No abnormal conditions”. | TERMINATIONS | 2958465 | 14.003 | Y | Health/Condition
|  | Indicate if any of the following Riser conditions are observed on the structure. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2035 | Sec_Riser_Conditions_2 | Indicate if any of the following Riser conditions are observed on the structure. Select all that apply or select “No abnormal conditions”. | TERMINATIONS | 2958465 | 14.003 | Y | Health/Condition
|  | Are any of the following Riser/Pothead conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1064 | Pri_Rise_Pothead_Conditions | (AERIAL/GROUND) Are any of the following Riser/Pothead conditions observed? Select all that apply. | TERMINATIONS | 2958465 | 14.004 | Y | Health/Condition
|  | Are any of the following Riser/Pothead conditions observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1064 | Pri_Rise_Pothead_Conditions_1 | Are any of the following Riser/Pothead conditions observed? Select all that apply. | TERMINATIONS | 2958465 | 14.004 | Y | Health/Condition
|  | WHAT TYPE OF SERVICE DROPS ARE INSTALLED? SELECT ALL THAT APPLY. | SECONDARY-LEVEL | 0 | 2037 | Sec_ServiceDrops_Type | WHAT TYPE OF SERVICE DROPS ARE INSTALLED? SELECT ALL THAT APPLY. | SERVICE DROPS | 2958465 | 15.001 | N | Data Capture
|  | WHAT TYPE OF SERVICE DROPS ARE INSTALLED? | SECONDARY-LEVEL | 0 | 2037 | Sec_ServiceDrops_Type_1 | WHAT TYPE OF SERVICE DROPS ARE INSTALLED? SELECT ALL THAT APPLY. | SERVICE DROPS | 2958465 | 15.001 | N | Data Capture
|  | What type of service drops are installed? | SECONDARY-LEVEL | 0 | 2037 | Sec_ServiceDrops_Type_2 | What type of service drops are installed? | SERVICE DROPS | 2958465 | 15.001 | N | Data Capture
|  | INDICATE IF ANY OF THE FOLLOWING INADEQUATE CLEARANCES FROM SERVICE DROP CONDUCTORS ARE OBSERVED AT TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2036 | Sec_ServiceDrops_Clearance | INDICATE IF ANY OF THE FOLLOWING INADEQUATE CLEARANCES FROM SERVICE DROP CONDUCTORS ARE OBSERVED AT TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SERVICE DROPS | 2958465 | 15.004 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING SIGNS OF INADEQUATE CLEARANCE DISTANCES ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2036 | Sec_ServiceDrops_Clearance_1 | INDICATE IF ANY OF THE FOLLOWING INADEQUATE CLEARANCES FROM SERVICE DROP CONDUCTORS ARE OBSERVED AT TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SERVICE DROPS | 2958465 | 15.004 | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING INADEQUATE CLEARANCES ARE OBSERVED AT TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2036 | Sec_ServiceDrops_Clearance_2 | INDICATE IF ANY OF THE FOLLOWING INADEQUATE CLEARANCES FROM SERVICE DROP CONDUCTORS ARE OBSERVED AT TIME OF INSPECTION. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SERVICE DROPS | 2958465 | 15.004 | Y | Health/Condition
|  | Indicate if any of the following inadequate clearances from service drop conductors are observed at time of inspection. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2036 | Sec_ServiceDrops_Clearance_3 | (AERIAL/GROUND) Indicate if any of the following inadequate clearances are observed at time of inspection. Select all that apply or select “No abnormal conditions”. | SERVICE DROPS | 2958465 | 15.004 | Y | Health/Condition
|  | Indicate if any of the following inadequate clearances from service drop conductors are observed at time of inspection. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2036 | Sec_ServiceDrops_Clearance_4 | Indicate if any of the following inadequate clearances from service drop conductors are observed at time of inspection. Select all that apply or select “No abnormal conditions”. | SERVICE DROPS | 2958465 | 15.004 | Y | Health/Condition
|  | HAS THE GROUND LEAD DISCONNECTED OR ANY ARRESTER OPERATED? | PRIMARY-LEVEL | 0 | 1006 | Pri_Arrester_Ground_Lead | HAS THE GROUND LEAD DISCONNECTED OR ANY ARRESTER OPERATED? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 16.001 | Y | Health/Condition
|  | Has the ground lead disconnected or any arrester operated? | PRIMARY-LEVEL | 0 | 1006 | Pri_Arrester_Ground_Lead_1 | Has the ground lead disconnected or any arrester operated? | LIGHTNING ARRESTERS | 2958465 | 16.001 | Y | Health/Condition
Pri_Pole_Ground_Lead | HAS THE GROUND LEAD DISCONNECTED OR ANY ARRESTER OPERATED? | HAS THE GROUND LEAD DISCONNECTED OR ANY ARRESTER OPERATED? | PRIMARY-LEVEL | 99 | 1006 | Pri_Arrester_Ground_Lead_2 | HAS THE GROUND LEAD DISCONNECTED OR ANY ARRESTER OPERATED? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 16.001 | Y | Health/Condition
|  | Are any of the following structure conditions observed? Select all that apply. | PUBLIC-LEVEL | 0 | 4035 | Pub_Pole_Steel_Conditions | Are any of the following structure conditions observed? Select all that apply. | POLES - STEEL, STREETLIGHT ONLY POLE - STEEL | 2958465 | 17.001 | Y | Health/Condition
|  | Indicate which of the following defects are present on or around the structure. Select all that apply. | PUBLIC-LEVEL | 0 | 4036 | Pub_Pole_Steel_Defects_1 | Indicate which of the following defects are present on or around the structure. Select all that apply. | POLES - STEEL, STREETLIGHT ONLY POLE - STEEL | 2958465 | 17.002 | Y | Health/Condition
|  | Indicate if any of the following types of structural failure are observed at this level. Select all that apply. | PUBLIC-LEVEL | 0 | 4038 | Pub_Pole_Steel_Structural_Failure | Indicate if any of the following types of structural failure are observed at this level. Select all that apply. | POLES - STEEL, STREETLIGHT ONLY POLE - STEEL | 2958465 | 17.003 | Y | Health/Condition
|  | Indicate if the pole is showing any of the following signs of pole lean. Otherwise, select “Pole not leaning". | PUBLIC-LEVEL | 0 | 4037 | Pub_Pole_Steel_Lean_1 | Indicate if the pole is showing any of the following signs of pole lean. | POLES - STEEL, STREETLIGHT ONLY POLE - STEEL | 2958465 | 17.004 | Y | Health/Condition
|  | Indicate if the pole is showing any of the following signs of pole lean. Otherwise, select “Pole not leaning". | PUBLIC-LEVEL | 0 | 4037 | Pub_Pole_Steel_Lean_2 | Indicate if the pole is showing any of the following signs of pole lean. Otherwise, select “Pole not leaning". | POLES - STEEL, STREETLIGHT ONLY POLE - STEEL | 2958465 | 17.004 | Y | Health/Condition
|  | Are any of the following structure conditions observed? Select all that apply. | PUBLIC-LEVEL | 0 | 4026 | Pub_Pole_Concrete_Conditions | Are any of the following structure conditions observed? Select all that apply. | STREETLIGHT ONLY POLE - CONCRETE | 2958465 | 18.001 | Y | Health/Condition
|  | Indicate which of the following defects are present on or around the structure. Select all that apply. | PUBLIC-LEVEL | 0 | 4027 | Pub_Pole_Concrete_Defects | Indicate which of the following defects are present on or around the structure. Select all that apply. | STREETLIGHT ONLY POLE - CONCRETE | 2958465 | 18.002 | Y | Health/Condition
|  | Indicate if any of the following types of structural damage are observed on the pole. Select all that apply. | PUBLIC-LEVEL | 0 | 4028 | Pub_Pole_Concrete_Structural_Failure | Indicate if any of the following types of structural damage are observed on the pole. Select all that apply. | STREETLIGHT ONLY POLE - CONCRETE | 2958465 | 18.003 | Y | Health/Condition
|  | DOES THE POLE NUMBER IN THE APP MATCH THE STRUCTURE NUMBER ON THE STRUCTURE THAT YOU ARE INSPECTING? | PUBLIC-LEVEL | 0 | 4041 | Pub_Pole_Structure_Num_Matched | DOES THE POLE NUMBER IN THE APP MATCH THE STRUCTURE NUMBER ON THE STRUCTURE THAT YOU ARE INSPECTING? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.005A | Y | Health/Condition
|  | IS THE STRUCTURE NUMBER THE YELLOW AND BLACK STYLE? | PUBLIC-LEVEL | 0 | 4043 | Pub_Pole_Structure_Num_YellowBlack | IS THE STRUCTURE NUMBER THE YELLOW AND BLACK STYLE? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.005B | N | Data Capture
|  | HOW MANY INSULATORS ARE INSTALLED AT THIS LEVEL? NOTE: DEAD-END INSULATORS COUNT AS 1, COUNT PRIMARY POLYMER INSULATORS IF APPLICABLE, COUNT 3 PHASE BANK DELTA INSULATORS AND/OR ALL PRIMARY TAP SUPPORTING INSULATORS. | PRIMARY-LEVEL | 0 | 1055 | Pri_Insulator_Qty | HOW MANY INSULATORS ARE INSTALLED AT THIS LEVEL? NOTE: DEAD-END INSULATORS COUNT AS 1, COUNT PRIMARY POLYMER INSULATORS IF APPLICABLE, COUNT 3 PHASE BANK DELTA INSULATORS AND/OR ALL PRIMARY TAP SUPPORTING INSULATORS. | INSULATORS | 2958465 | 0.014A | N | Data Capture
|  | HOW MANY PRIMARY INSULATORS ARE INSTALLED AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1055 | Pri_Insulator_Qty_1 | HOW MANY INSULATORS ARE INSTALLED AT THIS LEVEL? NOTE: DEAD-END INSULATORS COUNT AS 1, COUNT PRIMARY POLYMER INSULATORS IF APPLICABLE, COUNT 3 PHASE BANK DELTA INSULATORS AND/OR ALL PRIMARY TAP SUPPORTING INSULATORS. | INSULATORS | 2958465 | 0.014A | N | Data Capture
|  | HOW MANY INSULATORS ARE INSTALLED AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1055 | Pri_Insulator_Qty_2 | HOW MANY INSULATORS ARE INSTALLED AT THIS LEVEL? NOTE: DEAD-END INSULATORS COUNT AS 1, COUNT PRIMARY POLYMER INSULATORS IF APPLICABLE, COUNT 3 PHASE BANK DELTA INSULATORS AND/OR ALL PRIMARY TAP SUPPORTING INSULATORS. | INSULATORS | 2958465 | 0.014A | N | Data Capture
|  | How many insulators are installed at this level? | PRIMARY-LEVEL | 0 | 1055 | Pri_Insulator_Qty_3 | How many insulators are installed at this level? | INSULATORS | 2958465 | 0.014A | N | Data Capture
|  | How many insulators are installed at this level? | PRIMARY-LEVEL | 0 | 1055 | Pri_Insulator_Qty_4 | How many primary insulators are installed at this level? | INSULATORS | 2958465 | 0.014A | N | Data Capture
|  | HOW MANY LINE/HIGH SIDE CONDUCTORS ARE INSTALLED AT THIS LEVEL? NOTE: THIS IS NOT LOAD-SIDE PRIMARY. DO NOT COUNT BUCK ARM PRIMARY OR PRIMARY FED FROM SAME CIRCUIT/TAP-LINE – ONLY DIFFERENT CIRCUITS/VOLTAGES. | PRIMARY-LEVEL | 0 | 1033 | Pri_Conductor_Phase_Qty | HOW MANY LINE/HIGH SIDE CONDUCTORS ARE INSTALLED AT THIS LEVEL? NOTE: THIS IS NOT LOAD-SIDE PRIMARY. DO NOT COUNT BUCK ARM PRIMARY OR PRIMARY FED FROM SAME CIRCUIT/TAP-LINE – ONLY DIFFERENT CIRCUITS/VOLTAGES. | CONDUCTORS - PRIMARY | 2958465 | 0.014B | N | Data Capture
|  | HOW MANY PHASES ARE INSTALLED AT THIS LEVEL? (MULTI-PLEX IS COUNTED AS 1 PHASE) | PRIMARY-LEVEL | 0 | 1033 | Pri_Conductor_Phase_Qty_1 | HOW MANY LINE/HIGH SIDE CONDUCTORS ARE INSTALLED AT THIS LEVEL? NOTE: THIS IS NOT LOAD-SIDE PRIMARY. DO NOT COUNT BUCK ARM PRIMARY OR PRIMARY FED FROM SAME CIRCUIT/TAP-LINE – ONLY DIFFERENT CIRCUITS/VOLTAGES. | CONDUCTORS - PRIMARY | 2958465 | 0.014B | N | Data Capture
|  | HOW MANY PHASES ARE INSTALLED AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1033 | Pri_Conductor_Phase_Qty_2 | HOW MANY LINE/HIGH SIDE CONDUCTORS ARE INSTALLED AT THIS LEVEL? NOTE: THIS IS NOT LOAD-SIDE PRIMARY. DO NOT COUNT BUCK ARM PRIMARY OR PRIMARY FED FROM SAME CIRCUIT/TAP-LINE – ONLY DIFFERENT CIRCUITS/VOLTAGES. | CONDUCTORS - PRIMARY | 2958465 | 0.014B | N | Data Capture
|  | How many line side phases are installed at this level? | PRIMARY-LEVEL | 0 | 1033 | Pri_Conductor_Phase_Qty_3 | How many conductors are installed at this level? | CONDUCTORS - PRIMARY | 2958465 | 0.014B | N | Data Capture
|  | How many phases are installed at this level? | PRIMARY-LEVEL | 0 | 1033 | Pri_Conductor_Phase_Qty_4 | How many line side phases are installed at this level? | CONDUCTORS - PRIMARY | 2958465 | 0.014B | N | Data Capture
|  | How many phases are installed at this level? (multi-plex is counted as 1 phase) | PRIMARY-LEVEL | 0 | 1033 | Pri_Conductor_Phase_Qty_5 | How many phases are installed at this level? | CONDUCTORS - PRIMARY | 2958465 | 0.014B | N | Data Capture
|  | How many phases are installed at this level? (multi-plex is counted as 1 phase) | PRIMARY-LEVEL | 0 | 1033 | Pri_Conductor_Phase_Qty_6 | How many phases are installed at this level? (multi-plex is counted as 1 phase) | CONDUCTORS - PRIMARY | 2958465 | 0.014B | N | Data Capture
|  | HOW MANY OVERHEAD TRANSFORMERS ARE INSTALLED ON THIS STRUCTURE? | PRIMARY-LEVEL | 0 | 1110 | Pri_XFMR_Qty | HOW MANY OVERHEAD TRANSFORMERS ARE INSTALLED ON THIS STRUCTURE? | OVERHEAD TRANSFORMERS | 2958465 | 0.014C | N | Data Capture
|  | HOW MANY OVERHEAD CAPACITOR BANKS ARE INSTALLED ON THIS STRUCTURE? NOTE: ONLY COUNT ENTIRE CAPACITOR BANK AND NOT INDIVIDUAL CAPACITOR UNITS. | PRIMARY-LEVEL | 0 | 1013 | Pri_CAP_Bank_Qty | HOW MANY OVERHEAD CAPACITOR BANKS ARE INSTALLED ON THIS STRUCTURE? NOTE: ONLY COUNT ENTIRE CAPACITOR BANK AND NOT INDIVIDUAL CAPACITOR UNITS. | OVERHEAD CAPACITORS | 2958465 | 0.014D | N | Data Capture
|  | HOW MANY OVERHEAD CAPACITORS ARE INSTALLED ON THIS STRUCTURE? | PRIMARY-LEVEL | 0 | 1013 | Pri_CAP_Bank_Qty_1 | HOW MANY OVERHEAD CAPACITOR BANKS ARE INSTALLED ON THIS STRUCTURE? NOTE: ONLY COUNT ENTIRE CAPACITOR BANK AND NOT INDIVIDUAL CAPACITOR UNITS. | OVERHEAD CAPACITORS | 2958465 | 0.014D | N | Data Capture
|  | How many overhead capacitor banks are installed on this structure? NOTE: Only count entire capacitor bank and NOT individual capacitor units. | PRIMARY-LEVEL | 0 | 1013 | Pri_CAP_Bank_Qty_2 | How many overhead capacitors are installed on this structure? | OVERHEAD CAPACITORS | 2958465 | 0.014D | N | Data Capture
|  | How many overhead capacitor banks are installed on this structure? NOTE: Only count entire capacitor bank and NOT individual capacitor units. | PRIMARY-LEVEL | 0 | 1013 | Pri_CAP_Bank_Qty_3 | How many overhead capacitor banks are installed on this structure? NOTE: Only count entire capacitor bank and NOT individual capacitor units. | OVERHEAD CAPACITORS | 2958465 | 0.014D | N | Data Capture
|  | HOW MANY SPAN GUYS ARE INSTALLED AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1068 | Pri_SpanGuy_Qty | HOW MANY SPAN GUYS ARE INSTALLED AT THIS LEVEL? | SPAN GUYS | 2958465 | 0.014E | N | Data Capture
|  | HOW MANY SPAN GUYS ARE INSTALLED AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2041 | Sec_SpanGuy_Qty | HOW MANY SPAN GUYS ARE INSTALLED AT THIS LEVEL? | SPAN GUYS | 2958465 | 0.014E | N | Data Capture
|  | HOW MANY SCE DOWN GUYS ARE INSTALLED ON THIS STRUCTURE? | PUBLIC-LEVEL | 0 | 4014 | Pub_DownGuy_Qty | HOW MANY SCE DOWN GUYS ARE INSTALLED ON THIS STRUCTURE? | DOWN GUYS | 2958465 | 0.014F | N | Data Capture
|  | HOW MANY DOWN GUYS ARE INSTALLED ON THIS STRUCTURE? | PUBLIC-LEVEL | 0 | 4014 | Pub_DownGuy_Qty_1 | HOW MANY SCE DOWN GUYS ARE INSTALLED ON THIS STRUCTURE? | DOWN GUYS | 2958465 | 0.014F | N | Data Capture
|  | How many SCE down guys are installed on this structure? | PUBLIC-LEVEL | 0 | 4014 | Pub_DownGuy_Qty_2 | How many down guys are installed on this structure? | DOWN GUYS | 2958465 | 0.014F | N | Data Capture
|  | HOW MANY SURGE ARRESTER/LIGHTNING ARRESTERS ARE INSTALLED ON THIS STRUCTURE? | PRIMARY-LEVEL | 0 | 1007 | Pri_Arrester_Install_Qty | HOW MANY SURGE ARRESTER/LIGHTNING ARRESTERS ARE INSTALLED ON THIS STRUCTURE? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.014G | N | Data Capture
|  | How many surge arrester/lightning arresters are installed on this structure? | PRIMARY-LEVEL | 0 | 1007 | Pri_Arrester_Install_Qty_1 | How many surge arrester/lightning arresters are installed on this structure? | LIGHTNING ARRESTERS | 2958465 | 0.014G | N | Data Capture
arrester_qty | How many surge arrester/lightning arresters are installed on this structure? | HOW MANY SURGE ARRESTER/LIGHTNING ARRESTERS ARE INSTALLED ON THIS STRUCTURE? | PRIMARY-LEVEL | 6 | 1006 | Pri_Arrester_Install_Qty_2 | HOW MANY SURGE ARRESTER/LIGHTNING ARRESTERS ARE INSTALLED ON THIS STRUCTURE? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.014G | N | Data Capture
|  | How many total crossarms are at this level? | PRIMARY-LEVEL | 0 | 1078 | Pri_XARM_Composite_Qty | How many crossarms are at this level? | CROSSARMS - COMPOSITE | 2958465 | 0.014H | N | Data Capture
|  | HOW MANY CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1078 | Pri_XARM_Composite_Qty_1 | NULL | CROSSARMS - COMPOSITE | 2958465 | 0.014H | N | Data Capture
|  | How many total crossarms are at this level? | PRIMARY-LEVEL | 0 | 1078 | Pri_XARM_Composite_Qty_2 | How many total crossarms are at this level? | CROSSARMS - COMPOSITE | 2958465 | 0.014H | N | Data Capture
xarm_pri | Quantity of Crossarms at the PRIMARY level? | HOW MANY CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 22 | 1078 | Pri_XARM_Composite_Qty_3 | NULL | CROSSARMS - COMPOSITE | 43846 | 0.014H | N | Data Capture
|  | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | PRIMARY-LEVEL | 0 | 1078 | Pri_XARM_Composite_Single_Qty | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - COMPOSITE | 2958465 | 0.014H | N | Data Capture
|  | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1078 | Pri_XARM_Composite_Single_Qty_1 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - COMPOSITE | 2958465 | 0.014H | N | Data Capture
|  | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | PRIMARY-LEVEL | 0 | 1078 | Pri_XARM_Composite_Single_Qty_2 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - COMPOSITE | 2958465 | 0.014H | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including triples, fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | PRIMARY-LEVEL | 0 | 1078 | Pri_XARM_Composite_Single_Qty_3 | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - COMPOSITE | 2958465 | 0.014H | N | Data Capture
|  | How many crossarms are at this level? | PRIMARY-LEVEL | 0 | 1078 | Pri_XARM_Composite_Single_Qty_4 | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including triples, fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - COMPOSITE | 2958465 | 0.014H | N | Data Capture
|  | How many crossarms are at this level? | PRIMARY-LEVEL | 0 | 1085 | Pri_XARM_Steel_Qty | How many crossarms are at this level? | CROSSARMS - STEEL | 2958465 | 0.014H | N | Data Capture
|  | How many total crossarms are at this level? | PRIMARY-LEVEL | 0 | 1085 | Pri_XARM_Steel_Qty_1 | How many total crossarms are at this level? | CROSSARMS - STEEL | 2958465 | 0.014H | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | PRIMARY-LEVEL | 0 | 1087 | Pri_XARM_Steel_Single_Qty_3 | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - STEEL | 2958465 | 0.014H | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including triples, fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | PRIMARY-LEVEL | 0 | 1087 | Pri_XARM_Steel_Single_Qty_4 | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including triples, fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - STEEL | 2958465 | 0.014H | N | Data Capture
|  | How many crossarms are at this level? | PRIMARY-LEVEL | 0 | 1102 | Pri_XARM_Wood_Qty | How many crossarms are at this level? | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | How many total crossarms are at this level? | PRIMARY-LEVEL | 0 | 1102 | Pri_XARM_Wood_Qty_1 | How many total crossarms are at this level? | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | HOW MANY WOOD, VERTICAL CONSTRUCTION CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1102 | Pri_XARM_Wood_Qty_2 | NULL | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | HOW MANY WOOD, HORIZONTAL CONSTRUCTION CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1102 | Pri_XARM_Wood_Qty_3 | NULL | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | PRIMARY-LEVEL | 0 | 1102 | Pri_XARM_Wood_Single_Qty | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1102 | Pri_XARM_Wood_Single_Qty_1 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | PRIMARY-LEVEL | 0 | 1102 | Pri_XARM_Wood_Single_Qty_2 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | PRIMARY-LEVEL | 0 | 1102 | Pri_XARM_Wood_Single_Qty_3 | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including triples, fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | PRIMARY-LEVEL | 0 | 1102 | Pri_XARM_Wood_Single_Qty_4 | How many total single crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including triples, fuse-holder arms, transformer hanger arms, etc. NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | How many crossarms are at this level? | SECONDARY-LEVEL | 0 | 2051 | Sec_XARM_Composite_Qty | How many crossarms are at this level? | CROSSARMS - COMPOSITE | 2958465 | 0.014H | N | Data Capture
|  | How many total crossarms are at this level? | SECONDARY-LEVEL | 0 | 2051 | Sec_XARM_Composite_Qty_1 | How many total crossarms are at this level? | CROSSARMS - COMPOSITE | 2958465 | 0.014H | N | Data Capture
|  | How many crossarms are at this level? | SECONDARY-LEVEL | 0 | 2058 | Sec_XARM_Steel_Qty | How many crossarms are at this level? | CROSSARMS - STEEL | 2958465 | 0.014H | N | Data Capture
|  | How many total crossarms are at this level? | SECONDARY-LEVEL | 0 | 2058 | Sec_XARM_Steel_Qty_1 | How many total crossarms are at this level? | CROSSARMS - STEEL | 2958465 | 0.014H | N | Data Capture
|  | How many crossarms are at this level? | SECONDARY-LEVEL | 0 | 2073 | Sec_XARM_Wood_Qty | How many crossarms are at this level? | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | How many total crossarms are at this level? | SECONDARY-LEVEL | 0 | 2073 | Sec_XARM_Wood_Qty_1 | How many total crossarms are at this level? | CROSSARMS - WOOD | 2958465 | 0.014H | N | Data Capture
|  | HOW MANY PHASES ARE INSTALLED AT THIS LEVEL? NOTE: ONLY COUNT SECONDARY PHASES, NOT SERVICES. (MULTI-PLEX IS COUNTED AS 1 PHASE). | SECONDARY-LEVEL | 0 | 2016 | Sec_Conductor_Phase_Qty | HOW MANY PHASES ARE INSTALLED AT THIS LEVEL? NOTE: ONLY COUNT SECONDARY PHASES, NOT SERVICES. (MULTI-PLEX IS COUNTED AS 1 PHASE). | CONDUCTORS - SECONDARY | 2958465 | 0.014I | N | Data Capture
|  | HOW MANY PHASES ARE INSTALLED AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2016 | Sec_Conductor_Phase_Qty_1 | HOW MANY PHASES ARE INSTALLED AT THIS LEVEL? NOTE: ONLY COUNT SECONDARY PHASES, NOT SERVICES. (MULTI-PLEX IS COUNTED AS 1 PHASE). | CONDUCTORS - SECONDARY | 2958465 | 0.014I | N | Data Capture
|  | HOW MANY PHASES ARE INSTALLED AT THIS LEVEL? (MULTI-PLEX IS COUNTED AS 1 PHASE) | SECONDARY-LEVEL | 0 | 2016 | Sec_Conductor_Phase_Qty_2 | HOW MANY PHASES ARE INSTALLED AT THIS LEVEL? NOTE: ONLY COUNT SECONDARY PHASES, NOT SERVICES. (MULTI-PLEX IS COUNTED AS 1 PHASE). | CONDUCTORS - SECONDARY | 2958465 | 0.014I | N | Data Capture
|  | How many line side phases are installed at this level? | SECONDARY-LEVEL | 0 | 2016 | Sec_Conductor_Phase_Qty_3 | How many conductors are installed at this level? | CONDUCTORS - SECONDARY | 2958465 | 0.014I | N | Data Capture
|  | How many phases are installed at this level? (multi-plex is counted as 1 phase) | SECONDARY-LEVEL | 0 | 2016 | Sec_Conductor_Phase_Qty_4 | How many line side phases are installed at this level? | CONDUCTORS - SECONDARY | 2958465 | 0.014I | N | Data Capture
|  | How many conductors are installed at this level? | SECONDARY-LEVEL | 0 | 2016 | Sec_Conductor_Phase_Qty_5 | How many phases are installed at this level? | CONDUCTORS - SECONDARY | 2958465 | 0.014I | N | Data Capture
|  | How many phases are installed at this level? (multi-plex is counted as 1 phase) | SECONDARY-LEVEL | 0 | 2016 | Sec_Conductor_Phase_Qty_6 | How many phases are installed at this level? (multi-plex is counted as 1 phase) | CONDUCTORS - SECONDARY | 2958465 | 0.014I | N | Data Capture
|  | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | PRIMARY-LEVEL | 0 | 1076 | Pri_XARM_Composite_Double_Qty | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - COMPOSITE | 2958465 | 0.014J | N | Data Capture
|  | How many total sets of double crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | PRIMARY-LEVEL | 0 | 1076 | Pri_XARM_Composite_Double_Qty_1 | How many total sets of double crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - COMPOSITE | 2958465 | 0.014J | N | Data Capture
|  | How many total sets of double crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | PRIMARY-LEVEL | 0 | 1084 | Pri_XARM_Steel_Double_Qty_1 | How many total sets of double crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - STEEL | 2958465 | 0.014J | N | Data Capture
|  | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | PRIMARY-LEVEL | 0 | 1100 | Pri_XARM_Wood_Double_Qty | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - WOOD | 2958465 | 0.014J | N | Data Capture
|  | How many total sets of double crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | PRIMARY-LEVEL | 0 | 1100 | Pri_XARM_Wood_Double_Qty_1 | How many total sets of double crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - WOOD | 2958465 | 0.014J | N | Data Capture
|  | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | PRIMARY-LEVEL | 0 | 1079 | Pri_XARM_Composite_Triple_Qty | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - COMPOSITE | 2958465 | 0.014K | N | Data Capture
|  | How many total sets of triple crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | PRIMARY-LEVEL | 0 | 1079 | Pri_XARM_Composite_Triple_Qty_1 | How many total sets of triple crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - COMPOSITE | 2958465 | 0.014K | N | Data Capture
|  | How many total sets of triple crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | PRIMARY-LEVEL | 0 | 1089 | Pri_XARM_Steel_Triple_Qty_1 | How many total sets of triple crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - STEEL | 2958465 | 0.014K | N | Data Capture
|  | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | PRIMARY-LEVEL | 0 | 1104 | Pri_XARM_Wood_Triple_Qty | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - WOOD | 2958465 | 0.014K | N | Data Capture
|  | How many total sets of triple crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | PRIMARY-LEVEL | 0 | 1104 | Pri_XARM_Wood_Triple_Qty_1 | How many total sets of triple crossarms of this material type are at this level? NOTE: Count all crossarms of this material type at this level – including fuse-holder arms, transformer hanger arms, etc. NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - WOOD | 2958465 | 0.014K | N | Data Capture
|  | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | SECONDARY-LEVEL | 0 | 2052 | Sec_XARM_Composite_Single_Qty | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - COMPOSITE | 2958465 | 0.014L | N | Data Capture
|  | HOW MANY CROSSARMS ARE AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2052 | Sec_XARM_Composite_Single_Qty_1 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - COMPOSITE | 2958465 | 0.014L | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | SECONDARY-LEVEL | 0 | 2052 | Sec_XARM_Composite_Single_Qty_2 | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - COMPOSITE | 2958465 | 0.014L | N | Data Capture
|  | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2052 | Sec_XARM_Composite_Single_Qty_3 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - COMPOSITE | 2958465 | 0.014L | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | SECONDARY-LEVEL | 0 | 2052 | Sec_XARM_Composite_Single_Qty_4 | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - COMPOSITE | 2958465 | 0.014L | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | SECONDARY-LEVEL | 0 | 2060 | Sec_XARM_Steel_Single_Qty_2 | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - STEEL | 2958465 | 0.014L | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | SECONDARY-LEVEL | 0 | 2060 | Sec_XARM_Steel_Single_Qty_4 | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - STEEL | 2958465 | 0.014L | N | Data Capture
|  | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | SECONDARY-LEVEL | 0 | 2074 | Sec_XARM_Wood_Single_Qty | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD | 2958465 | 0.014L | N | Data Capture
|  | HOW MANY CROSSARMS ARE AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2074 | Sec_XARM_Wood_Single_Qty_1 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD | 2958465 | 0.014L | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | SECONDARY-LEVEL | 0 | 2074 | Sec_XARM_Wood_Single_Qty_2 | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - WOOD | 2958465 | 0.014L | N | Data Capture
|  | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2074 | Sec_XARM_Wood_Single_Qty_3 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD | 2958465 | 0.014L | N | Data Capture
|  | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | SECONDARY-LEVEL | 0 | 2074 | Sec_XARM_Wood_Single_Qty_4 | How many total single crossarms of this material type are at this level? NOTE: A single crossarm is when only one crossarm piece exists at a specific elevation on the pole. | CROSSARMS - WOOD | 2958465 | 0.014L | N | Data Capture
|  | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | SECONDARY-LEVEL | 0 | 2050 | Sec_XARM_Composite_Double_Qty | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - COMPOSITE | 2958465 | 0.014M | N | Data Capture
|  | How many total sets of double crossarms of this material type are at this level? NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2050 | Sec_XARM_Composite_Double_Qty_2 | How many total sets of double crossarms of this material type are at this level? NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - COMPOSITE | 2958465 | 0.014M | N | Data Capture
|  | How many total sets of double crossarms of this material type are at this level? NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2057 | Sec_XARM_Steel_Double_Qty_1 | How many total sets of double crossarms of this material type are at this level? NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - STEEL | 2958465 | 0.014M | N | Data Capture
|  | How many total sets of double crossarms of this material type are at this level? NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2057 | Sec_XARM_Steel_Double_Qty_2 | How many total sets of double crossarms of this material type are at this level? NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - STEEL | 2958465 | 0.014M | N | Data Capture
|  | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | SECONDARY-LEVEL | 0 | 2071 | Sec_XARM_Wood_Double_Qty | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - WOOD | 2958465 | 0.014M | N | Data Capture
|  | How many total sets of double crossarms of this material type are at this level? NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2071 | Sec_XARM_Wood_Double_Qty_1 | How many total sets of double crossarms of this material type are at this level? NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - WOOD | 2958465 | 0.014M | N | Data Capture
|  | How many total sets of double crossarms of this material type are at this level? NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2071 | Sec_XARM_Wood_Double_Qty_2 | How many total sets of double crossarms of this material type are at this level? NOTE: A double crossarm is when two crossarm pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - WOOD | 2958465 | 0.014M | N | Data Capture
|  | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | SECONDARY-LEVEL | 0 | 2053 | Sec_XARM_Composite_Triple_Qty | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - COMPOSITE | 2958465 | 0.014N | N | Data Capture
|  | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2053 | Sec_XARM_Composite_Triple_Qty_1 | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - COMPOSITE | 2958465 | 0.014N | N | Data Capture
|  | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2053 | Sec_XARM_Composite_Triple_Qty_2 | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - COMPOSITE | 2958465 | 0.014N | N | Data Capture
|  | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2062 | Sec_XARM_Steel_Triple_Qty_1 | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - STEEL | 2958465 | 0.014N | N | Data Capture
|  | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2062 | Sec_XARM_Steel_Triple_Qty_2 | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - STEEL | 2958465 | 0.014N | N | Data Capture
|  | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | SECONDARY-LEVEL | 0 | 2076 | Sec_XARM_Wood_Triple_Qty | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - WOOD | 2958465 | 0.014N | N | Data Capture
|  | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2076 | Sec_XARM_Wood_Triple_Qty_1 | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - WOOD | 2958465 | 0.014N | N | Data Capture
|  | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | SECONDARY-LEVEL | 0 | 2076 | Sec_XARM_Wood_Triple_Qty_2 | How many total sets of triple crossarms of this material type are at this level? NOTE: A triple crossarm is when three crossarms pieces exist in a parallel orientation at the same elevation on the pole. | CROSSARMS - WOOD | 2958465 | 0.014N | N | Data Capture
|  | HOW MANY INSULATORS ARE INSTALLED AT THIS LEVEL? NOTE: DEAD-END INSULATORS COUNT AS 1. | SECONDARY-LEVEL | 0 | 2030 | Sec_Insulator_Qty | HOW MANY INSULATORS ARE INSTALLED AT THIS LEVEL? NOTE: DEAD-END INSULATORS COUNT AS 1. | INSULATORS | 2958465 | 0.014O | N | Data Capture
|  | HOW MANY PRIMARY INSULATORS ARE INSTALLED AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2030 | Sec_Insulator_Qty_1 | HOW MANY INSULATORS ARE INSTALLED AT THIS LEVEL? NOTE: DEAD-END INSULATORS COUNT AS 1. | INSULATORS | 2958465 | 0.014O | N | Data Capture
|  | HOW MANY INSULATORS ARE INSTALLED AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2030 | Sec_Insulator_Qty_2 | HOW MANY INSULATORS ARE INSTALLED AT THIS LEVEL? NOTE: DEAD-END INSULATORS COUNT AS 1. | INSULATORS | 2958465 | 0.014O | N | Data Capture
|  | How many insulators are installed at this level? | SECONDARY-LEVEL | 0 | 2030 | Sec_Insulator_Qty_3 | How many insulators are installed at this level? | INSULATORS | 2958465 | 0.014O | N | Data Capture
|  | How many insulators are installed at this level? | SECONDARY-LEVEL | 0 | 2030 | Sec_Insulator_Qty_4 | How many primary insulators are installed at this level? | INSULATORS | 2958465 | 0.014O | N | Data Capture
|  | IS THERE ADEQUATE CLIMBING SPACE AT THIS LEVEL? | COMMUNICATION-LEVEL | 0 | 3002 | Comm_Pole_Climbing_Space | IS THERE ADEQUATE CLIMBING SPACE AT THIS LEVEL? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.020B | Y | Health/Condition
|  | IS THERE ADEQUATE CLIMBING SPACE AT THIS LEVEL? | PUBLIC-LEVEL | 0 | 4019 | Pub_Pole_Climbing_Space | IS THERE ADEQUATE CLIMBING SPACE AT THIS LEVEL? | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.020B | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT SWITCH MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT SWITCH PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | PRIMARY-LEVEL | 0 | 1003 | Pri_Apparatus_NonExempt_Switch | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT SWITCH MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT SWITCH PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021A | N | Data Capture
|  | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT SWITCH MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 0 | 1003 | Pri_Apparatus_NonExempt_Switch_1 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT SWITCH MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT SWITCH PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021A | N | Data Capture
|  | Indicate which of the following types of non-exempt SWITCH material are present on the pole. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1003 | Pri_Apparatus_NonExempt_Switch_2 | Indicate if any of the following types of non-exempt SWITCH material are present on the pole. Select all that apply or select "No non-exempt switch present" or select “Pole not in High Fire Area”. | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 0.021A | N | Data Capture
|  | Indicate if any of the following types of non-exempt SWITCH material are present on the pole. Select all that apply or select "No non-exempt switch present" or select “Pole not in High Fire Area”. | PRIMARY-LEVEL | 0 | 1003 | Pri_Apparatus_NonExempt_Switch_3 | Indicate if any of the following types of non-exempt SWITCH material are present on the pole. Select all that apply or select "No non-exempt switch present." | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 0.021A | N | Data Capture
|  | Indicate which of the following types of non-exempt SWITCH material are present on the pole. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1003 | Pri_Apparatus_NonExempt_Switch_4 | Indicate which of the following types of non-exempt SWITCH material are present on the pole. Select all that apply or "None of the above". | RECLOSERS, PE GEAR, REGULATORS, SECTIONALIZERS, AN | 2958465 | 0.021A | N | Data Capture
ne_switch | Indicate which of the following types of non-exempt SWITCH material are present on the pole. | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT SWITCH MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT SWITCH PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | PRIMARY-LEVEL | 8 | 1003 | Pri_Apparatus_NonExempt_Switch_5 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT SWITCH MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT SWITCH PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021A | N | Data Capture
ne_switch | Indicate which of the following types of non-exempt SWITCH material are present on the pole. | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT SWITCH MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 8 | 1003 | Pri_Apparatus_NonExempt_Switch_6 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT SWITCH MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT SWITCH PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 44286 | 0.021A | N | Data Capture
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT FUSE MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT FUSE PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | PRIMARY-LEVEL | 0 | 1046 | Pri_Fuse_NonExempt | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT FUSE MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT FUSE PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021B | N | Data Capture
|  | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT FUSE MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 0 | 1046 | Pri_Fuse_NonExempt_1 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT FUSE MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT FUSE PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021B | N | Data Capture
|  | Indicate which of the following types of non-exempt FUSE material are present on the pole. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1046 | Pri_Fuse_NonExempt_2 | Indicate if any of the following types of non-exempt FUSE material are present on the pole. Select all that apply or select "No non-exempt fuse present" or select “Pole not in High Fire Area”. | FUSES | 2958465 | 0.021B | N | Data Capture
|  | Indicate if any of the following types of non-exempt FUSE material are present on the pole. Select all that apply or select "No non-exempt fuse present" or select “Pole not in High Fire Area”. | PRIMARY-LEVEL | 0 | 1046 | Pri_Fuse_NonExempt_3 | Indicate if any of the following types of non-exempt FUSE material are present on the pole. Select all that apply or select "No non-exempt fuse present." | FUSES | 2958465 | 0.021B | N | Data Capture
|  | Indicate which of the following types of non-exempt FUSE material are present on the pole. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1046 | Pri_Fuse_NonExempt_4 | Indicate which of the following types of non-exempt FUSE material are present on the pole. Select all that apply or "None of the above". | FUSES | 2958465 | 0.021B | N | Data Capture
ne_fuse | Indicate which of the following types of non-exempt FUSE material are present on the pole. | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT FUSE MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT FUSE PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | PRIMARY-LEVEL | 9 | 1046 | Pri_Fuse_NonExempt_5 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT FUSE MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT FUSE PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021B | N | Data Capture
ne_fuse | Indicate which of the following types of non-exempt FUSE material are present on the pole. | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT FUSE MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 9 | 1046 | Pri_Fuse_NonExempt_6 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT FUSE MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT FUSE PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 44286 | 0.021B | N | Data Capture
|  | Indicate which of the following types of non-exempt FUSE material are present on the pole. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1046 | Pri_Fuse_NonExempt_7 | Indicate which of the following types of non-exempt FUSE material are present on the pole. Select all that apply or "None of the above". | FUSES | 2958465 | 0.021B | N | Data Capture
|  | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT ARRESTER MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 0 | 1008 | Pri_Arrester_NonExempt | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT ARRESTER MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT ARRESTER PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021C | N | Data Capture
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT ARRESTER MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT ARRESTER PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | PRIMARY-LEVEL | 0 | 1008 | Pri_Arrester_NonExempt_1 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT ARRESTER MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT ARRESTER PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021C | N | Data Capture
|  | Indicate which of the following types of non-exempt ARRESTER material are present on the pole. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1008 | Pri_Arrester_NonExempt_2 | Indicate if any of the following types of non-exempt ARRESTER material are present on the pole. Select all that apply or select "No non-exempt arrester present" or select “Pole not in High Fire Area”. | LIGHTNING ARRESTERS | 2958465 | 0.021C | N | Data Capture
|  | Indicate if any of the following types of non-exempt ARRESTER material are present on the pole. Select all that apply or select "No non-exempt arrester present" or select “Pole not in High Fire Area”. | PRIMARY-LEVEL | 0 | 1008 | Pri_Arrester_NonExempt_3 | Indicate if any of the following types of non-exempt ARRESTER material are present on the pole. Select all that apply or select "No non-exempt arrester present." | LIGHTNING ARRESTERS | 2958465 | 0.021C | N | Data Capture
|  | Indicate which of the following types of non-exempt ARRESTER material are present on the pole. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1008 | Pri_Arrester_NonExempt_4 | Indicate which of the following types of non-exempt ARRESTER material are present on the pole. Select all that apply or "None of the above". | LIGHTNING ARRESTERS | 2958465 | 0.021C | N | Data Capture
ne_arrester | Indicate which of the following types of non-exempt ARRESTER material are present on the pole. | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT ARRESTER MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT ARRESTER PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | PRIMARY-LEVEL | 10 | 1008 | Pri_Arrester_NonExempt_5 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT ARRESTER MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT ARRESTER PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021C | N | Data Capture
ne_arrester | Indicate which of the following types of non-exempt ARRESTER material are present on the pole. | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT ARRESTER MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 10 | 1008 | Pri_Arrester_NonExempt_6 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT ARRESTER MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT ARRESTER PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 44286 | 0.021C | N | Data Capture
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT CONNECTOR PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | PRIMARY-LEVEL | 0 | 1032 | Pri_Conductor_NonExempt_Connector | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT CONNECTOR PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021D | N | Data Capture
|  | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 0 | 1032 | Pri_Conductor_NonExempt_Connector_1 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT CONNECTOR PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021D | N | Data Capture
ne_connectors_pri | Indicate which of the following types of non-exempt CONNECTOR material are present on the pole. | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 11 | 1032 | Pri_Conductor_NonExempt_Connector_10 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT CONNECTOR PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 44286 | 0.021D | N | Data Capture
|  | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 0 | 1032 | Pri_Conductor_NonExempt_Connector_2 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT CONNECTOR PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021D | N | Data Capture
|  | Indicate if any of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or select "No non-exempt connector present." | PRIMARY-LEVEL | 0 | 1032 | Pri_Conductor_NonExempt_Connector_3 | (AERIAL/GROUND) Indicate if any of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or select "No non-exempt connector present." | CONDUCTORS - PRIMARY | 2958465 | 0.021D | N | Data Capture
|  | Indicate which of the following types of non-exempt CONNECTOR material are present on the pole. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1032 | Pri_Conductor_NonExempt_Connector_4 | Indicate if any of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or select "No non-exempt connector present" or select “Pole not in High Fire Area”. | CONDUCTORS - PRIMARY | 2958465 | 0.021D | N | Data Capture
|  | Indicate if any of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or select "No non-exempt connector present" or select “Pole not in High Fire Area”. | PRIMARY-LEVEL | 0 | 1032 | Pri_Conductor_NonExempt_Connector_5 | Indicate if any of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or select "No non-exempt connector present." | CONDUCTORS - PRIMARY | 2958465 | 0.021D | N | Data Capture
|  | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1032 | Pri_Conductor_NonExempt_Connector_6 | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or "None of the above". | CONDUCTORS - PRIMARY | 2958465 | 0.021D | N | Data Capture
|  | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1032 | Pri_Conductor_NonExempt_Connector_7 | Indicate which of the following types of non-exempt CONNECTOR material are present on the pole. Select all that apply or "None of the above". | CONDUCTORS - PRIMARY | 2958465 | 0.021D | N | Data Capture
ne_connectors_pri | Indicate which of the following types of non-exempt CONNECTOR material are present on the pole. | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT CONNECTOR PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | PRIMARY-LEVEL | 11 | 1032 | Pri_Conductor_NonExempt_Connector_8 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT CONNECTOR PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021D | N | Data Capture
ne_connectors_pri_2 | Indicate which of the following types of non-exempt CONNECTOR material are present on the pole. | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 11 | 1032 | Pri_Conductor_NonExempt_Connector_9 | INDICATE IF ANY OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT "NO NON-EXEMPT CONNECTOR PRESENT" OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 43852 | 0.021D | N | Data Capture
|  | ARE THERE ANY LM CONNECTORS PRESENT ON THE POLE? | SECONDARY-LEVEL | 0 | 2013 | Sec_Conductor_NonExempt_Connector | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO NON-EXEMPT MATERIAL PRESENT” OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021D | N | Data Capture
|  | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | SECONDARY-LEVEL | 0 | 2013 | Sec_Conductor_NonExempt_Connector_1 | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO NON-EXEMPT MATERIAL PRESENT” OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021D | N | Data Capture
|  | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO NON-EXEMPT MATERIAL PRESENT” OR SELECT “POLE NOT IN HIGH FIRE AREA”. | SECONDARY-LEVEL | 0 | 2013 | Sec_Conductor_NonExempt_Connector_2 | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO NON-EXEMPT MATERIAL PRESENT” OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021D | N | Data Capture
ne_connectors_sec | Indicate which of the following types of non-exempt CONNECTOR material are present on the pole. | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | SECONDARY-LEVEL | 71 | 2014 | Sec_Conductor_NonExempt_Connector_10 | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO NON-EXEMPT MATERIAL PRESENT” OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 44286 | 0.021E | N | Data Capture
|  | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or "None of the above". | SECONDARY-LEVEL | 0 | 2014 | Sec_Conductor_NonExempt_Connector_3 | Are there any LM Connectors present on the pole? | CONDUCTORS - SECONDARY | 2958465 | 0.021E | N | Data Capture
|  | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or "None of the above". | SECONDARY-LEVEL | 0 | 2014 | Sec_Conductor_NonExempt_Connector_4 | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or "None of the above". | CONDUCTORS - SECONDARY | 2958465 | 0.021E | N | Data Capture
|  | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or select "No non-exempt material present." | SECONDARY-LEVEL | 0 | 2014 | Sec_Conductor_NonExempt_Connector_5 | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or select "No non-exempt connector present." | CONDUCTORS - SECONDARY | 2958465 | 0.021E | N | Data Capture
|  | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or select “No non-exempt material present” or select “Pole not in High Fire Area”. | SECONDARY-LEVEL | 0 | 2014 | Sec_Conductor_NonExempt_Connector_6 | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or select "No non-exempt material present." | CONDUCTORS - SECONDARY | 2958465 | 0.021E | N | Data Capture
|  | Are there any LM Connectors present on the pole? | SECONDARY-LEVEL | 0 | 2014 | Sec_Conductor_NonExempt_Connector_7 | Indicate which of the following types of non-exempt CONNECTOR material are present at this level. Select all that apply or select “No non-exempt material present” or select “Pole not in High Fire Area”. | CONDUCTORS - SECONDARY | 2958465 | 0.021E | N | Data Capture
ne_connectors_sec | Indicate which of the following types of non-exempt CONNECTOR material are present on the pole. | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO NON-EXEMPT MATERIAL PRESENT” OR SELECT “POLE NOT IN HIGH FIRE AREA”. | SECONDARY-LEVEL | 71 | 2014 | Sec_Conductor_NonExempt_Connector_8 | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO NON-EXEMPT MATERIAL PRESENT” OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | 0.021E | N | Data Capture
LM_connector | NULL | ARE THERE ANY LM CONNECTORS PRESENT ON THE POLE? | SECONDARY-LEVEL | 999 | 2014 | Sec_Conductor_NonExempt_Connector_9 | INDICATE WHICH OF THE FOLLOWING TYPES OF NON-EXEMPT CONNECTOR MATERIAL ARE PRESENT AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO NON-EXEMPT MATERIAL PRESENT” OR SELECT “POLE NOT IN HIGH FIRE AREA”. | POLES - WOOD, POLES - COMPOSITE | 43851 | 0.021E | N | Data Capture
|  | IS THE PRIMARY CIRCUIT HORIZONTAL OR VERTICAL CONSTRUCTION? NOTE: IF A DOUBLE CIRCUIT AND/OR BOTH TYPES OF CONSTRUCTION EXIST ON THE POLE, SELECT BOTH OPTIONS. ON MULTI-ARM AND TRIANGULAR CONSTRUCTION, ONLY SELECT VERTICAL, IF PRIMARY CONDUCTORS ROLL/TRANSPOSE MID-SPAN; OTHERWISE SELECT HORIZONTAL. | PRIMARY-LEVEL | 0 | 1044 | Pri_Conductor_Vertical_Horizontal | IS THE PRIMARY CIRCUIT HORIZONTAL OR VERTICAL CONSTRUCTION? NOTE: IF A DOUBLE CIRCUIT AND/OR BOTH TYPES OF CONSTRUCTION EXIST ON THE POLE, SELECT BOTH OPTIONS. ON MULTI-ARM AND TRIANGULAR CONSTRUCTION, ONLY SELECT VERTICAL, IF PRIMARY CONDUCTORS ROLL/TRANSPOSE MID-SPAN; OTHERWISE SELECT HORIZONTAL. | CONDUCTORS - PRIMARY | 2958465 | 0.026A | N | Data Capture
|  | IS THE PRIMARY CIRCUIT HORIZONTAL OR VERTICAL CONSTRUCTION? | PRIMARY-LEVEL | 0 | 1044 | Pri_Conductor_Vertical_Horizontal_1 | IS THE PRIMARY CIRCUIT HORIZONTAL OR VERTICAL CONSTRUCTION? NOTE: IF A DOUBLE CIRCUIT AND/OR BOTH TYPES OF CONSTRUCTION EXIST ON THE POLE, SELECT BOTH OPTIONS. ON MULTI-ARM AND TRIANGULAR CONSTRUCTION, ONLY SELECT VERTICAL, IF PRIMARY CONDUCTORS ROLL/TRANSPOSE MID-SPAN; OTHERWISE SELECT HORIZONTAL. | CONDUCTORS - PRIMARY | 2958465 | 0.026A | N | Data Capture
|  | Is the primary circuit horizontal or vertical construction? | PRIMARY-LEVEL | 0 | 1044 | Pri_Conductor_Vertical_Horizontal_2 | Is the primary circuit horizontal or vertical construction? | CONDUCTORS - PRIMARY | 2958465 | 0.026A | N | Data Capture
|  | Is the primary circuit horizontal or vertical construction? NOTE: If a double circuit and/or both types of construction exist on the pole, select both options. On multi-arm and triangular construction, only select Vertical, if primary conductors roll/transpose mid-span; otherwise select Horizontal. | PRIMARY-LEVEL | 0 | 1044 | Pri_Conductor_Vertical_Horizontal_3 | Is the primary circuit horizontal or vertical construction? NOTE: If a double circuit and/or both types of construction exist on the pole, select both options. On multi-arm and triangular construction, only select "Vertical", if primary conductors roll/transpose mid-span; otherwise select "Horizontal". | CONDUCTORS - PRIMARY | 2958465 | 0.026A | N | Data Capture
|  | Is the primary circuit horizontal or vertical construction? | PRIMARY-LEVEL | 0 | 1044 | Pri_Conductor_Vertical_Horizontal_4 | Is the primary circuit horizontal or vertical construction? NOTE: If a double circuit and/or both types of construction exist on the pole, select both options. On multi-arm and triangular construction, only select Vertical, if primary conductors roll/transpose mid-span; otherwise select Horizontal. | CONDUCTORS - PRIMARY | 2958465 | 0.026A | N | Data Capture
|  | IS THERE ANY INDICATION OF THE PRIMARY CONDUCTOR ROLLING/TRANSPOSING FROM VERTICAL-TO-HORIZONTAL OR HORIZONTAL-TO-VERTICAL? | PRIMARY-LEVEL | 0 | 1041 | Pri_Conductor_Transpose_VerticalHorizontal | IS THERE ANY INDICATION OF THE PRIMARY CONDUCTOR ROLLING/TRANSPOSING FROM VERTICAL-TO-HORIZONTAL OR HORIZONTAL-TO-VERTICAL? | CONDUCTORS - PRIMARY | 2958465 | 0.026B | Y | Health/Condition
|  | FOR VERTICAL CONSTRUCTION – IS THERE ANY INDICATION OF THE PRIMARY CONDUCTOR ROLLING/TRANSPOSING FROM VERTICAL-TO-HORIZONTAL OR HORIZONTAL-TO-VERTICAL? | PRIMARY-LEVEL | 0 | 1041 | Pri_Conductor_Transpose_VerticalHorizontal_1 | IS THERE ANY INDICATION OF THE PRIMARY CONDUCTOR ROLLING/TRANSPOSING FROM VERTICAL-TO-HORIZONTAL OR HORIZONTAL-TO-VERTICAL? | CONDUCTORS - PRIMARY | 2958465 | 0.026B | Y | Health/Condition
|  | For vertical construction – Is there any indication of the primary conductor rolling/transposing from vertical-to-horizontal or horizontal-to-vertical? | PRIMARY-LEVEL | 0 | 1041 | Pri_Conductor_Transpose_VerticalHorizontal_2 | For vertical construction – Is there any indication of the primary conductor rolling/transposing from vertical-to-horizontal or horizontal-to-vertical? | CONDUCTORS - PRIMARY | 2958465 | 0.026B | Y | Health/Condition
|  | Is there any indication of the primary conductor rolling/transposing from vertical-to-horizontal or horizontal-to-vertical? | PRIMARY-LEVEL | 0 | 1041 | Pri_Conductor_Transpose_VerticalHorizontal_3 | Is there any indication of the primary conductor rolling/transposing from vertical-to-horizontal or horizontal-to-vertical? | CONDUCTORS - PRIMARY | 2958465 | 0.026B | Y | Health/Condition
|  | FOR ROLLING/TRANSPOSING PRIMARY CONDUCTOR – IS THERE AT LEAST 12 INCHES OF CLEARANCE BETWEEN CONDUCTORS? | PRIMARY-LEVEL | 0 | 1040 | Pri_Conductor_Transpose_12Inch_Clearance | FOR ROLLING/TRANSPOSING PRIMARY CONDUCTOR – IS THERE AT LEAST 12 INCHES OF CLEARANCE BETWEEN CONDUCTORS? | CONDUCTORS - PRIMARY | 2958465 | 0.026C | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE TO DOWN GUYS ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PUBLIC-LEVEL | 0 | 4013 | Pub_DownGuy_Damage | INDICATE IF ANY OF THE FOLLOWING TYPES OF DAMAGE TO DOWN GUYS ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | DOWN GUYS | 2958465 | 13.001A | Y | Health/Condition
|  | Indicate if any of the following types of damage to down guys are observed. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4013 | Pub_DownGuy_Damage_1 | Indicate if any of the following types of damage to down guys are observed. Select all that apply. | DOWN GUYS | 2958465 | 13.001A | Y | Health/Condition
|  | Indicate if any of the following types of damage to down guys are observed. Select all that apply. | PUBLIC-LEVEL | 0 | 4013 | Pub_DownGuy_Damage_2 | Indicate if any of the following types of damage to SCE distribution down guys are observed. Select all that apply. | DOWN GUYS | 2958465 | 13.001A | Y | Health/Condition
|  | Indicate if any of the following types of damage to down guys are observed. Select all that apply or select “No abnormal conditions”. | PUBLIC-LEVEL | 0 | 4013 | Pub_DownGuy_Damage_3 | Indicate if any of the following types of damage to down guys are observed. Select all that apply or select “No abnormal conditions”. | DOWN GUYS | 2958465 | 13.001A | Y | Health/Condition
|  | ARE THERE SIGNS OF CONTACT BETWEEN GUY WIRE AND CONDUCTORS (ARCING MARKS)? | PRIMARY-LEVEL | 0 | 1045 | Pri_DownGuy_Contact_Arcing | ARE THERE SIGNS OF CONTACT BETWEEN GUY WIRE AND CONDUCTORS (ARCING MARKS)? | DOWN GUYS | 2958465 | 13.001B | Y | Health/Condition
|  | Are there signs of contact between guy wire and conductors (arcing marks)? | PRIMARY-LEVEL | 0 | 1045 | Pri_DownGuy_Contact_Arcing_1 | Are there signs of contact between guy wire and conductors (arcing marks)? | DOWN GUYS | 2958465 | 13.001B | Y | Health/Condition
downguy_contact_pri | At PRIMARY level: Are there signs of contact between guy wire and conductors (arcing marks)? | ARE THERE SIGNS OF CONTACT BETWEEN GUY WIRE AND CONDUCTORS (ARCING MARKS)? | PRIMARY-LEVEL | 67 | 1045 | Pri_DownGuy_Contact_Arcing_2 | ARE THERE SIGNS OF CONTACT BETWEEN GUY WIRE AND CONDUCTORS (ARCING MARKS)? | DOWN GUYS | 2958465 | 13.001B | Y | Health/Condition
|  | ARE THERE SIGNS OF CONTACT BETWEEN GUY WIRE AND CONDUCTORS (ARCING MARKS)? | SECONDARY-LEVEL | 0 | 2022 | Sec_DownGuy_Contact_Arcing | ARE THERE SIGNS OF CONTACT BETWEEN GUY WIRE AND CONDUCTORS (ARCING MARKS)? | DOWN GUYS | 2958465 | 13.001B | Y | Health/Condition
|  | Are there signs of contact between guy wire and conductors (arcing marks)? | SECONDARY-LEVEL | 0 | 2022 | Sec_DownGuy_Contact_Arcing_1 | Are there signs of contact between guy wire and conductors (arcing marks)? | DOWN GUYS | 2958465 | 13.001B | Y | Health/Condition
downguy_contact_sec | At SECONDARY level: Are there signs of contact between guy wire and conductors (arcing marks)? | ARE THERE SIGNS OF CONTACT BETWEEN GUY WIRE AND CONDUCTORS (ARCING MARKS)? | SECONDARY-LEVEL | 104 | 2022 | Sec_DownGuy_Contact_Arcing_2 | ARE THERE SIGNS OF CONTACT BETWEEN GUY WIRE AND CONDUCTORS (ARCING MARKS)? | DOWN GUYS | 2958465 | 13.001B | Y | Health/Condition
|  | How many crossarms at this level are bowed/twisted? | PRIMARY-LEVEL | 0 | 1081 | Pri_XARM_Steel_Bowed_Qty_2 | How many crossarms at this level are bowed/twisted? | CROSSARMS - STEEL | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1081 | Pri_XARM_Steel_Bowed_Qty_3 | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? | CROSSARMS - STEEL | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms at this level are bowed/twisted? | PRIMARY-LEVEL | 0 | 1081 | Pri_XARM_Steel_Bowed_Qty_4 | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - STEEL | 2958465 | 2.003A | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING SIGNS OF BOWING/TWISTING ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1091 | Pri_XARM_Wood_Bowed_Detail_1 | ARE ANY CROSSARMS OF THIS MATERIAL TYPE SHOWING ANY OF THE FOLLOWING SIGNS OF BOWING/TWISTING AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE BOWED/TWISTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 0 | 1093 | Pri_XARM_Wood_Bowed_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE BOWED/TWISTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL ARE BOWED/TWISTED? | PRIMARY-LEVEL | 0 | 1093 | Pri_XARM_Wood_Bowed_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE BOWED/TWISTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms at this level are bowed/twisted? | PRIMARY-LEVEL | 0 | 1093 | Pri_XARM_Wood_Bowed_Qty_2 | How many crossarms at this level are bowed/twisted? | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? | PRIMARY-LEVEL | 0 | 1093 | Pri_XARM_Wood_Bowed_Qty_3 | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1093 | Pri_XARM_Wood_Bowed_Qty_4 | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms at this level are bowed/twisted? | SECONDARY-LEVEL | 0 | 2054 | Sec_XARM_Steel_Bowed_Qty | How many crossarms at this level are bowed/twisted? | CROSSARMS - STEEL | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? | SECONDARY-LEVEL | 0 | 2054 | Sec_XARM_Steel_Bowed_Qty_1 | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? | CROSSARMS - STEEL | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? NOTE: Notification required if answer is greater than 0. | SECONDARY-LEVEL | 0 | 2054 | Sec_XARM_Steel_Bowed_Qty_2 | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - STEEL | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms at this level are bowed/twisted? | SECONDARY-LEVEL | 0 | 2064 | Sec_XARM_Wood_Bowed_Qty | How many crossarms at this level are bowed/twisted? | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE BOWED/TWISTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 0 | 2064 | Sec_XARM_Wood_Bowed_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE BOWED/TWISTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? | SECONDARY-LEVEL | 0 | 2064 | Sec_XARM_Wood_Bowed_Qty_2 | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL ARE BOWED/TWISTED? | SECONDARY-LEVEL | 0 | 2064 | Sec_XARM_Wood_Bowed_Qty_3 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE BOWED/TWISTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? NOTE: Notification required if answer is greater than 0. | SECONDARY-LEVEL | 0 | 2064 | Sec_XARM_Wood_Bowed_Qty_4 | How many crossarms of this material type at this level are bowed/twisted and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - WOOD | 2958465 | 2.003A | Y | Health/Condition
|  | ARE ANY CROSSARMS OF THIS MATERIAL TYPE SHOWING ANY OF THE FOLLOWING SIGNS OF BOWING/TWISTING AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1090 | Pri_XARM_Wood_Bowed_Detail | ARE ANY CROSSARMS OF THIS MATERIAL TYPE SHOWING ANY OF THE FOLLOWING SIGNS OF BOWING/TWISTING AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | FOR BOWED/TWISTED CROSSARMS – WHICH OF THE FOLLOWING SIGNS OF BOWING/TWISTING ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1092 | Pri_XARM_Wood_Bowed_Detail_2 | ARE ANY CROSSARMS OF THIS MATERIAL TYPE SHOWING ANY OF THE FOLLOWING SIGNS OF BOWING/TWISTING AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | Are any crossarms of this material type showing any of the following signs of bowing/twisting at this level and need to be replaced? Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1092 | Pri_XARM_Wood_Bowed_Detail_3 | Are any crossarms of this material type showing any of the following signs of bowing/twisting at this level and need to be replaced? Select all that apply. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | For bowed/twisted crossarms – Which of the following signs of bowing/twisting are observed at this level. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1092 | Pri_XARM_Wood_Bowed_Detail_4 | For bowed/twisted crossarms – Which of the following signs of bowing/twisting are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | Indicate if any of the following signs of bowing/twisting are observed at this level. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1092 | Pri_XARM_Wood_Bowed_Detail_5 | Indicate if any of the following signs of bowing/twisting are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | ARE ANY CROSSARMS OF THIS MATERIAL TYPE SHOWING ANY OF THE FOLLOWING SIGNS OF BOWING/TWISTING AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2063 | Sec_XARM_Wood_Bowed_Detail | ARE ANY CROSSARMS OF THIS MATERIAL TYPE SHOWING ANY OF THE FOLLOWING SIGNS OF BOWING/TWISTING AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING SIGNS OF BOWING/TWISTING ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2063 | Sec_XARM_Wood_Bowed_Detail_1 | ARE ANY CROSSARMS OF THIS MATERIAL TYPE SHOWING ANY OF THE FOLLOWING SIGNS OF BOWING/TWISTING AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | FOR BOWED/TWISTED CROSSARMS – WHICH OF THE FOLLOWING SIGNS OF BOWING/TWISTING ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2063 | Sec_XARM_Wood_Bowed_Detail_2 | ARE ANY CROSSARMS OF THIS MATERIAL TYPE SHOWING ANY OF THE FOLLOWING SIGNS OF BOWING/TWISTING AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | Are any crossarms of this material type showing any of the following signs of bowing/twisting at this level and need to be replaced? Select all that apply. | SECONDARY-LEVEL | 0 | 2063 | Sec_XARM_Wood_Bowed_Detail_3 | Are any crossarms of this material type showing any of the following signs of bowing/twisting at this level and need to be replaced? Select all that apply. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | For bowed/twisted crossarms – Which of the following signs of bowing/twisting are observed at this level. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2063 | Sec_XARM_Wood_Bowed_Detail_4 | For bowed/twisted crossarms – Which of the following signs of bowing/twisting are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | Indicate if any of the following signs of bowing/twisting are observed at this level. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2063 | Sec_XARM_Wood_Bowed_Detail_5 | Indicate if any of the following signs of bowing/twisting are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - WOOD | 2958465 | 2.003B | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 0 | 1075 | Pri_XARM_Composite_Deteriorated_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 2.003C | Y | Health/Condition
|  | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL ARE DETERIORATED? | PRIMARY-LEVEL | 0 | 1075 | Pri_XARM_Composite_Deteriorated_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 2.003C | Y | Health/Condition
|  | How many crossarms of this material type at this level are deteriorated and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1075 | Pri_XARM_Composite_Deteriorated_Qty_2 | How many crossarms of this material type at this level are deteriorated and need to be replaced? | CROSSARMS - COMPOSITE | 2958465 | 2.003C | Y | Health/Condition
|  | How many total crossarms are at this level are deteriorated? | PRIMARY-LEVEL | 0 | 1075 | Pri_XARM_Composite_Deteriorated_Qty_3 | How many total crossarms are at this level are deteriorated? | CROSSARMS - COMPOSITE | 2958465 | 2.003C | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 0 | 1099 | Pri_XARM_Wood_Deteriorated_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.003C | Y | Health/Condition
|  | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL ARE DETERIORATED? | PRIMARY-LEVEL | 0 | 1099 | Pri_XARM_Wood_Deteriorated_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.003C | Y | Health/Condition
|  | How many crossarms of this material type at this level are deteriorated and need to be replaced? | PRIMARY-LEVEL | 0 | 1099 | Pri_XARM_Wood_Deteriorated_Qty_2 | How many crossarms of this material type at this level are deteriorated and need to be replaced? | CROSSARMS - WOOD | 2958465 | 2.003C | Y | Health/Condition
|  | How many total crossarms are at this level are deteriorated? | PRIMARY-LEVEL | 0 | 1099 | Pri_XARM_Wood_Deteriorated_Qty_3 | How many total crossarms are at this level are deteriorated? | CROSSARMS - WOOD | 2958465 | 2.003C | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 0 | 2049 | Sec_XARM_Composite_Deteriorated_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 2.003C | Y | Health/Condition
|  | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL ARE DETERIORATED? | SECONDARY-LEVEL | 0 | 2049 | Sec_XARM_Composite_Deteriorated_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 2.003C | Y | Health/Condition
|  | How many crossarms of this material type at this level are deteriorated and need to be replaced? | SECONDARY-LEVEL | 0 | 2049 | Sec_XARM_Composite_Deteriorated_Qty_2 | How many crossarms of this material type at this level are deteriorated and need to be replaced? | CROSSARMS - COMPOSITE | 2958465 | 2.003C | Y | Health/Condition
|  | How many total crossarms are at this level are deteriorated? | SECONDARY-LEVEL | 0 | 2049 | Sec_XARM_Composite_Deteriorated_Qty_3 | How many total crossarms are at this level are deteriorated? | CROSSARMS - COMPOSITE | 2958465 | 2.003C | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 0 | 2070 | Sec_XARM_Wood_Deteriorated_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.003C | Y | Health/Condition
|  | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL ARE DETERIORATED? | SECONDARY-LEVEL | 0 | 2070 | Sec_XARM_Wood_Deteriorated_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.003C | Y | Health/Condition
|  | How many crossarms of this material type at this level are deteriorated and need to be replaced? | SECONDARY-LEVEL | 0 | 2070 | Sec_XARM_Wood_Deteriorated_Qty_2 | How many crossarms of this material type at this level are deteriorated and need to be replaced? | CROSSARMS - WOOD | 2958465 | 2.003C | Y | Health/Condition
|  | How many total crossarms are at this level are deteriorated? | SECONDARY-LEVEL | 0 | 2070 | Sec_XARM_Wood_Deteriorated_Qty_3 | How many total crossarms are at this level are deteriorated? | CROSSARMS - WOOD | 2958465 | 2.003C | Y | Health/Condition
|  | How many crossarms of this material type at this level are excessively rusted and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1086 | Pri_XARM_Steel_Rusted_Qty | How many crossarms of this material type at this level are excessively rusted and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - STEEL | 2958465 | 2.003D | Y | Health/Condition
|  | How many crossarms of this material type at this level are excessively rusted or corroded and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1086 | Pri_XARM_Steel_Rusted_Qty_1 | How many crossarms of this material type at this level are excessively rusted or corroded and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - STEEL | 2958465 | 2.003D | Y | Health/Condition
|  | How many crossarms of this material type at this level are excessively rusted and need to be replaced? NOTE: Notification required if answer is greater than 0. | SECONDARY-LEVEL | 0 | 2059 | Sec_XARM_Steel_Rusted_Qty | How many crossarms of this material type at this level are excessively rusted and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - STEEL | 2958465 | 2.003D | Y | Health/Condition
|  | How many crossarms of this material type at this level are excessively rusted or corroded and need to be replaced? NOTE: Notification required if answer is greater than 0. | SECONDARY-LEVEL | 0 | 2059 | Sec_XARM_Steel_Rusted_Qty_1 | How many crossarms of this material type at this level are excessively rusted or corroded and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - STEEL | 2958465 | 2.003D | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE CANTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 0 | 1096 | Pri_XARM_Wood_Canted_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE CANTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.004A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL ARE CANTED? | PRIMARY-LEVEL | 0 | 1096 | Pri_XARM_Wood_Canted_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE CANTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.004A | Y | Health/Condition
|  | How many crossarms at this level are canted? | PRIMARY-LEVEL | 0 | 1096 | Pri_XARM_Wood_Canted_Qty_2 | How many crossarms at this level are canted? | CROSSARMS - WOOD | 2958465 | 2.004A | Y | Health/Condition
|  | How many crossarms of this material type at this level are canted and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1096 | Pri_XARM_Wood_Canted_Qty_3 | How many crossarms of this material type at this level are canted and need to be replaced? | CROSSARMS - WOOD | 2958465 | 2.004A | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE CANTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 0 | 2067 | Sec_XARM_Wood_Canted_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE CANTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.004A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL ARE CANTED? | SECONDARY-LEVEL | 0 | 2067 | Sec_XARM_Wood_Canted_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE CANTED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.004A | Y | Health/Condition
|  | How many crossarms at this level are canted? | SECONDARY-LEVEL | 0 | 2067 | Sec_XARM_Wood_Canted_Qty_2 | How many crossarms at this level are canted? | CROSSARMS - WOOD | 2958465 | 2.004A | Y | Health/Condition
|  | How many crossarms of this material type at this level are canted and need to be replaced? | SECONDARY-LEVEL | 0 | 2067 | Sec_XARM_Wood_Canted_Qty_3 | How many crossarms of this material type at this level are canted and need to be replaced? | CROSSARMS - WOOD | 2958465 | 2.004A | Y | Health/Condition
|  | How many crossarms at this level are tracking? | PRIMARY-LEVEL | 0 | 1088 | Pri_XARM_Steel_Tracking_Qty | How many crossarms of this material type at this level are tracking and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - STEEL | 2958465 | 2.005B | Y | Health/Condition
|  | How many crossarms at this level are tracking? | PRIMARY-LEVEL | 0 | 1088 | Pri_XARM_Steel_Tracking_Qty_1 | How many crossarms at this level are tracking? | CROSSARMS - STEEL | 2958465 | 2.005B | Y | Health/Condition
|  | How many crossarms of this material type at this level are tracking and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1088 | Pri_XARM_Steel_Tracking_Qty_2 | How many crossarms of this material type at this level are tracking and need to be replaced? | CROSSARMS - STEEL | 2958465 | 2.005B | Y | Health/Condition
|  | How many crossarms of this material type at this level are tracking and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1103 | Pri_XARM_Wood_Tracking_Qty | How many crossarms of this material type at this level are tracking and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - WOOD | 2958465 | 2.005B | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE TRACKING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 0 | 1103 | Pri_XARM_Wood_Tracking_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE TRACKING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.005B | Y | Health/Condition
|  | How many crossarms at this level are tracking? | PRIMARY-LEVEL | 0 | 1103 | Pri_XARM_Wood_Tracking_Qty_2 | How many crossarms at this level are tracking? | CROSSARMS - WOOD | 2958465 | 2.005B | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL ARE TRACKING? | PRIMARY-LEVEL | 0 | 1103 | Pri_XARM_Wood_Tracking_Qty_3 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE TRACKING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.005B | Y | Health/Condition
|  | How many crossarms of this material type at this level are tracking and need to be replaced? | PRIMARY-LEVEL | 0 | 1103 | Pri_XARM_Wood_Tracking_Qty_4 | How many crossarms of this material type at this level are tracking and need to be replaced? | CROSSARMS - WOOD | 2958465 | 2.005B | Y | Health/Condition
|  | How many crossarms of this material type at this level are tracking and need to be replaced? NOTE: Notification required if answer is greater than 0. | SECONDARY-LEVEL | 0 | 2061 | Sec_XARM_Steel_Tracking_Qty | How many crossarms of this material type at this level are tracking and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - STEEL | 2958465 | 2.005B | Y | Health/Condition
|  | How many crossarms of this material type at this level are tracking and need to be replaced? | SECONDARY-LEVEL | 0 | 2061 | Sec_XARM_Steel_Tracking_Qty_2 | How many crossarms of this material type at this level are tracking and need to be replaced? | CROSSARMS - STEEL | 2958465 | 2.005B | Y | Health/Condition
|  | How many crossarms of this material type at this level are tracking and need to be replaced? NOTE: Notification required if answer is greater than 0. | SECONDARY-LEVEL | 0 | 2075 | Sec_XARM_Wood_Tracking_Qty | How many crossarms of this material type at this level are tracking and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - WOOD | 2958465 | 2.005B | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE TRACKING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 0 | 2075 | Sec_XARM_Wood_Tracking_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE TRACKING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.005B | Y | Health/Condition
|  | How many crossarms at this level are tracking? | SECONDARY-LEVEL | 0 | 2075 | Sec_XARM_Wood_Tracking_Qty_2 | How many crossarms at this level are tracking? | CROSSARMS - WOOD | 2958465 | 2.005B | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL ARE TRACKING? | SECONDARY-LEVEL | 0 | 2075 | Sec_XARM_Wood_Tracking_Qty_3 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE TRACKING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.005B | Y | Health/Condition
|  | How many crossarms of this material type at this level are tracking and need to be replaced? | SECONDARY-LEVEL | 0 | 2075 | Sec_XARM_Wood_Tracking_Qty_4 | How many crossarms of this material type at this level are tracking and need to be replaced? | CROSSARMS - WOOD | 2958465 | 2.005B | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED BRACES AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 0 | 1095 | Pri_XARM_Wood_Brace_Damage_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED BRACES AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.006A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL HAVE DAMAGED BRACES? | PRIMARY-LEVEL | 0 | 1095 | Pri_XARM_Wood_Brace_Damage_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED BRACES AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.006A | Y | Health/Condition
|  | How many crossarms at this level have damaged braces? | PRIMARY-LEVEL | 0 | 1095 | Pri_XARM_Wood_Brace_Damage_Qty_2 | How many crossarms at this level have damaged braces? | CROSSARMS - WOOD | 2958465 | 2.006A | Y | Health/Condition
|  | How many crossarms of this material type at this level have damaged braces and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1095 | Pri_XARM_Wood_Brace_Damage_Qty_3 | How many crossarms of this material type at this level have damaged braces and need to be replaced? | CROSSARMS - WOOD | 2958465 | 2.006A | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED BRACES AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 0 | 2066 | Sec_XARM_Wood_Brace_Damage_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED BRACES AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.006A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL HAVE DAMAGED BRACES? | SECONDARY-LEVEL | 0 | 2066 | Sec_XARM_Wood_Brace_Damage_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED BRACES AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.006A | Y | Health/Condition
|  | How many crossarms at this level have damaged braces? | SECONDARY-LEVEL | 0 | 2066 | Sec_XARM_Wood_Brace_Damage_Qty_2 | How many crossarms at this level have damaged braces? | CROSSARMS - WOOD | 2958465 | 2.006A | Y | Health/Condition
|  | How many crossarms of this material type at this level have damaged braces and need to be replaced? | SECONDARY-LEVEL | 0 | 2066 | Sec_XARM_Wood_Brace_Damage_Qty_3 | How many crossarms of this material type at this level have damaged braces and need to be replaced? | CROSSARMS - WOOD | 2958465 | 2.006A | Y | Health/Condition
|  | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING BRACE DAMAGE AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1094 | Pri_XARM_Wood_Brace_Damage_Detail | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING BRACE DAMAGE AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | FOR CROSSARMS WITH BRACE DAMAGE – WHICH OF THE FOLLOWING SIGNS OF BRACE DAMAGE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1094 | Pri_XARM_Wood_Brace_Damage_Detail_1 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING BRACE DAMAGE AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING SIGNS OF BRACE DAMAGE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1094 | Pri_XARM_Wood_Brace_Damage_Detail_2 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING BRACE DAMAGE AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | FOR CROSSARMS WITH BRACE DAMAGE – WHICH OF THE FOLLOWING BRACE DAMAGES ARE OBSERVED AT THIS LEVEL AT TIME OF INSPECTION? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1094 | Pri_XARM_Wood_Brace_Damage_Detail_3 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING BRACE DAMAGE AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | Do any crossarms of this material type have any of the following brace damage at this level and need to be replaced? Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1094 | Pri_XARM_Wood_Brace_Damage_Detail_4 | Do any crossarms of this material type have any of the following brace damage at this level and need to be replaced? Select all that apply. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | For crossarms with brace damage – Which of the following brace damages are observed at this level at time of inspection? Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1094 | Pri_XARM_Wood_Brace_Damage_Detail_5 | For crossarms with brace damage – Which of the following brace damages are observed at this level at time of inspection? Select all that apply or select “No abnormal conditions”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | For crossarms with brace damage – Which of the following brace damages are observed at this level at time of inspection? Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1094 | Pri_XARM_Wood_Brace_Damage_Detail_6 | For crossarms with brace damage – Which of the following signs of brace damage are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | For crossarms with brace damage – Which of the following signs of brace damage are observed at this level. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1094 | Pri_XARM_Wood_Brace_Damage_Detail_7 | Indicate if any of the following signs of brace damage are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING BRACE DAMAGE AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2065 | Sec_XARM_Wood_Brace_Damage_Detail | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING BRACE DAMAGE AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | FOR CROSSARMS WITH BRACE DAMAGE – WHICH OF THE FOLLOWING SIGNS OF BRACE DAMAGE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2065 | Sec_XARM_Wood_Brace_Damage_Detail_1 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING BRACE DAMAGE AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING SIGNS OF BRACE DAMAGE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2065 | Sec_XARM_Wood_Brace_Damage_Detail_2 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING BRACE DAMAGE AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | FOR CROSSARMS WITH BRACE DAMAGE – WHICH OF THE FOLLOWING BRACE DAMAGES ARE OBSERVED AT THIS LEVEL AT TIME OF INSPECTION? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2065 | Sec_XARM_Wood_Brace_Damage_Detail_3 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING BRACE DAMAGE AT THIS LEVEL AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | Do any crossarms of this material type have any of the following brace damage at this level and need to be replaced? Select all that apply. | SECONDARY-LEVEL | 0 | 2065 | Sec_XARM_Wood_Brace_Damage_Detail_4 | Do any crossarms of this material type have any of the following brace damage at this level and need to be replaced? Select all that apply. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | For crossarms with brace damage – Which of the following brace damages are observed at this level at time of inspection? Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2065 | Sec_XARM_Wood_Brace_Damage_Detail_5 | For crossarms with brace damage – Which of the following brace damages are observed at this level at time of inspection? Select all that apply or select “No abnormal conditions”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | For crossarms with brace damage – Which of the following signs of brace damage are observed at this level. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2065 | Sec_XARM_Wood_Brace_Damage_Detail_6 | For crossarms with brace damage – Which of the following signs of brace damage are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | Indicate if any of the following signs of brace damage are observed at this level. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2065 | Sec_XARM_Wood_Brace_Damage_Detail_7 | Indicate if any of the following signs of brace damage are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - WOOD | 2958465 | 2.006B | Y | Health/Condition
|  | How many crossarms at this level have damaged insulators? | PRIMARY-LEVEL | 0 | 1073 | Pri_XARM_Composite_Damaged_Insulator_Qty | How many crossarms at this level have damaged insulators? | CROSSARMS - COMPOSITE | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms at this level have damaged insulators? | PRIMARY-LEVEL | 0 | 1073 | Pri_XARM_Composite_Damaged_Insulator_Qty_1 | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - COMPOSITE | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms at this level have damaged insulators? | PRIMARY-LEVEL | 0 | 1083 | Pri_XARM_Steel_Damaged_Insulator_Qty | How many crossarms at this level have damaged insulators? | CROSSARMS - STEEL | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1083 | Pri_XARM_Steel_Damaged_Insulator_Qty_1 | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - STEEL | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms at this level have damaged insulators? | PRIMARY-LEVEL | 0 | 1098 | Pri_XARM_Wood_Damaged_Insulator_Qty | How many crossarms at this level have damaged insulators? | CROSSARMS - WOOD | 2958465 | 2.007A | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED INSULATORS AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 0 | 1098 | Pri_XARM_Wood_Damaged_Insulator_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED INSULATORS AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1098 | Pri_XARM_Wood_Damaged_Insulator_Qty_2 | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - WOOD | 2958465 | 2.007A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL HAVE DAMAGED INSULATORS? | PRIMARY-LEVEL | 0 | 1098 | Pri_XARM_Wood_Damaged_Insulator_Qty_3 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED INSULATORS AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms at this level have damaged insulators? | SECONDARY-LEVEL | 0 | 2047 | Sec_XARM_Composite_Damaged_Insulator_Qty | How many crossarms at this level have damaged insulators? | CROSSARMS - COMPOSITE | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | SECONDARY-LEVEL | 0 | 2047 | Sec_XARM_Composite_Damaged_Insulator_Qty_1 | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - COMPOSITE | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms at this level have damaged insulators? | SECONDARY-LEVEL | 0 | 2056 | Sec_XARM_Steel_Damaged_Insulator_Qty | How many crossarms at this level have damaged insulators? | CROSSARMS - STEEL | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | SECONDARY-LEVEL | 0 | 2056 | Sec_XARM_Steel_Damaged_Insulator_Qty_1 | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - STEEL | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms at this level have damaged insulators? | SECONDARY-LEVEL | 0 | 2069 | Sec_XARM_Wood_Damaged_Insulator_Qty | How many crossarms at this level have damaged insulators? | CROSSARMS - WOOD | 2958465 | 2.007A | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED INSULATORS AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 0 | 2069 | Sec_XARM_Wood_Damaged_Insulator_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED INSULATORS AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.007A | Y | Health/Condition
|  | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | SECONDARY-LEVEL | 0 | 2069 | Sec_XARM_Wood_Damaged_Insulator_Qty_2 | How many crossarms of this material type at this level have damaged insulators and need to be replaced? NOTE: Notification required if answer is greater than 0. | CROSSARMS - WOOD | 2958465 | 2.007A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL HAVE DAMAGED INSULATORS? | SECONDARY-LEVEL | 0 | 2069 | Sec_XARM_Wood_Damaged_Insulator_Qty_3 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL HAVE DAMAGED INSULATORS AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD | 2958465 | 2.007A | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 0 | 1071 | Pri_XARM_Composite_Bending_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL SHOW SIGNS OF BENDING? | PRIMARY-LEVEL | 0 | 1071 | Pri_XARM_Composite_Bending_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
|  | How many crossarms at this level show signs of bending? | PRIMARY-LEVEL | 0 | 1071 | Pri_XARM_Composite_Bending_Qty_2 | How many crossarms at this level show signs of bending? | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
|  | How many crossarms of this material type at this level show signs of bending and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1071 | Pri_XARM_Composite_Bending_Qty_3 | How many crossarms of this material type at this level show signs of bending and need to be replaced? | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
bending_pri | At PRIMARY level: How many crossarms show signs of bending? | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 30 | 1071 | Pri_XARM_Composite_Bending_Qty_4 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
bending_pri | At PRIMARY level: How many crossarms show signs of bending? | HOW MANY CROSSARMS AT THIS LEVEL SHOW SIGNS OF BENDING? | PRIMARY-LEVEL | 30 | 1071 | Pri_XARM_Composite_Bending_Qty_5 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 44286 | 7.002A | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 0 | 2045 | Sec_XARM_Composite_Bending_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL SHOW SIGNS OF BENDING? | SECONDARY-LEVEL | 0 | 2045 | Sec_XARM_Composite_Bending_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
|  | How many crossarms at this level show signs of bending? | SECONDARY-LEVEL | 0 | 2045 | Sec_XARM_Composite_Bending_Qty_2 | How many crossarms at this level show signs of bending? | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
|  | Do any crossarms of this material type have any of the following conditions of bending and need to be replaced? Select all that apply. | SECONDARY-LEVEL | 0 | 2045 | Sec_XARM_Composite_Bending_Qty_3 | Do any crossarms of this material type have any of the following conditions of bending and need to be replaced? Select all that apply. | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
|  | How many crossarms of this material type at this level are physically damaged and need to be replaced? | SECONDARY-LEVEL | 0 | 2045 | Sec_XARM_Composite_Bending_Qty_4 | How many crossarms of this material type at this level show signs of bending and need to be replaced? | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
bending_sec | At SECONDARY level: How many crossarms show signs of bending? | HOW MANY CROSSARMS AT THIS LEVEL SHOW SIGNS OF BENDING? | SECONDARY-LEVEL | 108 | 2045 | Sec_XARM_Composite_Bending_Qty_5 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 44286 | 7.002A | Y | Health/Condition
bending_sec | At SECONDARY level: How many crossarms show signs of bending? | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 108 | 2045 | Sec_XARM_Composite_Bending_Qty_6 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL SHOW SIGNS OF BENDING AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.002A | Y | Health/Condition
|  | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1070 | Pri_XARM_Composite_Bending_Detail | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING SIGNS OF CROSSARM BENDING ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1070 | Pri_XARM_Composite_Bending_Detail_1 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
|  | FOR BENDING CROSSARMS – WHICH OF THE FOLLOWING SIGNS OF CROSSARM BENDING ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1070 | Pri_XARM_Composite_Bending_Detail_2 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
|  | Do any crossarms of this material type have any of the following conditions of bending and need to be replaced? Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1070 | Pri_XARM_Composite_Bending_Detail_3 | Do any crossarms of this material type have any of the following conditions of bending and need to be replaced? Select all that apply. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
|  | For bending crossarms – Which of the following signs of crossarm bending are observed at this level. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1070 | Pri_XARM_Composite_Bending_Detail_4 | For bending crossarms – Which of the following signs of crossarm bending are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
|  | For bending crossarms – Which of the following signs of crossarm bending are observed at this level. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1070 | Pri_XARM_Composite_Bending_Detail_5 | Indicate if any of the following signs of crossarm bending are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
bending_pri_detail_2 | Which of the following signs of crossarm bending observed at PRIMARY level? | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 31 | 1070 | Pri_XARM_Composite_Bending_Detail_6 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
bending_pri_detail | Which of the following signs of crossarm bending observed at PRIMARY level? | INDICATE IF ANY OF THE FOLLOWING SIGNS OF CROSSARM BENDING ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 31 | 1070 | Pri_XARM_Composite_Bending_Detail_7 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - COMPOSITE | 43838 | 7.002B | Y | Health/Condition
bending_pri_detail_2 | Which of the following signs of crossarm bending observed at PRIMARY level? | FOR BENDING CROSSARMS – WHICH OF THE FOLLOWING SIGNS OF CROSSARM BENDING ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 31 | 1070 | Pri_XARM_Composite_Bending_Detail_8 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - COMPOSITE | 44286 | 7.002B | Y | Health/Condition
|  | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2044 | Sec_XARM_Composite_Bending_Detail | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
|  | FOR BENDING CROSSARMS – WHICH OF THE FOLLOWING SIGNS OF CROSSARM BENDING ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 0 | 2044 | Sec_XARM_Composite_Bending_Detail_1 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
|  | For bending crossarms – Which of the following signs of crossarm bending are observed at this level. Select all that apply or select “No abnormal conditions”. | SECONDARY-LEVEL | 0 | 2044 | Sec_XARM_Composite_Bending_Detail_2 | For bending crossarms – Which of the following signs of crossarm bending are observed at this level. Select all that apply or select “No abnormal conditions”. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
bending_sec_detail | Which of the following signs of crossarm bending observed at SECONDARY level? | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 109 | 2044 | Sec_XARM_Composite_Bending_Detail_3 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - COMPOSITE | 2958465 | 7.002B | Y | Health/Condition
bending_sec_detail | Which of the following signs of crossarm bending observed at SECONDARY level? | FOR BENDING CROSSARMS – WHICH OF THE FOLLOWING SIGNS OF CROSSARM BENDING ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 109 | 2044 | Sec_XARM_Composite_Bending_Detail_4 | DO ANY CROSSARMS OF THIS MATERIAL TYPE HAVE ANY OF THE FOLLOWING CONDITIONS OF BENDING AND NEED TO BE REPLACED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CROSSARMS - COMPOSITE | 44286 | 7.002B | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 0 | 1074 | Pri_XARM_Composite_Damaged_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.004A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL ARE PHYSICALLY DAMAGED? | PRIMARY-LEVEL | 0 | 1074 | Pri_XARM_Composite_Damaged_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.004A | Y | Health/Condition
|  | How many crossarms at this level are physically damaged? | PRIMARY-LEVEL | 0 | 1074 | Pri_XARM_Composite_Damaged_Qty_2 | How many crossarms at this level are physically damaged? | CROSSARMS - COMPOSITE | 2958465 | 7.004A | Y | Health/Condition
|  | How many crossarms of this material type at this level are physically damaged and need to be replaced? NOTE: Notification required if answer is greater than 0. | PRIMARY-LEVEL | 0 | 1074 | Pri_XARM_Composite_Damaged_Qty_3 | How many crossarms of this material type at this level are physically damaged and need to be replaced? | CROSSARMS - COMPOSITE | 2958465 | 7.004A | Y | Health/Condition
damage_pri | At PRIMARY level: How many crossarms are physically damaged? | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 32 | 1074 | Pri_XARM_Composite_Damaged_Qty_4 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.004A | Y | Health/Condition
damage_pri | At PRIMARY level: How many crossarms are physically damaged? | HOW MANY CROSSARMS AT THIS LEVEL ARE PHYSICALLY DAMAGED? | PRIMARY-LEVEL | 32 | 1074 | Pri_XARM_Composite_Damaged_Qty_5 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 44286 | 7.004A | Y | Health/Condition
damage_sec | At SECONDARY level: How many crossarms are physically damaged? | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 110 | 2048 | Sec_XARM_Comp_Damaged_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.004A | Y | Health/Condition
damage_sec | At SECONDARY level: How many crossarms are physically damaged? | HOW MANY CROSSARMS AT THIS LEVEL ARE PHYSICALLY DAMAGED? | SECONDARY-LEVEL | 110 | 2048 | Sec_XARM_Comp_Damaged_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 44286 | 7.004A | Y | Health/Condition
|  | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 0 | 2048 | Sec_XARM_Composite_Damaged_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.004A | Y | Health/Condition
|  | HOW MANY CROSSARMS AT THIS LEVEL ARE PHYSICALLY DAMAGED? | SECONDARY-LEVEL | 0 | 2048 | Sec_XARM_Composite_Damaged_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE PHYSICALLY DAMAGED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - COMPOSITE | 2958465 | 7.004A | Y | Health/Condition
|  | How many crossarms at this level are physically damaged? | SECONDARY-LEVEL | 0 | 2048 | Sec_XARM_Composite_Damaged_Qty_2 | How many crossarms at this level are physically damaged? | CROSSARMS - COMPOSITE | 2958465 | 7.004A | Y | Health/Condition
|  | How many crossarms of this material type at this level are physically damaged and need to be replaced? | SECONDARY-LEVEL | 0 | 2048 | Sec_XARM_Composite_Damaged_Qty_3 | How many crossarms of this material type at this level are physically damaged and need to be replaced? | CROSSARMS - COMPOSITE | 2958465 | 7.004A | Y | Health/Condition
|  | ARE THERE INADEQUATE CLEARANCE DISTANCES OBSERVED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1020 | Pri_Conductor_Clearance_Observered | ARE THERE INADEQUATE CLEARANCE DISTANCES OBSERVED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CONDUCTORS - PRIMARY | 2958465 | 8.002A | Y | Health/Condition
|  | ARE ANY OF THE FOLLOWING SIGNS OF INADEQUATE CLEARANCE DISTANCES TO VEGETATION OBSERVED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1020 | Pri_Conductor_Clearance_Observered_1 | ARE THERE INADEQUATE CLEARANCE DISTANCES OBSERVED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CONDUCTORS - PRIMARY | 2958465 | 8.002A | Y | Health/Condition
|  | INDICATE IF ANY OF THE FOLLOWING SIGNS OF INADEQUATE CLEARANCE DISTANCES ARE OBSERVED. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1020 | Pri_Conductor_Clearance_Observered_2 | ARE THERE INADEQUATE CLEARANCE DISTANCES OBSERVED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CONDUCTORS - PRIMARY | 2958465 | 8.002A | Y | Health/Condition
|  | Are there inadequate clearance distances observed? Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1020 | Pri_Conductor_Clearance_Observered_3 | Are any of the following signs of inadequate clearance distances to vegetation observed? Select all that apply or select “No abnormal conditions”. | CONDUCTORS - PRIMARY | 2958465 | 8.002A | Y | Health/Condition
|  | Indicate if any of the following signs of inadequate clearance distances are observed. Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1020 | Pri_Conductor_Clearance_Observered_4 | Are there inadequate clearance distances observed? Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.002A | Y | Health/Condition
|  | Are any of the following signs of inadequate clearance distances to vegetation observed? Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1020 | Pri_Conductor_Clearance_Observered_5 | Indicate if any of the following signs of inadequate clearance distances are observed. Select all that apply or select “No abnormal conditions”. | CONDUCTORS - PRIMARY | 2958465 | 8.002A | Y | Health/Condition
|  | (AERIAL/GROUND) Are there inadequate clearance distances observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1020 | Pri_Conductor_Clearance_Observered_6 | (AERIAL/GROUND) Are there inadequate clearance distances observed? Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.002A | Y | Health/Condition
|  | ARE THERE ESTIMATED INADEQUATE CLEARANCE DISTANCES BETWEEN ENERGIZED CONDUCTORS AND OTHER STRUCTURES OBSERVED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1028 | Pri_Conductor_Energized_Clearance | ARE THERE ESTIMATED INADEQUATE CLEARANCE DISTANCES BETWEEN ENERGIZED CONDUCTORS AND OTHER STRUCTURES OBSERVED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CONDUCTORS - PRIMARY | 2958465 | 8.002B | Y | Health/Condition
|  | ARE ANY OF THE FOLLOWING SIGNS OF INADEQUATE CLEARANCE DISTANCES BETWEEN ENERGIZED CONDUCTORS AND OTHER STRUCTURES OBSERVED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 0 | 1028 | Pri_Conductor_Energized_Clearance_1 | ARE THERE ESTIMATED INADEQUATE CLEARANCE DISTANCES BETWEEN ENERGIZED CONDUCTORS AND OTHER STRUCTURES OBSERVED? SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | CONDUCTORS - PRIMARY | 2958465 | 8.002B | Y | Health/Condition
|  | Are there estimated inadequate clearance distances between energized conductors and other structures observed? Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1028 | Pri_Conductor_Energized_Clearance_2 | Are any of the following signs of inadequate clearance distances between energized conductors and other structures observed? Select all that apply or select “No abnormal conditions”. | CONDUCTORS - PRIMARY | 2958465 | 8.002B | Y | Health/Condition
|  | Are any of the following signs of inadequate clearance distances between energized conductors and other structures observed? Select all that apply or select “No abnormal conditions”. | PRIMARY-LEVEL | 0 | 1028 | Pri_Conductor_Energized_Clearance_3 | Are there estimated inadequate clearance distances between energized conductors and other structures observed? Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.002B | Y | Health/Condition
|  | (AERIAL/GROUND) Are there estimated inadequate clearance distances between energized conductors and other structures observed? Select all that apply. | PRIMARY-LEVEL | 0 | 1028 | Pri_Conductor_Energized_Clearance_4 | (AERIAL/GROUND) Are there estimated inadequate clearance distances between energized conductors and other structures observed? Select all that apply. | CONDUCTORS - PRIMARY | 2958465 | 8.002B | Y | Health/Condition
|  | IS ANY COPPER PRIMARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET, AND ARE LINE SPACERS INSTALLED? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. NOTE: IF ONE SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “YES, AND LINE SPACERS ARE NOT INSTALLED”. | PRIMARY-LEVEL | 0 | 1024 | Pri_Conductor_Copper_240Feet | IS ANY COPPER PRIMARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET, AND ARE LINE SPACERS INSTALLED? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. NOTE: IF ONE SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “YES, AND LINE SPACERS ARE NOT INSTALLED”. | CONDUCTORS - PRIMARY | 2958465 | 8.007A | N | Data Capture
|  | IS THE SPAN LENGTH FOR COPPER PRIMARY CONDUCTORS GREATER THAN 240 FEET? | PRIMARY-LEVEL | 0 | 1024 | Pri_Conductor_Copper_240Feet_1 | IS ANY COPPER PRIMARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET, AND ARE LINE SPACERS INSTALLED? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. NOTE: IF ONE SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “YES, AND LINE SPACERS ARE NOT INSTALLED”. | CONDUCTORS - PRIMARY | 2958465 | 8.007A | N | Data Capture
|  | FOR COPPER PRIMARY CONDUCTORS – IS THE SPAN LENGTH GREATER THAN 240 FEET? | PRIMARY-LEVEL | 0 | 1024 | Pri_Conductor_Copper_240Feet_2 | IS ANY COPPER PRIMARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET, AND ARE LINE SPACERS INSTALLED? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. NOTE: IF ONE SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “YES, AND LINE SPACERS ARE NOT INSTALLED”. | CONDUCTORS - PRIMARY | 2958465 | 8.007A | N | Data Capture
|  | For copper primary conductors – Is the span length greater than 240 feet? | PRIMARY-LEVEL | 0 | 1024 | Pri_Conductor_Copper_240Feet_3 | For copper primary conductors – Is the span length greater than 240 feet? | CONDUCTORS - PRIMARY | 2958465 | 8.007A | N | Data Capture
|  | Is any copper primary conductor span length in any direction greater than 240 feet, and are line spacers installed? NOTE: If one span is greater than 240 feet and one span is less than 240 feet – select “Yes”. NOTE: If one span has line spacers and the other does not, select “Yes, and line spacers are not installed”. | PRIMARY-LEVEL | 0 | 1024 | Pri_Conductor_Copper_240Feet_4 | Is any copper primary conductor span length in any direction greater than 240 feet, and are line spacers installed? NOTE: If one span is greater than 240 feet and one span is less than 240 feet – select one of the “Yes” responses. NOTE: If one span has line spacers and the other does not, select one of the “... and line spacers are not installed” responses. | CONDUCTORS - PRIMARY | 2958465 | 8.007A | N | Data Capture
|  | For copper primary conductors – Is the span length greater than 240 feet? | PRIMARY-LEVEL | 0 | 1024 | Pri_Conductor_Copper_240Feet_5 | Is the span length for copper primary conductors greater than 240 feet? | CONDUCTORS - PRIMARY | 2958465 | 8.007A | N | Data Capture
|  | IS ANY ALUMINUM PRIMARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET AND ARE LINE SPACERS INSTALLED? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. NOTE: IF ONE SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “YES, AND LINE SPACERS ARE NOT INSTALLED” | PRIMARY-LEVEL | 0 | 1016 | Pri_Conductor_Aluminum_240Feet | IS ANY ALUMINUM PRIMARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET AND ARE LINE SPACERS INSTALLED? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. NOTE: IF ONE SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “YES, AND LINE SPACERS ARE NOT INSTALLED” | CONDUCTORS - PRIMARY | 2958465 | 8.007B | N | Data Capture
|  | IS THE SPAN LENGTH FOR ACSR PRIMARY CONDUCTORS GREATER THAN 240 FEET? | PRIMARY-LEVEL | 0 | 1016 | Pri_Conductor_Aluminum_240Feet_1 | IS ANY ALUMINUM PRIMARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET AND ARE LINE SPACERS INSTALLED? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. NOTE: IF ONE SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “YES, AND LINE SPACERS ARE NOT INSTALLED” | CONDUCTORS - PRIMARY | 2958465 | 8.007B | N | Data Capture
|  | FOR ACSR PRIMARY CONDUCTORS – IS THE SPAN LENGTH GREATER THAN 240 FEET? | PRIMARY-LEVEL | 0 | 1016 | Pri_Conductor_Aluminum_240Feet_2 | IS ANY ALUMINUM PRIMARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET AND ARE LINE SPACERS INSTALLED? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. NOTE: IF ONE SPAN HAS LINE SPACERS AND THE OTHER DOES NOT, SELECT “YES, AND LINE SPACERS ARE NOT INSTALLED” | CONDUCTORS - PRIMARY | 2958465 | 8.007B | N | Data Capture
|  | For ACSR primary conductors – Is the span length greater than 240 feet? | PRIMARY-LEVEL | 0 | 1016 | Pri_Conductor_Aluminum_240Feet_3 | For ACSR primary conductors – Is the span length greater than 240 feet? | CONDUCTORS - PRIMARY | 2958465 | 8.007B | N | Data Capture
|  | Is any Aluminum primary conductor span length in any direction greater than 240 feet and are line spacers installed? NOTE: If one span is greater than 240 feet and one span is less than 240 feet – select one of the “Yes” responses. NOTE: If one span has line spacers and the other does not, select “Yes, and line spacers are not installed” | PRIMARY-LEVEL | 0 | 1016 | Pri_Conductor_Aluminum_240Feet_4 | Is any Aluminum primary conductor span length in any direction greater than 240 feet and are line spacers installed? NOTE: If one span is greater than 240 feet and one span is less than 240 feet – select one of the “Yes” responses. NOTE: If one span has line spacers and the other does not, select one of the “... and line spacers are not installed” responses. | CONDUCTORS - PRIMARY | 2958465 | 8.007B | N | Data Capture
|  | Is any Aluminum primary conductor span length in any direction greater than 240 feet and are line spacers installed? NOTE: If one span is greater than 240 feet and one span is less than 240 feet – select “Yes”. NOTE: If one span has line spacers and the other does not, select “Yes, and line spacers are not installed” | PRIMARY-LEVEL | 0 | 1016 | Pri_Conductor_Aluminum_240Feet_5 | Is any Aluminum primary conductor span length in any direction greater than 240 feet and are line spacers installed? NOTE: If one span is greater than 240 feet and one span is less than 240 feet – select one of the “Yes” responses. NOTE: If one span has line spacers and the other does not, select “Yes, and line spacers are not installed” | CONDUCTORS - PRIMARY | 2958465 | 8.007B | N | Data Capture
|  | For ACSR primary conductors – Is the span length greater than 240 feet? | PRIMARY-LEVEL | 0 | 1016 | Pri_Conductor_Aluminum_240Feet_6 | Is the span length for ACSR primary conductors greater than 240 feet? | CONDUCTORS - PRIMARY | 2958465 | 8.007B | N | Data Capture
|  | IS ANY COPPER SECONDARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. | SECONDARY-LEVEL | 0 | 2010 | Sec_Conductor_Copper_240Feet | IS ANY COPPER SECONDARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. | CONDUCTORS - SECONDARY | 2958465 | 9.007A | N | Data Capture
|  | IS THE SPAN LENGTH FOR COPPER SECONDARY CONDUCTORS GREATER THAN 240 FEET? | SECONDARY-LEVEL | 0 | 2010 | Sec_Conductor_Copper_240Feet_1 | IS ANY COPPER SECONDARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. | CONDUCTORS - SECONDARY | 2958465 | 9.007A | N | Data Capture
|  | FOR COPPER SECONDARY CONDUCTORS – IS THE SPAN LENGTH GREATER THAN 240 FEET? | SECONDARY-LEVEL | 0 | 2010 | Sec_Conductor_Copper_240Feet_2 | IS ANY COPPER SECONDARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. | CONDUCTORS - SECONDARY | 2958465 | 9.007A | N | Data Capture
|  | For copper secondary conductors – Is the span length greater than 240 feet? | SECONDARY-LEVEL | 0 | 2010 | Sec_Conductor_Copper_240Feet_3 | For copper secondary conductors – Is the span length greater than 240 feet? | CONDUCTORS - SECONDARY | 2958465 | 9.007A | N | Data Capture
|  | For copper secondary conductors – Is the span length greater than 240 feet? | SECONDARY-LEVEL | 0 | 2010 | Sec_Conductor_Copper_240Feet_4 | Is the span length for copper secondary conductors greater than 240 feet? | CONDUCTORS - SECONDARY | 2958465 | 9.007A | N | Data Capture
|  | IS ANY ALUMINUM SECONDARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. | SECONDARY-LEVEL | 0 | 2005 | Sec_Conductor_Aluminum_240Feet | IS ANY ALUMINUM SECONDARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. | CONDUCTORS - SECONDARY | 2958465 | 9.007B | N | Data Capture
|  | IS THE SPAN LENGTH FOR ACSR SECONDARY CONDUCTORS GREATER THAN 240 FEET? | SECONDARY-LEVEL | 0 | 2005 | Sec_Conductor_Aluminum_240Feet_1 | IS ANY ALUMINUM SECONDARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. | CONDUCTORS - SECONDARY | 2958465 | 9.007B | N | Data Capture
|  | FOR ACSR SECONDARY CONDUCTORS – IS THE SPAN LENGTH GREATER THAN 240 FEET? | SECONDARY-LEVEL | 0 | 2005 | Sec_Conductor_Aluminum_240Feet_2 | IS ANY ALUMINUM SECONDARY CONDUCTOR SPAN LENGTH IN ANY DIRECTION GREATER THAN 240 FEET? NOTE: IF ONE SPAN IS GREATER THAN 240 FEET AND ONE SPAN IS LESS THAN 240 FEET – SELECT “YES”. | CONDUCTORS - SECONDARY | 2958465 | 9.007B | N | Data Capture
|  | For ACSR secondary conductors – Is the span length greater than 240 feet? | SECONDARY-LEVEL | 0 | 2005 | Sec_Conductor_Aluminum_240Feet_3 | For ACSR secondary conductors – Is the span length greater than 240 feet? | CONDUCTORS - SECONDARY | 2958465 | 9.007B | N | Data Capture
|  | For ACSR secondary conductors – Is the span length greater than 240 feet? | SECONDARY-LEVEL | 0 | 2005 | Sec_Conductor_Aluminum_240Feet_4 | Is the span length for ACSR secondary conductors greater than 240 feet? | CONDUCTORS - SECONDARY | 2958465 | 9.007B | N | Data Capture
|  | SELECT ALL THE EQUIPMENT YOU SEE AT THE COMMUNICATION LEVEL: | COMMUNICATION-LEVEL | 0 | 3001 | Comm_Mat_List | SELECT ALL THE EQUIPMENT YOU SEE AT THE COMMUNICATION LEVEL: | MATERIALVERIFICATION | 2958465 | MAT_COMM | N | Data Capture
|  | Select all the equipment you see at the communication level: | COMMUNICATION-LEVEL | 0 | 3001 | Comm_Mat_List_1 | Select all the equipment you see at the communication level: | COMMUNICATION MATERIAL | 2958465 | MAT_COMM | N | Data Capture
equip_comm | NULL | SELECT ALL THE EQUIPMENT YOU SEE AT THE COMMUNICATION LEVEL: | COMMUNICATION-LEVEL | 999 | 3001 | Comm_Mat_List_2 | SELECT ALL THE EQUIPMENT YOU SEE AT THE COMMUNICATION LEVEL: | MATERIALVERIFICATION | 2958465 | MAT_COMM | N | Data Capture
|  | SELECT ALL THE EQUIPMENT YOU SEE AT THE PRIMARY LEVEL: | PRIMARY-LEVEL | 0 | 1000 | Pri_Mat_List | SELECT ALL THE EQUIPMENT YOU SEE AT THE PRIMARY LEVEL: | MATERIALVERIFICATION | 2958465 | MAT_PRI | N | Data Capture
|  | Select all the equipment you see at the primary level: | PRIMARY-LEVEL | 0 | 1000 | Pri_Mat_List_1 | Select all the equipment you see at the primary level: | PRIMARY MATERIAL | 2958465 | MAT_PRI | N | Data Capture
|  | SELECT ALL THE EQUIPMENT YOU SEE AT THE PUBLIC LEVEL: | PUBLIC-LEVEL | 0 | 4000 | Pub_Mat_List | SELECT ALL THE EQUIPMENT YOU SEE AT THE PUBLIC LEVEL: | MATERIALVERIFICATION | 2958465 | MAT_PUB | N | Data Capture
|  | Select all the equipment you see at the public level: | PUBLIC-LEVEL | 0 | 4000 | Pub_Mat_List_1 | Select all the equipment you see at the public level: | PUBLIC MATERIAL | 2958465 | MAT_PUB | N | Data Capture
equip_pub | NULL | SELECT ALL THE EQUIPMENT YOU SEE AT THE PUBLIC LEVEL: | PUBLIC-LEVEL | 999 | 4000 | Pub_Mat_List_2 | SELECT ALL THE EQUIPMENT YOU SEE AT THE PUBLIC LEVEL: | MATERIALVERIFICATION | 2958465 | MAT_PUB | N | Data Capture
|  | SELECT ALL THE EQUIPMENT YOU SEE AT THE SECONDARY LEVEL: | SECONDARY-LEVEL | 0 | 2000 | Sec_Mat_List | SELECT ALL THE EQUIPMENT YOU SEE AT THE SECONDARY LEVEL: | MATERIALVERIFICATION | 2958465 | MAT_SEC | N | Data Capture
|  | Select all the equipment you see at the secondary level: | SECONDARY-LEVEL | 0 | 2000 | Sec_Mat_List_1 | Select all the equipment you see at the secondary level: | SECONDARY MATERIAL | 2958465 | MAT_SEC | N | Data Capture
equip_sec | NULL | SELECT ALL THE EQUIPMENT YOU SEE AT THE SECONDARY LEVEL: | SECONDARY-LEVEL | 999 | 2000 | Sec_Mat_List_2 | SELECT ALL THE EQUIPMENT YOU SEE AT THE SECONDARY LEVEL: | MATERIALVERIFICATION | 2958465 | MAT_SEC | N | Data Capture
|  | Select all the equipment you see at the transmission level: | TRANSMISSION-LEVEL | 0 | 5000 | Trans_MAT_List | Select all the equipment you see at the transmission level: | POLES - STEEL, POLES - TREE, POLES - COMPOSITE, PO | 2958465 | MAT_TRAN | N | Data Capture
hardware_fuse | NULL | ARE ANY FUSE HOLDERS BURNED OR TRACKING? | PRIMARY-LEVEL | 61 | 1900 | Pri_Hardware_Fuse_Tracking | ARE ANY FUSE HOLDERS BURNED OR TRACKING? | HARDWARE/FRAMING | 2958465 | NULL | N
equip_pri | NULL | SELECT ALL THE EQUIPMENT YOU SEE AT THE PRIMARY LEVEL: | PRIMARY-LEVEL | 999 | 1000 | Pri_Mat_List_2 | SELECT ALL THE EQUIPMENT YOU SEE AT THE PRIMARY LEVEL: | MATERIALVERIFICATION | 2958465 | NULL | N
wind_6feet_pri | NULL | WILL 6 FEET OF CLEARANCE BETWEEN CONDUCTORS AND TREES REMAIN DURING WIND EVENTS? | PRIMARY-LEVEL | 7 | 1901 | Pri_Pole_6Feet_Clearance | WILL 6 FEET OF CLEARANCE BETWEEN CONDUCTORS AND TREES REMAIN DURING WIND EVENTS? | POLES - WOOD, POLES - COMPOSITE | 2958465 | NULL | N
str_6feet_pri | NULL | WILL 6 FEET OF CLEARANCE BETWEEN STRUCTURE AND TREES REMAIN DURING WIND EVENTS? | PRIMARY-LEVEL | 999 | 1901 | Pri_Pole_6Feet_Clearance_1 | WILL 6 FEET OF CLEARANCE BETWEEN CONDUCTORS AND TREES REMAIN DURING WIND EVENTS? | POLES - WOOD, POLES - COMPOSITE | 43846 | NULL | N
abnormal_pri | Indicate if any of the following types of structural failure are observed on pole. | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | PRIMARY-LEVEL | 12 | 1905 | Pri_Pole_Structure_Failure | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | NULL | N
xarm_pri_det | NULL | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | PRIMARY-LEVEL | 999 | 1910 | Pri_XARM_Deteriorated_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 2958465 | NULL | N
xarm_pri_det | NULL | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL ARE DETERIORATED? | PRIMARY-LEVEL | 999 | 1910 | Pri_XARM_Deteriorated_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 44286 | NULL | N
Pri_XARM_Double |  | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | PRIMARY-LEVEL | 99 | 1911 | Pri_XARM_Double_Qty | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 2958465 | NULL | N
xarm_pri_2 | Quantity of Crossarms at the PRIMARY level? | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | PRIMARY-LEVEL | 22 | 1912 | Pri_XARM_Single_Qty | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 2958465 | NULL | N
xarm_pri_2 | Quantity of Crossarms at the PRIMARY level? | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 22 | 1912 | Pri_XARM_Single_Qty_1 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 44286 | NULL | N
xarm_pri_2 | Quantity of Crossarms at the PRIMARY level? | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | PRIMARY-LEVEL | 22 | 1912 | Pri_XARM_Single_Qty_2 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING TRIPLES, FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 44286 | NULL | N
Pri_XARM_Triple |  | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | PRIMARY-LEVEL | 99 | 1913 | Pri_XARM_Triple_Qty | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: COUNT ALL CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL – INCLUDING FUSE-HOLDER ARMS, TRANSFORMER HANGER ARMS, ETC. NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 2958465 | NULL | N
abnormal_sec | Indicate if any of the following types of structural failure are observed on pole. | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 72 | 2900 | Sec_Pole_Structure_Failure | INDICATE IF ANY OF THE FOLLOWING TYPES OF STRUCTURAL FAILURE ARE OBSERVED AT THIS LEVEL. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | POLES - WOOD, POLES - COMPOSITE | 2958465 | NULL | N | Health/Condition
riser_sec | NULL | INDICATE IF ANY OF THE FOLLOWING RISER CONDITIONS ARE OBSERVED ON THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | SECONDARY-LEVEL | 105 | 2035 | Sec_Riser_Conditions_4 | INDICATE IF ANY OF THE FOLLOWING RISER CONDITIONS ARE OBSERVED ON THE STRUCTURE. SELECT ALL THAT APPLY OR SELECT “NO ABNORMAL CONDITIONS”. | TERMINATIONS | 2958465 | NULL | N | Health/Condition
xarm_sec_det | NULL | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | SECONDARY-LEVEL | 999 | 2905 | Sec_XARM_Deteriorated_Qty | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 2958465 | NULL | N
xarm_sec_det | NULL | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL ARE DETERIORATED? | SECONDARY-LEVEL | 999 | 2905 | Sec_XARM_Deteriorated_Qty_1 | HOW MANY CROSSARMS OF THIS MATERIAL TYPE AT THIS LEVEL ARE DETERIORATED AND NEED TO BE REPLACED? NOTE: NOTIFICATION REQUIRED IF ANSWER IS GREATER THAN 0. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 44286 | NULL | N
Sec_XARM_Double |  | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | SECONDARY-LEVEL | 99 | 2906 | Sec_XARM_Double_Qty | HOW MANY TOTAL SETS OF DOUBLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A DOUBLE CROSSARM IS WHEN TWO CROSSARM PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 2958465 | NULL | N
xarm_sec_2 | Quantity of Crossarms at the SECONDARY level? | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | SECONDARY-LEVEL | 90 | 2906 | Sec_XARM_Single_Qty | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 2958465 | NULL | N
xarm_sec | Quantity of Crossarms at the SECONDARY level? | HOW MANY CROSSARMS ARE AT THIS LEVEL? | SECONDARY-LEVEL | 90 | 2906 | Sec_XARM_Single_Qty_1 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 43838 | NULL | N
xarm_sec_2 | Quantity of Crossarms at the SECONDARY level? | HOW MANY TOTAL CROSSARMS ARE AT THIS LEVEL? | SECONDARY-LEVEL | 90 | 2906 | Sec_XARM_Single_Qty_2 | HOW MANY TOTAL SINGLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A SINGLE CROSSARM IS WHEN ONLY ONE CROSSARM PIECE EXISTS AT A SPECIFIC ELEVATION ON THE POLE. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 44286 | NULL | N
Sec_XARM_Triple |  | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | SECONDARY-LEVEL | 99 | 2907 | Sec_XARM_Triple_Qty | HOW MANY TOTAL SETS OF TRIPLE CROSSARMS OF THIS MATERIAL TYPE ARE AT THIS LEVEL? NOTE: A TRIPLE CROSSARM IS WHEN THREE CROSSARMS PIECES EXIST IN A PARALLEL ORIENTATION AT THE SAME ELEVATION ON THE POLE. | CROSSARMS - WOOD, CROSSARMS - COMPOSITE | 2958465 | NULL | N
|  | Capture a picture of each distribution guy anchor-Include any stamp/marking if visible | PUBLIC-LEVEL | 0 | 4008 | Pub_DownGuy_Anchor_Photo | Capture a picture of each distribution guy anchor-Include any stamp/marking if visible | DOWN GUYS | 2958465 | PH.01 | N
|  | TAKE THE FOLLOWING PHOTOS, VERTICALLY AND NO ZOOM | STRUCTURE-VERIFICATION | 0 | 901 | Struc_Ver_Photo | TAKE THE FOLLOWING PHOTOS, VERTICALLY AND NO ZOOM | STRUCTURE-VERIFICATION | 2958465 | PH.02 | N
|  | PHOTOS | STRUCTURE-VERIFICATION | 0 | 901 | Struc_Ver_Photo_1 | TAKE THE FOLLOWING PHOTOS, VERTICALLY AND NO ZOOM | STRUCTURE-VERIFICATION | 2958465 | PH.02 | N
|  | TAKE A PICTURE OF THE ENTIRE STRUCTURE | STRUCTURE-VERIFICATION | 0 | 901 | Struc_Ver_Photo_2 | TAKE THE FOLLOWING PHOTOS, VERTICALLY AND NO ZOOM | STRUCTURE-VERIFICATION | 2958465 | PH.02 | N
|  | Take a picture of the entire structure | STRUCTURE-VERIFICATION | 0 | 900 | Struc_Ver_Struc_Photos | Photos | STRUCTURE-VERIFICATION | 2958465 | PH.02 | N
|  | Take the following photos, vertically and no zoom | STRUCTURE-VERIFICATION | 0 | 900 | Struc_Ver_Struc_Photos_1 | Take a picture of the entire structure | STRUCTURE-VERIFICATION | 2958465 | PH.02 | N
|  | Take the following photos, vertically and no zoom | STRUCTURE-VERIFICATION | 0 | 900 | Struc_Ver_Struc_Photos_2 | Take the following photos, vertically and no zoom | STRUCTURE-VERIFICATION | 2958465 | PH.02 | N
Survey_Completed_By |  | THIS SURVEY IS BEING COMPLETED BY: | STRUCTURE-VERIFICATION | 99 | 1 | Struc_Ver_Survey_Completed_By | THIS SURVEY IS BEING COMPLETED BY: | STRUCTURE-VERIFICATION | 2958465 | SV001 | N | Data Capture
|  | This survey is being completed by: | STRUCTURE-VERIFICATION | 0 | 1 | Struc_Ver_Survey_Completed_By_1 | THIS SURVEY IS BEING COMPLETED BY: | STRUCTURE-VERIFICATION | 2958465 | SV001 | N | Data Capture
completeSurvey | Are you able to complete the survey? | ARE YOU ABLE TO COMPLETE THE DATA CAPTURE SURVEY? | STRUCTURE-VERIFICATION | 1 | 2 | Struc_Ver_Complete_Survey | ARE YOU ABLE TO COMPLETE THE DATA CAPTURE SURVEY? | STRUCTURE-VERIFICATION | 2958465 | SV002 | N | Data Capture
|  | ARE YOU ABLE TO COMPLETE THE DATA CAPTURE SURVEY? | STRUCTURE-VERIFICATION | 0 | 2 | Struc_Ver_Complete_Survey_1 | ARE YOU ABLE TO COMPLETE THE DATA CAPTURE SURVEY? | STRUCTURE-VERIFICATION | 2958465 | SV002 | N | Data Capture
|  | Indicate why the survey is unable to be completed | STRUCTURE-VERIFICATION | 0 | 3 | Struc_Ver_Unable_To_Complete_Reason | Indicate why the survey is unable to be completed | STRUCTURE-VERIFICATION | 2958465 | SV002A | N | Data Capture
|  | Indicate why the survey is unable to be completed: | STRUCTURE-VERIFICATION | 0 | 3 | Struc_Ver_Unable_To_Complete_Reason_1 | Indicate why the survey is unable to be completed: | STRUCTURE-VERIFICATION | 2958465 | SV002A | N | Data Capture
structureType | What is the structure type? | WHAT IS THE STRUCTURE TYPE? | STRUCTURE-VERIFICATION | 3 | 4 | Struc_Ver_Struc_Type | WHAT IS THE STRUCTURE TYPE? | STRUCTURE-VERIFICATION | 2958465 | SV003 | N | Data Capture
|  | What is the structure type? | STRUCTURE-VERIFICATION | 0 | 4 | Struc_Ver_Struc_Type_1 | WHAT IS THE STRUCTURE TYPE? | STRUCTURE-VERIFICATION | 2958465 | SV003 | N | Data Capture
|  | What is the structure material? | STRUCTURE-VERIFICATION | 0 | 5 | Struc_Ver_Structure_Material | WHAT IS THE STRUCTURE MATERIAL? | STRUCTURE-VERIFICATION | 2958465 | SV004 | N | Data Capture
structureMaterial | What is the structure material? | WHAT IS THE STRUCTURE MATERIAL? | STRUCTURE-VERIFICATION | 2 | 5 | Struc_Ver_Structure_Material_1 | WHAT IS THE STRUCTURE MATERIAL? | STRUCTURE-VERIFICATION | 2958465 | SV004 | N | Data Capture
structureLevel |  | WHAT LEVEL EXIST ON THIS STRUCTURE? | STRUCTURE-VERIFICATION | 4 | 6 | Struc_Ver_Levels | WHAT LEVEL EXIST ON THIS STRUCTURE? | STRUCTURE-VERIFICATION | 2958465 | SV005 | N | Data Capture
|  | What level exist on this structure? | STRUCTURE-VERIFICATION | 0 | 6 | Struc_Ver_Levels_1 | WHAT LEVEL EXIST ON THIS STRUCTURE? | STRUCTURE-VERIFICATION | 2958465 | SV005 | N | Data Capture
|  | What level exist on this structure? | STRUCTURE-VERIFICATION | 0 | 6 | Struc_Ver_Levels_2 | What levels exist on this structure? | STRUCTURE-VERIFICATION | 2958465 | SV005 | N | Data Capture
|  | Is this structure located in a High Fire Area? | STRUCTURE-VERIFICATION | 0 | 7 | Struc_Ver_High_Fire | Is this structure located in a High Fire Area? | STRUCTURE-VERIFICATION | 2958465 | SV006 | N | Data Capture
|  | Is the structure one of these multi-pole configurations? | STRUCTURE-VERIFICATION | 0 | 8 | Struc_Ver_MultiPole | Is the structure one of these multi-pole configurations? | STRUCTURE-VERIFICATION | 2958465 | SV007 | N | Data Capture
|  | Is the structure one of these multi-pole configurations? | STRUCTURE-VERIFICATION | 0 | 8 | Struc_Ver_MultiPole_1 | Is the structure one of these multi-pole configurations? | STRUCTURE-VERIFICATION | 2958465 | SV007 | N | Data Capture
|  | How many poles does the structure contain? | STRUCTURE-VERIFICATION | 0 | 9 | Struc_Ver_MultiPole_Qty | How many poles does the structure contain? | STRUCTURE-VERIFICATION | 2958465 | SV008 | N | Data Capture
|  | Record the structure numbers for the other poles that make up the structure | STRUCTURE-VERIFICATION | 0 | 10 | Struc_Ver_MultiPole_StrucNums | Record the structure numbers for the other poles that make up the structure | STRUCTURE-VERIFICATION | 2958465 | SV009 | N | Data Capture
|  | What type of Steel pole is the structure? | STRUCTURE-VERIFICATION | 0 | 11 | Struc_Ver_Steel_Type | What type of Steel pole is the structure? | STRUCTURE-VERIFICATION | 2958465 | SV010 | N | Data Capture
|  | Were any conditions identified at the Transmission level that require immediate attention (e.g. Priority 1 notification)? | TRANSMISSION-LEVEL | 0 | 5001 | Trans_Conditions | Were any conditions identified at the Transmission level that require immediate attention (e.g. Priority 1 notification)? | POLES - STEEL, POLES - TREE, POLES - COMPOSITE, PO | 2958465 | T001 | N | Health/Condition
|  | What type of components or condition(s) at the transmission level require immediate attention? Select all that apply. | TRANSMISSION-LEVEL | 0 | 5002 | Trans_Conditions_Component | What type of components or condition(s) at the transmission level require immediate attention? Select all that apply. | POLES - STEEL, POLES - TREE, POLES - COMPOSITE, PO | 2958465 | T002 | N | Health/Condition
|  | Confirm Transmission Operations was notified of conditions requiring immediate attention? | TRANSMISSION-LEVEL | 0 | 5003 | Trans_Ops_Contacted | Confirm Transmission Operations was notified of conditions requiring immediate attention? | POLES - STEEL, POLES - TREE, POLES - COMPOSITE, PO | 2958465 | T003 | N | Health/Condition
|  | How many composite, horizontal construction crossarms are at this level? | PRIMARY-LEVEL | 0 | 1077 | Pri_XARM_Composite_Horizontal_Qty | How many composite, horizontal construction crossarms are at this level? | CROSSARMS - COMPOSITE | 2958465 | X.01 | N
|  | HOW MANY COMPOSITE, HORIZONTAL CONSTRUCTION CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1077 | Pri_XARM_Composite_Horizontal_Qty_1 | NULL | CROSSARMS - COMPOSITE | 2958465 | X.01 | N
comp_hor_pri | NULL | HOW MANY COMPOSITE, HORIZONTAL CONSTRUCTION CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 999 | 1077 | Pri_XARM_Composite_Horizontal_Qty_2 | NULL | CROSSARMS - COMPOSITE | 43838 | X.01 | N
|  | How many composite, vertical construction crossarms are at this level? | PRIMARY-LEVEL | 0 | 1080 | Pri_XARM_Composite_Vert_Qty | How many composite, vertical construction crossarms are at this level? | CROSSARMS - COMPOSITE | 2958465 | X.02 | N
|  | HOW MANY COMPOSITE, VERTICAL CONSTRUCTION CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1080 | Pri_XARM_Composite_Vertical_Qty_1 | NULL | CROSSARMS - COMPOSITE | 2958465 | X.02 | N
comp_ver_pri | NULL | HOW MANY COMPOSITE, VERTICAL CONSTRUCTION CROSSARMS ARE AT THIS LEVEL? | PRIMARY-LEVEL | 999 | 1080 | Pri_XARM_Composite_Vertical_Qty_2 | NULL | CROSSARMS - COMPOSITE | 43838 | X.02 | N
|  | Is there at least 6 feet of clearance between trees/foliage and conductors? | PRIMARY-LEVEL | 0 | 1014 | Pri_Conductor_6ft_Tree_Clearance | Is there at least 6 feet of clearance between trees/foliage and conductors? | CONDUCTORS - PRIMARY | 2958465 | X.03 | N
|  | HOW MANY LINE SIDE PHASES ARE INSTALLED AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1031 | Pri_Conductor_LinePhase_Qty_1 | NULL | CONDUCTORS - PRIMARY | 2958465 | X.04 | N
|  | HOW MANY CONDUCTORS ARE INSTALLED AT THIS LEVEL? | PRIMARY-LEVEL | 0 | 1035 | Pri_Conductor_Qty_1 | NULL | CONDUCTORS - PRIMARY | 2958465 | X.05 | N
|  | Indicate which of the following type(s) of non-exempt material are present on the pole. Select all that apply or "None of the above". | PRIMARY-LEVEL | 0 | 1060 | Pri_Pole_NonExempt_Material | Indicate which of the following type(s) of non-exempt material are present on the pole. Select all that apply or "None of the above". | POLES - STEEL, POLES - TREE, POLES - COMPOSITE, PO | 2958465 | X.06 | N
|  | INDICATE WHICH OF THE FOLLOWING TYPE(S) OF NON-EXEMPT MATERIAL ARE PRESENT ON THE POLE. SELECT ALL THAT APPLY OR "NONE OF THE ABOVE". | PRIMARY-LEVEL | 0 | 1060 | Pri_Pole_NonExempt_Material_1 | NULL | POLES - WOOD, POLES - COMPOSITE | 2958465 | X.06 | N
|  | How many wood, horizontal construction crossarms are at this level? | PRIMARY-LEVEL | 0 | 1101 | Pri_XARM_Wood_Hrz_Qty | How many wood, horizontal construction crossarms are at this level? | CROSSARMS - WOOD | 2958465 | X.07 | N
|  | How many wood, vertical construction crossarms are at this level? | PRIMARY-LEVEL | 0 | 1105 | Pri_XARM_Wood_Vert_Qty | How many wood, vertical construction crossarms are at this level? | CROSSARMS - WOOD | 2958465 | X.08 | N
|  | HOW MANY LINE SIDE PHASES ARE INSTALLED AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2012 | Sec_Conductor_LinePhase_Qty_1 | NULL | CONDUCTORS - SECONDARY | 2958465 | X.10 | N
|  | HOW MANY CONDUCTORS ARE INSTALLED AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2018 | Sec_Conductor_Qty_1 | NULL | CONDUCTORS - SECONDARY | 2958465 | X.11 | N
|  | How many wood, horizontal construction crossarms are at this level? | SECONDARY-LEVEL | 0 | 2072 | Sec_XARM_Wood_Horizontal_Qty | How many wood, horizontal construction crossarms are at this level? | CROSSARMS - WOOD | 2958465 | X.12 | N
wood_hor_sec | NULL | HOW MANY WOOD, HORIZONTAL CONSTRUCTION CROSSARMS ARE AT THIS LEVEL? | SECONDARY-LEVEL | 999 | 2072 | Sec_XARM_Wood_Horizontal_Qty_1 | NULL | CROSSARMS - WOOD | 43838 | X.12 | N
|  | HOW MANY WOOD, HORIZONTAL CONSTRUCTION CROSSARMS ARE AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2072 | Sec_XARM_Wood_Horizontal_Qty_2 | NULL | CROSSARMS - WOOD | 2958465 | X.12 | N
|  | How many wood, vertical construction crossarms are at this level? | SECONDARY-LEVEL | 0 | 2077 | Sec_XARM_Wood_Vertical_Qty | How many wood, vertical construction crossarms are at this level? | CROSSARMS - WOOD | 2958465 | X.13 | N
|  | HOW MANY WOOD, VERTICAL CONSTRUCTION CROSSARMS ARE AT THIS LEVEL? | SECONDARY-LEVEL | 0 | 2077 | Sec_XARM_Wood_Vertical_Qty_1 | NULL | CROSSARMS - WOOD | 2958465 | X.13 | N
wood_ver_sec | NULL | HOW MANY WOOD, VERTICAL CONSTRUCTION CROSSARMS ARE AT THIS LEVEL? | SECONDARY-LEVEL | 999 | 2077 | Sec_XARM_Wood_Vertical_Qty_2 | NULL | CROSSARMS - WOOD | 43838 | X.13 | N

## InspectApp Notification Matrix (hidden)
id | questionId | answer | problemStatement | problemCode | level | material | createdAt | updatedAt | removedAt | actionText1 | actionText2 | objectType | priority | multiProblemStatements
000b2bd1-ee01-4621-b8c3-b8a223ec32b8 | 2.003C | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
003ccc87-a675-46f3-b936-29a49c06a6b3 | 6.003 | Insulator chipped (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Insulators | 2022-03-08 06:05 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
004523a8-e288-4c08-939f-2c0014656d0f | 7.004A | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
00989b7a-fef5-431b-9541-f8ecebdf1b7e | 1.002 | Hole approximately >2 inches near through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | secondary-level | ED_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
015f430c-6b5d-48f1-baa9-5bf4c06d44e5 | 7.002A | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
0194626c-350b-4a9d-aa1b-95c0282a12c8 | 1.009 | Animal nests with potential to contact energized components or interfere with equipment operation (Notification Required) | REMV ANIMNST SEC STLTPOLE | 0IZU | public-level | Poles - Wood | 2022-03-08 06:03 |  |  | A remove animal nest Problem Statement does not exist at the public level. If this condition exist in the field, then select secondary. |  | ED_SL
01d58d81-0090-4b99-847e-3d3a95575eac | 2.007A | 1 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
01ff5b70-49b9-4dc9-81dd-1003a6ff1a88 | 2.003A | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
0204f713-7c6b-4afe-a1a8-6aeccb223725 | 13.001A | Anchor rods broken/corroded, pole leaning, public hazard (Notification Required) | REPLC DAMAGE PUBLIC ANCHOR POLE | COP6 | public-level | Down Guys | 2022-03-08 06:03 | 2021-12-22 03:27 | 2021-12-22 03:27 |  | Create notification based on severity of issue. | ED_POLE
0253c301-edfe-41b0-94ee-9ccd255db9ff | 7.004A | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
025f6cd5-3ad0-4f2e-a2a7-81c331947eb5 | 2.003A | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
0315d2d5-ed3a-4aad-8ff3-aa0b7f8ee7e4 | 2.003A | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
032e8851-585c-483d-81dc-9ba9b2e6b666 | 14.001 | In contact with animal nest (Notification Required) | REMV ANIMNST PRI POLE | 343A | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
035377a3-49ca-46fd-b018-6a50baa67044 | 7.002A | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
036642d2-043d-40cb-9aa9-101e00d8a525 | 8.002A | Immediate danger concerning palm fronds falling or blowing into conductors (Notification Required) | TRIM VEG TREE PRI CBL/CND POLE | 046B | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed vegetation clearance issues are present in the primary conductors/phases/taps/equipment.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
03cbe37a-c135-4a2e-a401-59eac7aa81f5 | 11.004 | Damaged equipment brackets or braces (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Hardware/Framing | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_POLE
0418e0ae-d164-49a8-baf9-61118e75989a | 0.020B | No (Notification Required) | REPAIR CLEARNC PUBLIC POLE | C0Q0 | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if the appropriate amount of climbing space per GO-95 is present on pole at this level. | Create notification if inadequate climbing space exist. | ED_POLE
0419ff13-e36f-41e7-9495-3b8ccfdfca7c | 2.006A | 10 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
045872cb-0f39-49c3-aeb8-16a0971b414d | 0.016 | Between 2 feet and 6 feet (Notification Required) | TRIM VEG TREE PRI CBL/CND POLE | 046B | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Select option that best represents primary line clearance from trees/foliage. | Create notification if <6’ and based on severity. | EZ_POLE
04b67b01-654e-48f8-95b1-8809dacb2a06 | 8.015 | Pothead cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | 983A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | EZ_POLE
04e42be2-ab02-4df2-a36b-2988cdcb20e5 | 5.001 | Depth of embedment less than 10% + 1 feet of the pole height (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
0583d5c5-b129-4a7d-a229-2cebc21eee02 | 2.004A | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
0599a709-3692-4ef9-ba59-6fbb7dda5455 | 14.001 | Pothead not properly attached to supporting structure (Notification Required) | REPLC DAMAGE PRI TERM POLE | 778A | primary-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
059eea95-52d5-40d7-bf05-021fbb6a1f3f | 7.002A | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
05aad6ce-1b7e-4bc5-8996-69c2d9f30ffc | 2.006A | 18 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
05cf4289-ae5d-46bb-8e68-c1438422f8a6 | 2.005B | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
05e66da0-9d18-4d69-94de-2a938db4bc18 | 2.006A | 14 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
05f99ad9-849c-494a-8c08-a2f71e601303 | 7.002A | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
06723172-5a6a-42f0-b8cd-54f0268f2178 | 13.002 | SCE energized components (Notification Required) | REPAIR CLEARNC PUBLIC GUY POLE | 457A | public-level | Down Guys | 2022-03-08 06:04 |  |  | Determine if down guys have the appropriate amount of clearance per GO-95 or could potentially contact the listed options. | Create notification based on severity of issue. | EZ_POLE
06be0507-6540-49d4-81ba-df5c685b43d0 | 8.017 | No (Notification Required) | REPLC DAMAGE PRI LTNGARR POLE | 795A | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if primary lightning arrestor(s) are properly installed and protecting primary equipment. | Create notification if primary equipment is missing lighting arrestor(s). | EZ_POLE
06e4bc1a-efc0-45cc-b1d5-4f76682e73ec | 2.007A | 17 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
0796991a-3bcf-40aa-9db0-579dc120ef92 | 6.003 | Insulator squatting (Notification Required) | REPLC FLOTR/SQTR SEC INSLTR POLE | 826A | secondary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
0810ec45-7174-4510-bb83-882ba550f3b7 | 8.002B | Less than 6 feet radially between conductor and non-climbable pole (e.g. streetlight) (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable energized conductor- structure clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
084131f5-5365-47e9-8723-b8d6cbd5f621 | 2.003A | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
085c7683-951e-48ca-888d-a39bf6ff2f74 | 6.003 | Insulator broken (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
0872680c-d6a5-4e05-a56a-283a701b476a | 18.001 | Damage to anchor bolts or foundation (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Pole - Concrete | 2022-03-08 06:03 |  |  |  |  | ED_SL
0873f60c-bd74-43bd-86df-683a2f1e8d24 | 1.002 | Three or more holes approximately >2 inch diameter, within approximately 18 inches vertical of a through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | primary-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
090ebb5a-237b-4bc4-ab0c-9f421c2ed838 | 7.002A | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
094e7e27-da27-4683-be57-5cef2e42d8b7 | 2.004A | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
09746a33-976c-4cc3-a276-1ce632da2b2e | 2.003A | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
09c68e49-9f6a-4725-b63e-d9bc79ee3af8 | 2.004A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
09d70832-4c64-4cc5-b506-c3e97725eeeb | 12.002 | SCE non-energized electrical components (Notification Required) | REPAIR CLEARNC PRI GUY POLE | 612A | primary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if span guy has the appropriate amount of clearance per GO-95 or could potentially contact the listed options.• Select “No abnormal condition” if span guys have appropriate clearance. | Create notification based on severity of issue. | EZ_POLE
0a39cba0-8871-4a11-9db5-9ee5b4257ff6 | 2.005B | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
0aefb621-e920-499b-9c8b-42479d4dd481 | 2.005B | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
0b1f4ae1-e28e-4e2e-bbf8-8d8fea6246f1 | 16.001 | Yes (Notification Required) | REPLC DAMAGE PRI LTNGARR POLE | CPE8 | primary-level | Lightning Arresters | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if primary arrestor ground is connected to equipment and/or ground, or primary arrestor has operated and/or damaged. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
0b6d07ce-440b-4289-bd7f-e3d42261b1d4 | 2.005B | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
0bbe43cb-6e0b-4d7e-bee4-23c4e4d3c4ca | 7.004A | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
0bde3095-f506-4575-aaf3-2f1f00d61d83 | 2.003A | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
0bf7ecd0-2657-47bf-8b1b-0b9711b61a91 | 1.002 | Exterior damage approximately >2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | secondary-level | ED_POLE | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
0c14b274-081b-4b8d-b7f6-5af430ef1075 | 7.004A | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
0c1ea492-bf30-423a-9331-25e77f3972ec | 11.004 | Damaged equipment brackets or braces (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Hardware/Framing | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | EZ_POLE
0c46fa12-6515-4e9a-a2a3-d9cb4a5ed5e2 | 11.005 | Luminaire (streetlight head) or hardware corroded, missing, broken, or bending (Notification Required) | REPLC DAMAGE SEC LNS/RFRCTR STLTLAMP | 0I0B | secondary-level | ED_LAMP | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_LAMP
0c7a5043-d3da-4ffb-8505-138eb3a228c6 | 10.006 | Yes (Notification Required) | TRIM VEG TREE SEC POLE | 058B | secondary-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if vegetation is currently or will interfere with operation of primary equipment. | Create notification based on severity of issue. | EZ_POLE
0ccc0c42-6518-4fe3-8228-4350104d5451 | 2.003C | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
0ccd6442-e695-4ead-ab3b-2823eaf369af | 2.006A | 9 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create notification and prioritize based on severity of issue. | ED_POLE
0cea639e-a299-4014-93f3-9dd26ea875f4 | 14.003 | Cables in Riser exposed (Notification Required) | REPLC DAMAGE PUBLIC RISER POLE | 713A | public-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | EZ_POLE
0d06825e-f2aa-4f36-8e52-25f12b665b6a | 7.004A | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
0d0b11f2-0ac3-4ce7-9be5-14d39dfebe03 | 7.004A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
0d1b61dc-2be3-42c8-b8fe-e65c14d022c5 | 11.004 | Corroded, missing, broken or bending hardware (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Hardware/Framing | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_POLE
0d2f8ac4-16bb-4d19-a57f-b2fa9b817952 | 0.016 | 2 feet or less (Notification Required) | TRIM VEG TREE PRI CBL/CND POLE | 046B | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Select option that best represents primary line clearance from trees/foliage. | Create notification if <6’ and based on severity. | EZ_POLE
0d358bc7-df37-4630-8774-0aa4ce8cc94a | 2.003C | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
0d44b119-2250-4c2d-bc4c-5351616240e7 | 2.003C | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
0d477820-cd11-4f4e-8425-a59eebbbbb32 | 2.005B | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
0d56ffce-d532-4700-9f7b-8825efda3320 | 7.004A | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
0d776901-5395-4dc4-82ce-f34da046b084 | 14.002 | Pothead sparking, arcing, or noisy during normal ‘dry’ weather conditions (Notification Required) | REPLC DAMAGE PRI TERM POLE | 778A | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
0da280c1-250c-4358-a188-fb1f692e3f58 | 7.002A | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
0da47f1c-adae-4fbc-9acb-a176409f8068 | 2.003C | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
0daca98d-69c3-4148-af33-b4a66dfa9d08 | 2.003A | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
0dc9fd6f-6c24-455e-98bf-9a79ff0bbbb5 | 2.007A | 20 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
0dca196e-7b78-430d-98da-f6543776b67f | 2.005B | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
0de9171d-ba82-44be-bdae-6fc95fdb0e1a | 6.006 | Missing parts (Notification Required) | REPLC LOOSE SEC INSLTR POLE | CFL5 | secondary-level | Insulators | 2022-03-08 06:04 |  |  |  |  | ED_POLE
0e00ea49-8e12-4224-be28-c7e52290b837 | 6.003 | Upward strain (lift) on pin in tangent configuration (Notification Required) | REPLC LOOSE PRI INSLTR POLE | 962A | primary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
0e10b86d-0768-4f95-a4cb-37c02dd5c7b6 | 2.003A | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
0e261e69-f891-4192-8b49-17355f353521 | 2.005B | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
0e73443a-f2e0-4f0f-873d-b4071e8a749b | 3.002 | Bushings damaged (Notification Required) | REPLC DAMAGE PRI XFMR-D | D0E8 | primary-level | ED_XFMR | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
0ee38a75-6a52-41b6-8a08-0fcaafbe0aff | 2.003C | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
0f127ce2-1433-4528-a4ce-bc340eefc3b6 | 6.003 | Improper angle on pin insulator (Notification Required) | REPAIR DAMAGE SEC INSLTR POLE | CFJ9 | secondary-level | Insulators | 2022-03-08 06:05 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
0f406a6e-ceaf-4ef3-9b01-1e55cc293075 | 0.016 | 2 feet or less (Notification Required) | TRIM VEG TREE PRI CBL/CND POLE | CWF4 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Select option that best represents primary line clearance from trees/foliage. | Create notification if <6’ and based on severity. | ED_POLE
0f6787b0-069b-4664-8994-901c3a2a8f97 | 10.006 | Yes (Notification Required) | TRIM VEG TREE PRI POLE | C0F4 | primary-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if vegetation is currently or will interfere with operation of primary equipment. | Create notification based on severity of issue. | ED_POLE
0fb50022-0db3-41ba-9ba6-e65b25832c15 | 7.004A | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
0fde8e5a-53f6-421d-bb5b-85a0e4eeb135 | 2.004A | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
100931b9-a012-4b75-b668-38507a384b79 | 2.006A | 3 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
1026b034-3e03-41e6-b887-81457cbc1ac3 | 2.003C | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
10296c06-0787-4040-90ad-91189369f427 | 2.003D | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
10876705-f886-4e23-92a4-dbbd222d960d | 14.001 | Porcelain pothead insulators chipped or broken (Notification Required) | REPLC DAMAGE PRI TERM POLE | CSE8 | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
10d4571d-2b13-4dd3-92b7-4ffd13ac6a00 | 7.002B | Significant visual buckling (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
114d648b-72a0-45f2-8182-71530ac8e8b6 | 2.004A | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
1179f635-3bca-4861-ab64-d03b1aadc5d3 | 7.002A | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
118b53a3-f426-4935-b6e7-db0fb02a074e | 14.001 | Pothead sparking, arcing, or noisy during normal ‘dry’ weather conditions (Notification Required) | REPLC DAMAGE PRI TERM POLE | CSE8 | primary-level | Risers/Terminations | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
118ba9b5-cc12-4dfc-b3fb-22229ef25ad5 | 2.005B | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
11af1152-ab19-4d5e-844a-8f3f6f34a017 | 2.006A | 15 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
11d41687-ae6a-4d83-9db3-4d8a1cb0f813 | 9.003 | Bare conductors and through tree (Notification Required) | TRIM VEG TREE SEC CBL/CND POLE | CWK4 | secondary-level | Conductors - Secondary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable conductor clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
11d9bc37-156b-4a53-8fe7-6bc56ee8634f | 2.004A | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
11ef1ddf-3fb3-404f-ac98-842c3f2ff1d2 | 0.029 | Broken, damaged or severely strained communication guy wires (Notification Required) | CIP CLEARNC COMM GUY POLE | 0I50 | communication-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
11f51f63-a9b9-4f9e-827b-141f1f685803 | 2.003A | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
120f83e6-7b97-46eb-a101-00ff7648d0e7 | 1.007 | Pole leaning - public hazard (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Poles - Wood | 2022-03-08 06:04 |  |  | Identify if/how much the pole is leaning.• Select “pole is not leaning” if pole is not showing sins of leaning. | Create notification based on severity of issue. | ED_SL
1261023a-f877-4227-80bd-95550df8a438 | 7.002B | Bent mounting bracket and associated hardware (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
12950f45-dd9a-49f1-8451-51525c962825 | 1.002 | Exterior damage approximately >2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | primary-level | ED_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
12aa059f-62ab-4fa5-b58e-e2cb42a99053 | 2.006A | 16 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
12c0d303-085a-43c0-92c7-ad17fdf39962 | 2.005B | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
13051da0-6d51-4eb8-8dc8-fcaeb5d10939 | 7.002A | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
131da16e-a11d-487d-8295-0cd024fb0e27 | 8.016 | Span guy (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there is a possibility of primary conductors/phases clashing and/or public can contact.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearances. (Ex. Extreme condition should result in P1 notification). | ED_POLE
132026dc-eac4-4608-bf91-6174c12366ec | 2.003D | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
1337e4cc-5a5c-4128-b7fa-29b418aa0dd6 | 2.004A | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
13548f9e-cbe6-421a-b53e-593e35671c51 | 2.006A | 2 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
13bac298-f1c7-4999-a1a9-61bee65f8c29 | 8.001 | Metal debris in conductors (Notification Required) | REMV UNATH ATT PRI CBL/CND POLE | 278A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if there are metal and/or non-metal foreign objects in the primary conductors/phases/taps/equipment.• Select “No abnormal conditions” if no foreign objects are in primary. | Create notification based on severity of debris in conductors. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
13e24d0c-1a46-4774-b8d2-78c2606995dc | 2.004A | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
13f6a6d9-a644-4c20-b7df-305b5661258f | 7.002B | Significant visual fracturing (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
13febd24-9175-4ca6-a8f0-6dfc789f34bc | 2.003D | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
14008c01-823a-4912-a619-b96f964af734 | 2.007A | 14 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
141145da-4549-4cff-a4e1-84f3e55a4e45 | 2.003C | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
14d26f50-258e-4490-9157-e7c15fa87c4e | 2.005B | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
15236c37-feda-40ef-bec9-7dba2e0810d3 | 2.003D | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
159d107f-414e-42f8-b8bc-6f3a118d6003 | 12.004 | Cracked, damaged, deflected, frayed or loose (Notification Required) | REPLC DAMAGE SEC GUY POLE | 982A | secondary-level | Span Guys | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | EZ_POLE
15a55ecd-50a5-4584-8420-723208025a2b | 2.007A | 17 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
15d160f4-c3df-4505-a276-90fdd198015c | 7.002A | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
161ef38a-70ed-4d69-9847-5494be94c98f | 2.005B | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
1670cd8b-6d43-4089-a16d-9352b6deec11 | 2.003D | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
1677270d-8b23-415d-9935-890e6e4ea44e | 2.006A | 15 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
168a350e-cc9a-4b57-aafd-4f16ea3e9949 | 7.002A | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
16ccc58d-9caf-4270-bd09-fde55d8bcbba | 17.002 | 3rd party structure touching or surrounding SCE structure (Notification Required) | CUST CLEARNC PUBLIC STLTPOLE | 0IZW | public-level | Streetlight Only Pole - Steel | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
1719df79-e131-4dcf-b85f-6aa35801af7d | 18.001 | Animal nests with potential to contact energized components or interfere with equipment operation (Notification Required) | REMV ANIMNST SEC STLTPOLE | 0IZU | public-level | Streetlight Only Pole - Concrete | 2022-03-08 06:04 |  |  | A remove animal nest Problem Statement does not exist at the public level. If this condition exist in the field, then select secondary. |  | ED_SL
172cc887-4232-4f78-96fa-1c8b64a7cc7e | 2.004A | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
17424e96-bc35-4cd7-93f8-f184a7697244 | 2.003B | Crossarm bowed approximately >5 inches without splintering (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
17857f45-1241-4dc2-b8fa-fe79568600fc | 8.001 | Metal debris in conductors (Notification Required) | REMV UNATH ATT PRI CBL/CND POLE | CWG2 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if there are metal and/or non-metal foreign objects in the primary conductors/phases/taps/equipment.• Select “No abnormal conditions” if no foreign objects are in primary. | Create notification based on severity of debris in conductors. (Ex. Extreme condition should result in P1 notification). | ED_POLE
17963b6c-f093-4176-aaeb-beb083876cc4 | 7.002A | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
17c838c8-08c9-44ac-a708-210be102325e | 3.002 | In contact with animal nest (Notification Required) | REMV ANIMNST PRI POLE | C0I7 | primary-level | ED_POLE | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
17d4e779-4625-4f6f-aa2c-23a2ecc486c5 | 12.004 | Cracked, damaged, deflected, frayed or loose (Notification Required) | REPLC DAMAGE PRI GUY POLE | 989A | primary-level | Span Guys | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | EZ_POLE
183d29d7-3fca-4411-9e2f-92a7df6a8b96 | 2.005B | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
19296b44-e9a9-48d3-91e8-2c345ad65b39 | 7.006 | Damaged bonding wire under crossarm for 12kV and higher (Notification Required only if crossarm does not require replacement) | REPLC DAMAGE PRI BOND POLE | 799A | primary-level | Crossarms - Composite | 2022-03-08 06:03 |  |  | If the crossarm is damaged and requires a notification, changing the cross arm will remediate the bonding issue | If the crossarm does not need to be replaced and the bonding wire is missing or damaged use one of the above listed bond problem statements: REPLC DAMAGE PRI XARM POLE, REPLC MISSING PRI BOND POLE, REPLC DAMAGE PRI BOND POLE | EZ_POLE
192a1c7d-a607-4039-bdca-d608e4eb7310 | 1.012 | Exterior damage approximately >2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
196503f5-5458-485f-81cf-fb4713048495 | 7.002B | Bent mounting bracket and associated hardware (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
19bb256e-9512-41a1-bf32-392db56ccd7d | 2.007A | 3 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
19eb1273-c1c1-4b91-b66b-2d379012808f | 2.003A | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
19f98fb7-db06-49fe-8b63-54389b5df2b0 | 8.015 | Dead-end cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | 983A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | EZ_POLE
1a25c875-8291-4e4c-97d0-7a500672dee4 | 2.003D | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
1aa5a80f-56cc-471e-99a9-56a4ba495f4f | 6.003 | Insulator floating (Notification Required) | REPLC FLOTR/SQTR PRI INSLTR POLE | 827A | primary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
1ae8f216-f274-4ca9-835c-937096794154 | 2.003D | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
1b128342-c0e7-4422-acc1-b9623180930d | 2.007A | 5 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
1b346201-aa95-4eb1-8b91-69e3b60a340d | 2.005B | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
1cc708e5-912d-4b75-ad5e-92044c93b95c | 9.003 | Tree condition causing significant strain and/or visible abrasion damage - either open wire or Triplex (Notification Required) | TRIM VEG TREE SEC CBL/CND POLE | CWK4 | secondary-level | Conductors - Secondary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable conductor clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
1ceffb5a-40eb-4b48-872a-568a2c118c3f | 14.003 | Riser broken (Notification Required) | REPLC DAMAGE PUBLIC RISER POLE | 713A | public-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | EZ_POLE
1d0d2fda-4c20-4c9f-81ce-373ad2ddb934 | 6.003 | Insulator squatting (Notification Required) | REPLC FLOTR/SQTR PRI INSLTR POLE | 827A | primary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
1d365559-24be-4a7b-b678-4845d210e5ec | 2.003A | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
1d47786c-900e-45dd-bcd8-be729a5d9729 | 6.003 | Insulator cracked, damaged or loose (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
1db81d59-266b-419d-b17b-0be5832312a7 | 2.004A | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count all crossarms at this level that are canted. | Create notification and prioritize based on severity of issue. | EZ_POLE
1dc43272-ccbb-433d-83e8-e30d0586062e | 13.001B | Yes (Notification Required) | REPAIR CLEARNC PRI GUY POLE | CHF2 | primary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if guy wire(s) have contacted or will contact energized conductors. | Create notification based on severity of issue. | ED_POLE
1dc5995e-eb89-47e8-a9c2-4379fe20cbab | 1.009 | Animal nests with potential to contact energized components or interfere with equipment operation (Notification Required) |  |  | public-level | Poles - Wood | 2022-03-08 06:04 |  |  | Since this answer applies to all levels the ESI must select from the above problem statements based on the location of the animal nest. |  | EZ_POLE |  | [{"problemCode":"343A","problemStatement":"REMV ANIMNST PRI POLE"},{"problemCode":"355A","problemStatement":"REMV ANIMNST SEC POLE"}]
1dda84bf-1864-493c-8a39-b2d8b993c9a2 | 1.002 | Exterior damage approximately >2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | communication-level | ED_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
1ddb86b8-a5d8-41e5-8496-16cc20792a9b | 2.006A | 3 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
1deefd41-88b0-488b-b851-a22c2c87c40d | 2.005B | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
1e55b66e-f948-4e5b-8568-aa0bef897738 | 2.004A | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
1e5a85fc-dc7b-4707-9a00-19323f035e97 | 3.002 | Blown fuse (Notification Required) | REPLC DAMAGE PRI CUT/FUS POLE | 718A | primary-level | Cutout/Fuse | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
1e6afdd4-5ff1-488e-9197-f37e23b91ab6 | 8.015 | Lightning arrestor cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | CDC0 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | ED_POLE
1e7d0e98-ad03-4ec8-8a33-694b9b331ddb | 12.002 | SCE energized components (Notification Required) | REPAIR CLEARNC PRI GUY POLE | CHF2 | primary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if span guy has the appropriate amount of clearance per GO-95 or could potentially contact the listed options.• Select “No abnormal condition” if span guys have appropriate clearance. | Create notification based on severity of issue. | ED_POLE
1e9e39a0-dc55-4211-a149-b0ad579f3ac4 | 14.003 | Cables in Riser exposed (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | secondary-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
1ef8c433-9988-41e0-92bc-5e763155285b | 2.007A | 1 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
1f22d74e-23e9-42c9-825f-8826a2f19ecb | 2.005B | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
1f5a35c3-74ca-4f4e-814e-1a0fe2c1a8ed | 1.002 | Exterior damage approximately >2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | communication-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
1fad5f45-2910-486a-8680-de5c1e995fe6 | 2.006A | 13 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
1fb78884-1a0f-4017-b9b5-56b41dc4e89b | 2.004A | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
20139287-95df-4e84-9060-79e6fae463ef | 8.002B | Less than 6 feet radially between conductor and non-climbable pole (e.g. streetlight) (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable energized conductor- structure clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
202c271e-a154-46ae-99c6-ea6999ccdf8a | 7.004A | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
2034c031-1741-4abc-8951-4ef17c85489c | 7.002A | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
20449a58-1301-45cb-8164-0aa466a470f6 | 3.002 | Secondary leads in contact with the case (Notification Required) | REPAIR CLEARNC PRI XFMR-D | D0F2 | primary-level | ED_XFMR | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
205ee4ce-e355-44bb-af83-47db886c8a26 | 8.002A | Vines, branches or foliage presenting an overhang or other imminent threat (Notification Required) | TRIM VEG TREE PRI CBL/CND POLE | 046B | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed vegetation clearance issues are present in the primary conductors/phases/taps/equipment.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
20720f0d-3db6-4ba1-a602-af2eb08f3f93 | 2.004A | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
20c57e47-4460-4ec8-8e92-e2b5a2391cbe | 14.004 | Damage/Discoloration (Notification Required) | REPLC DAMAGE PRI TERM POLE | 778A | primary-level | Risers/Terminations | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
21361685-ee72-4d36-9ba4-2786f7c72d85 | 2.006A | 6 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
21aa595e-1a77-44d4-844b-e2a2194abcb8 | 14.002 | Pothead leaking (Notification Required) | REPLC LEAKING PRI TERM POLE | C545 | primary-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
21bf9f61-3944-4cf0-9e51-70e20dc709ca | 14.003 | Riser swollen (Notification Required) | REPLC DAMAGE PUBLIC RISER POLE | 713A | public-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | EZ_POLE
22784845-d810-4c3e-87e1-2b321b18da41 | 2.006B | Braces missing (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | CDC0 | primary-level | Crossarm - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
2284e98c-1f8e-45dc-a40b-1952ad355500 | 2.003D | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
22d665c1-4a8b-4100-9df9-ece0096f8ba2 | 2.007A | 6 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
22d85d0b-2d7b-48eb-9ea5-4d45496b2302 | 2.007A | 13 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
232e624d-37e8-413f-8385-142eb334ea57 | 7.002A | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
2339bfe4-637e-42bb-a297-1ec78c609b4e | 2.007A | 12 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
23701c4a-dd6e-4566-876b-3723e57f70ed | 7.004A | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
24424a00-8ffd-4b7b-9969-bcf76a2c8815 | 2.005B | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
24598ae8-a850-41a1-ae20-c86e99a523c4 | 2.005B | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
248ea584-fec0-469b-a3d5-194cfda4f2da | 5.005 | Switch (Notification Required) | REMV ANIMNST PUBLIC POLE | C0T5 | public-level | Poles - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | ED_POLE
24a319a8-fe0e-4e18-aa1e-9d82eca40056 | 2.003C | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
24d47cb1-1661-45aa-a5d4-9c18ef35ebf5 | 0.029 | Broken or separated messenger wire (Notification Required) | CIP CLEARNC COMM POLE | 0I5G | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
24fd9eea-3a20-4b49-ae59-ba229b1f2d19 | 7.002A | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
2541e34e-f974-49b1-9d98-a3c4e037349a | 8.016 | Slack primary conductor (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there is a possibility of primary conductors/phases clashing and/or public can contact.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearances. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
25730c09-7fee-4aa7-9c21-9034dbd64913 | 2.006B | Braces loose (Notification Required) | REPLC LOOSE PRI HWARE/FR POLE | CDI1 | primary-level | Crossarm - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
258a77a4-92a3-4480-a445-644371a35bd1 | 9.003 | Vines, branches, or foliage presenting an overhang or other imminent threat * (Notification Required) | TRIM VEG TREE SEC CBL/CND STLTPOLE | 481B | secondary-level | Conductors - Secondary | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
259549fc-76fa-4a90-ae70-cca9e560d46a | 2.007A | 15 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
2595a839-5658-4d00-88c0-2874275a87be | 2.003D | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
25af858e-dc0d-4555-af19-811f23b66632 | 0.026C | No | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if rolling and transposing conductor has at least 12” of clearance between primary conductors/phases. | Create notification if primary conductor clearance is <12”. | EZ_POLE
25fc4424-6563-4072-b0b3-db0f523ec048 | 0.026B | Yes and clearance between conductors appears to be less than 12 inches (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:05 |  |  | Identify if rolling and transposing conductor has at least 12” of clearance between primary conductors/phases. | Create notification if primary conductor clearance is <12”. | EZ_POLE
2640e2a7-9f9a-4e72-8fe2-5ca80c949e9f | 7.004A | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
266eec40-07c0-485d-8f1e-d3317f932ab1 | 17.004 | Pole leaning - public hazard (Notification Required) | REPLC LEANING PUBLIC STLTPOLE | 478B | public-level | Streetlight Only Poles - Steel | 2022-03-08 06:03 |  |  |  |  | ED_SL
26b478cc-cdb8-4cd3-95bd-0eb327a71b2a | 2.007A | 5 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
26b68457-d195-415b-8fde-4296841ddabc | 3.003 | Rust or corrosion compromising equipment integrity (Notification Required) | REPLC CORR PRI XFMR-D | D0J1 | primary-level | ED_XFMR | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
27589349-24af-4b1d-b62b-6719ae2f6619 | 13.001A | Anchor rods broken corroded, pole not leaning (Notification Required) | REPLC DAMAGE PUBLIC ANCHOR POLE | COP6 | public-level | Down Guys | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_POLE
275da94f-06a9-481a-beb7-b131c93a3854 | 2.003A | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
279d440d-0bf9-42ad-9d00-3c2afba90064 | 7.002A | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
27bb7b13-ec84-4cb0-acca-1f756923ef25 | 2.007A | 16 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
282b7cb4-09a9-4c78-8cd7-563cbf18fe32 | 10.007 | Animal guards damaged (Notification Required only for Primary Level) | REPLC DAMAGE PRI AVIPROT POLE | 0IZA | primary-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
283072d5-32bc-433e-a719-a85f7c7063fd | 2.003A | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
283da44c-bfdd-4de4-80ee-3229436afa40 | 14.003 | Riser broken (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | secondary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
28875d17-826c-4f5a-97d9-dc0723f53533 | 2.007A | 2 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
28b9fded-054f-4059-9e48-33149e8326ad | 5.005 | Crossarm (Potential Notification Required) | REMV ANIMNST PUBLIC POLE | C0T5 | public-level | Poles - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | ED_POLE
298bd03c-4459-44f0-bb30-a08eb6a0ca1c | 2.005B | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
29b5f9ef-7a5e-40fb-82ef-9e2803782af8 | 2.003C | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
29ea1e9e-1973-4488-94c5-8a6c0a7248d7 | 7.002A | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
2a006a4c-0686-44ba-a2ed-f66c624bb686 | 7.004A | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
2a01dfe2-5e62-4c09-9e4d-1bf71276a0ed | 1.007 | Pole leaning more than 1 foot per 10 feet of pole height (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Poles - Wood | 2022-03-08 06:03 |  |  | Identify if/how much the pole is leaning.• Select “pole is not leaning” if pole is not showing sins of leaning. | Create notification based on severity of issue. | ED_SL
2a1dff12-cb9e-4609-b536-3cbe91090301 | 11.005 | Mastarm or mounting hardware corroded, missing, broken, loose or bending (Notification Required) | REPLC DAMAGE SEC MASTARM STLTPOLE | 490B | secondary-level | Streetlight | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
2a639372-4d46-412a-872e-4e294a19e7cd | 2.003C | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
2a92d88a-3222-45a6-9866-48281babb39d | 2.005B | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
2b14facb-a86c-48d6-adcb-0f3ba5c8b717 | 2.003A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
2b32d10f-e2aa-45c8-9454-d7c46f0351aa | 2.004A | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
2b35856c-7d82-4e9f-81a2-ebf320674e5f | 3.002 | In contact with animal nest (Notification Required) | REMV ANIMNST PRI POLE | 343A | primary-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
2b5f5d05-2ed7-4010-abd0-423857b4b521 | 8.01 | Yes (Notification Required) | REPLC DAMAGE PRI CBL/CND POLE | 760A | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there are any signs of damage or tracking to covered conductor at insulators and spans. | Create notification based on severity of issue. | EZ_POLE
2b86460d-ed72-4518-aa1d-88f56396fb57 | 0.016 | Between 2 feet and 6 feet (Notification Required) | TRIM VEG TREE PRI CBL/CND POLE | CWF4 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Select option that best represents primary line clearance from trees/foliage. | Create notification if <6’ and based on severity. | ED_POLE
2bae5847-5e27-49ff-bf61-d1a3f84a846f | 1.002 | Three or more holes approximately >2 inch diameter, within approximately 18 inches vertical of a through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | communication-level | EZ_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
2be3506b-d774-46a8-9df8-99adbdb0faeb | 2.005B | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
2c277c9e-0db0-4872-95b7-c0d92b5fdc7e | 7.004A | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
2c6f2922-bbd5-4eb6-a95c-29731f893ce3 | 2.004A | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
2ccec652-9cec-4bce-a6b5-49721b21e645 | 1.002 | Exterior damage approximately 1–2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | secondary-level | Streetlight Only Pole - Wood | 2022-03-08 06:04 |  |  | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_SL
2d21e1ca-ee69-4574-adde-4ebe4620f88d | 2.003B | Crossarm bowed approximately >5 inches & splintering (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
2d6a422e-91c3-4639-a983-c87bbdbb9a3d | 2.003C | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
2d96a376-2d92-4825-a700-33a7438d6786 | 2.004A | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
2dc2d712-727f-4cf6-ac44-a30fa1a35dbf | 2.007A | 2 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
2dc2e002-4b44-4df0-aa1c-9ba663197225 | 2.006A | 4 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
2df13052-1b2e-4144-a60e-b2ca447f6495 | 2.004A | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
2e4e17e0-e1f8-434e-bfdd-617e024fcd0a | 2.004A | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
2e67fe01-4208-43a4-a13a-9ee6399d2806 | 13.001A | Anchor rods broken corroded, pole leaning, public hazard (Notification Required) | REPLC DAMAGE PUBLIC ANCHOR POLE | COP6 | public-level | Down Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_POLE
2e713800-5353-4317-812f-100d27ed8135 | 2.003A | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
2eb16984-191b-448c-a1de-77558fb0bad0 | 7.002A | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
2ed0fec8-b0cb-49f6-8ea2-6ef59fc409fd | 2.006A | 4 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
2f366bf8-7304-4fed-a90c-1078f9151e99 | 2.004A | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
2f5d61c8-a3f8-4c8f-bf4d-e76485705533 | 7.002A | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
2f72b27b-69bc-49d3-86e6-1b304071041d | 2.004A | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
2f991bfc-2c4f-45c7-b59d-0ac73415a56d | 7.004A | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
2fb236cf-4c73-4131-8526-db15509c755e | 9.003 | Bare conductors and through tree (Notification Required) | TRIM VEG TREE SEC CBL/CND STLTPOLE | 481B | secondary-level | Conductors - Secondary | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
2fe21136-5035-4818-ab56-91c98756571d | 2.004A | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
30a00846-e786-4c56-8c3b-c0a75b75ecbd | 2.004A | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
30bb3a70-cd0e-4ff3-9d9a-ca28a35a901e | 2.003C | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
30eede69-599e-4027-82cc-f5bd63533a3b | 2.007A | 11 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
30f1c18f-4111-4aba-b641-537dd41741c2 | 7.002A | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
3106baa5-bce3-4f5c-8d74-2f9a38eb14ce | 2.005B | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
318f42ed-371a-4427-b298-078b6cfe5c0d | 13.001A | Anchor rods broken corroded, pole leaning, public hazard (Notification Required) | REPLC DAMAGE PUBLIC ANCHOR POLE | 768A | public-level | Down Guys | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | EZ_POLE
3191bbfe-b078-4999-abd0-b8774e9690b4 | 8.016 | Encroachment primary conductor with span/down guy (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there is a possibility of primary conductors/phases clashing and/or public can contact.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearances. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
31d6c97f-4060-460d-b822-5f2d4ad7c1b0 | 2.006A | 1 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
327ed85d-9301-4668-8997-212c842b750c | 2.003A | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
32defcde-7a21-4da7-9108-9f33e1c28144 | 2.007A | 14 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
334276fb-eeba-487f-bd98-9e66f06636d1 | 7.004A | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
3388f528-5264-46fa-b03b-a517e9ac8912 | 2.003C | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
338fabeb-e5bc-4149-b411-afb3855bff25 | 2.006B | Braces missing (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | 983A | primary-level | Crossarm - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
33c7a5f2-396b-4b07-b065-1ddbb2aade15 | 9.012 | Foreign objects (Notification Required) | REMV UNATH ATT SEC CBL/CND POLE | 282A | secondary-level | Conductors - Secondary | 2022-03-08 06:03 | 2021-12-23 17:45 | 2021-12-23 17:45 |  |  | EZ_POLE
33cfdff8-6745-42f4-aacb-895b8cfbb790 | 2.004A | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
33f532c7-3b83-4890-b645-349104406e69 | 2.007A | 20 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
34116bba-72cf-4048-9d22-77177f50fd0f | 5.001 | Pole embedded on soil/heavy ponding (water) (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
341d57f5-6c70-40e1-bd7a-2f2f6219ecf0 | 2.003C | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
34302967-324b-4a1c-92fb-e54576ed8cd7 | 2.005B | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
3450786f-0143-4151-afb2-560f1a860d49 | 11.004 | Corroded, missing, broken or bending hardware (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Hardware/Framing | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | EZ_POLE
3485eab8-e4bd-4164-a866-e666e143a362 | 1.002 | Exterior damage approximately 1–2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | communication-level | ED_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
348c62c7-60e6-4bd9-bf32-68901dc52a56 | 7.002A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
349003a7-1df4-41b9-9300-ae90014615a1 | 7.004A | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
34967d52-2f84-468b-9867-093cd715016e | 2.003D | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
34d668db-8168-4c34-98c6-6bbb93ce5d6d | 2.003C | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
35537e3e-2970-4391-9e2d-35bf3723c39e | 1.004 | Evidence of soil erosion around base of pole (Notification Required) | REPAIR DAMAGE PUBLIC POLE | 660A | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any listed conditions exist at base of pole.• Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | EZ_POLE
355c3985-0952-4bf2-a03c-8bc0c1b93639 | 2.005B | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
3598e0e3-96ff-41a7-99bc-6e71ede69488 | 5.005 | Crossarm (Potential Notification Required) | REMV ANIMNST PUBLIC POLE | 361A | public-level | Poles - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | EZ_POLE
35ee52e8-094a-4b20-b9d9-846dfb371713 | 7.004A | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
3601c8eb-b483-4d57-a2de-bc95a5bc7188 | 2.007A | 3 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
36217530-121a-4979-8ff4-0d0e8a33357c | 2.003D | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
363902d4-43b9-40d1-9de6-47e487cfdf3e | 1.008 | Recloser (Notification Required) | REMV ANIMNST PUBLIC POLE | 361A | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | EZ_POLE
36439960-3651-4892-babd-406130f85196 | 2.003D | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
367d39a2-09bf-48e6-a5fd-1781aaffb93b | 8.01 | Yes (Notification Required) | REPLC DAMAGE PRI CBL/CND POLE | CWE8 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there are any signs of damage or tracking to covered conductor at insulators and spans. | Create notification based on severity of issue. | ED_POLE
36aef03b-b9e4-42c2-aed3-82a13f8f136e | 8.002B | Conductor NOT located above building, but is vertically is less than 12 feet from top surface of building (commonly roof) (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable energized conductor- structure clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
36e2ff3a-0c7d-45f4-b361-09ebac3c3b12 | 2.003D | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
36faaaaa-0c0a-4ec9-b801-fc6f66095107 | 7.002A | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
3746e02c-d344-4675-b0f2-f2f995a1d239 | 6.003 | Insulator broken (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
37543b26-221d-489b-9fb8-be24e32507cf | 2.004A | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
37812768-88ba-4df0-84d0-96f27c350f10 | 2.004A | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
37cdba3f-1d98-48d2-8c8e-cac3e814ad6b | 13.001A | Anchor rods missing, pole not leaning (Notification Required) | REPLC MISSING PUBLIC ANCHOR POLE | COB1 | public-level | Down Guys | 2022-03-08 06:03 | 2021-12-22 03:27 | 2021-12-22 03:27 |  | Create notification based on severity of issue. | ED_POLE
37e91c2a-f359-47bd-a0d7-99d907f30502 | 2.006A | 19 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:05 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
3850249a-c0b2-4b10-a4ae-db4663b56a42 | 2.003A | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
3870f9fc-e519-4abd-a541-13e1ae59e9c1 | 2.003A | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
387a1b67-c970-469d-bb8f-9db7af148331 | 2.006A | 13 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
389d9297-1cf1-41d3-930a-f9c8194d550d | 2.003A | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
38db14ea-e74a-4aa1-a848-1b43be322621 | 14.003 | Cables in Riser exposed (Notification Required) | REPLC DAMAGE SEC RISER POLE | 735A | secondary-level | Risers/Terminations | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | EZ_POLE
38dff363-458f-4ff1-9d01-f260964c2458 | 8.002B | Conductor NOT located above building, but is vertically is less than 12 feet from top surface of building (commonly roof) (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable energized conductor- structure clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
390928b8-871c-4f0f-9d89-88fc9900e282 | 2.005B | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
392d28ce-0928-4cd2-88bb-7c458a93c050 | 2.007A | 10 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
3999373e-c7ca-44d5-8ce6-aeb2f22dd4d1 | 12.004 | Cracked, damaged, deflected, frayed or loose (Notification Required) | REPLC DAMAGE PRI GUY POLE | CHE8 | primary-level | Span Guys | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_POLE
39d579a7-4b7b-415d-af8d-5cf369c35d66 | 6.003 | Insulator chipped (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
3a12bf2a-0df6-4110-933f-bbef46b49f8c | 6.003 | Insulator cracked, damaged or loose (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
3a259163-a141-4543-a711-b1451e187366 | 7.004A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
3aac57e3-dc96-4564-82d2-647cdb59f1b4 | 0.024 | Unauthorized Attachment (Notification Required) |  |  | public-level | Poles - Wood | 2022-03-08 06:04 |  |  | CUST CLEARNC PUBLIC POLE Priority 2 only –If owner is known. REMV UNATH ATT PUBLIC POLE Priority 3 – If unable to identify owner |  | ED_POLE |  | [{"problemCode":"0IJD","problemStatement":"CUST CLEARNC PUBLIC POLE"},{"problemCode":"RB03","problemStatement":"REMV UNATH ATT PUBLIC POLE"}]
3ab2d55a-b8f1-4e9e-8991-b8b86a0e4fcf | 8.016 | Encroachment bare secondary conductor with span/down guy (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there is a possibility of primary conductors/phases clashing and/or public can contact.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearances. (Ex. Extreme condition should result in P1 notification). | ED_POLE
3ab44985-094f-493b-b4e2-f40815d763f2 | 7.002A | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
3b2e9e0c-14a9-4357-b4e5-7b0c12b91218 | 0.024 | 3rd party structure touching or surrounding SCE structure (Notification Required) | CUST CLEARNC PUBLIC POLE | 0IJD | public-level | Poles - Wood | 2022-03-08 06:04 |  |  | Identify if any of the listed defects are present on or around the structure.• Select “No abnormal condition” if no listed condition options are present. | Create notification if condition type is severe and warranted. | ED_POLE
3b634479-61c7-448d-96d4-f442f3102e7f | 2.003D | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:05 |  |  |  |  | ED_POLE
3b776d9f-8a67-4079-be04-2b7640d2944d | 2.005B | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
3b957639-7ced-4ac7-ba79-1c434eafc02a | 1.002 | Three or more holes approximately >2 inch diameter, within approximately 18 inches vertical of a through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | secondary-level | EZ_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
3bbe8f3d-c579-4192-a16f-d30fe8042afc | 7.002A | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
3bc887d0-1298-477c-8c3a-37924e82703a | 7.004A | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
3bd89865-3f85-408f-9b83-b6c326ce62f9 | 2.003A | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
3bf58e1f-a0da-4d2f-9977-20e6ec6da49c | 2.003C | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
3c0d952b-e5c1-4117-a0b3-66abc2cea87f | 2.005B | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
3c144ad2-b68c-4897-b43f-c5eeee56d6c2 | 2.003B | Crossarm bowed approximately >5 inches without splintering (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
3c223b37-a8d3-40f4-ba14-7d3bf58c490c | 2.003C | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
3c5e0f36-fcc2-4edb-8a25-544e8715717f | 2.003A | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
3ca80b0b-e4ab-4240-bd55-3c8cb6427df9 | 12.002 | SCE energized components (Notification Required) | REPAIR CLEARNC PRI GUY POLE | 612A | primary-level | Span Guys | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if span guy has the appropriate amount of clearance per GO-95 or could potentially contact the listed options.• Select “No abnormal condition” if span guys have appropriate clearance. | Create notification based on severity of issue. | EZ_POLE
3d465fac-8d52-4392-a8c5-efa7e6d28552 | 2.003D | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
3d5ab073-0a47-44ae-b9ca-4e8cf95e2c87 | 2.007A | 5 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
3dcae349-9ca3-48ab-9cca-fb66d1140662 | 7.004A | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
3e0ff2e7-67be-4c0e-a165-6ae156a81777 | 14.003 | In contact with animal nest (Notification Required) | REMV ANIMNST SEC POLE | 355A | secondary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | EZ_POLE
3e117ca3-5bc6-486b-8bdb-264f30485199 | 11.004 | Damaged equipment brackets or braces (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Hardware/Framing | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | EZ_POLE
3e126b6d-5a5e-4ba7-8e03-858c9ce0ad77 | 0.029 | Excessive sag of communication cables (Notification Required) | CIP CLEARNC COMM POLE | 0IAG | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
3e30511a-b31b-4deb-b2ba-4ff4e3992ad6 | 2.006A | 6 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:05 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
3e3f58b0-8cbb-4a25-9718-b70d8d7fb2a0 | 2.003A | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
3ee710cf-45a5-4092-ab22-94d651aff0d9 | 14.003 | Riser swollen (Notification Required) | REPLC DAMAGE PUBLIC RISER POLE | CIP6 | public-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_POLE
3efaf2a4-327b-46b8-87f0-2028b8c2e05e | 7.002A | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
3f393dc1-3334-4d31-893a-08a9786720cb | 2.003A | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
3f57f70d-29a2-41e8-a229-4066b786dc48 | 2.003A | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
3f737ff4-bba5-4d0f-a87b-e596b444a5b2 | 14.002 | Pothead swollen (Notification Required) | REPLC DAMAGE PRI TERM POLE | 778A | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
3fbc2201-68b3-4919-a602-0bb8fd089fa2 | 0.024 | 3rd party structure touching or surrounding SCE structure (Notification Required) | CUST CLEARNC PUBLIC POLE | 0IF2 | public-level | Poles - Wood | 2022-03-08 06:04 |  |  | Identify if any of the listed defects are present on or around the structure.• Select “No abnormal condition” if no listed condition options are present. | Create notification if condition type is severe and warranted. | EZ_POLE
3fd8ac0b-24ca-49cd-81a8-0fdcef9497f2 | 14.004 | Damage/Discoloration (Notification Required) | REPLC DAMAGE PRI TERM POLE | CSE8 | primary-level | Risers/Terminations | 2022-03-08 06:03 |  |  |  |  | ED_POLE
40209d12-ea56-4994-95c9-31eed87a586d | 2.004A | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
41047b67-c095-43d8-993a-330c3431cf38 | 6.003 | Tie wire broken/missing/damaged or loose (Notification Required) | REPLC LOOSE SEC INSLTR POLE | CFL5 | secondary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
4106d486-6044-485f-8cdf-03bbd46d35a9 | 2.003D | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
410b4bc5-7268-43b1-bd34-06f8b536879a | 2.003C | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
41b33cf6-245c-4887-89ae-b6319d932c73 | 5.005 | Recloser (Notification Required) | REMV ANIMNST PUBLIC POLE | C0T5 | public-level | Poles - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | ED_POLE
41cf6365-2c01-41e9-a5cc-bab7012a3eb2 | 2.005B | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking.• Select “0” if no crossarms are tracking at this level. NOTE: Notification required if answer is greater than 0. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
41d66f9e-09b5-4079-93dc-7f57936fe3b3 | 2.003C | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
42650f3e-3525-4f87-b0d7-13fc079f2bb0 | 2.003C | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
431f6460-22a3-4019-b0fb-8f520f26c69e | 2.007A | 1 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
434b1783-43f5-4b6e-8b3e-5bbeb5e42247 | 2.003D | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
43a40ff3-e09d-4ad5-8831-e4dd1d88095d | 2.006B | Braces broken (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
43e87ddd-de04-4ec2-8120-e8a2b1cbba06 | 2.004A | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
43f58eaf-9ac8-482f-aa9a-0b1f1a2119f2 | 0.005A | No (Notification Required) | null | E2 | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | You have indicated that the pole number does not match, please create a corresponding E2 notification. | Make appropriate corrections in the field – replace pole number and/or map correction. | EZ_POLE
4402aa3c-8385-4024-b2a5-47ca594cf1ca | 7.004A | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
4408164e-4c50-4821-bbba-acee0ac18b21 | 14.002 | Pothead sparking, arcing, or noisy during normal ‘dry’ weather conditions (Notification Required) | REPLC DAMAGE PRI TERM POLE | CSE8 | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
441148e9-5e55-4e87-b0e7-d1919b6429aa | 11.004 | Corroded, missing, broken or bending hardware (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Hardware/Framing | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | EZ_POLE
4449bdae-0eae-4fdd-8a25-e0381d1aebb9 | 14.003 | Riser broken (Notification Required) | REPLC DAMAGE PUBLIC RISER POLE | CIP6 | public-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_POLE
445c8a52-cd53-4e59-bd17-b81437981abc | 6.003 | Improper angle on pin insulator (Notification Required) | REPAIR DAMAGE SEC INSLTR POLE | 627A | secondary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
4472ebe2-2f26-4565-bb48-6b3744dfc50a | 2.003C | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
44ec144b-e7dc-45e4-a9ca-19fc5005b54a | 7.004A | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
44f9685d-7524-4427-96a6-22e878c3ab8d | 2.005B | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4533cd93-84b6-489f-8034-ec9b5b2faaae | 13.001A | Anchor rods broken corroded, pole not leaning (Notification Required) | REPLC DAMAGE PUBLIC ANCHOR POLE | 768A | public-level | Down Guys | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | EZ_POLE
45a9ebec-0d6e-4855-b2a8-2c41d4c5ced5 | 2.003A | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
45e19927-d092-4a37-af57-7bd5490a2fee | 9.012 | Conductor has less than appropriate radial clearance with potential for contact, no public safety hazard (Notification Required) | REPAIR CLEARNC SEC CBL/CND POLE | 482A | secondary-level | Conductors - Secondary | 2022-03-08 06:04 | 2021-12-23 17:45 | 2021-12-23 17:45 |  |  | EZ_POLE
45ff3435-b139-4a49-adc6-a20d1eed08e3 | 2.003B | Crossarm bowed approximately >5 inches & splintering (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4667b9c3-f40b-4da2-b9b8-6f6dff5452a8 | 2.003D | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
46a53990-a60f-4551-9952-3d47dd63728c | 2.003A | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
470fc673-62f7-4f7b-a7e4-694805d64132 | 2.004A | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
477fefb3-50ea-4f55-8d1b-3385ac052fa1 | 2.004A | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4782b088-4596-476c-9c62-8e6b5a5cd06b | 2.003C | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
47be93d8-05dd-4c62-bce9-26c2f9259205 | 2.003D | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
480d44cc-7e08-4052-b44c-e3fb73d6cfda | 7.002A | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
48795929-5483-4622-85fa-8e5ce49312a3 | 7.004A | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
48a38f9c-7c5d-46b3-a268-cc30ee37bd81 | 7.004A | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
48ad5509-19f2-46d0-94a9-5fd59541ad0c | 2.005B | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
48f420c0-45bd-4ce1-8d71-70ae2fce3495 | 2.004A | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
491a1e43-3b2a-48cf-9e2f-de93570c6e3c | 10.006 | Yes (Notification Required) | TRIM VEG TREE COMM POLE | 060B | communication-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if vegetation is currently or will interfere with operation of primary equipment. | Create notification based on severity of issue. | EZ_POLE
49c1ae82-26a9-4de0-a9a8-ebb945c8e67a | 2.007A | 10 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
49e4cf7f-9901-485f-a468-c8c6b222ce4c | 2.007A | 6 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
4a025a1d-4861-4537-88ba-6bbbf39d582a | 2.005B | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  | Count all crossarms at this level that are tracking. | Create notification and prioritize based on severity of issue. | EZ_POLE
4a2ac364-7bd0-4429-ac6d-7425cf177dec | 6.003 | Insulator floating (Notification Required) | REPLC FLOTR/SQTR SEC INSLTR POLE | 826A | secondary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
4a599c7a-9599-4771-9199-7686ad0f1376 | 2.005B | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4a5cbfec-2d0c-4113-aa1e-60e48eafb686 | 11.007 | Streetlight brackets damaged (Notification Required) | REPAIR DAMAGE SEC STLTPOLE | 469B | secondary-level | Streetlight | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
4a6fa43a-5dd7-4876-b472-ad251f579ecf | 2.003A | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
4a7d4d57-c42d-438f-8fdb-5382caf1f5f7 | 7.002A | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4a8467fb-8050-4e47-a547-469cace15f9b | 0.029 | Loose lashing wires (Notification Required) | CIP LOOSE COMM CBL/CND POLE | 0IDG | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4aad5927-5e5c-4342-9b5c-bda7846d08a8 | 2.003A | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
4ab0e780-e580-46ee-bd3f-648ae601201b | 3.002 | One fuse is open/down (Notification Required) | REPLC DAMAGE PRI CUT/FUS POLE | CLE8 | primary-level | ED_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4b0210d8-1761-4f3a-8713-a07d9ab51860 | 2.003C | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:05 |  |  | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
4b5332ff-0c32-48a3-8569-32ff3753749c | 7.004A | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
4b60ba8c-c73d-45d7-8b6c-1e17f9a0b709 | 2.003C | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
4b6b390c-49e4-4458-af9a-2306695eef33 | 2.006A | 7 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4baaef53-e06b-4212-b24d-39ebfd7316ae | 2.004A | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4bcd59c4-5b96-4878-83d1-56cbf19afc07 | 2.003D | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
4bd04943-410b-4fec-a1e3-677e54c1052d | 2.004A | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4c03b4ee-99bd-4f76-8383-066c2546dfa1 | 2.003C | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
4c044178-2424-4e19-95e5-3a8b0b1b4303 | 2.003C | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
4cbe7e98-bd7f-4a9f-9cec-e49cfbf5ee49 | 2.006A | 11 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4ce7ddbb-6508-4b86-9505-c76a497336aa | 2.005B | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4d0861ff-c139-40c5-99d9-f803789a1516 | 7.002A | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4d0bb610-711f-49cb-a09e-2ee854c2e5c1 | 2.006A | 7 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4d40089c-dc49-45cb-9bff-3c222202225a | 6.003 | Insulator cracked, damaged or loose (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
4d4602d7-222e-4017-b367-c5d63b3b9645 | 2.004A | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4d8a9447-4121-4630-996e-75204e30e363 | 9.003 | Tree condition causing significant strain and/or visible abrasion damage - either open wire or Triplex (Notification Required) | TRIM VEG TREE SEC CBL/CND POLE | 044B | secondary-level | Conductors - Secondary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable conductor clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
4d9946ce-233d-4ea8-93e0-2029cc235581 | 7.002B | Significantly unbalanced due to tension (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4dc6cc5a-3b8c-439e-b6e1-e9340496e9c0 | 2.003D | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
4dfaae8d-3f89-425a-8c21-c502a94af833 | 9.004 | Conductors not in good condition, broken, missing (Notification Required) | REPLC DAMAGE SEC CBL/CND POLE | 763A | secondary-level | Conductors - Secondary | 2022-03-08 06:03 |  |  | Identify if energized conductors and/or tie wires are damaged.• Select “No abnormal condition” if no damage is observed. | Create notification based on severity of issue. | EZ_POLE
4e5581ab-10be-466b-be44-0d927607d72d | 2.007A | 10 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
4e6b7599-3d2c-4004-aebf-fe635b2148cf | 2.006A | 12 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4ea155f4-6d36-4af5-8983-ef546b705b32 | 1.002 | Hole approximately >2 inches near through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | secondary-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4ed79624-0471-4fcc-83f3-a0387b5f649d | 2.006B | Braces broken (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4eec9388-47ef-4d43-8a24-92d192edbe41 | 7.002B | Bent mounting bracket and associated hardware (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4ef1c1a1-9311-40e8-9208-c5482f327274 | 2.003A | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
4f0c3bec-312e-4efb-aa67-3206249fee07 | 2.004A | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4f2716a3-ddcd-49d7-b730-36083ccf1dbe | 2.003A | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:05 |  |  | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
4f2f4451-e8ac-45d3-86e7-2b804c9e2caa | 7.002A | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4f38f839-9751-426f-b01f-575ec0639362 | 7.002A | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4f406ebc-2a53-42a2-b388-0a662c44ac58 | 14.003 | Cables in Riser exposed (Notification Required) | REPLC DAMAGE PUBLIC RISER POLE | CIP6 | public-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_POLE
4f5e8894-80c4-40a2-ba56-792d93f0d172 | 2.003A | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
4f753b7b-f3af-491d-835e-268dc1a729fb | 2.005B | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
4fd9789a-e351-48c3-8fa6-dca376864760 | 2.005B | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
4fdaa8c0-50c9-4906-8ace-38f04e755d2f | 2.005B | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
50507e70-a06e-4d59-b706-935379bf079f | 0.020B | No (Notification Required) | REPAIR CLEARNC COMM POLE | 581A | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if the appropriate amount of climbing space per GO-95 is present on pole at this level. | Create notification if inadequate climbing space exist. | EZ_POLE
505de137-1219-4da6-9c58-1e33b7e27ff3 | 1.002 | Exterior damage approximately >2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | secondary-level | EZ_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
50b9caf4-70e4-4d6e-8141-4ba870b93c3f | 2.006A | 20 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:05 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
50c233ed-f600-4550-9ab3-768055b6a49f | 2.003C | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
50f6810f-9be6-4899-a669-442fa6d0e2e7 | 7.002A | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
512219ee-7ee9-4061-8daa-5386bc53ea92 | 13.002 | SCE non-energized electrical components (Notification Required) | REPAIR CLEARNC PUBLIC GUY POLE | CHQ0 | public-level | Down Guys | 2022-03-08 06:04 |  |  | Determine if down guys have the appropriate amount of clearance per GO-95 or could potentially contact the listed options. | Create notification based on severity of issue. | ED_POLE
5175d280-35e2-4aec-a8c2-424bba56bdb1 | 2.004A | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
51a79cfd-f0ef-40c5-b0f8-dc31859d9eb9 | 2.007A | 3 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
51a8b7c6-f410-4316-9897-efaa1e72508b | 14.003 | Cables in Riser exposed (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | public-level | Risers/Terminations | 2022-03-08 06:03 |  |  |  |  | ED_SL
51e007b0-a858-4ab0-a132-7227dfb78347 | 2.004A | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
520b40b3-17aa-4b63-ae08-7ac1c4bdc0b2 | 2.006A | 20 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
5259a95e-a08e-40dc-a106-43ef360333ef | 2.003C | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
52a9aecf-ab66-4a9c-93a4-851cd7e7ad57 | 9.012 | Foreign objects (Notification Required) | REMV UNATH ATT SEC CBL/CND STLTPOLE | 0IZT | secondary-level | Conductors - Secondary | 2022-03-08 06:03 | 2021-12-23 17:45 | 2021-12-23 17:45 |  |  | ED_SL
5316ef10-dc59-4b2c-b996-ae51fc7e2cac | 2.003C | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
5328377d-5da0-4f64-8239-9b490fcb395e | 1.008 | Crossarm (Potential Notification Required) | REMV ANIMNST PUBLIC POLE | C0T5 | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | ED_POLE
537609ea-5130-4f00-b9bb-12945c01e5d8 | 0.029 | Broken or separated messenger wire (Notification Required) | CIP CLEARNC COMM POLE | 0IAG | communication-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
5428c1bf-f54a-413f-97b4-2da366a07dfb | 7.004A | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
5456d708-7a60-4cfe-a17a-40ccd777b87b | 2.003A | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
547c94df-ef95-4c92-a6fa-f1f39c40e1e6 | 14.001 | Pothead swollen (Notification Required) | REPLC DAMAGE PRI TERM POLE | CSE8 | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
54f451d4-2d85-40cd-9724-e9aa4408e1c2 | 7.002B | Bent mounting bracket and associated hardware (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
557dd806-db81-4741-b76d-48497f08bd7d | 2.003D | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:05 |  |  |  |  | EZ_POLE
55ad733b-79e3-4559-9498-680fae54d400 | 2.006B | Braces broken (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
55d072ba-b6ab-4323-b013-806f86991c64 | 2.007A | 7 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
55ec6407-7573-43db-b84a-1506abf21bdc | 15.004 | Mid-span service clearance not maintained (Notification Required) | REPAIR CLEARNC SERV CBL/CND POLE | CWE2 | secondary-level | Service Drops | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed clearance impairments are present on pole.• Select “No abnormal conditions” if no clearance impairment is identified on pole. | Create notification based on severity of issue. | ED_POLE
571dea81-439c-47a3-8d10-d16087c9c166 | 14.002 | Pothead not properly attached to supporting structure (Notification Required) | REPLC DAMAGE PRI TERM POLE | CSE8 | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
5730e4a7-fd1e-4342-abf7-85bd047da31e | 2.003D | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
57f6d040-6f4f-4c05-b559-33d44cd9e338 | 2.003D | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:05 |  |  |  |  | ED_POLE
5848765e-43c0-4b60-b718-28dde9a1078d | 2.003D | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
587675cc-48f2-4cba-9e78-2cb301ffcda7 | 2.005B | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
58aff654-32fe-423a-9f81-c751276eac32 | 1.007 | Pole leaning more than 1 foot per 10 feet of pole height (Notification Required) | REPLC LEANING PUBLIC POLE | 923A | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if/how much the pole is leaning.• Select “pole is not leaning” if pole is not showing sins of leaning. | Create notification based on severity of issue. | EZ_POLE
593b0ed9-0658-460a-a595-2b658ad93269 | 7.004A | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
5989ec3c-8d2e-476f-b299-e1b0dbf30d4d | 2.007A | 11 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
59db1fc2-7ee1-4f23-8dc4-d901f1357ea3 | 7.004A | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
59e244a1-5be6-417c-9580-a9df9291ee09 | 2.003C | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
5a3fd28b-70d1-42ba-ac23-dbf88f31f9f7 | 13.001A | Guys missing, pole not leaning (Notification Required) | REPLC MISSING PUBLIC GUY POLE | CHB1 | public-level | Down Guys | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_POLE
5a4627a3-f709-4dce-b074-7e13f8a3b8cd | 4.003 | Yes (Notification Required) |  |  | primary-level | Overhead Capacitors | 2022-03-08 06:03 | 2021-12-22 03:27 | 2021-12-22 03:27 | Identify if any capacitor bank fusing is open and creating a single-phase condition. |  | ED_CAP |  | [{"problemCode":"ELE8","problemStatement":"REPLC DAMAGE PRI CUT/FUS CAP-D"},{"problemCode":"ELE9","problemStatement":"REPAIR DAMAGE PRI CUT/FUS CAP-D"},{"problemCode":"ELI1","problemStatement":"REPLC LOOSE PRI CUT/FUS CAP-D"},{"problemCode":"ELI2","problemStatement":"REPAIR LOOSE PRI CUT/FUS CAP-D"},{"problemCode":"ELJ1","problemStatement":"REPLC CORRODED PRI CUT/FUS CAP-D"},{"problemCode":"ELJ2","problemStatement":"REPAIR CORRODED PRI CUT/FUS CAP-D"}]
5af13d90-3933-4c5b-99d9-dd2e0e1b5a95 | 2.005B | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
5b090a42-f940-43e2-8794-71a3098458d7 | 2.003D | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
5b0ad644-cd6e-4b0a-8339-45911da29b1f | 2.006A | 11 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:05 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
5b309d5b-9599-4a9b-bf4f-4a47a3a9e7ee | 2.003A | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
5b369834-8255-4dc1-bc7e-3fa5fea356c9 | 1.002 | Exterior damage approximately 1–2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | secondary-level | ED_POLE | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
5b63e25e-c62b-435c-9e78-af5ae52261ad | 2.006A | 2 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
5b96e5ce-37f0-4103-acc1-582f6a6e4824 | 2.007A | 6 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
5b97314f-a1e3-4fe5-9816-89c83b730760 | 1.012 | Exterior damage approximately 1–2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | ED_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
5b9e6927-07f7-49c4-8a45-1b8b68b03e64 | 0.029 | Excessive bowing or bending of pole from potential overloading at communication attachment points (Notification Required) | CIP CLEARNC COMM POLE | 0IAG | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
5bdda136-eaa1-4aed-bf55-45fd22b1ed49 | 5.003 | Excessive lean (approximately 10% or more of the pole height), caused by erosion of soil at groundline (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Examine public level of pole for any of the listed issues. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
5c39482a-76aa-4045-a8f1-5be546727475 | 2.006A | 16 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
5c3b49cf-d679-4955-a6c4-4c24a5aaa27d | 8.002A | Vines, branches or foliage presenting an overhang or other imminent threat (Notification Required) | TRIM VEG TREE PRI CBL/CND POLE | CWF4 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed vegetation clearance issues are present in the primary conductors/phases/taps/equipment.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
5cd79759-2edb-4345-88ba-85db8b2f9a2b | 2.006A | 1 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
5dba069f-4eec-43dc-9b2a-2c6b7d7fe450 | 2.003C | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
5e7299e3-81e8-4f3f-ab0f-a7e1620664f2 | 13.006 | Buried anchor (Notification Required) | REPAIR CLEARNC PUBLIC ANCHOR POLE | 434A | public-level | Down Guys | 2022-03-08 06:04 | 2021-12-22 03:27 | 2021-12-22 03:27 |  |  | EZ_POLE
5ede7249-46b9-4774-a123-2af728af6289 | 5.001 | Fracture or buckling of exterior wall (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
5f232011-ce4d-4ce5-9a56-5b94281f11f9 | 2.003A | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
5f30151e-1c00-400f-a2aa-808a59155a1d | 2.003C | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
5f541909-6119-4474-9214-15be52a45f49 | 2.005B | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
5f77c63c-66ef-4b09-9590-691c8c707c1c | 2.004A | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
5fbaa20c-42d2-46b9-bb76-4c2126aae3f7 | 2.003D | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
5fc584ca-8b08-42f5-b199-a03e346fca6d | 6.005 | Yes (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Insulators | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if any insulator is connected to the crossarm/structure or insulator with a C-hook. | Create notification if any primary attachment is attached with C-hook. | EZ_POLE
5ff7fcaf-3062-44cb-b176-8cae0761eaf2 | 2.005B | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
600e6443-5623-49f7-9da1-8e540409f644 | 7.002A | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
605e58c7-f7d1-4e4b-8f68-6c3f1887ee9d | 2.003D | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
607d09b3-6447-4191-915a-1f5409ddc756 | 7.004A | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
60c59799-8464-4866-b7e7-fe34b73045aa | 14.003 | Non-Schedule 80 Riser installed (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | secondary-level | Risers/Terminations | 2022-03-08 06:04 | 2022-01-11 17:01 | 2022-01-11 17:01 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_SL
60cf581c-2626-48d8-b1e8-753c72112c7f | 2.003C | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
60e127a2-c244-43e9-b408-84e23f00fe6f | 7.002A | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
60e7f37e-dc9c-4844-94b9-4d51805bfaa2 | 2.004A | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
60f425bf-ef73-4248-931b-9189cc048e30 | 8.002A | Immediate danger concerning palm fronds falling or blowing into conductors (Notification Required) | TRIM VEG TREE PRI CBL/CND POLE | CWF4 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed vegetation clearance issues are present in the primary conductors/phases/taps/equipment.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
61116a64-a795-474c-ab67-b07b4c789acb | 2.003A | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
614aea5b-4511-4166-869d-b2dc1e2a3567 | 2.005B | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
6168111c-5052-4565-b4db-5a7eecffe921 | 18.002 | Unauthorized Attachment (Notification Required) | REMV UNATH ATT PUBLIC STLTPOLE | 542B | public-level | Streetlight Only Pole - Concrete | 2022-03-08 06:04 |  |  | A sign is not considered an unauthorized attachment on a steel streetlight pole. Therefore, a notification is not required. |  | ED_SL
619cacf5-6970-4714-b629-926390ff6ac5 | 7.002A | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
61a4b60b-1f41-4fed-9074-410d41b8bd0e | 7.002A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
62685257-a0cf-4661-a56d-21a2dae8f203 | 14.003 | Non-Schedule 80 Riser installed (Notification Required) | REPLC DAMAGE SEC RISER POLE | 735A | secondary-level | Risers/Terminations | 2022-03-08 06:04 | 2022-01-11 17:06 | 2022-01-11 17:06 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | EZ_POLE
627b3994-e050-4c37-a441-5cb9edfa3db8 | 2.004A | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
62831850-7abf-4a44-8a0a-15023dd2228c | 7.004A | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
631d5973-d02f-498e-8239-426976780849 | 6.003 | Upward strain (lift) on pin in tangent configuration (Notification Required) | REPLC LOOSE PRI INSLTR POLE | CFI1 | primary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
639c1aba-290a-487c-8e3c-71ecaf5cf4e8 | 2.008 | Damaged bonding wire under crossarm for 12kV and higher (Notification Required only if crossarm does not require replacement) | REPLC DAMAGE PRI BOND POLE | CNE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | If the crossarm is damaged and requires a notification, changing the cross arm will remediate the bonding issue. | If the crossarm does not need to be replaced and the bonding wire is missing or damaged use one of the above listed bond problem statements. | ED_POLE
63a5deef-8590-4e27-a800-23bb80810fe1 | 9.004 | Tie wire broken/missing/damaged or loose (Notification Required) | REPAIR DAMAGE SEC STLTPOLE | 469B | secondary-level | Conductors - Secondary | 2022-03-08 06:04 |  |  | Identify if energized conductors and/or tie wires are damaged.• Select “No abnormal condition” if no damage is observed. | Create notification based on severity of issue. NOTE: ESI will have to indicate tie wire | ED_SL
63d944ac-7f02-4558-ab68-cb13578861dc | 2.003A | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
63fc3997-eeb9-4947-ad99-ff81114e0fb2 | 1.002 | Exterior damage approximately >2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | secondary-level | Streetlight Only Pole - Wood | 2022-03-08 06:04 |  |  | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_SL
640ec219-dd62-4a4a-a037-448ce6e3817d | 0.005A | No (Notification Required) | null | E2 | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | You have indicated that the pole number does not match, please create a corresponding E2 notification. | Make appropriate corrections in the field – replace pole number and/or map correction. | ED_POLE
641cdbdd-4a33-45da-b2f9-a8dd41c8c8ac | 2.005B | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
64280db3-5dd5-4728-837f-22bce006ddf9 | 0.005A | No (Notification Required) |  | E2 | public-level |  | 2022-03-08 06:03 | 2022-01-06 17:23 | 2022-01-06 17:23 | You have indicated that the pole number does not match, please create a corresponding E2 notification. | Make appropriate corrections in the field – replace pole number and/or map correction. | ED_SL
6435b4b3-0cd4-4d19-b6f1-be7b2a0b0a16 | 6.003 | Insulator chipped (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Insulators | 2022-03-08 06:05 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
645db48b-72ac-4282-9a67-6e6416a63916 | 2.007A | 4 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
649567ad-0ac0-4bbb-8bb1-1d04925e533c | 2.005B | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
64a737fb-5153-416e-8117-cdd09a143cae | 2.003D | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
64c01baf-80ca-41fd-be8c-36722a3b6a70 | 7.002A | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
651c5bed-0f67-4cec-92f0-8385fb5f581a | 2.003D | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
652c8267-0e12-40aa-b454-4a333d242c05 | 2.006A | 15 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:05 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
6566ff40-d7ec-4c28-98f7-bad7ba15cf1f | 7.002A | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
658961ad-aee0-4f25-a9fd-0fb652fc7647 | 7.002A | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
6635f0ab-26d4-43f1-bae3-90896a544183 | 2.004A | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
66f88e1c-d0ba-48f7-a812-36fc35e929af | 2.004A | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
670f344f-683b-4324-bb8d-abcf517d3ce2 | 2.003D | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
6728dd8e-e2a2-46c9-a9ab-887141e9ed51 | 7.002A | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
67494afe-3c80-48b4-9cff-c24540cbe3a5 | 2.003A | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
67b6a66b-0b4f-4941-b9ab-b9a33a0365ff | 2.006B | Braces loose (Notification Required) | REPLC LOOSE SEC HWARE/FR POLE | 965A | secondary-level | Crossarm - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
67e37c49-331b-408d-977b-4d91ff086514 | 7.002A | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
67fcf5a1-1eab-4986-a5bf-2df7746a09f9 | 14.002 | Porcelain pothead insulators chipped or broken (Notification Required) | REPLC DAMAGE PRI TERM POLE | CSE8 | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
6803ebd2-40ae-4e1b-9cd3-eda5ab050ade | 2.007A | 15 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
68090c5a-a7a5-4c36-b00b-e08da847060b | 2.006A | 10 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
683df858-8225-45ce-9067-d937809ce1cf | 5.001 | Fracture or buckling of exterior wall (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
686682d6-95fc-450f-a15e-7beb275b3ee1 | 9.012 | Conductor has less than appropriate radial clearance with potential for contact, no public safety hazard (Notification Required) | REPAIR CLEARNC SEC CBL/CND STLTPOLE | 593B | secondary-level | Conductors - Secondary | 2022-03-08 06:03 | 2021-12-23 17:45 | 2021-12-23 17:45 |  |  | ED_SL
68fdfb68-c59b-4281-9a07-7a87f16c9d40 | 2.004A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
6950865e-cc75-4b4d-8ea2-7de1af763dc8 | 2.003D | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
696f566c-d619-48c0-8de8-e737c212777b | 5.003 | Excessive lean (approximately 10% or more of the pole height), caused by erosion of soil at groundline (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Examine public level of pole for any of the listed issues. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
6988c017-feb0-440d-ab47-161708a66f00 | 14.001 | Pothead swollen (Notification Required) | REPLC DAMAGE PRI TERM POLE | 778A | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
69abf910-e7b5-4ccc-aa70-4a2ff6edf57b | 5.001 | Vandalism that affects the structural integrity (i.e. gun damage) (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
69be524f-7016-48d9-918d-15753138e50a | 1.007 | Pole leaning - public hazard (Notification Required) | REPLC LEANING PUBLIC POLE | 923A | public-level | Poles - Wood | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if/how much the pole is leaning.• Select “pole is not leaning” if pole is not showing sins of leaning. | Create notification based on severity of issue. | EZ_POLE
6a889168-dfbb-4343-ab96-96ddb07a4356 | 6.005 | Yes (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Insulators | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if any insulator is connected to the crossarm/structure or insulator with a C-hook. | Create notification if any primary attachment is attached with C-hook. | ED_POLE
6b02e545-139c-49c2-a680-4e30eb9472ce | 2.005B | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count all crossarms at this level that are tracking. | Create notification and prioritize based on severity of issue. | ED_POLE
6b306de5-62b0-4359-8df3-0978ae7da3e3 | 7.002A | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
6b6cd3e1-cac1-4089-a4d8-ba8a237fbbb0 | 2.007A | 10 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
6b8073fd-04be-437d-a490-a0689a2040a0 | 10.007 | Animal guards damaged (Notification Required only for Primary Level) | REPLC DAMAGE PRI AVIPROT POLE | 0IZC | primary-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:03 |  |  |  |  | ED_POLE
6b871343-064f-486d-a01a-605a8ddf7870 | 7.002A | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
6b93993d-0814-41e2-acdc-caea25ec14f8 | 2.003C | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
6b9652d9-70a7-4512-8c53-90d748c34d34 | 11.004 | Damaged equipment brackets or braces (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Hardware/Framing | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_POLE
6bc4107b-c768-4947-a46a-5cbcc9fb7bb4 | 8.015 | Bare Tap (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | 983A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | EZ_POLE
6bd09208-5519-4d58-a87f-2793b2a371a1 | 7.004A | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
6be6edc3-ee30-43fc-9b53-c5ef0abf6253 | 7.002A | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
6c4e904a-a99b-4483-947c-15c42e602267 | 2.003A | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
6c72e8c9-13a0-4fc4-aef6-155ede6d212c | 2.003A | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
6c817d5f-c97f-4582-913b-edc8f9afdeae | 2.003D | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
6c9d545b-e8b5-40ba-96ff-e58d2e2fb4d9 | 2.003A | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
6cb6414d-5db8-485f-b666-fa4e04bb2140 | 2.006A | 4 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
6cc62222-7720-47a2-8fb8-6d4e97b1b989 | 2.004A | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
6cf415a3-ecaf-434d-be7d-e4bc5e99c755 | 7.002A | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
6d1bec54-33d1-43ae-b05c-b0661ad0a37c | 2.003A | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
6d581adc-6de5-416a-8fad-61b6db03c5a9 | 2.007A | 19 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
6d7e972b-ccef-472b-8c0c-608dce39feae | 1.002 | Exterior damage approximately >2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | primary-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
6dc7c8d2-3c93-4d53-969f-c2cf9182dd2a | 7.004A | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
6dd38f28-9408-4168-8e9f-0237b4bba90e | 2.006A | 17 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:05 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
6df7c3d6-f2e3-4aa8-8019-6dde0e3c2574 | 2.007A | 12 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
6e22b6b1-166d-4103-bb55-baf64aac4ba7 | 2.007A | 4 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
6e2df2ce-392b-49d9-b5b3-fd9c981970cc | 2.003C | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
6e872839-5c6e-4f93-b064-f5c03f285af4 | 1.002 | Hole approximately >2 inches near through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | communication-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
6eb30400-4bc5-4f58-aad5-1abe6fa8116b | 9.003 | Vines, branches, or foliage presenting an overhang or other imminent threat * (Notification Required) | TRIM VEG TREE SEC CBL/CND POLE | 044B | secondary-level | Conductors - Secondary | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable conductor clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
6f6bdd80-1385-4771-87b8-5244a29a1212 | 2.007A | 17 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
6f6c3820-897d-4db8-8fe0-fbfbee41a769 | 1.002 | Three or more holes approximately >2 inch diameter, within approximately 18 inches vertical of a through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | primary-level | ED_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
6f74f64d-92c9-458a-8000-8e721cd68358 | 2.004A | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
6f7c7b36-0aa3-4e7d-818a-3213993fdedf | 2.004A | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
6f856022-b0ab-4be4-b704-d0659e0e3eff | 7.004A | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
6fba6fa1-033f-420b-929d-90aff2f72677 | 7.004A | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
7007bd25-13b6-4431-8c33-46e462488ecd | 2.003D | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
704a5655-9c19-4aa6-9298-ac521073dc0c | 14.001 | Pothead leaking (Notification Required) | REPLC LEAKING PRI TERM POLE | 869A | primary-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
7076abe4-59b1-4274-af09-0da6b6cd7ad7 | 7.002A | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
70f88645-517b-466d-b0e1-2c61dd3f6082 | 2.003B | Crossarm bowed approximately >5 inches without splintering (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
7107fb48-e6b5-4e6a-9d3a-9e802dc5075c | 2.006A | 16 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
71cb14eb-75df-4bc9-8be3-6df1f120fb3e | 2.003A | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
71cf2c98-43fa-4338-9b31-9bffce27bae7 | 2.006A | 8 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
72268eb4-aafe-415b-bc4a-45ab9556d581 | 7.004A | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
7227470a-826b-43ff-badf-1f0ba08e9307 | 2.003A | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
72409971-6d30-4c7e-ad57-2b2918ab201c | 16.001 | Yes (Notification Required) | REPLC DAMAGE PRI LTNGARR POLE | 795A | primary-level | Lightning Arresters | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if primary arrestor ground is connected to equipment and/or ground, or primary arrestor has operated and/or damaged. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
72531706-01e5-41c6-b9a3-728dcb6fb60b | 6.003 | Upward strain (lift) on pin in tangent configuration (Notification Required) | REPLC LOOSE SEC INSLTR POLE | CFL5 | secondary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
729eff42-7a03-4fdf-ac36-6812ad1c244a | 2.003D | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
72eeb651-bf22-4a74-b0f8-76e8fcea152e | 2.003A | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
72fe0872-3668-40a9-9d5c-a1ef7b692a6f | 2.007A | 18 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
73091a36-183f-4d72-82e2-47bd50246925 | 14.001 | In contact with animal nest (Notification Required) | REMV ANIMNST PRI POLE | C0I7 | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
730f4e24-21b9-4260-bb0c-fa705dce45e3 | 2.006A | 9 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create notification and prioritize based on severity of issue. | EZ_POLE
73113871-d836-4777-83a5-2bebd8182417 | 2.005B | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
7353126b-18e9-4652-adb8-46f8e85e96c9 | 2.005B | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
73536e4c-ba6e-46c1-a5d9-2e475f10eb3b | 6.006 | Top/Side tie insulator touching crossarm (Notification Required) | REPLC FLOTR/SQTR SEC INSLTR POLE | B797 | secondary-level | Insulators | 2022-03-08 06:04 |  |  |  |  | ED_POLE
73861762-d028-4697-af57-2c656dd98489 | 2.003C | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
73d55974-8d64-4f66-82b9-9be192979665 | 7.002A | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
746a035b-bdfb-45ae-9fe8-30cdd5de1904 | 0.029 | Improperly secured communication conductor or equipment (Notification Required) | CIP CLEARNC COMM POLE | 0I5G | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
74eb206f-c208-45cd-a967-fa7fd04c4144 | 0.029 | Improperly secured communication conductor or equipment (Notification Required) | CIP CLEARNC COMM POLE | 0IAG | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
75103b67-aa23-4382-96cc-fbb06cc8a10f | 8.015 | Fuse cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | CDC0 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | ED_POLE
75301bdb-9a4b-40be-9745-aaf995b51f1d | 2.006A | 5 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
75456d91-3bb7-4dfd-a4dc-8f644c24a1a2 | 2.004A | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
756093cd-28e0-468d-8b1b-10516df21719 | 6.003 | Insulator broken (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
758119ee-8102-4073-b18b-b0c9d51ea05e | 0.005A | No (Notification Required) |  | E2 | public-level | Poles - Steel | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | You have indicated that the pole number does not match, please create a corresponding E2 notification. | Make appropriate corrections in the field – replace pole number and/or map correction. | EZ_POLE
75b5f3fb-6340-4835-a823-f4a445e47f3a | 8.018 | PGW (Notification Required) | REPAIR DAMAGE PRI CBL/CND POLE | 516A | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | For covered conductor installations only, determine if the proper jumper/tap insulation is installed on ALL jumpers/taps. | Create notification if ANY jumper/tap does not have the proper insulation. | EZ_POLE
7650c413-8843-4d2d-aeed-3ac615b5b919 | 2.008 | Missing bonding wire under crossarm for 12kV and higher (Notification Required only if crossarm does not require replacement) | REPLC MISSING PRI BOND POLE | CNC0 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2022-01-07 11:26 | 2022-01-07 11:26 | If the crossarm is damaged and requires a notification, changing the cross arm will remediate the bonding issue. | If the crossarm does not need to be replaced and the bonding wire is missing or damaged use one of the above listed bond problem statements. | ED_POLE
76962c9f-b4ac-483c-b0c9-ca3dd7b0b027 | 7.004A | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
76b8f7bd-bd8c-4289-819d-2fbe8f7a3830 | 2.003A | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
76e7c098-2c14-4d15-b2a4-b5e211679161 | 2.003C | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
77aab7d9-02ac-4067-b4ee-beba6bf8b2e3 | 2.003A | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
77d287fd-71c6-45cf-9ecb-6457a7cb2489 | 2.004A | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count all crossarms at this level that are canted. | Create notification and prioritize based on severity of issue. | ED_POLE
77d2d1ce-d41e-4d32-b8fa-1161852de3c9 | 1.002 | Exterior damage approximately 1–2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | secondary-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
7881d9cb-6b06-4e48-8c4b-7c1a15616568 | 2.003A | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
79109c2b-ff09-41aa-83c1-80bf602f24a0 | 11.007 | Mastarm or mounting hardware corroded, missing, broken, loose or bending (Notification Required) | REPLC DAMAGE SEC MASTARM STLTPOLE | 490B | secondary-level | Streetlight | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
7912d5c0-e990-40ad-a702-f3078595755a | 2.003D | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
7929cf28-d54b-4487-946c-401e8a9769f1 | 2.003C | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
792b08ae-3977-41a4-b351-f83065a79821 | 2.004A | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
7995dee2-4811-4b09-b414-cdaeffbca26f | 7.002A | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
7997a307-ec1f-4f98-81b2-d5ee0a1ed53c | 2.005B | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count all crossarms at this level that are tracking. | Create notification and prioritize based on severity of issue. | ED_POLE
79f01017-2a5b-42ee-af01-e136f0b73580 | 2.003A | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
7a214235-ddc6-49bc-8dfb-c2f2bda6ef06 | 0.026C | No | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if rolling and transposing conductor has at least 12” of clearance between primary conductors/phases. | Create notification if primary conductor clearance is <12”. | ED_POLE
7a40b99d-edb1-44ba-bacb-8240563ff500 | 2.007A | 7 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
7a5d1b8f-4631-4fd4-b92d-78ccb91be5e9 | 2.003D | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
7a5db36d-6421-42b1-a11c-56605adc184e | 2.003B | Significant damage at a bolt (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
7a6608bc-79e5-4c56-aa57-17b3e17854df | 2.006A | 12 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
7abe52b2-1d02-425c-ab5a-55ddf92e5e89 | 2.004A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
7b064523-7d30-4e8b-9962-d35ba0837365 | 7.006 | Missing bonding wire under crossarm for 12kV and higher (Notification Required only if crossarm does not require replacement) | REPLC MISSING PRI BOND POLE | 802A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2022-01-07 12:44 | 2022-01-07 12:44 | If the crossarm is damaged and requires a notification, changing the cross arm will remediate the bonding issue | If the crossarm does not need to be replaced and the bonding wire is missing or damaged use one of the above listed bond problem statements: REPLC DAMAGE PRI XARM POLE, REPLC MISSING PRI BOND POLE, REPLC DAMAGE PRI BOND POLE | EZ_POLE
7b314615-7ea7-4746-80a8-0369f4cabffd | 6.006 | Top/Side tie insulator touching crossarm (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | secondary-level | Insulators | 2022-03-08 06:04 |  |  |  |  | ED_SL
7b3bce80-c20a-4910-adb9-19d005e5a986 | 2.003C | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
7bb1726f-4617-45f0-a93a-b582f3799d75 | 6.003 | Insulator floating (Notification Required) | REPLC FLOTR/SQTR PRI INSLTR POLE | B795 | primary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
7c1f769d-2f1f-4889-87ac-ba72a37374f1 | 6.003 | Tie wire broken/missing/damaged or loose (Notification Required) | REPLC LOOSE PRI INSLTR POLE | CFI1 | primary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
7c49d8a9-1a1e-411a-9b75-52fecfea933d | 10.007 | Vegetation interfering with operation of apparatus equipment (Notification Required) | TRIM VEG TREE PRI POLE | 061B | primary-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
7c5359f2-7049-452e-ab3c-074d9c7dfbb1 | 7.004A | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
7c576ca9-4314-40be-8f4b-7ce716e9a0af | 2.006A | 8 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
7c66d4fe-54f7-4daf-be07-47b75fc19968 | 2.003D | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
7c978c4c-586b-48a7-b3b6-a91593e70072 | 2.005B | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
7ca5c623-5c27-445e-95e9-ea1e43b3d9f1 | 2.004A | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
7cdbad46-2601-4b3e-987a-e3dd395e97fe | 2.003D | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
7d39fcd8-15d4-44cc-afb9-29067e448ae6 | 2.003D | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:05 |  |  |  |  | ED_POLE
7dbd09ad-59cb-4106-85e6-16c4926e4a7a | 2.003A | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
7dd823be-7ae8-46f0-ab91-a9c772adbdcf | 2.003C | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
7debf0b5-af57-465f-a0ac-fdf50d49ac08 | 2.006B | Braces missing (Notification Required) | REPLC MISSING SEC HWARE/FR POLE | 970A | secondary-level | Crossarm - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
7e1c5066-3cec-4768-a957-9f740d5146a0 | 7.004A | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
7e1fd300-bbe6-4a05-ac38-768a3e229b78 | 2.003A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
7e2403ce-fd90-4624-9965-89072769ecf3 | 7.004A | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
7eb5ff2d-2974-4d8d-bbad-2230208bb16e | 8.015 | Equipment bushing cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | CDC0 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | ED_POLE
7ec4f5a4-6257-4959-a19c-b964aa6a98d3 | 8.016 | Encroachment primary conductor with span/down guy (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there is a possibility of primary conductors/phases clashing and/or public can contact.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearances. (Ex. Extreme condition should result in P1 notification). | ED_POLE
7eebaef7-0537-4b87-9475-1ad26304bc57 | 13.001A | Anchor rods missing, pole leaning, public hazard (Notification Required) | REPLC MISSING PUBLIC ANCHOR POLE | 769A | public-level | Down Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | EZ_POLE
7ef10fad-81dc-4dca-9a44-39574df50fa5 | 14.003 | Riser broken (Notification Required) | REPLC DAMAGE SEC RISER POLE | 735A | secondary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | EZ_POLE
7f28ef3a-8a07-4c7f-a849-8215d85c69a6 | 2.003D | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
7f4297c9-26fa-4051-9e2f-d9b956145d2c | 2.003C | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
7fcaa13e-6a44-4cea-a309-54d6a75e612c | 0.029 | Inadequate clearance between communication equipment or structures and SCE electrical equipment or structures (Notification Required) | CIP CLEARNC COMM POLE | 0I5G | communication-level | Poles - Wood | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
7fddb81e-e023-410e-bf1e-75d5fa133141 | 2.005B | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
8052252f-bc6b-441c-a77c-8c28cbc903dc | 7.002B | Significant visual buckling (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
80666df4-05f3-4e3b-9d69-3998b1f0435f | 2.003C | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
80c30f3a-19e6-4992-a429-f9faabf998c2 | 14.002 | In contact with animal nest (Notification Required) | REMV ANIMNST PRI POLE | C0I7 | primary-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
80c696d0-0625-42b8-858b-66b8399bc3b0 | 1.008 | Switch (Notification Required) | REMV ANIMNST PUBLIC POLE | 361A | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | EZ_POLE
80dda062-9caf-4614-85ad-c6c84941b9a8 | 7.002B | Significant visual fracturing (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
812967a6-11a1-4ceb-bf9c-af3abf1924c6 | 2.006A | 12 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
81308ef9-d5bc-4c68-8f82-021dde7d8740 | 13.002 | SCE non-energized electrical components (Notification Required) | REPAIR CLEARNC PUBLIC GUY POLE | 457A | public-level | Down Guys | 2022-03-08 06:03 |  |  | Determine if down guys have the appropriate amount of clearance per GO-95 or could potentially contact the listed options. | Create notification based on severity of issue. | EZ_POLE
8155812d-5a2e-41df-9a98-f0b4b7235591 | 2.003C | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
818cd89b-1231-4d27-becd-bbd50235f3a9 | 8.017 | No (Notification Required) | REPLC DAMAGE PRI LTNGARR POLE | CPE8 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if primary lightning arrestor(s) are properly installed and protecting primary equipment. | Create notification if primary equipment is missing lighting arrestor(s). | ED_POLE
8253212f-fab6-4f50-a1ed-a7c429e6af7a | 2.003D | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
82d200f2-1f29-406a-878c-293a9523568b | 7.002A | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
831b8c41-cfb3-4785-a499-0904b66caba9 | 13.001A | Guys broken/damaged, pole leaning, public hazard (Notification Required) | REPLC DAMAGE PUBLIC GUY POLE | 729A | public-level | Down Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | EZ_POLE
8321b3b5-4810-4a9f-a5ec-6d4604d8a3aa | 6.003 | Improper angle on pin insulator (Notification Required) | REPAIR DAMAGE PRI INSLTR POLE | 625A | primary-level | Insulators | 2022-03-08 06:05 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
8365a85b-0a54-4ed5-bc4e-8e13ce00d537 | 2.006B | Braces missing (Notification Required) | REPLC MISSING SEC HWARE/FR POLE | CDC3 | secondary-level | Crossarm - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
838dc360-b9a5-4ce3-b4a2-c4abb054875e | 14.001 | Pothead sparking, arcing, or noisy during normal ‘dry’ weather conditions (Notification Required) | REPLC DAMAGE PRI TERM POLE | 778A | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
840363a7-d94c-431c-b8ee-03a2fec118dd | 5.005 | Recloser (Notification Required) | REMV ANIMNST PUBLIC POLE | 361A | public-level | Poles - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | EZ_POLE
845733ae-68a2-4814-9006-ad1ea8789aae | 7.004A | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
84da65b3-7c7a-4245-8040-d57eaa8a0c33 | 7.002A | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
8509dff0-cfd7-468d-94f7-1088679dddb5 | 13.001A | Guys broken/damaged, pole leaning, public hazard (Notification Required) | REPLC DAMAGE PUBLIC GUY POLE | RB05 | public-level | Down Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_POLE
8514f805-1af8-42fa-8d4c-df336a7b8cf2 | 12.002 | SCE non-energized electrical components (Notification Required) | REPAIR CLEARNC SEC GUY POLE | CHK2 | secondary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if span guy has the appropriate amount of clearance per GO-95 or could potentially contact the listed options.• Select “No abnormal condition” if span guys have appropriate clearance. | Create notification based on severity of issue. | ED_POLE
8552085b-ecd9-485a-bf9a-3bd560b76324 | 9.004 | Tie wire broken/missing/damaged or loose (Notification Required) | REPLC DAMAGE SEC CBL/CND POLE | CWJ8 | secondary-level | Conductors - Secondary | 2022-03-08 06:03 |  |  | Identify if energized conductors and/or tie wires are damaged.• Select “No abnormal condition” if no damage is observed. | Create notification based on severity of issue. NOTE: ESI will have to indicate tie wire | ED_POLE
85d118d0-f001-42cb-acdc-6adb76acf2f8 | 2.007A | 1 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
861732ec-7b03-4dbb-95a8-74e04925fe7c | 2.003D | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
863cb0b3-b4de-4893-8187-426ba49f3997 | 7.002A | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
869a35e7-5157-445a-950d-9edb071d5ce4 | 0.029 | Vegetation straining communication messenger or guy wire and/or causing structural integrity issues (Notification Required) | CIP CLEARNC COMM POLE | 0I5G | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
872a57b7-793a-42ce-a6ca-bc4f45c16c25 | 2.005B | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
875e7db3-a42b-4d75-aacf-6c1aa2be3c2c | 2.007A | 2 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
87678e25-6d0b-446b-89aa-eab0c75f5c8d | 2.003A | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
87b0eedd-70ae-42d0-8d27-236c33028a48 | 2.003A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
87b8017b-1340-433b-a9b3-13e8cf903b35 | 2.007A | 10 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
87d10243-a9ca-4718-8346-091a92ab0c1d | 1.004 | Exposed decay pocket at ground line where part of shell is gone (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any listed conditions exist at base of pole.• Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_POLE
87e3d47b-35de-40d0-8ab2-8517a74b2cff | 18.003 | Vandalism that affects the structural integrity (i.e. gun damage) (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Pole - Concrete | 2022-03-08 06:05 |  |  |  |  | ED_SL
87f657eb-a773-43df-a5d6-a8396fa4dc92 | 2.003A | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
884fe2d8-4919-4959-a07c-1a2dd8eae7f6 | 7.004A | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
8896c1fb-629a-431f-b6df-d513a76dd9de | 1.007 | Pole leaning - public hazard (Notification Required) | REPLC LEANING PUBLIC POLE | C0U2 | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if/how much the pole is leaning.• Select “pole is not leaning” if pole is not showing sins of leaning. | Create notification based on severity of issue. | ED_POLE
88bd0bae-7e99-42dc-b8d3-0fc6856f5fa0 | 2.003D | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
894e6047-c4ed-4dd7-9fd2-7e6ee8a87fa0 | 7.002A | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
89749e6e-bfcf-4fef-a846-8bee780d50dc | 2.003A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
8986a699-ea22-4f81-9ed1-b39ad0ab47b6 | 2.007A | 19 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
89aaad1f-088b-4ab7-8a75-a685400a753b | 1.002 | Three or more holes approximately >2 inch diameter, within approximately 18 inches vertical of a through bolt (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | secondary-level | Streetlight Only Pole - Wood | 2022-03-08 06:04 |  |  | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_SL
89ef6962-6390-41b3-be46-0ae219f34f63 | 2.003C | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
8a47d2e3-0ca6-4c20-b170-355fcdaf6ab8 | 2.007A | 10 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
8abc73f3-3414-488f-be9b-404172263134 | 2.004A | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count all crossarms at this level that are canted. | Create notification and prioritize based on severity of issue. | EZ_POLE
8af0f7f0-09a7-41ef-8e39-8f24ea9a9b84 | 14.003 | In contact with animal nest (Notification Required) | REMV ANIMNST PUBLIC POLE | C0T5 | public-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_POLE
8afd737b-2b86-4cc8-9627-31524dc86e20 | 2.005B | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
8b0d81cf-96a1-4197-80eb-b6ef05b5b563 | 14.003 | Non-Schedule 80 Riser installed (Notification Required) | REPLC DAMAGE PUBLIC RISER POLE | CIP6 | public-level | Risers/Terminations | 2022-03-08 06:03 | 2022-01-11 17:10 | 2022-01-11 17:10 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_POLE
8b194647-ec95-4889-9623-7b470d435dcd | 2.004A | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
8b547b94-cec4-4c4d-b691-5ac9ad46b5d5 | 2.003C | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
8bd94b54-16d8-4e27-8321-138543466004 | 1.008 | Recloser (Notification Required) | REMV ANIMNST PUBLIC POLE | C0T5 | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | ED_POLE
8c23cddb-b989-481f-b178-6e6c946f8d3e | 2.005B | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
8c78954e-7507-42be-96c2-3507793e771d | 2.003D | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
8ccc0f75-3568-4ca7-b688-7e9b33c2c582 | 13.002 | SCE energized components (Notification Required) | REPAIR CLEARNC PUBLIC GUY POLE | CHQ0 | public-level | Down Guys | 2022-03-08 06:03 |  |  | Determine if down guys have the appropriate amount of clearance per GO-95 or could potentially contact the listed options. | Create notification based on severity of issue. | ED_POLE
8ce789c8-f91b-493b-9e0d-34dbd4bada1e | 2.005B | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
8cef5e56-99bd-439c-80ff-6365b0a328ac | 5.001 | Vandalism that affects the structural integrity (i.e. gun damage) (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
8d0adbba-7d8a-4242-8e1d-5f56e05f2794 | 7.004A | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
8d9245ae-1a39-4030-852d-bcbd34f6dad1 | 1.002 | Exterior damage approximately 1–2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | primary-level | ED_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
8da7d9eb-5b1d-4a03-8ffe-ec643ae3ed02 | 5.001 | Pole embedded on soil/heavy ponding (water) (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
8de21cc8-9fbc-47bb-aa28-93214a9fad51 | 8.015 | Lightning arrestor cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | 983A | primary-level | Conductors - Primary | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | EZ_POLE
8df732aa-28b7-4adf-b6c3-51546f9fb736 | 14.003 | Riser broken (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | public-level | Risers/Terminations | 2022-03-08 06:03 |  |  |  |  | ED_SL
8e59513a-2c24-4c2f-a705-8facc4eb5d61 | 8.016 | Down guy (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there is a possibility of primary conductors/phases clashing and/or public can contact.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearances. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
8ed8d6a6-fd14-4d80-9f88-1e93bba9a4d4 | 2.003A | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
8f057d04-f86a-44ee-b978-66b5af166198 | 7.002A | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
8f2d53d9-24ad-4d4b-b378-d1279fd6e8d2 | 2.005B | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
8f547847-5ffc-421b-abe6-3964cf68c286 | 2.006A | 1 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
8f5bd5bb-9f58-4e1f-907f-bd3c44a1bfb9 | 2.005B | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
8fda6f7b-0dea-4548-9e9c-323bee68a194 | 2.006A | 10 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
8fdb5516-6918-443a-8b86-037941745663 | 10.006 | Yes (Notification Required) | TRIM VEG TREE PRI POLE | 061B | primary-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if vegetation is currently or will interfere with operation of primary equipment. | Create notification based on severity of issue. | EZ_POLE
9014c5f2-900e-4683-b15c-f711b313425b | 1.009 | Animal nests with potential to contact energized components or interfere with equipment operation (Notification Required) |  |  | public-level | Poles - Wood | 2022-03-08 06:04 |  |  | Since this answer applies to all levels the ESI must select from the above problem statements based on the location of the animal nest. |  | ED_POLE |  | [{"problemCode":"C0I7","problemStatement":"REMV ANIMNST PRI POLE"},{"problemCode":"C0L8","problemStatement":"REMV ANIMNST SEC POLE"}]
906f95c8-e7b6-4a1f-9109-d692e36098ca | 2.004A | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  | Count all crossarms at this level that are canted. | Create notification and prioritize based on severity of issue. | ED_POLE
916dd6ef-aee5-49df-958c-1d73a680acc3 | 2.003A | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
9194bf6a-c802-4082-90ea-d3d154ac53c6 | 2.003B | Significant damage at a bolt (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
91c6bad0-2d54-4fd5-a1ad-ecd5bd393df7 | 2.003C | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
91e103fc-fdce-47d6-b341-ac4ab8417093 | 7.004A | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
920d28b3-fda7-4ee6-bb17-239263c46122 | 10.006 | Yes (Notification Required) | TRIM VEG TREE SEC POLE | C0K4 | secondary-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if vegetation is currently or will interfere with operation of primary equipment. | Create notification based on severity of issue. | ED_POLE
920de78b-4a6a-4104-ae27-6a21ee95dab6 | 2.003A | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
922b8ac6-9a57-43ed-b45d-1035111eaac0 | 8.002A | Vegetation arcing or in contact with energized conductor (Notification Required) | TRIM VEG TREE PRI CBL/CND POLE | CWF4 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed vegetation clearance issues are present in the primary conductors/phases/taps/equipment.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
9285941a-3fad-42ae-a298-a2bef48fba8e | 2.006A | 8 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
929beb78-aaa5-483b-95a4-edb1e0367044 | 5.003 | Excessive lean not caused by erosion of soil (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Examine public level of pole for any of the listed issues. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
92a2534f-c6c5-4dfe-af42-92147943e4b5 | 6.003 | Insulator squatting (Notification Required) | REPLC FLOTR/SQTR SEC INSLTR POLE | B797 | secondary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
92c52a27-a7de-41ef-8a92-982336955707 | 2.005B | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
92e4d6c0-fb94-479d-a9ad-3c4c400b032e | 14.003 | Non-Schedule 80 Riser installed (Notification Required) | REPLC DAMAGE PUBLIC RISER POLE | 713A | public-level | Risers/Terminations | 2022-03-08 06:03 | 2022-01-11 17:11 | 2022-01-11 17:11 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | EZ_POLE
932d4cef-7686-41d5-ae60-f422331b1960 | 3.001 | Excessive oil leakage, oil reaches ground or public access or environmentally sensitive area (Notification Required) | REPLC LEAKING PRI XFMR-D | D0I4 | primary-level | ED_XFMR | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
935d8ae2-ee83-4d9c-bb8a-77ba860a951d | 2.006A | 9 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create notification and prioritize based on severity of issue. | ED_POLE
93653b48-dd6c-40ba-a058-292c1d36e4f5 | 3.001 | Minor leakage, oil remains on equipment, does not reach ground or public access or environmentally sensitive area (Notification Required) | REPLC LEAKING PRI XFMR-D | D0I4 | primary-level | ED_XFMR | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
937a0311-15dd-4384-9953-5beabd16660b | 2.007A | 16 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
938283ab-ec1c-447d-b62c-2b13cf34a798 | 1.012 | Hole approximately >2 inches near through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | ED_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
93831cef-8a1a-42d0-a06e-43843041896e | 2.005B | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
93a3f145-1a2a-43d8-b71d-11a1aa0a7f29 | 2.006A | 3 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
94577693-0a32-4e95-b1bc-141ec8f35458 | 7.004A | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
945c9c12-67bb-4c17-8001-9d7898f6e821 | 2.005B | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
945cf9e7-9534-4682-bda8-b7bb8927c6a5 | 2.005B | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
9477d19f-85e8-4a97-a7c8-86662b81c1c2 | 2.003D | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
948cdbbf-be08-4495-b0ba-87f5c1be92e2 | 2.003C | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
94b6b829-5782-4d2d-a0f5-a4a4b3c75884 | 6.003 | Insulator cracked, damaged or loose (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
94c904f3-5c6f-4f52-b545-e92f77769f05 | 7.002A | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
95929036-3072-4a5d-bec4-a7ae4a8fc8f1 | 13.006 | Buried anchor (Notification Required) | REPAIR CLEARNC PUBLIC ANCHOR POLE | COQ0 | public-level | Down Guys | 2022-03-08 06:04 | 2021-12-22 03:27 | 2021-12-22 03:27 |  |  | ED_POLE
95e73989-9ad4-4312-afcc-c35536fdd473 | 2.008 | Damaged bonding wire under crossarm for 12kV and higher (Notification Required only if crossarm does not require replacement) | REPLC DAMAGE PRI BOND POLE | 799A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | If the crossarm is damaged and requires a notification, changing the cross arm will remediate the bonding issue. | If the crossarm does not need to be replaced and the bonding wire is missing or damaged use one of the above listed bond problem statements. | EZ_POLE
95f45c17-8ef5-4559-8535-ac3ef756bfe8 | 2.003C | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
967d69d0-1b4c-4ace-bdae-86183f4a76fc | 2.006A | 10 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
96eb0acb-5706-487c-baeb-17a2e3a63c5e | 0.024 | 3rd party structure touching or surrounding SCE structure (Notification Required) | CUST CLEARNC PUBLIC STLTPOLE | 0IZW | public-level | Streetlight Only Poles - Wood | 2022-03-08 06:04 |  |  | Identify if any of the listed defects are present on or around the structure.• Select “No abnormal condition” if no listed condition options are present. | Create notification if condition type is severe and warranted. | ED_SL
9713d23c-968d-43c5-916a-33d59d929630 | 2.003C | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
9716f222-d907-4cf1-856a-691c9d277d5b | 6.006 | Missing parts (Notification Required) | REPLC LOOSE SEC INSLTR POLE | 956A | secondary-level | Insulators | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
972826b0-429e-4288-97bb-d0207e35b97a | 2.004A | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
978a5ca4-3641-4499-bd33-d8b20dac76f7 | 7.002A | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
97a3ac1a-296e-4e35-abea-6511ec75f837 | 2.003D | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
9808f1c4-1272-4ee6-92ca-47abd24b2637 | 2.003A | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
98703d79-5709-4720-b614-b2f6acf6c829 | 2.006A | 11 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
989feda2-2161-4770-aab7-67fe08d0e61d | 2.004A | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
98c2a5c3-71e8-4479-9df0-fd2231d8d100 | 0.029 | Vegetation straining communication messenger or guy wire and/or causing structural integrity issues (Notification Required) | CIP CLEARNC COMM POLE | 0IAG | communication-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
98f1e8b6-2e8a-42fa-9ed8-3494fa49332d | 2.006B | Braces loose (Notification Required) | REPLC LOOSE SEC HWARE/FR POLE | CDL5 | secondary-level | Crossarm - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
99d98d41-d71c-46ef-9f89-ca0b01f5cf5f | 2.004A | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
9a2dd41c-ce77-4366-b2eb-b318ac9a5be3 | 2.005B | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
9a84b300-2e72-466e-b495-3ef964402438 | 2.006A | 10 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
9a87e728-0c3a-4c24-84cd-5872caaa6d35 | 14.002 | Pothead leaking (Notification Required) | REPLC LEAKING PRI TERM POLE | 869A | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
9a8b70ed-9cdf-477a-8be3-4214b24d599d | 2.005B | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
9a9b8368-8c74-4519-b4d7-c8be3a5aea24 | 2.007A | 13 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
9ab6bc15-559b-44cf-86e1-48e081195e36 | 10.007 | Vegetation interfering with operation of apparatus equipment (Notification Required) | TRIM VEG TREE SEC POLE | 058B | secondary-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:05 |  |  |  |  | EZ_POLE
9afe7d3f-c4f9-48ed-81b8-78a6382a2a14 | 7.002A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
9b85c697-0a3b-4aa7-8595-b7388a31938b | 8.002B | Less than 6 feet horizontally between conductor and any surface of a building (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable energized conductor- structure clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
9ba862ef-b513-4d8a-9a76-98132bd18f00 | 2.007A | 14 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
9bcd31b9-16c0-4038-86fa-269e6a0bf99f | 1.002 | Hole approximately >2 inches near through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | primary-level | EZ_POLE | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
9bf4c83b-f0ff-4211-962c-3badbbb75de8 | 7.004A | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
9c9f4e53-bbf2-4367-97b7-ba6e6118efd8 | 2.004A | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
9cd9a854-30c5-44ac-92ac-104acd9f317e | 9.003 | Vines, branches, or foliage presenting an overhang or other imminent threat * (Notification Required) | TRIM VEG TREE SEC CBL/CND POLE | CWK4 | secondary-level | Conductors - Secondary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable conductor clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
9d078493-a352-4168-bb1d-d8166ab5712b | 2.003D | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
9d177878-0bea-4d8f-ac1a-1ae43daf4a47 | 2.005B | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
9d1dfefc-f5b9-483e-8a57-03f74b6f71d2 | 1.012 | Exterior damage approximately >2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Pole - Wood | 2022-03-08 06:04 | 2022-01-13 10:13 | 2022-01-13 10:13 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_SL
9d5a756c-6615-4c89-b1a6-d00f1a1c0b33 | 2.007A | 19 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
9d6ca065-b645-4d81-a57f-de6590be5e64 | 2.005B | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
9dce9dd7-7007-44de-87c3-8890399fef2f | 6.003 | Insulator floating (Notification Required) | REPLC FLOTR/SQTR SEC INSLTR POLE | B797 | secondary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
9dd53883-9300-4ba7-ad29-e6a41cfcab5f | 6.006 | Top/Side tie insulator touching crossarm (Notification Required) | REPLC FLOTR/SQTR PRI INSLTR POLE | 827A | primary-level | Insulators | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
9ded2a4f-61b5-444e-94c2-e90e8b94dba6 | 2.006B | Braces loose (Notification Required) | REPLC LOOSE PRI HWARE/FR POLE | 967A | primary-level | Crossarm - Wood | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
9e23ab0b-6305-4afc-a989-9eedd7280029 | 2.003D | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
9e3f6303-1c2d-4fd2-8f4f-1dcc789a4724 | 2.007A | 16 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
9e4a225a-f907-47f0-88d5-2c524b0b79f8 | 17.004 | Pole leaning more than 1 foot per 10 feet of pole height (Notification Required) | REPLC LEANING PUBLIC STLTPOLE | 478B | public-level | Streetlight Only Poles - Steel | 2022-03-08 06:04 |  |  |  |  | ED_SL
9eb84bf5-e98a-44d0-ab55-6e6b8b2750dd | 2.003C | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
9f61fdfd-5d0a-4f7f-8f4f-571cafdd6ff2 | 3.002 | Improperly connected (loose) wire (Notification Required) | REPAIR DAMAGE PRI CBL/CND XFMR-D | DWE9 | primary-level | ED_XFMR | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
9fa75ecd-20f1-4912-bf9f-bcc65cdcecb8 | 2.007A | 15 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
9fe71af6-ba42-446b-b076-7fab29d8403a | 1.002 | Three or more holes approximately >2 inch diameter, within approximately 18 inches vertical of a through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | communication-level | ED_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
a07603df-c23b-4bbc-adeb-5ce23539665b | 7.002B | Significant visual buckling (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
a07b04d4-c819-4f40-8541-3b3b7d1a70b5 | 2.007A | 18 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
a0fcbc02-40f1-42b3-b57f-a08f229c048e | 2.003C | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
a11f99cb-6a27-4de7-9298-0e59255fd2bf | 2.006A | 6 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
a1289a0e-8bbc-45a5-9261-82ab62ae33a6 | 2.003C | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
a13edd6f-07b1-4612-9bf2-f9477e7495e2 | 2.003C | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
a1781337-b247-40d7-8a5f-421f04799d6e | 2.003A | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
a192e8ac-786f-4913-a566-e40fb627e9b4 | 7.002A | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
a1f610da-9c31-4b3f-ada0-621d57c9c1e1 | 2.003C | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
a2b2ac0f-6836-4df6-bfae-43a40c29b93f | 17.001 | Animal nests with potential to contact energized components or interfere with equipment operation (Notification Required) | REMV ANIMNST SEC STLTPOLE | 0IZU | public-level | Streetlight Only Poles - Steel | 2022-03-08 06:04 |  |  | A remove animal nest Problem Statement does not exist at the public level. If this condition exist in the field, then select secondary. |  | ED_SL
a2ddad52-477e-4f1f-98d3-37154fc17f93 | 7.002A | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
a379d5be-86fe-43b8-8212-bc69af0163ea | 7.004A | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
a3832ed6-6d55-48cb-bb02-7eb50b144a3e | 2.006A | 17 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
a3ba6508-653c-4d4b-b6dc-884a16612b67 | 2.004A | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
a3ea90b3-1636-4451-a72d-9f052b3c54a8 | 7.004A | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
a447aab9-e3ce-4395-bb5c-8283d3645b4b | 0.024 | Unauthorized Attachment (Notification Required) |  |  | public-level | Poles - Wood | 2022-03-08 06:04 |  |  | CUST CLEARNC PUBLIC POLE Priority 2 only –If owner is known. REMV UNATH ATT PUBLIC POLE Priority 3 – If unable to identify owner |  | EZ_POLE |  | [{"problemCode":"0IF2","problemStatement":"CUST CLEARNC PUBLIC POLE"},{"problemCode":"362A","problemStatement":"REMV UNATH ATT PUBLIC POLE"}]
a47172f4-f43f-4b37-9f94-e916fed16a63 | 17.002 | Unauthorized Attachment (Notification Required) | REMV UNATH ATT PUBLIC STLTPOLE | 542B | public-level | Streetlight Only Pole - Steel | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
a4894839-a442-4d49-b5cc-9f8f62d60c47 | 7.002A | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
a4d8b673-06e2-467c-b9ec-7a39f80cc7cc | 2.005B | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
a53b2927-7b62-4652-90ee-c3d63086366a | 2.007A | 8 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
a554e78b-f9a0-40df-bd15-558bd80ca2bc | 11.002 | Yes (Notification Required) | REPLC DAMAGE PRI CUT/FUS POLE | CLE8 | primary-level | Fuses | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if there is any evidence that primary fuse holders are burning or tracking. | Create notification based on severity of issue. | ED_POLE
a5d969a3-d716-4107-abbb-dda86c1db63a | 2.003B | Crossarm bowed approximately >5 inches & splintering (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
a5f34da2-4184-4822-b459-f7d31daf013e | 2.003D | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
a69d5b16-bc65-45e2-8f9c-5e6dd812e38c | 2.003D | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
a6ab392f-baff-4187-8d24-0920b9b32bca | 2.003A | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
a702f7bf-7da3-4810-97d4-6a483fdcc57e | 7.004A | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
a76a3f42-487d-402c-83bd-5f4519c5468c | 15.004 | Tree condition causing significant strain and/or visible abrasion damage — either open wire or Triplex (Notification Required) | TRIM VEG TREE SERV CBL/CND POLE | CWE4 | secondary-level | Service Drops | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed clearance impairments are present on pole.• Select “No abnormal conditions” if no clearance impairment is identified on pole. | Create notification based on severity of issue. | ED_POLE
a83ec544-aef9-4449-a07f-cac61d4911ef | 7.002A | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
a840f838-1c4c-4037-b21b-5dbe1056fa67 | 2.006A | 10 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
a8925ab7-4918-480d-9c6a-55699807c225 | 18.002 | 3rd party structure touching or surrounding SCE structure (Notification Required) | CUST CLEARNC PUBLIC STLTPOLE | 0IZW | public-level | Streetlight Only Pole - Concrete | 2022-03-08 06:04 |  |  | A sign is not considered an unauthorized attachment on a steel streetlight pole. Therefore, a notification is not required. |  | ED_SL
a8d93a6f-4a21-4e9f-9f78-fff3f04f5232 | 2.003B | Significant damage at a bolt (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
a8e5c392-4610-4cbd-8196-2a5676e31aae | 2.008 | Missing bonding wire under crossarm for 12kV and higher (Notification Required only if crossarm does not require replacement) | REPLC MISSING PRI BOND POLE | 802A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2022-01-07 11:25 | 2022-01-07 11:25 | If the crossarm is damaged and requires a notification, changing the cross arm will remediate the bonding issue. | If the crossarm does not need to be replaced and the bonding wire is missing or damaged use one of the above listed bond problem statements. | EZ_POLE
a8e971a4-cb40-4588-8fd2-9a4443a0bc7e | 2.003C | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
a96cb0f0-f358-4daa-8a4d-89462e5269b9 | 13.001B | Yes (Notification Required) | REPAIR CLEARNC PRI GUY POLE | 612A | primary-level | Span Guys | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if guy wire(s) have contacted or will contact energized conductors. | Create notification based on severity of issue. | EZ_POLE
a9a44e67-50e7-4f20-b41f-f180b2f0ed74 | 2.007A | 7 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
a9d29d85-530a-405a-a761-05aecd80f98f | 7.004A | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
a9fd9d88-b8fb-4fb2-89aa-67fbc5c930d5 | 9.003 | Tree condition causing significant strain and/or visible abrasion damage - either open wire or Triplex (Notification Required) | TRIM VEG TREE SEC CBL/CND STLTPOLE | 481B | secondary-level | Conductors - Secondary | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
aafaac72-7df7-4cdb-bf42-c9fa494d28bd | 2.005B | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
aafb9b41-5d49-4609-8a35-ba8ae90c5fb3 | 0.029 | Loose lashing wires (Notification Required) | CIP LOOSE COMM CBL/CND POLE | 0I5E | communication-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
ab4f7815-186a-4c70-8ee7-7f5522661a85 | 2.004A | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
ab57bfa7-5ce1-4b82-8824-efb82c7fce8b | 2.004A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
ab84b07a-35cf-427d-97f8-fe2da36605fe | 7.004A | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
ac382df6-ba30-424e-870f-cd3990bc9e61 | 2.006A | 4 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
ac77a799-02ec-4aa8-bcdd-643b9a793f28 | 6.003 | Insulator chipped (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
ac8a3278-8f66-4103-86e3-0354d0c1465f | 6.003 | Improper angle on pin insulator (Notification Required) | REPAIR DAMAGE PRI INSLTR POLE | CFE9 | primary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
ac8e8750-cf3f-4de3-93cb-26e602a8909e | 2.003C | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
ac8f9707-5b91-4204-a3ee-e5965e3e4d83 | 14.003 | Cables in Riser exposed (Notification Required) | REPLC DAMAGE SEC RISER POLE | CIJ8 | secondary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_POLE
aca696ac-dc6a-456c-9c94-9d29432f1e82 | 2.004A | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
acc25b30-1c79-4ff7-a96d-b48879cdceaa | 7.002A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
acdc1f20-6066-4d91-992b-ef851af0ee00 | 2.003D | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
ad083636-33c3-43ce-8b8e-a82f3a12d0a4 | 2.003D | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
ad315da1-b3b6-4cf2-8b29-3644409eab7a | 7.004A | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
adb30831-ae40-4f8d-9862-b53b994cf67b | 2.005B | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
adc1fc7b-3ac8-4ab8-b35d-80b58b4e9635 | 13.001A | Guys broken/damaged, pole not leaning (Notification Required) | REPLC DAMAGE PUBLIC GUY POLE | 729A | public-level | Down Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | EZ_POLE
ae6a8e3f-1335-430a-a3d5-af8bd14ef60d | 14.003 | Riser swollen (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | secondary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
ae9c860a-f9e7-4a6d-b3e8-f5eea4a9e6b0 | 2.003D | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
ae9ed291-99fb-435f-b335-59def2c29f70 | 2.003D | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
af58c820-a360-47ee-b541-0d71b38a7b7f | 5.003 | Excessive lean not caused by erosion of soil (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Examine public level of pole for any of the listed issues. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b00de073-1425-4880-8dd7-92bcbe1d9a07 | 7.002A | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b074bb31-e87e-467a-83e7-f983dfecd737 | 2.007A | 8 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
b0aaa2ab-b265-4c5d-bb1f-6e9efdaf2e83 | 2.007A | 14 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
b0be1907-1d42-4741-86dc-e6b2c8425b6e | 1.012 | Three or more holes approximately >2 inch diameter, within approximately 18 inches vertical of a through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | ED_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b1461a18-5879-4585-909e-8c20e43dc3f1 | 1.004 | Evidence of soil erosion around base of pole (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | public-level | Streetlight Only Poles - Wood | 2022-03-08 06:04 |  |  | Identify if any listed conditions exist at base of pole.• Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_SL
b16f95ac-7b50-4077-8931-9a74cade8eed | 2.004A | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b1b8f686-9468-4649-af37-23fdfc5d631b | 2.004A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
b1dda320-fb81-48f5-a832-36100b2c7378 | 2.003C | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
b1e8220b-7157-46a8-97f0-823da2131775 | 13.001B | Yes (Notification Required) | REPAIR CLEARNC SEC GUY POLE | CHK2 | secondary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if guy wire(s) have contacted or will contact energized conductors. | Create notification based on severity of issue. | ED_POLE
b28dd216-8a8e-4265-9e37-cebf496f2d6f | 2.003C | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
b2bbbd06-d8de-477a-a1e2-ef57412a7e1e | 7.002A | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b2e302e5-12fe-40ec-97e3-80629dfb5d93 | 13.001A | Guys broken/damaged, pole not leaning (Notification Required) | REPLC DAMAGE PUBLIC GUY POLE | RB05 | public-level | Down Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_POLE
b2fd38f2-1d5d-4cc7-912b-b095e6957bd4 | 2.003D | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
b3171745-caf3-4cf9-a817-f3d29af4f0e9 | 7.004A | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
b31fe36c-280d-441e-9863-01324f0bc39e | 2.007A | 19 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
b32c83c4-8342-4dcb-9244-44d84dda8d31 | 2.003A | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
b33b0c58-eeac-419b-9bfb-46b5706727d4 | 2.003C | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
b33d7800-3acc-4153-b639-b4f0d8f69c87 | 2.003C | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
b33eea67-b05e-4e70-96e4-d2315404eeff | 7.004A | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
b35acfa2-a9c7-4fdd-a558-fcaac413b033 | 7.002A | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
b3857456-ffff-4cea-834c-1cf9f8297f14 | 12.002 | SCE non-energized electrical components (Notification Required) | REPAIR CLEARNC SEC GUY POLE | 619A | secondary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if span guy has the appropriate amount of clearance per GO-95 or could potentially contact the listed options.• Select “No abnormal condition” if span guys have appropriate clearance. | Create notification based on severity of issue. | EZ_POLE
b3a7f271-d516-41df-858e-bcf60c184eed | 2.005B | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
b43c325b-3df9-475f-8aee-8f6a71ef252f | 7.004A | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
b43f55cb-dda3-4b38-8be2-551fb0ce2ee0 | 2.006A | 6 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b46234f6-91b5-403b-88d0-9d5686be60f0 | 15.004 | Does not meet G.O. 95 vertical clearances (Notification Required) | REPAIR CLEARNC SEC CBL/CND POLE | CWK2 | secondary-level | Service Drops | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed clearance impairments are present on pole.• Select “No abnormal conditions” if no clearance impairment is identified on pole. | Create notification based on severity of issue. | ED_POLE
b48cf5e2-cea4-4fe8-a7d7-40ce5db153d5 | 7.002A | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b4aa74f6-92cc-43b1-9620-2741e333fbec | 7.004A | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
b526992d-89d8-460a-8163-30d593da9231 | 7.002A | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b5280fa5-530f-4e16-8410-aeec532bbce7 | 2.006A | 5 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b542adaf-05b3-47a6-b32c-f8bf24ac2e18 | 7.002B | Significant visual fracturing (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
b57247b0-05eb-4540-8ee3-75e15eda998f | 2.005B | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b5c846af-6781-49fa-b73d-e20638dedaf4 | 3.002 | One fuse is open/down (Notification Required) | REPLC DAMAGE PRI CUT/FUS POLE | 718A | primary-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
b5fe61c2-d70b-4493-bc38-df97f231696f | 5.006 | Animal nests with potential to contact energized components or interfere with equipment operation (Notification Required) | REMV ANIMNST PUBLIC POLE | C0T5 | public-level | Poles - Composite | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_POLE
b62c9849-d2ab-441d-841c-63053bd1296f | 2.006A | 14 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:05 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b69543bc-95d7-4076-8db9-903bca04aebf | 8.002A | Vegetation arcing or in contact with energized conductor (Notification Required) | TRIM VEG TREE PRI CBL/CND POLE | 046B | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed vegetation clearance issues are present in the primary conductors/phases/taps/equipment.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
b6f054dd-7268-41f4-b0de-3fa87d7a2207 | 7.002A | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b7031c30-9335-435b-9c62-d0f89a81ce19 | 2.007A | 13 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
b70cd18c-ecbd-4e52-a6fb-61a6163ab3cb | 7.004A | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
b7182b9b-9950-4aa0-83a3-5e70510f9417 | 2.006A | 19 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b7246d4e-d267-488a-8bc2-db6b40c33d3b | 6.003 | Upward strain (lift) on pin in tangent configuration (Notification Required) | REPLC LOOSE SEC INSLTR POLE | 956A | secondary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
b75767ac-3aa6-4691-848e-30dc4a84aafb | 2.003D | 12 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
b7928a64-f1dc-4c7d-81f5-2d7560811b48 | 2.007A | 11 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
b8041383-393a-4fab-9233-244938d2dbaf | 1.004 | Evidence of soil erosion around base of pole (Notification Required) | REPAIR DAMAGE PUBLIC POLE | C0P7 | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any listed conditions exist at base of pole.• Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_POLE
b8049fd8-99de-41c2-8572-63b5c6dda60a | 13.001A | Guys missing, pole leaning, public hazard (Notification Required) | REPLC MISSING PUBLIC GUY POLE | CHB1 | public-level | Down Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_POLE
b82660e0-3d4f-438b-aece-e227d004568a | 5.001 | Visual cracks or rupture of exterior laminates or exterior wall exposing interior (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b84fa36d-a921-4ad8-8d8a-a85ea12d99d7 | 7.004A | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
b8602022-a8dd-4e0b-a6f1-78c5ccffc8d4 | 1.004 | Exposed decay pocket at ground line where part of shell is gone (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Poles - Wood | 2022-03-08 06:04 |  |  | Identify if any listed conditions exist at base of pole.• Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_SL
b896dc2f-f41c-45a9-a5e6-775a085e63c7 | 2.007A | 2 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
b8e31ffa-fc1e-42e2-bb9a-32bc42aba8cb | 2.006A | 9 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create notification and prioritize based on severity of issue. | EZ_POLE
b91943fd-cace-4c5d-b660-e5a786f4802e | 6.006 | Top/Side tie insulator touching crossarm (Notification Required) | REPLC FLOTR/SQTR SEC INSLTR POLE | 826A | secondary-level | Insulators | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
b949e601-6f75-4459-9f56-337d5d64c881 | 2.007A | 3 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
b9518267-0f97-46e1-92e0-b962e507bbdc | 2.006A | 17 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
b9745bc5-ed13-4966-bab2-d342411d4cfc | 2.003B | Significant damage at a bolt (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
b99c4458-23f8-4002-8bd5-76c0cbb1eca2 | 7.002B | Significantly unbalanced due to tension (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
b9d47600-ced6-4b22-8b1a-9bf39a797fc4 | 12.004 | Cracked, damaged, deflected, frayed or loose (Notification Required) | REPLC DAMAGE SEC GUY POLE | CHJ8 | secondary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_POLE
ba53a5b7-8635-4a3f-9485-c54aa7bb2aba | 2.005B | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
ba8dc535-f3b8-4730-9f5e-74b1f7477dd7 | 2.003C | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
baae60f5-fc68-4733-b88b-c36dbab7162a | 1.007 | Pole leaning more than 1 foot per 10 feet of pole height (Notification Required) | REPLC LEANING PUBLIC POLE | C0U2 | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if/how much the pole is leaning.• Select “pole is not leaning” if pole is not showing sins of leaning. | Create notification based on severity of issue. | ED_POLE
bac5be06-ec39-4d48-af05-9209af6847f1 | 7.002A | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
baecd9f7-78c3-42a3-9bca-44d1c2b8b0ef | 2.006A | 14 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
baf1a74d-b511-4636-8209-9380daccf5cc | 14.002 | In contact with animal nest (Notification Required) | REMV ANIMNST PRI POLE | 343A | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
baf9fcd0-fab4-4f4d-9238-b52d22445a6b | 7.002A | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
bb3cfeb6-725d-4e4a-964a-d289e44b22e3 | 2.005B | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
bb8ce519-fa0c-421a-b5eb-5511293980cb | 2.003C | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
bb8eda5c-2f5c-4d45-8417-4e1da66d0654 | 7.002A | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
bbe00eda-3495-42e7-80b4-2b4ef699a220 | 2.003C | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
bbf970b8-6058-45f4-a69d-f6212d7f8e7f | 2.003D | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
bc970ce6-98eb-4c4d-9b8b-2cfc345f71ba | 7.002A | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
bcde7906-3436-44f1-8632-625615447870 | 5.006 | Animal nests with potential to contact energized components or interfere with equipment operation (Notification Required) | REMV ANIMNST PUBLIC POLE | 361A | public-level | Poles - Composite | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | EZ_POLE
bcdf198d-62e1-4541-b076-8ccea138712b | 12.002 | SCE energized components (Notification Required) | REPAIR CLEARNC SEC GUY POLE | CHK2 | secondary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if span guy has the appropriate amount of clearance per GO-95 or could potentially contact the listed options.• Select “No abnormal condition” if span guys have appropriate clearance. | Create notification based on severity of issue. | ED_POLE
bcfa915d-fadf-4736-b0b1-f672af08597a | 2.003C | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
bd2cdf2b-f2e6-4ec3-b19c-04d707dc49b6 | 2.006A | 18 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
bdefb837-6c16-4022-98fb-6687ab240181 | 7.002A | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
bdfc3d47-ec83-43c9-8d24-f2b6e17c9501 | 2.003B | Crossarm bowed approximately >5 inches & splintering (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
be11a2b7-8198-4e36-acd8-b220df660efe | 2.005B | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
be528ac0-a599-47e4-9272-c906cdfaf1d8 | 15.004 | Does not meet G.O. 95 vertical clearances (Notification Required) | REPAIR CLEARNC SEC CBL/CND POLE | 482A | secondary-level | Service Drops | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed clearance impairments are present on pole.• Select “No abnormal conditions” if no clearance impairment is identified on pole. | Create notification based on severity of issue. | EZ_POLE
bf3b3112-8cb5-444c-819c-bc62006580da | 2.005B | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
bf3d7443-e2d0-46ec-8ca0-e98a521acb7f | 2.003D | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
bfc33c6b-2976-4a9e-b866-4723fb8d8571 | 1.012 | Exterior damage approximately >2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | public-level | ED_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
c026fd24-ed81-42da-877a-cfd2d27dcba6 | 13.001A | Anchor rods broken/corroded, pole not leaning (Notification Required) | REPLC DAMAGE PUBLIC ANCHOR POLE | COP6 | public-level | Down Guys | 2022-03-08 06:05 | 2021-12-22 03:27 | 2021-12-22 03:27 |  | Create notification based on severity of issue. | ED_POLE
c04299e1-1450-40dd-ac75-256a9e834866 | 2.003D | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
c05f39ba-58e8-4d7d-9319-cabbb0b73f7b | 18.003 | Visual cracks or rupture of exterior surface exposing interior (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Pole - Concrete | 2022-03-08 06:04 |  |  |  |  | ED_SL
c06b048c-6956-4e54-9c0c-360cce1a1999 | 2.004A | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
c07e2b6e-bd9c-434a-b9f4-be4988305f36 | 7.004A | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
c11d9895-ab9e-4cb4-bfe2-d23216559bdf | 12.004 | Sagging or extreme slack (Notification Required) | REPAIR LOOSE PRI GUY POLE | 606A | primary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | EZ_POLE
c12068a6-6221-48fd-8682-6652d29fc877 | 2.003D | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
c14f1697-46f6-444f-9e1d-4257d792799e | 9.012 | Conductor has less than appropriate radial clearance with potential for contact, no public safety hazard (Notification Required) | REPAIR CLEARNC SEC CBL/CND POLE | CWK2 | secondary-level | Conductors - Secondary | 2022-03-08 06:04 | 2021-12-23 17:45 | 2021-12-23 17:45 |  |  | ED_POLE
c180588b-1a78-46bd-a609-1d4cc0f084f5 | 2.003C | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
c1f499e6-f366-4485-8431-75a7796c8e0b | 1.012 | Exterior damage approximately 1–2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Pole - Wood | 2022-03-08 06:04 | 2022-01-13 10:10 | 2022-01-13 10:10 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_SL
c202742a-7b47-4bfc-8676-857fa05c45c1 | 8.015 | Dead-end cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | CDC0 | primary-level | Conductors - Primary | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | ED_POLE
c262427f-1036-4c4e-aad0-ff878375a02a | 14.003 | In contact with animal nest (Notification Required) | REMV ANIMNST SEC STLTPOLE | 0IZU | public-level | Risers/Terminations | 2022-03-08 06:04 |  |  |  |  | ED_SL
c2a0b457-9178-408a-a8df-c70d99c8137d | 2.006A | 1 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
c2bf5e74-c350-486f-aab1-9335a12fc536 | 8.015 | Pothead cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | CDC0 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | ED_POLE
c369acb2-ea2d-4ffc-bf42-d0688ba07ab6 | 2.003D | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
c37a9ef9-01d7-4288-8779-a89e05f599d3 | 7.004A | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
c381bc26-a91f-4f2b-b44e-e8845350db63 | 2.004A | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
c41615c5-6f5d-4936-8a11-d3228f8f47ab | 1.004 | Exposed decay pocket at ground line where part of shell is gone (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any listed conditions exist at base of pole.• Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | EZ_POLE
c438e6e4-4c68-4ff9-ad91-a1200ecea89e | 2.003A | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
c498d5f8-ea68-4a0e-9b13-d42469ed71c8 | 12.004 | Sagging or extreme slack (Notification Required) | REPAIR LOOSE SEC GUY POLE | CHL6 | secondary-level | Span Guys | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_POLE
c4c0dd0a-fc64-4651-b617-b8f40bde49ff | 2.007A | 8 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
c4c3e99b-726a-48f3-8a5d-e0f1f5797544 | 2.005B | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
c4f1bdd6-b647-4f13-8b8e-df431d11b689 | 14.003 | Non-Schedule 80 Riser installed (Notification Required) | REPLC DAMAGE SEC RISER POLE | CIJ8 | secondary-level | Risers/Terminations | 2022-03-08 06:03 | 2022-01-11 17:07 | 2022-01-11 17:07 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_POLE
c51760c3-c1a5-4d20-a46e-5f5dcccaeff1 | 2.006A | 16 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
c5ba458d-34a3-4376-b27a-93935fedcedb | 2.007A | 4 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
c63a9563-fbc9-4419-961a-db0015ff7885 | 7.004A | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
c66b6700-42bc-4090-b2c7-ada8dd8b8235 | 9.003 | Bare conductors and through tree (Notification Required) | TRIM VEG TREE SEC CBL/CND POLE | 044B | secondary-level | Conductors - Secondary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable conductor clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
c66f4784-5822-4867-85d4-e2d7af89f10b | 1.012 | Three or more holes approximately >2 inch diameter, within approximately 18 inches vertical of a through bolt (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Pole - Wood | 2022-03-08 06:03 | 2022-01-13 10:12 | 2022-01-13 10:12 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_SL
c749900c-8c04-4e5a-aeae-86103e9c8d06 | 7.004A | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
c7baeb23-2a87-405f-a25e-df77824e578e | 2.004A | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
c7e15af6-aa93-4f1f-b3ef-04238590ed22 | 2.003C | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
c8086f57-e59f-41df-8180-c26a1b2f488c | 2.003A | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
c85f700c-0aec-4f02-8f6b-f65cf70de4d6 | 7.004A | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
c8911ed4-3918-4b86-8f24-dbeebb7b1a02 | 9.003 | Immediate danger concerning palm fronds falling or blowing into conductors * (Notification Required) | TRIM VEG TREE SEC CBL/CND STLTPOLE | 481B | secondary-level | Conductors - Secondary | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
c94f2118-9af5-47cf-9ed7-0f2009b2d9b0 | 10.007 | Vegetation interfering with operation of apparatus equipment (Notification Required) | TRIM VEG TREE PRI POLE | C0F4 | primary-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:04 |  |  |  |  | ED_POLE
c9cec8f8-4816-40d3-8238-19c8463df641 | 2.003C | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
ca0c7e35-525b-4c32-bc39-c31a4cda6386 | 2.003C | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
ca151c62-0a76-4489-adf0-b9c133131b06 | 7.002A | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
cad10a0d-a2be-424d-9a6f-a3bc7855ae1b | 2.006A | 14 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
cb0adea1-31f2-4f5a-85bd-6a9e4ec19f86 | 2.003D | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
cb207e2f-cb8e-4984-85ed-c87e142cf324 | 7.002A | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
cb52c578-9962-4bec-8bc1-e5043c850f5d | 7.002A | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
cb65bea6-fca6-4f6f-9bad-f2a3a2cc3d6d | 9.004 | Conductors not in good condition, broken, missing (Notification Required) | REPLC DAMAGE SEC CBL/CND POLE | CWJ8 | secondary-level | Conductors - Secondary | 2022-03-08 06:04 |  |  | Identify if energized conductors and/or tie wires are damaged.• Select “No abnormal condition” if no damage is observed. | Create notification based on severity of issue. | ED_POLE
cb8d675f-9b48-4284-954f-b53a988dd88b | 13.001A | Anchor rods missing, pole not leaning (Notification Required) | REPLC MISSING PUBLIC ANCHOR POLE | 769A | public-level | Down Guys | 2022-03-08 06:04 | 2021-12-22 03:27 | 2021-12-22 03:27 |  | Create notification based on severity of issue. | EZ_POLE
cb97e8f7-f981-4801-993d-fea6c81a2e32 | 7.004A | 8 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
cbf72789-220a-4d35-b69d-3663df0ce354 | 2.003A | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
cc45b829-30c4-40f9-a501-8546973bb35e | 2.003C | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
cc6850bb-c980-4e72-b9d1-0b9624d4ec57 | 12.004 | Sagging or extreme slack (Notification Required) | REPAIR LOOSE PRI GUY POLE | CHI2 | primary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_POLE
ccc4f28e-63fe-4596-8099-75573ae0f20a | 2.006A | 7 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
ccdf89f3-63e3-4e44-a5f6-989cafc8fe16 | 2.006A | 12 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
cd307c88-bae7-4d51-80eb-13b4c685d65a | 1.002 | Exterior damage approximately 1–2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | primary-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
cd64d9a4-8c6c-410a-892a-c001582c931b | 7.002A | 17 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
cd763a14-21b9-4802-ae9a-00faf784af0c | 0.020B | No (Notification Required) | REPAIR CLEARNC PUBLIC POLE | 659A | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if the appropriate amount of climbing space per GO-95 is present on pole at this level. | Create notification if inadequate climbing space exist. | EZ_POLE
cd768508-c683-41ed-b958-96e124496921 | 15.004 | Tree condition causing significant strain and/or visible abrasion damage — either open wire or Triplex (Notification Required) | TRIM VEG TREE SERV CBL/CND POLE | 028B | secondary-level | Service Drops | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed clearance impairments are present on pole.• Select “No abnormal conditions” if no clearance impairment is identified on pole. | Create notification based on severity of issue. | EZ_POLE
cda8ba3f-8271-41e9-ac3d-d36eab5f0b0e | 1.008 | Crossarm (Potential Notification Required) | REMV ANIMNST PUBLIC POLE | 361A | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | EZ_POLE
cdb173a6-0f99-4bd3-98a2-120c2abea5c0 | 0.005A | No (Notification Required) |  | E2 | public-level | Poles - Steel | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | You have indicated that the pole number does not match, please create a corresponding E2 notification. | Make appropriate corrections in the field – replace pole number and/or map correction. | ED_POLE
cdc9175a-0feb-4c27-935e-6364e9098297 | 2.003C | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
ce1940c5-91d5-452f-bbfb-a5594c33e387 | 7.004A | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
ce861941-98a9-4ffd-a355-142815782f49 | 0.020B | No (Notification Required) | REPAIR CLEARNC COMM POLE | C0N0 | communication-level | Poles - Wood | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if the appropriate amount of climbing space per GO-95 is present on pole at this level. | Create notification if inadequate climbing space exist. | ED_POLE
ceb031e4-7ffd-44ab-bb5d-c68b69dd6431 | 12.002 | SCE energized components (Notification Required) | REPAIR CLEARNC SEC GUY POLE | 619A | secondary-level | Span Guys | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if span guy has the appropriate amount of clearance per GO-95 or could potentially contact the listed options.• Select “No abnormal condition” if span guys have appropriate clearance. | Create notification based on severity of issue. | EZ_POLE
cf296026-0193-492e-bebd-faf1bbecfe21 | 7.002A | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
cf5339ab-68d1-4a1b-91a1-e48a0d648ad6 | 2.006A | 15 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
cfa1bc31-2ff4-4f31-88e0-795b4a6128c0 | 2.003A | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
cfbbc8aa-ece3-4b71-8ad7-b4c4e7e39d3e | 5.001 | Depth of embedment less than 10% + 1 feet of the pole height (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
cfc4949a-a515-42e9-8667-def09a0ac43c | 2.004A | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
d020ecac-4afd-4b2d-882f-20b08d029a14 | 2.006A | 5 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
d073bac4-ccd3-4e60-a48a-651e71512a07 | 2.003C | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
d077f402-237d-4be7-a5f8-18512675941d | 8.015 | Connector cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | CDC0 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | ED_POLE
d09e0325-2a33-433a-bf86-de9b074c0cad | 7.004A | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
d0a326f5-59a6-4215-8b88-0ac848d30441 | 2.004A | 4 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
d11d184a-f27c-439e-9861-f415634ef662 | 2.004A | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
d129d81c-a73b-42de-a565-3b70f7efae8c | 2.003A | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
d1d9dca3-f312-4992-944d-a14103c281fb | 2.003D | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
d202c42e-183e-431b-bb6c-e4e21b29cb7e | 8.015 | Bare Tap (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | CDC0 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | ED_POLE
d26045a3-9c40-47c9-8e6f-71c5380b9ab8 | 2.003A | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
d2638c2d-f410-4de7-a11e-533f0af9c691 | 2.006A | 10 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
d275f3dc-ba98-4ad6-9063-c62f83537dec | 2.003D | 13 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
d2acc159-9c91-43c6-b467-9cd5f2f4c236 | 7.004A | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
d31f0c43-2e3f-49dc-9dc1-e040c59dade1 | 2.004A | 6 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
d33b35b9-bcba-47e8-81d2-7bc99055e021 | 2.007A | 10 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
d3593ad6-f7c0-41ba-8db3-d3268b54bcaf | 13.001A | Guys missing, pole not leaning (Notification Required) | REPLC MISSING PUBLIC GUY POLE | 724A | public-level | Down Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | EZ_POLE
d360d85b-f620-483e-9e21-4a8602dae3f3 | 2.006A | 20 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
d369480a-4c70-4f84-9a1f-04fd1de10249 | 14.002 | Pothead swollen (Notification Required) | REPLC DAMAGE PRI TERM POLE | CSE8 | primary-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
d40baadd-650b-4065-b553-103d70de8f2c | 2.003C | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
d4460ac5-8894-421c-81b3-c5dbf8dfd2f0 | 2.007A | 11 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
d45821ba-6c43-428a-8c20-82af5f03baf5 | 7.002A | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
d4604091-bea0-4d2e-aca6-1aa6981c7c02 | 2.007A | 20 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
d48d9730-a64c-4295-b9b5-ecd6d38c9daa | 14.003 | In contact with animal nest (Notification Required) | REMV ANIMNST SEC POLE | C0L8 | secondary-level | Risers/Terminations | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_POLE
d4b7ee7c-1cf9-4711-81a9-688cb9d24c93 | 1.012 | Exterior damage approximately 1–2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | EZ_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
d4f088e3-a5d9-4b8b-8590-fb3eb8c45986 | 6.006 | Missing parts (Notification Required) | REPLC LOOSE PRI INSLTR POLE | 962A | primary-level | Insulators | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
d504e216-baaa-4d92-b236-c68397ab0be9 | 2.003A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
d51cb146-0228-45eb-aece-40cbc215c350 | 2.005B | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
d53ea4d9-984c-44a6-930c-232aedcd766c | 2.003A | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
d57ac40a-6ffe-44e6-9f4c-a72c76ca8daf | 2.003C | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
d585921c-0b25-4eef-9d04-8e3bca41668a | 2.007A | 16 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
d6454e80-a3b1-4757-adb0-2ee1f71f431a | 7.004A | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
d6fc0a46-dd48-4727-b971-689f1de9a025 | 2.003D | 12 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
d728a051-4cd7-4a53-9034-718f3c770fc4 | 2.006A | 2 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
d79aa28c-b819-4f47-be60-20b9bb9a1940 | 1.002 | Hole approximately >2 inches near through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | primary-level | ED_POLE | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
d7a2c633-825e-46b2-ab0e-e440dcbafa8c | 2.003D | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
d7bfb5b7-36d2-47aa-9bfd-a2aaa1f170e0 | 2.003D | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
d7f88424-291b-40eb-9f17-3307a41c3ff0 | 2.007A | 10 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
d84ffc7a-9977-42ab-a295-5d9105adaa8b | 2.003A | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
d8e86f66-494b-4764-bf71-d025ed7fc797 | 2.003D | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
d906a5ab-62df-46d5-81b8-23071f978971 | 2.003D | 9 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:05 |  |  |  |  | ED_POLE
d908d85f-50d6-433e-a041-471473719f79 | 2.004A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
d92e9ec7-3ee5-4f06-8368-0b19bea4e823 | 2.006A | 19 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
d9cba7f7-a3e8-4a29-8d42-a1e9fda6acca | 7.004A | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
d9f32393-72be-4ca5-95cd-025dd4930743 | 2.005B | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
da02823a-0b85-4f5c-bbc5-088897405c8c | 7.002A | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
da164a2a-ef38-4e36-bd75-6d154bb6e8b7 | 1.002 | Exterior damage approximately 1–2 inch depth and approximately >1/4 pole circumference (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | communication-level | EZ_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
da29fba7-438b-41b3-9c38-ac6763f0bb32 | 7.004A | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
da46dc50-abe8-402b-ad8a-0479a7e1e6ff | 17.003 | Damage to anchor bolts or foundation (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Pole - Steel | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
da855fc3-9d02-4a52-bab9-8d926c7c7a69 | 7.004A | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
da9a85d5-ea22-41a6-838a-98458522358c | 2.006A | 8 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
db1e31df-a1a9-4af7-b646-14a6738ca875 | 7.004A | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
db3181d5-41c2-4179-a100-f7a02511fc09 | 2.004A | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
db364edb-c4bb-4fa1-a50d-c7dbf003ee93 | 2.003D | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:05 |  |  |  |  | EZ_POLE
dc2c0e84-633a-4811-9880-f447f6a8ec82 | 0.024 | Contamination from SCE equipment (Notification Required) | REPAIR DAMAGE PUBLIC POLE | 660A | public-level | Poles - Wood | 2022-03-08 06:03 |  |  | Identify if any of the listed defects are present on or around the structure.• Select “No abnormal condition” if no listed condition options are present. | Create notification if condition type is severe and warranted. | EZ_POLE
dc749714-a3ee-41ab-8b52-3682a6e89500 | 2.003C | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
dc9b8123-face-4956-8738-886fe9489473 | 2.003A | 19 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
dcd5ff82-213d-488c-ac27-a8fa2b4948e9 | 6.003 | Insulator squatting (Notification Required) | REPLC FLOTR/SQTR PRI INSLTR POLE | B795 | primary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
dcd89507-4ce7-4dac-9f6a-4270e2b0c92f | 2.003D | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
dd676909-46a8-40f1-a1f3-f80fb36e3615 | 2.003D | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  | NULL | NULL | ED_POLE
dd69860d-5b27-43e8-8536-a91a18808b9c | 2.003D | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
dd7ac538-5d6f-40b2-9ba0-98bca9e6598a | 2.003C | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
ddfba0d1-193c-42d5-a34a-dd6f930480ab | 2.003A | 17 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
de2f03d6-340e-4a90-babb-ed5a1e373dfc | 13.001A | Anchor rods missing, pole leaning, public hazard (Notification Required) | REPLC MISSING PUBLIC ANCHOR POLE | COB1 | public-level | Down Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | ED_POLE
de4f0380-42d2-46b9-a974-156408857b2f | 3.002 | Visibly loose hardware (Notification Required) | REPLC LOOSE PRI HWARE/FR XFMR-D | DDI1 | primary-level | ED_XFMR | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
deaf4233-cbc5-48ef-9435-f275720ba682 | 0.026B | Yes and clearance between conductors appears to be less than 12 inches (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:03 |  |  | Identify if rolling and transposing conductor has at least 12” of clearance between primary conductors/phases. | Create notification if primary conductor clearance is <12”. | ED_POLE
defcaa37-6e0c-4305-9e0b-1613fbc54daa | 13.001A | Anchor rods broken/corroded, pole not leaning (Notification Required) | REPLC DAMAGE PUBLIC ANCHOR POLE | 768A | public-level | Down Guys | 2022-03-08 06:05 | 2021-12-22 03:27 | 2021-12-22 03:27 |  | Create notification based on severity of issue. | EZ_POLE
df0db325-48a7-4a7a-b164-81cc28112cba | 2.003C | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
df2a38c1-c373-4dcc-b9f2-dab5e9dbce95 | 8.002B | Conductor located above a building, and is vertically less than 12 feet from top surface of building (commonly roof) (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable energized conductor- structure clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
dfa41cc1-8ffe-4d4b-90a4-62ea36a96e0a | 8.016 | Down guy (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there is a possibility of primary conductors/phases clashing and/or public can contact.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearances. (Ex. Extreme condition should result in P1 notification). | ED_POLE
dfcee5b4-afc6-4deb-ac34-5498c15a7fb2 | 2.004A | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
dfe9c922-f8a5-4796-b068-dbc0463459d3 | 2.004A | 14 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e0081db7-7b9c-42d7-a781-45b32007529a | 14.001 | Porcelain pothead insulators chipped or broken (Notification Required) | REPLC DAMAGE PRI TERM POLE | 778A | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
e021900d-e4f4-41fe-8f5d-1f2de0868633 | 12.002 | SCE non-energized electrical components (Notification Required) | REPAIR CLEARNC PRI GUY POLE | CHF2 | primary-level | Span Guys | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if span guy has the appropriate amount of clearance per GO-95 or could potentially contact the listed options.• Select “No abnormal condition” if span guys have appropriate clearance. | Create notification based on severity of issue. | ED_POLE
e061b2a8-93b7-4335-b50e-04702f1c9506 | 2.005B | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  | Count all crossarms at this level that are tracking. | Create notification and prioritize based on severity of issue. | EZ_POLE
e07367e1-ba3c-4b7d-ba67-a7c6a19cec52 | 2.005B | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e07f5d86-e77b-427b-bf0f-b7ede2c3fcc3 | 2.005B | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e0a56736-6b6c-4021-b180-db7c2b634bb5 | 2.003C | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
e0e33a47-9a5b-4661-998e-449ce0b2fbdb | 3.002 | Signs of burn (Notification Required) | REPLC DAMAGE PRI XFMR-D | D0E8 | primary-level | ED_XFMR | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
e11866fc-fbef-459d-8b2c-1faaf82bea4f | 2.006A | 19 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e12c0a09-481e-4c1e-bdf9-feb383c89cfb | 2.006A | 3 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e1667f75-8907-4dcf-b313-ea544837f4d5 | 9.004 | Tie wire broken/missing/damaged or loose (Notification Required) | REPLC DAMAGE SEC CBL/CND POLE | 763A | secondary-level | Conductors - Secondary | 2022-03-08 06:04 |  |  | Identify if energized conductors and/or tie wires are damaged.• Select “No abnormal condition” if no damage is observed. | Create notification based on severity of issue. NOTE: ESI will have to indicate tie wire | EZ_POLE
e17071b3-c6e1-4905-bb2a-089bf740e5ef | 2.003D | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | EZ_POLE
e17203d8-7833-4455-9125-8e9c3b22cd70 | 7.002B | Significant visual buckling (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e17d8620-b2d0-4cce-86c2-7a04b53271b9 | 5.005 | Switch (Notification Required) | REMV ANIMNST PUBLIC POLE | 361A | public-level | Poles - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | EZ_POLE
e18e1db7-2514-4662-8c97-c8f5ebc0f5dc | 2.006A | 2 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e1969030-2966-47eb-b0fb-94446f17641a | 2.007A | 6 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
e1a13e9c-0b90-4e23-8360-19f9eb5aae84 | 6.006 | Missing parts (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | secondary-level | Insulators | 2022-03-08 06:04 |  |  |  |  | ED_SL
e25cbcaf-81a6-49f4-81a1-a1cb3dcb688a | 11.002 | Yes (Notification Required) | REPLC DAMAGE PRI CUT/FUS POLE | 718A | primary-level | Fuses | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if there is any evidence that primary fuse holders are burning or tracking. | Create notification based on severity of issue. | EZ_POLE
e2af992c-0102-480e-a226-2af11e7131b4 | 7.006 | Missing bonding wire under crossarm for 12kV and higher (Notification Required only if crossarm does not require replacement) | REPLC MISSING PRI BOND POLE | CNC0 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2022-01-07 12:45 | 2022-01-07 12:45 | If the crossarm is damaged and requires a notification, changing the cross arm will remediate the bonding issue | If the crossarm does not need to be replaced and the bonding wire is missing or damaged use one of the above listed bond problem statements: REPLC DAMAGE PRI XARM POLE, REPLC MISSING PRI BOND POLE, REPLC DAMAGE PRI BOND POLE | ED_POLE
e2cafdd3-ffd4-468b-ac1e-ef383f9dd867 | 13.001A | Anchor rods broken/corroded, pole leaning, public hazard (Notification Required) | REPLC DAMAGE PUBLIC ANCHOR POLE | 768A | public-level | Down Guys | 2022-03-08 06:05 | 2021-12-22 03:27 | 2021-12-22 03:27 |  | Create notification based on severity of issue. | EZ_POLE
e2d5c3da-90d0-4c77-955f-f96e9a3a3e29 | 0.024 | Contamination from SCE equipment (Notification Required) | REPAIR DAMAGE PUBLIC POLE | C0P7 | public-level | Poles - Wood | 2022-03-08 06:03 |  |  | Identify if any of the listed defects are present on or around the structure.• Select “No abnormal condition” if no listed condition options are present. | Create notification if condition type is severe and warranted. | ED_POLE
e2eed60c-9d82-494f-b517-fc7c02ef997f | 18.003 | Fracture or buckling of exterior wall (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Pole - Concrete | 2022-03-08 06:04 |  |  |  |  | ED_SL
e2f941c2-fbea-404b-8639-419444cff601 | 0.029 | Inadequate clearance between communication equipment or structures and SCE electrical equipment or structures (Notification Required) | CIP CLEARNC COMM POLE | 0IAG | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e30c4c33-6aaf-4949-970b-1d3a2d64bf7c | 3.002 | Brackets damaged (Notification Required) | REPLC DAMAGE PRI HWARE/FR XFMR-D | DDE8 | primary-level | ED_XFMR | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
e38144e2-284f-41c5-b353-28ad38b7bafd | 2.003A | 9 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
e3971c0a-25fe-43ce-a0f5-6308878118f2 | 8.015 | Equipment bushing cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | 983A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | EZ_POLE
e3a21fbf-4130-4e13-9a11-b036af41f14d | 2.007A | 4 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
e3a3501a-43c5-4765-9d08-38509f4fb43b | 2.003C | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
e3b229c2-a5dd-43b1-a931-10031affc622 | 2.004A | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e41c2236-700d-485c-afa0-d68712db7713 | 2.004A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e44ee76c-62d1-4ad8-9a49-2830babe665b | 14.001 | Pothead leaking (Notification Required) | REPLC LEAKING PRI TERM POLE | C545 | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
e457ef8c-71b3-439d-abef-c64d60c17d77 | 6.006 | Missing parts (Notification Required) | REPLC LOOSE PRI INSLTR POLE | CFI1 | primary-level | Insulators | 2022-03-08 06:04 |  |  |  |  | ED_POLE
e45b2f13-e897-4a04-a4c1-1c74cef1ea0e | 8.015 | Connector cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | 983A | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | EZ_POLE
e4f9ab65-e05d-4f8d-a966-7b8d1ee2055f | 14.002 | Pothead not properly attached to supporting structure (Notification Required) | REPLC DAMAGE PRI TERM POLE | 778A | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
e521a759-986e-4935-9b5b-1c7a1280619e | 10.007 | Vegetation interfering with operation of apparatus equipment (Notification Required) | TRIM VEG TREE SEC POLE | C0K4 | secondary-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:03 |  |  |  |  | ED_POLE
e5292741-6780-4801-b8ba-2991fcb6a6c5 | 2.005B | 16 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e56cad2c-fdb1-4224-8d1e-ff548d31724c | 2.003D | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:03 |  |  |  |  | ED_POLE
e5bfe235-49f8-4ad2-a7ae-228d950e1a18 | 5.001 | Visual cracks or rupture of exterior laminates or exterior wall exposing interior (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e5f4d0e7-d3fc-43ba-8655-727f953ccdd1 | 7.002B | Significant visual fracturing (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e6969a00-4a5b-4ecc-827b-048d309204dc | 2.006A | 13 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e6995bcf-d550-40c9-a626-b6d47f7bc031 | 2.003A | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
e6a19359-30fa-4efe-b9b0-b2e6b760711d | 9.012 | Foreign objects (Notification Required) | REMV UNATH ATT SEC CBL/CND POLE | CWK6 | secondary-level | Conductors - Secondary | 2022-03-08 06:05 | 2021-12-23 17:45 | 2021-12-23 17:45 |  |  | ED_POLE
e6a9fb3f-b226-4b38-a096-0299812249ab | 8.015 | Fuse cover (Notification Required) | REPLC MISSING PRI HWARE/FR POLE | 983A | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | If primary covered conductor exists on pole, validate all provided options are properly installed per SCE standards, or select “no missing covered conductor cover” if all construction standards are correct. | Create notification for any violation of SCE covered conductor construction standards. | EZ_POLE
e7013f3d-6278-4d16-8f3e-2b415a4ddeb4 | 2.003D | 7 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
e72b0e36-9a49-4098-acd9-fbe537dec714 | 14.003 | In contact with animal nest (Notification Required) | REMV ANIMNST SEC STLTPOLE | 0IZU | secondary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
e72f38c6-91ad-4570-8701-811c7afcfdd8 | 7.004A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
e72ffc35-be15-42cf-b37a-df000a3f1825 | 10.006 | Yes (Notification Required) | TRIM VEG TREE COMM POLE | C0N2 | communication-level | Reclosers, PE Gear, Regulators, and Switches | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if vegetation is currently or will interfere with operation of primary equipment. | Create notification based on severity of issue. | ED_POLE
e7a7e1e7-9eac-40e0-aae8-ab7f31d231ca | 2.004A | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e7ab3fb5-a3e3-4ef3-bfac-7c5bf8a43eb4 | 14.003 | Riser swollen (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | public-level | Risers/Terminations | 2022-03-08 06:03 |  |  |  |  | ED_SL
e7c8c176-939f-4ec5-bfc3-e49f47cc9b1b | 2.006A | 20 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e7d40fb0-8e5c-413d-9826-6bc80286eb83 | 2.006A | 7 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e7e0d5f9-1565-4648-beec-eca469a1a766 | 6.006 | Top/Side tie insulator touching crossarm (Notification Required) | REPLC FLOTR/SQTR PRI INSLTR POLE | B795 | primary-level | Insulators | 2022-03-08 06:03 |  |  |  |  | ED_POLE
e7fac8cb-6f47-4dea-8e77-844243c589b0 | 3.002 | Scott brackets fiberglass pads present (Notification Required) | REPLC SPECIAL PRI XFMR-D | YY01 | primary-level | ED_XFMR | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
e815b1d0-c4e7-4083-b3da-50b1403a6c55 | 8.016 | Encroachment bare secondary conductor with span/down guy (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there is a possibility of primary conductors/phases clashing and/or public can contact.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearances. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e8237779-0090-4d85-84ad-52e7d9df5dfc | 2.004A | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e8255b6c-b167-48a7-a7f7-4b5556e920d6 | 2.006A | 18 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | 990A | primary-level | Crossarm | 2022-03-08 06:05 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e8734998-5f44-47db-a021-51560ef13d4e | 2.005B | 1 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e87e5b70-d3a8-443e-8b62-032475718979 | 7.004A | 20 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
e8ad92b3-f36f-4e57-8c00-0e1eedbfdf5a | 2.004A | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e8c891e4-0267-46b0-9de1-359c2645db42 | 7.004A | 19 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
e8ee4a82-7293-4171-bfe2-019c8230021d | 11.004 | Corroded, missing, broken or bending hardware (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Hardware/Framing | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_POLE
e95b82e8-8d42-486a-bb95-6e2c76da317c | 2.003D | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
e9872c5b-89e3-436d-a7b2-6d0448c234d6 | 2.003B | Crossarm bowed approximately >5 inches without splintering (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bowed/twisted crossarm(s).Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bowed/twisted crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e996b75f-31d7-4eaf-af31-ae5a6c21df1f | 8.002B | Conductor located above a building, and is vertically less than 12 feet from top surface of building (commonly roof) (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable energized conductor- structure clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
e99a3163-97cf-4045-aa6b-1f8d2dd9786c | 2.003D | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:05 |  |  |  |  | EZ_POLE
e9b5f136-0fef-45d9-bf5f-544cc6b83dc7 | 2.006A | 17 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
e9e2da25-bd91-4569-94a7-7e9ca2e05b5b | 2.006A | 11 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
e9f7eb2a-f145-4b04-b231-25f8ba0747a4 | 3.002 | Blown fuse (Notification Required) | REPLC DAMAGE PRI CUT/FUS POLE | CLE8 | primary-level | Cutout/Fuse | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
ea16b7f7-9b5c-41b1-85d5-3d6b1023998a | 14.001 | Pothead not properly attached to supporting structure (Notification Required) | REPLC DAMAGE PRI TERM POLE | CSE8 | primary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any issues present on the Potheads.• Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | ED_POLE
ea1799a9-786a-4a05-9a1e-046de55e9d3d | 2.005B | 7 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
ea3aeb26-dd35-43f9-a77d-7e8ea3d017c2 | 8.018 | Bare wire (If bare, will need to be covered with split tube) (Notification Required) | REPAIR DAMAGE PRI CBL/CND POLE | CWE9 | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | For covered conductor installations only, determine if the proper jumper/tap insulation is installed on ALL jumpers/taps. | Create notification if ANY jumper/tap does not have the proper insulation. | ED_POLE
eadef7da-c411-4358-81a0-d81ffa999ff9 | 2.003A | 3 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
eb15c8fa-b980-4e70-a471-6fba38d71b3e | 1.002 | Three or more holes approximately >2 inch diameter, within approximately 18 inches vertical of a through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | secondary-level | ED_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
eb69e98e-efbb-4322-83fc-70e0019985e6 | 9.003 | Immediate danger concerning palm fronds falling or blowing into conductors * (Notification Required) | TRIM VEG TREE SEC CBL/CND POLE | 044B | secondary-level | Conductors - Secondary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable conductor clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | EZ_POLE
eb78c295-aa5a-4557-97b6-3ada95680427 | 7.004A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | EZ_POLE
ebba40a8-6d49-47b2-b0fe-4c6355386151 | 2.003A | 11 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
ebe967f5-a09d-4056-932f-42da8fe277d8 | 14.003 | Riser swollen (Notification Required) | REPLC DAMAGE SEC RISER POLE | 735A | secondary-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | EZ_POLE
ec0b825f-6498-42d0-a606-3414785b424d | 0.029 | Excessive bowing or bending of pole from potential overloading at communication attachment points (Notification Required) | CIP CLEARNC COMM POLE | 0I5G | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
ed1532f6-009d-4d04-8029-e0c40d9709e8 | 14.002 | Porcelain pothead insulators chipped or broken (Notification Required) | REPLC DAMAGE PRI TERM POLE | 778A | primary-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the Potheads.Select “no abnormal conditions” if no issue with pothead OR no pothead is present on pole. | Create notification based on severity of issue. | EZ_POLE
edcbab5e-2a03-4416-9b0a-4fc75b4482ea | 2.005B | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
ee2001b5-a3ba-48cc-bdce-1df674732ede | 6.003 | Insulator broken (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | ED_POLE
ee8056fa-6d35-48c7-af2d-2a738ea47e3e | 14.003 | Riser swollen (Notification Required) | REPLC DAMAGE SEC RISER POLE | CIJ8 | secondary-level | Risers/Terminations | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_POLE
eeb5fe91-7127-4c7b-9a2f-7d4ad125f38e | 0.029 | Excessive sag of communication cables (Notification Required) | CIP CLEARNC COMM POLE | 0I5G | communication-level | Poles - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
eeeca17e-3aff-4b2c-8908-e3f69ee915f5 | 13.001A | Guys missing, pole leaning, public hazard (Notification Required) | REPLC MISSING PUBLIC GUY POLE | 724A | public-level | Down Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify if any of the listed down guy damages are present.Select “No abnormal condition” if no conditions are identified. | Create notification based on severity of issue. | EZ_POLE
ef0808f9-c7c0-4a6c-b654-b3e4e9c285e4 | 2.003A | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
efc2a0e6-1641-443e-af05-2320cd45278f | 2.003C | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
efc783b4-6026-4da2-9df7-c1aecd7b2db3 | 1.012 | Three or more holes approximately >2 inch diameter, within approximately 18 inches vertical of a through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | EZ_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
efd67ca7-c65a-42f0-8d4a-c2c6011e7317 | 3.002 | Signs of swelling (Notification Required) | REPLC DAMAGE PRI XFMR-D | D0E8 | primary-level | ED_XFMR | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any issues present on the transformer(s). | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_XFMR
efe86f6f-63ca-44b9-9f68-db434844a170 | 2.003C | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
efe873b4-e51b-4b78-84bb-d86c7cbff3ae | 8.018 | PGW (Notification Required) | REPAIR DAMAGE PRI CBL/CND POLE | CWE9 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | For covered conductor installations only, determine if the proper jumper/tap insulation is installed on ALL jumpers/taps. | Create notification if ANY jumper/tap does not have the proper insulation. | ED_POLE
f002ed39-4f84-44cf-ae88-ad32fb3ebb24 | 2.004A | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
f0dd64bf-62af-4acd-9581-85bb29163ce5 | 2.003C | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
f0f353f8-aace-4fff-b1b3-ba4eaafe2a96 | 7.004A | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:05 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
f12aa2b4-aade-4d5f-ab4e-fb0cd6826edc | 15.004 | Mid-span service clearance not maintained (Notification Required) | REPAIR CLEARNC SERV CBL/CND POLE | 486A | secondary-level | Service Drops | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed clearance impairments are present on pole.• Select “No abnormal conditions” if no clearance impairment is identified on pole. | Create notification based on severity of issue. | EZ_POLE
f13d367a-c97c-4163-b401-01c6f49b16ea | 2.003D | 16 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
f14aac27-f4e8-41a5-bcdb-d509eb309fec | 2.007A | 12 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
f1805671-f6de-440f-aec8-eeb203f8586a | 2.007A | 18 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | CFJ8 | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
f1d31c3c-1066-432d-8b34-bbefeb2a8e4e | 2.007A | 12 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
f2014d6f-7ad3-428d-9e36-6cc62ee5d3c6 | 2.003C | 20 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | ED_POLE
f2084374-7c1e-4d55-9fc5-f14954175e08 | 2.006A | 10 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
f22e15d2-995d-493e-aedd-6f14b5ad5403 | 6.003 | Tie wire broken/missing/damaged or loose (Notification Required) | REPLC LOOSE PRI INSLTR POLE | 962A | primary-level | Insulators | 2022-03-08 06:03 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
f27e829c-3b3c-444f-9dde-70eae9345e54 | 2.003A | 5 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
f2a0258a-8a2e-42c1-9189-35e8520bc9be | 8.016 | Slack primary conductor (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there is a possibility of primary conductors/phases clashing and/or public can contact.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearances. (Ex. Extreme condition should result in P1 notification). | ED_POLE
f2a302dc-2725-4c5b-99d9-4f2aa43f18fc | 2.007A | 8 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
f2b8b5e4-9d4a-4924-bb3f-4c961ca0b183 | 2.007A | 17 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
f2cb9840-8c28-4b16-8765-f8b42c0d23f7 | 2.005B | 8 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
f2e20f7c-3a19-4836-8ed3-eeda2c79a235 | 14.003 | Riser broken (Notification Required) | REPLC DAMAGE SEC RISER POLE | CIJ8 | secondary-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | ED_POLE
f3035f73-269d-468f-8a29-7f8177dc6c79 | 0.029 | Broken, damaged or severely strained communication guy wires (Notification Required) | CIP CLEARNC COMM GUY POLE | 0IBR | communication-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | SCE is required to inspect communications facilities and is responsible to ensure communication facilities do not threaten safety to the public and/or reliability.Examine all communication equipment and conductors associated with structure and determine if any of the listed conditions exist. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
f3849272-f8fc-4851-9f26-a5bf09416f74 | 2.003D | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:05 |  |  |  |  | EZ_POLE
f3cfe900-b568-405f-8a32-690dd7b223a2 | 13.001B | Yes (Notification Required) | REPAIR CLEARNC SEC GUY POLE | 619A | secondary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if guy wire(s) have contacted or will contact energized conductors. | Create notification based on severity of issue. | EZ_POLE
f3e616ea-bda5-42b8-804f-8f2fe87bb16f | 2.007A | 18 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
f41334da-daae-4eaa-b2c5-67663b9179c5 | 7.002B | Significantly unbalanced due to tension (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
f43d0528-eb62-4bf7-8c56-2a76a049ff7e | 1.002 | Hole approximately >2 inches near through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | C0P6 | communication-level | ED_POLE | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
f45b8869-908a-4cfe-a90d-47129a5fdec1 | 11.005 | Streetlight brackets damaged (Notification Required) | REPAIR DAMAGE SEC STLTPOLE | 469B | secondary-level | Streetlight | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | ED_SL
f48dbf6b-f763-42a1-afab-039cb5fba1f7 | 7.002A | 18 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
f4a0ba67-ecae-4336-bda3-ef0db26b324b | 6.003 | Tie wire broken/missing/damaged or loose (Notification Required) | REPLC LOOSE SEC INSLTR POLE | 956A | secondary-level | Insulators | 2022-03-08 06:04 |  |  | Identify the type of insulator damage at this level. | Create notification based on severity of damage. | EZ_POLE
f52a89ab-f451-46e5-b44e-34d092ad9519 | 7.006 | Damaged bonding wire under crossarm for 12kV and higher (Notification Required only if crossarm does not require replacement) | REPLC DAMAGE PRI BOND POLE | CNE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 |  |  | If the crossarm is damaged and requires a notification, changing the cross arm will remediate the bonding issue | If the crossarm does not need to be replaced and the bonding wire is missing or damaged use one of the above listed bond problem statements: REPLC DAMAGE PRI XARM POLE, REPLC MISSING PRI BOND POLE, REPLC DAMAGE PRI BOND POLE | ED_POLE
f5ad2e8b-961b-4f23-ba9d-34eec92f4947 | 2.007A | 7 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | 960A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
f5e43dd6-fbfa-482f-aca3-ca4d59ba8593 | 2.006B | Braces broken (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm - Wood | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of crossarm brace damage. | Create a notification based on severity of damaged crossarm brace(s)’ identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
f66bdf6a-8950-47db-8728-aaee32972a73 | 2.007A | 5 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
f675e580-65fe-42cb-843b-7df276c969f8 | 8.018 | Bare wire (If bare, will need to be covered with split tube) (Notification Required) | REPAIR DAMAGE PRI CBL/CND POLE | 516A | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | For covered conductor installations only, determine if the proper jumper/tap insulation is installed on ALL jumpers/taps. | Create notification if ANY jumper/tap does not have the proper insulation. | EZ_POLE
f696ee06-35a9-4f98-ad8a-bdc20404e63c | 2.005B | 2 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
f6b95622-09f6-4b89-8be6-63de52845fb7 | 2.007A | 13 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
f6ce7d54-bc93-4966-860e-eaa838fbfe3e | 2.003D | 2 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
f70cd417-0148-49cf-a111-7720e8c286c4 | 2.003C | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are deteriorated. | Create notification and prioritize based on severity of issue. | EZ_POLE
f7326efa-941a-4071-990c-b1b7a7aa5b7f | 2.006A | 18 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | CDJ8 | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
f76a5a58-78ba-4ef0-8866-8535e8ea215d | 2.003A | 14 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
f7968a08-7807-49ab-b37f-a592ef9431dd | 0.024 | Contamination from SCE equipment (Notification Required) | REPAIR DAMAGE PUBLIC STLTPOLE | 473B | public-level | Streetlight Only Poles - Wood | 2022-03-08 06:03 |  |  | Identify if any of the listed defects are present on or around the structure.• Select “No abnormal condition” if no listed condition options are present. | Create notification if condition type is severe and warranted. | ED_SL
f7995ed4-ba7e-481b-a885-6b24ccbb35de | 7.004A | 6 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
f7b86271-3ef9-46dd-aefd-1f6aa1599e2a | 2.004A | 11 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
f7bc6d15-65a7-4c48-9acd-2459483bf5f6 | 14.003 | In contact with animal nest (Notification Required) | REMV ANIMNST PUBLIC POLE | 361A | public-level | Risers/Terminations | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if any of the listed primary/secondary riser conditions are present.• Select “no abnormal conditions” if no issue with installed riser OR no riser is present on pole. | Create notification based on severity of issue. | EZ_POLE
f86bd781-703c-40ec-8844-27b95731ea23 | 2.003A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
f8849210-d52f-4517-8703-d1542ecd0659 | 7.002A | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
f8d43e23-7505-4c23-b32a-809a8036affa | 7.002B | Significantly unbalanced due to tension (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify the type/severity of bending crossarm(s).• Select “no abnormal condition” if no crossarms are bowed/twisted. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
f919e8b6-3346-4055-a108-789ce4c92fe8 | 2.004A | 5 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
f97ff121-ac6e-49a2-b2b7-cfd5d79e6bad | 2.003D | 15 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | ED_POLE
f98853fc-145a-43e4-8716-d0586a90b7af | 7.004A | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
f99f2ac2-7391-4965-9f52-9fcc2ad42e13 | 1.012 | Hole approximately >2 inches near through bolt (Notification Required) | REPLC DAMAGE PUBLIC POLE | 924A | public-level | EZ_POLE | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
fa02f844-3e59-4b44-89c3-a67c37a4e37b | 2.007A | 20 (Notification Required) | REPLC DAMAGE SEC INSLTR POLE | 955A | secondary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | EZ_POLE
fa1f7a13-f0cc-4f60-b352-59051ada91c9 | 1.008 | Switch (Notification Required) | REMV ANIMNST PUBLIC POLE | C0T5 | public-level | Poles - Wood | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify if animal nests are present on any of the listed pieces of equipment.• Select “No animal nest observed” if no animal nests are present at pole. | Create notification based on severity of issue. | ED_POLE
fa543baa-929f-4761-ad78-eca12af73c74 | 2.003A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
fa75e8ef-12f7-4870-af76-67da279e18ee | 2.003D | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 |  |  |  |  | EZ_POLE
fa78011d-f276-4f03-ab07-5f9b3ebaa23e | 2.004A | 18 (Notification Required) | REPLC DAMAGE SEC XARM POLE | 912A | secondary-level | Crossarm | 2022-03-08 06:03 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
fad0eefd-11c1-4302-9620-76ee478a404f | 9.004 | Conductors not in good condition, broken, missing (Notification Required) | REPAIR DAMAGE SEC CBL/CND STLTPOLE | 467B | secondary-level | Conductors - Secondary | 2022-03-08 06:04 |  |  | Identify if energized conductors and/or tie wires are damaged.• Select “No abnormal condition” if no damage is observed. | Create notification based on severity of issue. | ED_SL
fad6a45a-d4f6-4028-98d7-50e3147abde7 | 2.004A | 10 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are canted. | Create a notification based on severity of canted crossarm(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
fadf1d8d-2095-479e-8528-c61833ed1c3e | 2.003A | 10 (Notification Required) | REPLC DAMAGE SEC XARM POLE | CEJ8 | secondary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
fb5ba5ad-9ca8-474f-8da0-ca545c44c2b5 | 2.003A | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Wood | 2022-03-08 06:05 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | ED_POLE
fb99c8da-53a5-494a-a5eb-7536d3d49058 | 2.005B | 1 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are tracking. | Create a notification based on severity of tracking crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
fbd0b6b0-858e-457c-943f-74ae49a7ea30 | 2.003A | 4 (Notification Required) | REPLC DAMAGE PRI XARM POLE | 916A | primary-level | Crossarms - Wood | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count all crossarms at this level that are bowed/twisted. | Create notification and prioritize based on severity of issue. | EZ_POLE
fcefbd65-b4b6-40c1-96d5-fe1525a84b2d | 2.006A | 5 (Notification Required) | REPLC DAMAGE SEC HWARE/FR POLE | 980A | secondary-level | Crossarm | 2022-03-08 06:04 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
fd413ba6-9c90-4043-a5ae-5175d1cf1c7a | 8.002B | Less than 6 feet horizontally between conductor and any surface of a building (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | CWF2 | primary-level | Conductors - Primary | 2022-03-08 06:03 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable energized conductor- structure clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
fd6f4ed5-c47d-4ce3-b64b-d1709174135f | 2.006A | 13 (Notification Required) | REPLC DAMAGE PRI HWARE/FR POLE | CDE8 | primary-level | Crossarm | 2022-03-08 06:03 |  |  | Count number of damaged/missing crossarm braces at this level. | Create a notification based on severity of damaged crossarm(s) braces identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
fd992dad-0527-4aab-b001-53b805919e5a | 1.002 | Hole approximately >2 inches near through bolt (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | secondary-level | Streetlight Only Pole - Wood | 2022-03-08 06:04 |  |  | Identify any of the listed structure failures that are present. 1. Select “no abnormal conditions” if no structural failures present on pole. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_SL
fde0c6e8-bf20-4de0-856c-a0b9faa9e605 | 2.007A | 15 (Notification Required) | REPLC DAMAGE PRI INSLTR POLE | CFE8 | primary-level | Crossarm | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 | Count the number insulators that are not in good condition/do not pass inspection (damaged, flashed over, missing hardware, or missing).• Select “0” if all insulators are in good condition/pass inspection. NOTE: Notification required if answer is greater than 0. | Create notification based on severity of insulator(s) damage. | ED_POLE
fdf3580f-1149-4171-a817-ba1db41c273a | 7.004A | 3 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
ff1893d0-9388-4159-9478-1864e6bae92e | 12.004 | Sagging or extreme slack (Notification Required) | REPAIR LOOSE SEC GUY POLE | 399A | secondary-level | Span Guys | 2022-03-08 06:04 | 2021-11-22 06:26 | 2021-11-22 06:26 |  |  | EZ_POLE
ff3264a2-af3a-4f8e-8a1a-e55066f0c685 | 9.003 | Immediate danger concerning palm fronds falling or blowing into conductors * (Notification Required) | TRIM VEG TREE SEC CBL/CND POLE | CWK4 | secondary-level | Conductors - Secondary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Identify any applicable conductor clearance issues.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearance issue. | ED_POLE
ff341c3e-9605-4db5-a13d-d1c2a6472759 | 7.004A | 13 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count the number of crossarms at this level that are physically damaged. | Create notification based on severity of crossarm damage. | ED_POLE
ff5ffd41-f2c4-413e-aa85-a3d99413c074 | 8.016 | Span guy (Notification Required) | REPAIR CLEARNC PRI CBL/CND POLE | 514A | primary-level | Conductors - Primary | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Determine if there is a possibility of primary conductors/phases clashing and/or public can contact.• Select “No abnormal conditions” if no clearance issue exist. | Create notification based on severity of clearances. (Ex. Extreme condition should result in P1 notification). | EZ_POLE
ffc2cc74-23ab-4c6c-983d-bd9ca706ff66 | 1.012 | Hole approximately >2 inches near through bolt (Notification Required) | REPLC DAMAGE PUBLIC STLTPOLE | 479B | public-level | Streetlight Only Pole - Wood | 2022-03-08 06:03 | 2022-01-13 10:12 | 2022-01-13 10:12 | Identify any of the listed structure failures that are present. | Create a notification based on severity of condition(s) identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_SL
ffdfefa5-4e96-4a5d-852c-7f0fd1b57bc5 | 7.002A | 15 (Notification Required) | REPLC DAMAGE PRI XARM POLE | CEE8 | primary-level | Crossarms - Composite | 2022-03-08 06:04 | 2021-11-22 06:25 | 2021-11-22 06:25 | Count all crossarms at this level that are bending. | Create a notification based on severity of bending crossarm(s) condition identified on pole. (Ex. Extreme condition should result in P1 notification). | ED_POLE
| 4.002 | Indicate if any of the following types of capacitor bank oil leakage or weepage are observed. Select all that apply