## Weekly Log
Weekly Weather Network Performance Log
Date | #CellComOut | TotalStations | % In Comm | Status/Known Issues
2017-04-21 | 12 | 171 | 93% | 1 long term unresolved cell service, 2 due to W2S, 4 ATT 2G shutoff, 5 LS300 failures
2017-04-28 | 12 | 171 | 93% | 1 long term unresolved cell service, 2 due to W2S, 4 ATT 2G shutoff, 5 LS300 failures
2017-05-05 | 12 | 171 | 93% | 1 long term unresolved cell service, 2 due to W2S, 4 ATT 2G shutoff, 5 LS300 failures
2017-05-12 | 11 | 171 | 94% | 1 long term unresolved cell service, 2 due to W2S, 3 ATT 2G shutoff, 5 LS300 failures
2017-05-19 | 8 | 170 | 95% | 1 long term unresolved cell service, 1 due to W2S (Note: Cameron site retired, will not re-install), 3 ATT 2G shutoff, 3 LS300 failures
2017-05-26 | 6 | 170 | 96% | 1 long term unresolved cell service, 1 due to W2S, 2 ATT 2G shutoff, 2 LS300 failures
2017-06-02 | 5 | 170 | 97% | 1 long term unresolved cell service, 1 due to W2S, 2 ATT 2G shutoff, 1 out (RBV) chronic at this site
2017-06-09 | 5 | 170 | 97% | 1 long term unresolved cell service, 1 due to W2S, 2 ATT 2G shutoff, 1 (GTY) with comms cutting out daily between 2-3 a.m.
2017-06-16 | 5 | 170 | 97% | 1 long term unresolved cell service, 1 due to W2S, 2 ATT 2G shutoff, 1 (GTY) with comms cutting out daily between 2-3 a.m.
2017-06-23 | 4 | 170 | 98% | 1 long term unresolved cell service, 1 due to W2S, 2 ATT 2G shutoff, 1 (GTY) with comms cutting out daily between 2-3 a.m.
2017-06-30 | 5 | 170 | 97% | 1 long term unresolved cell service, 1 due to W2S, 2 ATT 2G shutoff, 1 (RBV) out since 6/5. Not counted: 1 (GTY) with comms cutting out daily between 2-3 a.m.
2017-07-07 | 5 | 170 | 97% | 1 long term unresolved cell service, 1 due to W2S, 2 ATT 2G shutoff, 1 (RBV) out since 6/5 (back in briefly on 7/3). Not counted: 1 (GTY) with comms sometimes cutting out early a.m.
2017-07-14 | 4 | 170 | 98% | 1 long term unresolved cell service, 1 due to W2S, 2 ATT 2G shutoff, Not counted: RBV and GTY, in and out of comm.
2017-07-21 | 4 | 170 | 98% | 1 long term unresolved cell service, 1 due to W2S, 2 ATT 2G shutoff, Not counted: RBV and GTY, in and out of comm.
2017-07-28 | 5 | 170 | 97% | 1 long term unresolved cell service, 1 due to W2S, 2 ATT 2G shutoff, 1 reason unknown. Not counted: RBV and GTY, in and out of comm, El Monte & Olivenhain bad Temp/RH reads.
2017-08-04 | 3 | 170 | 98% | 1 long term unresolved cell service, 1 due to W2S, 1 ATT 2G shutoff; Not counted: RBV and GTY, in and out of comm, Olivenhain bad temp/RH.
2017-08-11 | 3 | 170 | 98% | 1 long term unresolved cell service, 1 due to W2S, 1 ATT 2G shutoff (also cell service issues); Not counted: RBV and GTY, in and out of comm, Olivenhain bad temp/RH.
2017-08-18 | 3 | 170 | 98% | 1 long term unresolved cell service, 1 due to W2S, 1 ATT 2G shutoff (also cell service issues); Not counted: RBV and GTY, in and out of comm, Olivenhain bad temp/RH.
2017-08-25 | 4 | 170 | 97% | 1 dropped cell comm, 1 long term unresolved cell service, 1 due to W2S (re-install noted on 6/5/17 but no notification sent, still not up on data feeds/dashboards), 1 ATT 2G shutoff (also cell service issues); Not counted: JAM, RBV and GTY, in and out of comm, Olivenhain bad temp/RH.
2017-09-01 | 3 | 170 | 98% | 1 dropped/intermittant cell comm (LCM), 1 long term unresolved cell service, 1 ATT 2G shutoff (also cell service issues)
2017-09-08 | 2 | 170 | 99% | 1 long term unresolved cell service, 1 ATT 2G shutoff (also cell service issues)
2017-09-15 | 2 | 170 | 99% | 1 long term unresolved cell service, 1 ATT 2G shutoff (also cell service issues)
2017-09-22 | 3 | 170 | 98% | 1 long term unresolved cell service, 1 ATT 2G shutoff (also cell service issues); 1 W2S swap
2017-09-29 | 5 | 170 | 97% | 1 long term unresolved cell service, 1 ATT 2G shutoff (also cell service issues); 1 W2S swap; 2 due to modem swap problem, awaiting fix from WW
2017-10-06 | 5 | 170 | 97% | 1 long term unresolved cell service, 1 ATT 2G shutoff (also cell service issues); 1 W2S swap; 2 due to unsuccessful modem swap (ATT weak signal, need to go back and use VZ)
2017-10-13 | 3 | 170 | 98% | 1 long term unresolved cell service, 1 ATT 2G shutoff (also cell service issues); 1 W2S swap
2017-10-20 | 0 | 170 | 100% | All working stations functional; Not counting: 1 long term unresolved cell service, 1 ATT 2G shutoff (also cell service issues); 1 W2S swap
2017-10-27 | 1 | 170 | 99% | All but 1 working stations functional; No longer counting: 1 long term unresolved cell service, 1 ATT 2G shutoff (also cell service issues); 1 W2S swap
2017-11-03 | 32 | 170 | 81% | AT&T re-assigned static IPs due to migration to LTE. They corrected the problem and cell service was restored on 11/7
2017-11-10 | 2 | 170 | 99% | 1 still out from AT&T IP issue, 1 w/data stopped at 14:30 11/9. No longer counting 3 w/known issues.
2017-11-17 | 2 | 170 | 99% | 1 still out from AT&T IP issue, 1 w/data stopped at 14:30 11/9. No longer counting 3 w/known issues.
2017-11-24 | 1 | 170 | 99% | 3 known issues: Warners W2S; De Luz and N. Descanso cellular (they are in SCADA comm)
2017-12-01 | 1 | 170 | 99% | 3 known issues: Warners W2S; De Luz and N. Descanso cellular (they are in SCADA comm)
2017-12-08 | 2 | 170 | 99% | 4 known issues: Warners & Tierra del Sol W2S, De Luz & North Descanso cellular (they are in SCADA comm)
2017-12-15 | 2 | 170 | 99% | 4 known issues: Warners & Tierra del Sol W2S, De Luz & North Descanso cellular (they are in SCADA comm)
2017-12-22 | 2 | 170 | 99% | Hidden Meadows and Corte Madera dropped cell comm on 12/19. 4 known issues: Warners & Tierra del Sol W2S, De Luz & North Descanso cellular (they are in SCADA comm)
2017-12-29 | 2 | 170 | 99% | Hidden Meadows and Corte Madera dropped cell comm on 12/19. 4 known issues: Warners & Tierra del Sol W2S, De Luz & North Descanso cellular (they are in SCADA comm)
2018-01-05 | 6 | 170 | 96.5 | Rainbow Heights stolen again. 5 known issues: Warners, Tierra del Sol & Corte Madera W2S, De Luz & North Descanso cellular (they are in SCADA comm)
2018-01-12 | 6 | 170 | 96.5 | Rainbow Heights pending re-install. 5 known issues: Warners, Tierra del Sol & Corte Madera W2S, De Luz & North Descanso cellular (they are in SCADA comm)
2018-01-19 | 6 | 170 | 96.5 | Rainbow Heights pending re-install. 5 known issues: Warners, Tierra del Sol & Corte Madera W2S, De Luz & North Descanso cellular (they are in SCADA comm)
2018-01-26 | 6 | 170 | 96.5 | 6 known issues: Rainbow Heights pending re-install. Warners, Tierra del Sol & Corte Madera W2S, De Luz & North Descanso cellular (they are in SCADA comm)
2018-02-02 | 5 | 170 | 97% | 5 known issues: Rainbow Heights pending re-install. Tierra del Sol De Luz & Corte Madera W2S; North Descanso cellular (in SCADA comm)
2018-02-09 | 6 | 170 | 96.5 | 6 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz, Cuca Ranch & Corte Madera W2S; North Descanso cellular (in SCADA comm)
2018-02-16 | 6 | 170 | 96.5 | 6 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz, Cuca Ranch & Corte Madera W2S; North Descanso cellular (in SCADA comm)
2018-02-23 | 7 | 170 | 96 | 7 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz and Cuca Ranch W2S; North Descanso cellular (in SCADA comm). Lake Cuyamaca dropped comm 2/19, RBV dropped 2/20, may be weather-related.
2018-03-02 | 6 | 170 | 96.5 | 6 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz and Cuca Ranch W2S; North Descanso cellular (in SCADA comm). Lake Cuyamaca dropped comm 2/19
2018-03-09 | 6 | 170 | 96.5 | 6 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz and Cuca Ranch W2S; North Descanso cellular (in SCADA comm). Lake Cuyamaca intermittant comm, out 17:50 on 3/8
2018-03-16 | 5 | 170 | 97% | 5 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz and Cuca Ranch W2S; North Descanso cellular (in SCADA comm). Some intermittant reads/bad Temp/RH sensor issues
2018-03-23 | 5 | 170 | 97% | (Calibration Training Week) 5 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz and Cuca Ranch W2S; North Descanso cellular (in SCADA comm). Some intermittant reads/bad Temp/RH sensor issues. New RRs tested at North Descanso and Deluz, they will work. We'll get these back in cell comm asap. Dennis & crew fixed a few Temp/RH problems.
2018-03-30 | 5 | 170 | 97% | 5 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz and Cuca Ranch W2S; North Descanso cellular (in SCADA comm). Some intermittant reads/bad Temp/RH sensor issues.
2018-04-06 | 5 | 170 | 97% | 5 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz and Cuca Ranch W2S; North Descanso cellular (in SCADA comm). Some intermittant reads/bad Temp/RH sensor issues.
2018-04-13 | 6 | 170 | 96.5% | 6 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz and Cuca Ranch W2S; North Descanso cellular (in SCADA comm). Palomar out of comm. Several intermittant reads/bad Temp/RH sensor issues.
2018-04-20 | 11 | 170 | 93.5% | 11 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz and Cuca Ranch W2S; North Descanso cellular (in SCADA comm). 6 stations out due to testing new firmware. Note that 10 stations are out of SCADA comm due to problems with new radios.
2018-04-27 | 11 | 170 | 93.5% | 10 known issues: Rainbow Heights pending re-install. Tierra del Sol, De Luz and Cuca Ranch W2S; North Descanso cellular (in SCADA comm). 5 stations out due to testing new firmware, 1 for unknown reason. Note that 10 stations are out of SCADA comm due to problems with new radios and several others have intermittantcy issues
2018-05-04 | 7 | 170 | 96% | 7 known issues: Rainbow Heights pending re-install. Tierra del Sol, Cuca Ranch W2S; North Descanso cellular (in SCADA comm). 2 station out due to testing new firmware, 1 for unknown reason. 1 station w/intermittant outages. Note that 16 stations are out of SCADA comm due to problems with new radios and 10 others have intermittantcy issues
2018-05-11 | 7 | 170 | 96% | 8 known issues: Rainbow Heights pending re-install. Tierra del Sol, Cuca Ranch W2S; North Descanso cellular (in SCADA comm). 1 station out due to testing new firmware, 1 for unknown reason. 2 stations w/intermittant comm, currently out. Note that 16 stations are out of SCADA comm due to problems with new radios. Seems fewer stations w/intermittancy, 4 at last count, but that changes one moment to next.
2018-05-18 | 7 | 170 | 96% | 7 known issues: Rainbow Heights pending re-install w/alarm. Tierra del Sol, Cuca Ranch W2S; North Descanso cellular (in SCADA comm). 1 station out due to testing new firmware. 2 stations w/intermittant comm, currently out. 14 stations are out of SCADA comm, showing progress with jobs being worked. 4 intermittant/short term outages at last count.
5/24/18 (reporting on Thurs./ooto Fri) | 7 | 170 | 96% | 7 known issues: Escondido taken out by contractor 4/28, notice recieved 5/22 after time spent on diagnostics and truck rolled; not acceptable! De Luz brought back in w/new RRs but sadly dropped out again. Lake Cuyamaca was intermittant, now out solid since 5/15; Rainbow Heights pending re-install w/alarm. Tierra del Sol, Cuca Ranch W2S; North Descanso cellular (in SCADA comm), new RRs recieved, pending install. 2 stations w/intermittant comm (LCM, RPQ) currently out. NOTE: We contintue to see failures of old Temp/RH sensors. We need to replace the old model across the network. SCADA: 16 stations are out of SCADA comm, losing ground here. 3 intermittant/short term outages at last count.
2018-06-01 | 7 | 170 | 96% | 7 known issues: Escondido taken out by contractor 4/28, notice recieved 5/22 after time spent on diagnostics and truck rolled; not acceptable! De Luz brought back in w/new RRs but sadly dropped out again. Lake Cuyamaca was intermittant, now out solid since 5/15; Rainbow Heights pending re-install w/alarm. Tierra del Sol, Cuca Ranch W2S; North Descanso cellular (in SCADA comm), new RRs recieved, pending install. 1 stations w/intermittant comm Lake Cuyamaca out solid since 5/15. NOTE: We contintue to see failures of old Temp/RH sensors. We need to replace the old model across the network. SCADA: no check this week
2018-06-08 | 7 | 170 | 96% | 7 known issues: 3 out due to W2S; ESC (new site id'd 6/7), CCR, TDS. 1 pending re-install (RBH). 1 pending new RR (NDC). 2 dropped comm for unknown reason (DLZ, LCM). Note that there are now 19 out of SCADA comm, no progress on fixes.
2018-06-15 | 8 | 170 | 95% | 8 known issues: 3 out due to W2S; ESC (new site id'd 6/7), CCR, TDS. 1 pending re-install (RBH). 1 pending new RR (NDC). 3 dropped comm for unknown reason, need site visit (DLZ, LCM, RPQ). SCADA: Kearny is currently focused on 4F radio issues, resulting in some progress; 15 out of comm, 8 have no ticket issued.
2018-06-22 | 7 | 170 | 96% | 7 known issues: 3 W2S pending re-install (ESC, CCR, TDS); 2 pending new radios (DLZ, NDC); 1 intermittant comm (LCM); 1 vandalized pending re-install w/alarm system (RBH). SCADA: 13 out of comm, 5 with no ticket issued.
2018-06-29 | 8 | 170 | 95% | 8 known issues: 3 W2S pending re-install (ESC, CCR, TDS); 2 pending radios (DLZ, NDC); 1 intermittant comm/bad T/RH sensor (LCM); 1 dropped comm (WAR);1 vandalized pending re-install w/alarm system (RBH). SCADA: 14 out of comm, 4 with no ticket issued. VZ upgrade: 15 of 72 completed (1 slated for Sat.)
2018-07-06 | 7 | 170 | 96% | 7 known issues: 4 W2S pending re-install (ESC, CCR, TDS, RIN); 2 pending radios (DLZ, NDC);1 vandalized pending re-install w/alarm system (RBH). LCM and WAR still intermittant but back in at present. SCADA: no check done this week. VZ upgrade: stalled at 15 of 72 completed
2018-07-13 | 7 | 170 | 96% | 9 known issues: 4 W2S pending re-install (ESC, CCR, TDS, RIN); 2 pending radios (DLZ, NDC);1 vandalized pending re-install w/alarm system (RBH). LCM and WAR still intermittant, LCM bad temp/RH sensor and WAR low battery. SCADA: 19 out of comm. VZ upgrade: still stalled at 15 of 72 completed
2018-07-20 | 8 | 172 | 96% | 8 known issues: 2 new stations not yet in comm. 4 W2S pending re-install (ESC, CCR, TDS, RIN); BIG NEWS De Luz finally back, problem was bad cable, NDC still needs RR;1 vandalized pending re-install w/alarm system (RBH). LCM bad temp/RH sensor and intermittent (WAR fixed today). VZ upgrade: 17 of 72 completed, getting back on track, 2nd batch modems to arrive today. SCADA: 89%, 19 out of comm (4 due to W2S); 6 w/no ticket ANE 1921, CMC 5112, NBC 5125, MVN 5145, SPV 5151, LJH 5186
2018-07-27 | 9 | 172 | 95% | 9 known issues: 2 new stations not yet in comm. 5 W2S pending re-install (ESC, CCR, TDS, RIN, CLN) I'd like to know what is delaying TDS (8 mo) and CCR (6 mo). NDC still needs new RR; RBH vandalized pending re-install w/alarm system. LCM bad temp/RH sensor and intermittent. VZ Upgrade stuck at 17 of 72, supposed to hit 24 completed by end of month. Heat related issues may have derailed work. SCADA: 18 out of comm, 5 of those due to W2S. No tickets on ANE, NBC, MVN, SPV, LJH Would like to know if these are known issues such as no appropriate RR site.
2018-08-03 | 7 | 172 | 96% | 7 known issues (7 OOC): 5 W2S pending re-install (ESC, CCR, TDS, RIN, CLN) NDC still needs new RR; RBH vandalized pending re-install w/alarm system. 2 in comm but with bad temp/RH sensors, MPE and LCM (also intermittent). VZ Upgrade still at 17 of 72. SCADA: 18 out of comm, 5 of those due to W2S. More tickets opened, just 4 with no ticket, 2 of those have been intermittant. We're told 4F radio issues will finally be resolved next week and weather station work will pick up.
8/10/18 (submitted 8/9) | 8 | 172 | 95% | 8 known issues (8 OOC): 5 W2S pending re-install (ESC, CCR, TDS, RIN, CLN) NDC still needs new RR; RBH vandalized pending re-install w/alarm system. LCM now dropped out of comm completely. VZ Upgrade still at 17 of 72. SCADA: 20 out of comm, 5 of those due to W2S. More tickets opened, just 2 with no ticket. Issue w/radio sig at Woodson made 2 more drop out this week.
2018-08-17 | 7 | 175 | 96% | Interesting problem on 8/15, all stations dropped off dashboards because massive data dump on WW system caused data collection to stop; issue resolved by cob. On 8/16 time stamp issue, one hour behind due to standard time setting on dataloggers, also resolved by cob. 3 new FiRM stations built; VMT, GUR, LHC. 7 known issues: 4 W2S pending re-install, NDC pending new RRs, RBH pending reinstall w/alarm, LCM ooc pending repair. Good progress this week: VZ upgrade: 23 of 72; SCADA work also picking up, 15 OOC, 5 due to W2S.
2018-08-24 | 7 | 177 | 96% | ALL 7 NEW STATIONS IN! 2 IN SCADA, 5 pending radio install! Problem with switching RRs on SCADA system has several stations out but this is being worked. 25 currently OOC includes 5 W2S. 7 known cell comm issues: 4 W2S pending re-install, NDC pending new RRs, RBH pending reinstall w/alarm, LCM ooc pending repair. Good progress this week on VZ upgrades 29 of 72.
2018-08-31 | 7 | 177 | 96% | 7 known issues: 4 out of comm due to W2S; Cuca Ranch, Crestline, Tierra del Sol, Escondido (to be relocated). Rainbow Heights still pending re-install w/alarm. NDC pending RRs; LCM pending modem/tempRH sensor replacement. 3 of 7 new stations now in SCADA comm. 15 station out of SCADA comm, 4 due to W2S. 36 of 72 VZ modem upgrades completed.
9/14/2018 (ooto on 9/7; some progress but no net change) | 7 | 177 | 96% | Kearny reports roads rutted out, no access to Crestline and Poomacha. 7 known issues: 3 pending W2S re-install, Crestline, Tierra del Sol and Escondido (ESC also being relocated). LCM & HDM OOC. NDC needs new RRs installed. RBH needs to be re-installed w/alarm system. SCADA: Significant progress getting several back in comm, but new 4F radio and intermittant issues cropping up. Also access issues. 13 OOC, 3 due to W2S. 4 of 7 new stations now in SCADA, though one, Paradise Mtn, is intermittant.
2018-09-21 | 7 | 177 | 96% | 7 known issues: 3 W2S still pending: ESC, CLN, TDS. Telecomm did go to ESC, determined where to point radio. 1 OOC; (NBC anemometer replaced, back in comm, but...) HMD ooc both cell & SCADA. 3 Long term issues, LCM, NDC, RBH. VZ modem upgrades halted until 3rd RV50X batch purchase, remaining new modems needed for re-installs or ooc repairs. SCADA: 15 OOC including 3 W2S pending reinstall. 8 chronic intermittant issues. 3 new stations remain to be brought in, some progress with LHC, telecomm survey done, need to re-direct antenna, but PMT is intermittant.
2018-09-28 | 5 | 177 | 97% | 5 known issues: 3W2S pending, CLN, TSD & ESC relo. NDC waiting new RRs. RBH waiting re-install w/alarm system. VZ upgrades: 50 of 72 completed. SCADA: 15 ooc (3 due to W2S); 1 new station (VIC) to be brought in. 7 w/intermittant comm.
2018-10-05 | 5 | 177 | 97% | 5 known issues: 3W2S pending, CLN, TSD & ESC relo. NDC waiting new RRs. RBH waiting re-install w/alarm system. 1 intermittent, BMS, needs new battery. Kearny crews scheduled for week of the 15th. VZ upgrades: 50 of 72 completed. SCADA: ? ooc (3 due to W2S);
2018-10-12 | 6 | 177 | 97% | 6 known issues: 1 station, West Descanso, taken down for CMP job; this is scheduled for re-install 10/12. There will also be an attempt to get NDC back in comm. 3 other W2S still down. RBH still pending re-install. Cannot currently access SCADA site, but checking against SPARC, usual suspects are out.
2018-10-19 | 4 | 177 | 98% | 4 known issues: ESC & CLN remain down from W2S, Escondido to be relocated and CLN may need grading for access. North Descanso pending radios installed. Rainbow Heights pending re-install w/alarm system. SCADA: can't access UI. From bad reads in SPARC, approx 10 ooc, incl. 3 W2S
2018-10-26 | 4 | 177 | 98% | 4 known issues: ESC, RBH, CLN pending re-install. RBH needs alarm system, CLN needs grading for access. LJH dropped cell comm. SCADA: Can't report, lost portal access. If it's showing up in SPARC, it's in comm.
2018-11-02 | 4 | 177 | 98% | 4 known issues: ESC, RBH, CLN pending re-install. RBH needs alarm system, CLN needs grading for access. LJH dropped cell comm. It's showing up in SPARC, it's in SCADA comm.
2018-11-09 | 4 | 177 | 98% | Heroic effort with push from Sherwin Edra and top down mandate to get devices associated to new stations tested and in SCADA, all done by 11/7 at 7:30 pm. LJH fixed late 11/2. Other than 4 known issues, everything that should be working is working. 4 known issues: ESC, RBH, CLN pending re-install. RBH needs alarm system, CLN needs grading for access.
2018-11-16 | 3 | 177 | 98% | 4 known issues: ESC, RBH, CLN pending re-install. RBH needs alarm system, CLN needs grading for access. Network held up great all week during RFW conditions. The few stations w/intermittent cell com were in SCADA. HHC is out of cell com this a.m., guess it deserves a rest.
2018-11-23 | 3 | 177 | 98% | 3 known issues: ESC, RBH, CLN pending re-install. RBH needs alarm system, CLN needs grading for access. HHC back in comm on 11/19, new modem. Sherilton Valley ooc on 11/23, but remote reboot brought it back.
2018-11-30 | 3 | 177 | 98% | 4 known issues: ESC, RBH, CLN pending re-install. RBH needs alarm system, CLN needs grading for access. HHC back in comm on 11/19, new modem. RBV ooc (in SCADA) since 15:30 11/28
2018-12-07 | 4 | 177 | 98% | 4 known issues: ESC, RBH, CLN pending re-install. RBH needs alarm system, CLN needs grading for access. Waiting for Kearny to install ESC at new location. Monitoring RBV, ooc 12/5 at 12:40.
2018-12-14 | 3 | 177 | 98% | 4 known issues: ESC, RBH, CLN pending re-install. RBH needs alarm system, CLN needs grading for access. Waiting for Kearny to install ESC at new location. RBV drops cell com daily around sunset, comes back in late morning.
2018-12-21 | 2 | 177 | 99% | 2 known issues: (Woohoo, ESC re-installed on 12/18!) CLN access issue still to be resolved; RBH still pending re-install. RBV intermittancy continues. Usual SCADA intermittancy, most chronic ones have open tickets.
2018-12-28 | 2 | 177 | 99% | 2 known issues: CLN access issue still to be resolved; RBH still pending re-install. RBV intermittancy continues. Usual SCADA intermittancy, most chronic ones have open tickets.
2019-01-04 | 2 | 177 | 99% | 2 known issues: CLN access issue still to be resolved; RBH still pending re-install. RBV intermittancy continues. Usual SCADA intermittancy, most chronic ones have open tickets.
2019-01-11 | 2 | 177 | 99% | 2 known issues: CLN access issue still to be resolved; RBH still pending re-install. RBV intermittancy continues. NDC, LSV, BVY & WSY occasionally intermittent. Usual SCADA intermittancy, most chronic ones have open tickets.
2019-01-18 | 2 | 177 | 99% | 2 known issues: CLN access issue still to be resolved; RBH still pending re-install (Chris Brandt now recommending steel pole.) Long rainy spell taking a toll: Temp/RH sensor failures at Sill Hill, Boulevard West, Goose Valley, West Potrero. Intermittency at RBV, De Luz, Hoskings Ranch, Cameron Corners. All are in SCADA comm.
2019-01-25 | 2 | 177 | 99% | 2 known issues: CLN access issue still to be resolved; RBH still pending re-install (Chris Brandt now recommending steel pole.) Stations that had temp/RH issues last week were either fixed or came back as we got some sunny and dry weather. Intermittent stations are back in comm, even Rainbow Valley just lagging a bit today. Verizon modem upgrades ongoing, 53 of 72 completed. SCADA comm good, La Jolla Heights back on line this week. RBH is showing up in SPARC 1/25/19... ghost???
2019-02-01 | 2 | 177 | 99% | 2 known issues: CLN access issue still to be resolved; RBH still pending re-install (Chris Brandt now recommending steel pole.) RBV sleepy as usual; Blossom Vly and West Wynola intermittent probably due to rainy spell. SCADA comm good. VZ upgrade at 53 of 62. Access issues need to be addressed at some stations.
2019-02-08 | 2 | 177 | 99% | 2 known issues: CLN access issue still to be resolved; RBH still pending re-install. Contacted NE about putting in steel pole, they will handle it soon as we get new IO for capital project. RBV sleepy as usual; West Wynola lagging. SCADA comm good but a few ooc w/no tickets open. VZ upgrade at 53 of 72, need to get rolling again with this to stay on schedule. Access issues need to be addressed at some stations.
2019-02-15 | 3 | 177 | 98% | 4 known issues: CLN access issue still to be resolved; RBH still pending re-install. Contacted NE about putting in steel pole, they will handle it soon as we get new IO for capital project. WWY now out solid since 2/3/29. VGD now showing bad Temp/RH reads. RBV sleepy as usual; Some stations dropped cell com briefly due to low battery after prolonged rains, but came back in (CMC, DLZ, HOS) and were in SCADA. SCADA comm good. VZ upgrade at 53 of 72, need to get rolling again with this to stay on schedule. Access issues need to be addressed at some stations, probably more now with record rainfall/erosion.
2019-02-22 | 3 | 177 | 98% | 3 known issues: CLN, RBH remain down long-term. Chollas Lake ooc 04:00 2/15, site inspection showed no apparent physical damage. Intermittent: RBV, WWY. Suspect temp/rh at DHV. Volcan anemometer failed 2/16, likely due to icing, followed by about a half dozen other mountain stations. Volcan viewed on camera on 2/22 shows large chunks of ice hitting equipment. It will likely be some time before the snow melts and the ground dried enough to roll in there. Dearhorn Valley has suspect temp reads for last couple days---Monitor.
2019-03-01 | 3 | 177 | 98% | 4 known issues: CLN, RBH remain down long-term. Volcan confirmed anemometer down. Chollas Lake ooc 04:00 2/15, SCADA comm intermittent. Will roll truck soon as it's dry enough. Intermittent: RBV, WWY. VZ upgrades have commenced where accessible, 55 of 72 completed.
2019-03-08 | 3 | 177 | 98% | 4 known issues: CLN, RBH remain down long-term. Chollas Lake ooc on 2/15, in SCADA. Will roll truck soon as it's dry enough, ditto for Volcan. Intermittent: usual suspects. No VZ upgrades due to weather, 55 of 72 complete.
2019-03-15 | 3 | 177 | 98% | 4 known issues: CLN, RBH remain down long-term. Chollas Lake ooc on 2/15, in SCADA. Will roll truck soon as it's dry enough, ditto for Volcan (wind meter down). Intermittent: usual suspects. No VZ upgrades this week, 55 of 72 complete.
2019-03-22 | 3 | 177 | 98% | 4 known issues: CLN, RBH remain down long-term. Chollas Lake ooc on 2/15, in SCADA. Will roll truck soon as it's dry enough, ditto for Volcan (wind meter down). Intermittent: usual suspects. No VZ upgrades this week, 55 of 72 complete. Modem swap at NDC, calibration training completed.
2019-03-29 | 3 | 177 | 98% | 3 known issues: CLN, RBH remain down long-term. Chollas Lake ooc on 2/15, in SCADA. Will push Kearny to fix, ditto for Volcan (wind meter down). Intermittent: usual suspects. No VZ upgrades this week, 55 of 72 complete.
2019-04-01 | 3 | 177 | 98% | 3 known issues: CLN, RBH remain down long-term. Chollas Lake ooc on 2/15, in SCADA. Will push Kearny to fix, ditto for Volcan (wind meter down). Intermittent: not bad, RBV actually woke up this a.m. No VZ upgrades this week, 17 left to do.
2019-04-12 | 4 | 177 | 98% | 5 known issues: CLN, RBH remain down long-term. Chollas Lake ooc on 2/15, in SCADA. Will push Kearny to fix, ditto for Volcan (wind meter down). Rebuild/Upgrade project commenced this week, 4 sites done. Viejas Grade was done 4/10 but IT team ooto and new tech at WW means #s not provided and Stormgeo feed down. Nathan is working on this. VZ modem upgrades at 15 remaining.
2019-04-19 | 4 | 177 | 98% | Known issues: CLN, RBH remain down long-term. Volcan wind meter down, access still pending. Pauma showing no wind reads and Chollas ooc, both on schedule for 4/29. Pauma will get upgrades. Rebuild/Upgrade project: 7 sites done. VZ modem upgrades at 15 remaining. SCADA tickets open on all chronic intermittent sites.
2019-04-26 | 3 | 177 | 98% | Known issues: CLN, RBH remain down long-term. Volcan wind meter down, access still pending. Pauma showing no wind reads and Chollas ooc, both on schedule for 4/29. Pauma will get upgrades. Rebuild/Upgrade project: 7 sites done. VZ modem upgrades at 12 remaining. SCADA tickets open on all chronic intermittent sites.
2019-05-03 | 4 | 177 | 98% | Known issues: CLN, RBH remain down long-term. MVN dropped cell comm at 1500 on 5/2. Volcan wind meter down, access still pending. Pauma showing no wind reads, was on schedule for 4/29 but not fixed. Rebuild/Upgrade project: 18 sites done. VZ modem upgrades at 8 remaining. SCADA tickets open on all chronic intermittent sites.
2019-05-10 | 3 | 177 | 98% | Known issues: CLN, RBH remain down long-term. Volcan wind meter down and also high priority VZ/Rebuild, access still pending. Pauma showing no wind reads, was on schedule for 4/29 but not fixed. Rebuild/Upgrade project: 18 sites done. VZ modem upgrades at 8 remaining. SCADA tickets open on all chronic intermittent sites. Weather realated cell & SCADA intermittency.
2019-05-17 | 3 | 177 | 98% | Known issues: CLN, RBH remain down long-term. Volcan wind meter down and also high priority VZ/Rebuild, access still pending. Pauma showing no wind reads, was on schedule for 4/29 but not fixed. Rebuild/Upgrade project: 29 sites done. VZ modem upgrades at 2 remaining. SCADA tickets open on all chronic sites, very minor intermittency. Considering the weather, cell intermittency not bad either.
2019-05-24 | 3 | 177 | 98% | Known issues: CLN, RBH remain down long-term. Volcan wind meter down and also high priority VZ/Rebuild, access still pending. Pauma showing no wind reads, was on schedule for 4/29 but not fixed. Hoskings Ranch down since 4/30, have requested high priority from Kearny. Rebuild/Upgrade project: 29 sites done. VZ modem upgrades at 2 remaining. SCADA tickets open on all chronic sites, very minor intermittency. Considering the weather, cell intermittency not bad either.
2019-05-31 | 3 | 177 | 98% | Known issues: CLN, RBH remain down long-term. Volcan wind meter down and also high priority VZ/Rebuild, on Kearny schedule for 6/3 along with Hoskings Ranch. Pauma showing no wind reads, was on schedule for 4/29 but not fixed. Rebuild/Upgrade project: 29 sites done. No new progress this week, pending receipt of Q2 equipment order. VZ modem upgrades at 2 remaining. SCADA tickets open on all chronic sites, very minor intermittency.
2019-06-07 | 3 | 177 | 98% | Known issues: CLN, RBH remain down long-term. Volcan was to be fixed on 6/3 but it didn't happen. Pauma showing no wind reads, was on schedule for 4/29 but not fixed. Otay Mtn. broken upon upgrade, fix tbd. Rebuild/Upgrade project: 33 sites done. VZ modem upgrades at 2 remaining, Volcan and Santa Teresa Valley. SCADA tickets open on all chronic sites, very minor intermittency.
2019-06-14 | 3 | 177 | 98% | Known issues: CLN, RBH remain down long-term. Archie Moore went out on 6/10, remains down. Pauma in comm but broken anemometer. Rebuild/Upgrade project: s/b 35 sites done by cob today. VZ modem upgrades to be completed by cob today. Nathan sent new list of stations with poor cell comm, some known, some not. SCADA: very minor intermittency, lots of tickets resolved, a few sites ooc w/no tickets.
2019-06-21 | 2 | 177 | 99% | Known issues: CLN, RBH remain down long-term. Requested estimate for steel pole for RBH from NE, have not heard back. We still need to make time to get up to Crestline and assess situation. VZ Modem Upgrades COMPLETED 6/14/19! Rebuild/Upgrades; 39 of 55 (Phase 1) completed. SCADA comm good, open tickets assigned to TCC or KY. There are some ooc that don't have tickets: JAM, LLC, CRI, NHG, STV. We have some access issues to resolve, but finally got easement for Poway.
2019-06-28 | 3 | 177 | 98% | Known issues: Cameron Corners dropped cell comm on 6/26 at 19:30. CLN, RBH remain down long-term. Requested estimate for steel pole for RBH from NE, have not heard back. We still need to make time to get up to Crestline and assess situation. Rebuild/Upgrades; 39 of 55 (Phase 1) completed (70%). SCADA comm good, open tickets assigned to TCC or KY. OOC w/no tickets: LLC, CRI, NHG, STV, SQT. Access issue to resolve: Poomacha
2019-07-05 | 4 | 177 | 98% | CVX down for W2S, to be back up after 7/14. CLN, RBH remain down long-term. Requested estimate for steel pole for RBH from NE, still no word. Rebuild/Upgrades; 39 of 55 (Phase 1) completed (70%). No SCADA check this week, I was on vacation. Access issues to resolve: Poomacha, Crestline
2019-07-12 | 4 | 177 | 98% | CVX down for W2S, to be back up after 7/14. CLN, RBH remain down long-term. Requested estimate for steel pole for RBH from NE, still no word. Rebuild/Upgrades; 43 of 55 (Phase 1) completed (78%). New Stations: No changes to report from last week; 13 Sites sent to Districts. Planners reporting 6 jobs written, some pending load calcs or Trans request to attach.
2019-07-19 | 11 | 177 | 94% | CVX down for W2S, cleared to reinstall 7/15. Requested estimate for steel pole for RBH from NE, still no word. Rebuild/Upgrades; 43 of 55 (Phase 1) completed (78%). New Stations: No changes to report from last week; 13 Sites sent to Districts. Planners reporting 6 jobs written, some pending load calcs or Trans request to attach. 7 VZ stations with new IP range dropped comm at 4:50 am, APN issue fixed and back in comm by cob.
2019-07-26 | 2 | 177 | 99% | CVX reinstalled 7/22, upgraded. Rebuild/Upgrades at 45 of 55 completed (80%). New stations:13 submitted to Planners, 10 jobs written, pending permissions, SCADA site requests. We're expecting these to start reaching Kearny by August 2. CLN, RBH remain down long-term. SCADA comm excellent, very little intermittency but 11 open tickets.
2019-08-02 | 2 | 177 | 99% | Rebuild/Upgrades at 45 of 55 completed (80%). New stations:13 submitted to Planners, 11 jobs written, pending permissions, SCADA site requests. 2 jobs from NE to KY 7/30. CLN, RBH remain down long-term. SCADA comm excellent, very little intermittency but 12 open tickets.
2019-08-09 | 1 | 177 | 99.5% | No progress due to veg access issue, can't drive over dry grasses/brush. Rebuild/Upgrades at 45 of 55 completed (80%). New stations:13 submitted to Planners, 12 jobs written, 9 pending permissions, SCADA site requests. 3 jobs from NE to KY. CLN reinstalled 8/2, RBH remains. SCADA comm excellent, very little intermittency but still 12 open tickets.
2019-08-16 | 1 | 177 | 99.5% | No progress due to veg access issue, can't drive over dry grasses/brush. Also focus on just doing calibrations rather than upgrades. Rebuild/Upgrades at 45 of 55 completed (80%). New stations:13 submitted to Planners, 12 jobs written, 9 pending permissions, SCADA site requests. 3 jobs from NE to KY. CLN reinstalled 8/2, RBH remains. SCADA comm excellent, very little intermittency but still 12 open tickets.
2019-08-30 | 3 | 187* | 99.4% | *By COB today: 11 new stations, 1 more to be installed on 9/1, 1 more pending. Rebuild/Upgrades at 46 of 55 completed (84%). RBH remains down long term. OMB dropped cell com on 8/21, still in SCADA. WAR logger killed by attempt to install new OS, still in SCADA. Have requested Kearny roll on these asap. SCADA comm good, no time to do station-by-station status today.
2019-09-06 | 5 | 188 | 97% | 12 new stations in cell comm; 1 pending. Rebuild/Upgrades 46 of 55 (84%). RBH remains down long term. OMB dropped cell com on 8/21, still in SCADA. Warners & Campo loggers killed on attempt to install new OS. Pine Hills dropped cell on 8/31, they are in SCADA comm. No SCADA check this week, ooto on vacation.
2019-09-13 | 3 | 189 | 98.5% | 12 new stations in cell comm; 1 install pending. Rebuild/Upgrades: 47 of 55 (85%). RBH remains down long term. OMB/CPO fixed 9/12. Warners & Pine Hills remain ooc, PIH in SCADA. SCADA has lots of issues; 10 open tickets, some are for chronic issues. 13 ooc w/no tickets, 7 of those have been ooc for 2 weeks+. Most noteable Sill Hill ooc since 8/25, KY issued 9/3. CLN still showing taken down though it was re-installed 8/2/19. POW
2019-09-20 | 2 | 190 | 99% | 13 new stations in cell comm; no SCADA until #s issue resolved. Rebuild/Upgrades: 47 of 55 (85%). RBH remains down long term. Warners & Pine Hills back in comm but not upgraded.SCADA: Very little intermittency in general, but many of the 15 tickets (9 issued to TCC, 6 to KY) have been open for quite some time. CLN still showing taken down though it was re-installed 8/2/19. POW showing access issue though that was resolved months ago, as I noted on the ticket.
10/4/19 (9/27/19 not filed due to Safety Congress) | 1 | 190 | 99.5% | New SCADA#s assigned, hopefully work on radio comm will commence. Rebuild/Upgrades: 47 of 55 (85%). Discussed RBH w/Wagner and Brandt, will push now to get something done. 9 SCADA tickets open, some being worked by Greg Clark.Of concern is Sill Hill still not resolved and BNA, NDC, OTM out for a month w/no tickets.
2019-10-11 | 2 | 190 | 99% | We are told Kearny will start working SCADA radios on new stations this coming week. Rebuild/Upgrades 47 of 55 (85%). I will ask CB to get Rainbow Heights back up, will order fake camera and gps tracker. Campo SCADA 1970 dropped cell com 01:40 on 10/10; just got upgraded 9/12 so may be cell tower issue. Will monitor over weekend and get truck out next week if necessary.
2019-10-18 | 3 | 190 | 98.5% | GPS for RBH received/setup but needs some testing before we proceed w/install. Campo fixed on Monday and Poway back in SCADA, but we lost RPT and GTY on Thurs-Fri. Some SCADA tickets re-assigned. No progress on Upgrade/Rebuild, remains at 47/55 85%. No new stations in SCADA.
2019-10-25 | 2 | 190 | 99% | Rainbow Heights to be re-installed w/GPS asap. Stations with issues this week have been brought back in, except Tierra del Sol but it's in SCADA. Upgrade/Rebuild remains at 47/55 85%. No new stations have SCADA set up yet; Eucalyptus Hills now has R2A approved.
2019-11-01 | 0 | 190 | 100% | Woohoo, Rainbow Heights re-installed w/GPS tracker hidden in cabinet. Kearny crews went above and beyond to get issues resolved ahead of RFW. 100% CELL COMM! We started keeping Issues Log in 2016; 203 reported to date---roughly 60 per year average. I started a Performance Log 4/21/17. Jan. '18 I set a goal to reach 100% by year end… took a bit longer but we're finally there. We still have a few sites w/chronic intermittency; Lucky Five Ranch, Escondido, Coronado Hills... so now we shoot for perfect cell comm and getting new sites in SCADA. Rebuild/Upgrade Project; 49 of 55, 89%
2019-11-08 | 0 | 190 | 100% | 190 stations, 100% cell comm with minor intermittency (Lucky Five Ranch started napping at 7:40 as usual). A couple of issues this week were corrected remotely by Western Weather. SCADA comm normal; tickets open on all sites w/issues except North Descanso (5126) and Otay Mtn (5129). WMP Rebuild/Upgrades: 49 of 55 completed (89%). Living Coast Discovery Center Portable install: asked Kearny to schedule as soon as crew available, sent contact info.
2019-11-15 | 0 | 190 | 100% | 190 stations, 100% cell com; usual suspects intermittent. Currently 12 stations with known issues not in SCADA comm; SCADA sites up for all 13 new stations with 9 in comm. Rainbow Heights 1981 needs ticket to get SCADA; it’s doing fine with GPS tracking signal steady. WMP Rebuild/Upgrade – 49 of 55 completed, 89%. Spend complete for Phase with labor factored in. Camera for Veg. monitoring: Western Weather is testing; we need to finalize site selection.
2019-11-22 | 0 | 190 | 100% | 190 stations, 100% cell comm. Rios Canyon SCADA 1942 has bad Temp/RH reads; have requested crew visit. SCADA: Good comm, very little intermittency. 2 stations fixed, back in comm since last week, 10 open tickets. WMP Rebuild/Upgrades Phase 1: 49 of 55; 89%. Living Coast Portable: Installation on schedule for Monday, 11/25
11/27/19 (early due to holiday) | 4 | 191 | 98% | 191* Stations; 98% cell comm. BOC, RPQ ooc 11/26; AMO 11/28; PVD 11/29. Bad Temp/RH reads at RIO and SHC. *Living Coast (DJZ) installed 11/26. (NHG ooc 12/1, ooc in SCADA since June)
2019-12-06 | 6 | 191 | 97% | 6 stations OOC since last week but they are in SCADA (except for NHG). Crew visits requested on 12/4 for AMO, NHG, RPQ, PVD, BOC, RIO (bad T/RH). SCADA: Comms good, slight intermittency. No tickets resolved this week. WMP Rebuild/Upgrades: 51 of 55, 93% more scheduled.
2019-12-13 | 4 | 191 | 98% | 4 still OOC, hopefully to be fixed soon now that WMP is at 100%. SCADA comms great this week, very little intermittency but long term OOC need to be addressed.
2019-12-20 | 2 | 191 | 99% | Jamul upgraded 12/18 then dropped cell comm today. WMP exceeded, 57 done. SCADA comms normal, 8 stations with longstanding issues, 4 new stations not in yet, 5 ooc w/no tickets.
2019-12-27 | 1 | 191 | 99.5% | Usual cell intermitency at LFR and others. SCADA comm good, very little intermittency. 12 of 13 new stations now in SCADA. Jamul SCADA 1940 out of cell comm since 12/20, crew visit requested.
2020-01-03 | 1 | 191 | 99.5% | Jamul still out. RBH GPS has lost sat connection since 12/30. LFR intermittency worse than usual. SCADA comm good.
2020-01-10 | 0 | 191 | 100% | Telematics help says GPS contact lost due to firmware upgrade. It cannot be reset remotely, will require batteries to be changed out. Jamul fixed on 1/8, new modem installed. LFR was awake this morning until 8:50, hence momentary 100%. It is ticketed for SCADA RR re-align and voltage spike, hope to get cell comms improved as well.
2020-01-17 | 1 | 191 | 99.5% | Volcan Mt dropped comm at 4:40, wind gusting 50-60, may be damage. SHC and AVY Temp/RH reads gone wonky, like weather related AND they have old sensors which should have been replaced long ago. Skype call on 1/15 addressed scope for 2020; 20+ new stations, real-time reads, comms issues/fixes.
2020-01-24 | 1 | 191 | 99.5 | LFR ooc at 22:20. SHC & AVY T/RH dried out and reads back to normal, but sensors still need to be replaced. WW reported on real-time reads, priority list updated accordingly. Real-time reads are bumped up to high priority. Lots of SCADA issues, reported in detail in status email. 20 stations OOC, 12 intermittent.
2020-01-31 | 1 | 191 | 99.5 | TCN fixed, LFR out solid. HD crashed on 1/30. Using loaner but lost all links.
2020-02-07 | 1 | 191 | 99.5 | LFR actually woke up for about a day this week, then back out cold. Received 20 modems from kits. Still limping along on loaner laptop so can't check SCADA site. Lost PowerBi link so can't look there. Reads look ok in SPARC. Sited 7 new stations on 2/7.
2020-02-14 | 1 | 191 | 99.5 | LFR OOC all week. Site sheets for 7 new stations released to planning on 2/12, one more on 2/13 (Del Dios N visited on Saturday).
2020-02-21 | 1 | 191 | 99.5 | LFR out cold though time stamp change indicates it pops in on rare occasions. 6 new sites ok'd, 1 we couldn't get to (San Elijo Cyn) and DDN verified by Steve.
2020-02-28 | 2 | 191 | 99% | LFR OOC; Goose Valley ooc since 10:30 2/27. Fielded 3 sites on 2/27; Hauser Cyn excellent, Morena Dam iffy, has a can, 2nd choice not as windy; Bently's Lookout a no-go. Still no new laptop/SCADA access.
2020-03-06 | 1 | 191 | 99.5 | LFR OOC. No new sites fielded this week. Still no new laptop or SCADA access.
2020-03-13 | 2 | 191 | 99% | LFR OOC. No new sites fielded this week. Still no direct SCADA access but can check in PowerBI. DLZ ooc/intermittent; AVY & SHC temp/rh failure due to rain. Calibration training next week cancelled due to coronavirus. Weather, social distancing plus travel restrictions will disrupt progress on fielding new sites etc.
2020-03-20 | 3 | 191 | 98% | LFR remains OOC. Volcan & Campo dropped out early am 3/20, possibly weather related. All appear to be in SCADA (PowerBI, SPARC). Dennis got Campo back in.
2020-03-27 | 1 | 191 | 99.5% | LFR WOKE! On 3/23, Dennis was able to do firmware upgrade. It has remained in comm all week! NBC has been severely intermittent all week, ooc since 3/26 18:10. SHC showing typical wet weather bad T/RH reads.
2020-04-03 | 0 | 191 | 100% | Only SHV a bit sleepy this week. NBC was, but came back in. Reads at SHC came back to normal. Nice dry week.
2020-04-10 | 4 | 191 | 98.5% | Record rainfall causing intermittency; DeLuz, LFR, White Star, MTL OOC (all in SCADA). AVY & SCH bad T/RH as usual in wet weather.
2020-04-17 | 1 | 191 | 99.5% | Bell Canyon intermittent, LFR up for an hour last night, now out cold, Both are in SCADA.
2020-04-24 | 1 | 191 | 99.5% | LFR ooc since 4/16, in SCADA comm. 133 sites in 30 Sec.Reads. 6 new sites fielded this week.
2020-05-01 | 1 | 191 | 99.5% | LFR ooc since 4/30 (seems to be waking up briefly once a day or so), in SCADA. Otay Mtn bad T/RH reads, Sweetwater River intermittent. 141 sites w/30 sec reads. 2 sites fielded, VCH ok'd, BOB blocked by TCM.
2020-05-08 | 0 | 191 | 100% | OTM bad T/RH, kearny notified. Kearny picking up the pace of upgrades, 160 w/30 sec.
2020-05-15 | 2 | 191 | 99% | VCM ooc, in SCADA. De Luz intermittent, likely cell tower issue, in SCADA. 169 upgrades completed. Of 32 new sites fielded, just 21 viable in Apollo scope.
2020-05-22 | 0 | 191 | 100% | 106 upgrades; 49 in 2020.173 stations w/30 sec.; 21 new sites in planning/design, Brianne Nelson working to expedite R2As. Paul Greco will now PM 9 new sites to reach 30 goal. 4 sites fielded this week. All comms good.
2020-05-29 | 0 | 191 | 100% | All stations in cell comm this morning. 173 w/30 sec. reads. Calibrations ongoing. 21 new sites in planning/design,still working to expedite R2As w/info on attaching to towers. 3 sites fielded by BRIAN this week!
2020-06-05 | 1 | 191 | 99.5% | De Luz out cold; OMB intermittent, both in SCADA. Anderson Valley bad temp/rh reads. 29 new sites in planning, 8 more sited this week. 7 sites remaining to do 30 sec reads, 3 w/access issues. Access to BFD needs brushng. No upgrades this week. Calibrations seem to be the focus now.
2020-06-12 | 0 | 191 | 100% | AVY fixed during calibration this week. 2020 Site Selection complete unless 5 or more sites get rejected. Getting negative push back about attaching to lattice towers. Viejas Grade showing no T/RH. Lots of glitchy T/RH reads this week.
2020-06-19 | 1 | 191 | 99.5% | Potrero ooc since 6/16, modem failed during calibration. Intermittency and bad reads not an issue this morning. However… SCADA comm out due to cut-over. Subbu is working on fix. Progress on new stations unknown.
2020-06-26 | 1 | 191 | 99.5% | Rios Canyon ooc since 6/20. No intermittency this moring. SCADA comm was restored but has dropped out again, have notified Betty Pelgen and Subbu. Meetings to expedite new installs seem successful, progress reports provided and we have a clearer understanding of timelines. SCADA/Telecomm surveys and R2As, eviro/access issues remain roadblocks.
2020-07-03 | 0 | 191 | 100% | SCADA comm normal; post-cutover issues seem to be resolved. No telling when jobs for new sites will begin to get to Kearny
2020-07-10 | 1 | 191 | 99.5% | Viejas Mtn Trl 5189 dropped cell comm 7/9, in SCADA. Escondido intermittent. No progress to report on new installs.
2020-07-17 | 2 | 191 | 99% | Laguna SCADA 1968 was taken down for ongoing C440 work; it may be down for a week or more. Viejas Mt Trail SCADA 5198 dropping cell comm daily since 7/9, was scheduled to be fixed this week but crew not available. It is in SCADA comm.
2020-07-24 | 1 | 191 | 99.5% | Laguna was re-installed w/upgrades but couldn't restore cell comm. Kim scheduled to go this week but got called off for emergency work. Will roll asap. New installs will be escalated to emergency status, possibly starting next week?
2020-07-31 | 1 | 191 | 99.5% | Laguna remains down. 7 jobs released to construction.
2020-08-07 | 3 | 191 | 98% | Ongoing RFS work on 442, 626 and other work on 79, 222 is causing a lot of OOC. Inaja Park and North Boulder creek to be RFS possibly this weekend. Laguna, Lake Cuyamaca, Sunrise Highway are OOC.
2020-08-14 | 3 | 191 | 98% | Laguna, Lake Cuyamaca, Sunrise Highway are OOC, cell & SCADA; unknown if this is due to Circuit/TL work. Laguna restored to service and w/30 sec reads. One new station, Old Castle, installed and on MesoWest. Inaja Park RFS on 8/8/20. 30 jobs have been released to Kearny.
2020-08-21 | 3 | 191 | 98% | 3 stations remain OOC. North Boulder Creek RFS on 8/15/20. 2 new installs keep the count at 191. Calle de Vista installed 8/19, live on MesoWest. Houser Mt was supposed to be installed 8/20 but no word from Kim.
2020-08-28 | 4 | 201 | 98% | 201 stations! Same 3 stations remain OOC. 11 of 12 new installs in cell comm, 1, De Luz Creek, built but no comm yet. I'm not going to report on SCADA comm in general any more until provided with access to current platform.
2020-09-04 | 3 | 213 | 98.6% | Lawson Valey, Lake Cuyamaca & Sunrise Hwy OOC cell & SCADA long term. 24 new installs to date, 1 more scheduled for today. Extreme heat and Santa Ana conditions may stall work over weekend and next week. Little or no intermittency. PowerBI shows 173 stations in SCADA comm.
2020-09-11 | 3 | 215 | 98.7% | LSV, LCM, SRH still OOC. 26 new installs completed. 4 sites w/bad PI data, showing up in SPARC with false wind speed/gust reads of 75/75 and Temp/RH stuck at 70/50 (cell comm is good): tickets have been issued to Kearny. Stations w/30 Sec. Reads: 205
2020-09-18 | 3 | 219 | 99% | 30 Station goal reached on 9/16, 219 stations! Only LCM out solid (W2S), but BOB & POT are intermittent, dropped at 3-4 am. Volcan will require a visit, bad T/RH sensor. SCADA issues being addressed, 2 remain w/stuck reads. 210 stations on 30sec.
2020-09-25 | 1 | 220 | 99.5% | 31 new stations, Buffalo Bump portable installed this week. Volcan & N Miller Rd now have bad T/RH sensors. 1 station, Poomacha still has bad SCADA reads. Chihuahua Valley serverely intermittent (chronic)
2020-10-02 | 1 | 220 | 99.5% | The Bump showed up top of the gust board this week. NMR fixed but Volcan still bad; it will get on schedule next week. Poomacha allegedly still can't be reached, waiting road grading. LCM should get re-installed soon; Chris admitted it fell off the radar. Jamie under the impression steel pole hasn't gone in yet. Mystery.
2020-10-09 | 0 | 220 | 100% | Lake Cuyamaca re-installed 10/7. Volcan on schedule for 10/15. Pala Temecula had bad T/RH reads this moring but has returned to normal. Poomacha remains OOC/SCADA due to access issue.
2020-10-16 | 1 | 220 | 99.5% | Volcan did not get fixed. Poomacha remains OOC/SCADA due to access issue. Otay Mesa Border & Chihuahua Valley showing usual intermittency.
2020-10-23 | 1 | 220 | 99.5 | Volcan T/RH still not fixed. Poomacha remains OOC/SCADA due to access issue. Otay Mesa Border OOC/intermittent. BOB OOC for 72 hours this week, pattern seems to be drop/in/out around 22:00. EUC SCADA built but never put in service because they "didn't know what comms channel to use"
2020-10-30 | 0 | 220 | 100% | Volcan T/RH out since 9/14, Pala Temecula & Vista also showing bad reads, all supposed to be fixed Monday 11/2. Poomacha has disappeared from SPARC. Usual suspects intermittent with addition of De Luz Creek.
2020-11-06 | 0 | 220 | 100% | Vista repaired; Pala Tem has bandaid fix, needs new logger. Volcan fix foiled by ATT lock on gate, needs to be rescheduled. Very slight intermittency this week.
2020-11-13 | 1 | 220 | 99.5% | PTM now OOC, hoping crew can get there w/new logger soon. Volcan visit now will have to wait for dry-out. De Luz sights intermittent this week.
2020-11-20 | 0 | 220 | 100% | De Luz sleepy overnight most of this week. A few other usual suspects slightly intermittent. PTM fixed w/new logger 11/16. Volcan T/RH remains to be fixed.
2020-11-27 | 0 | 220 | 100% | De Luz sleepy overnight most days. A few other usual suspects slightly intermittent. Volcan T/RH remains to be fixed.
2020-12-04 | 0 | 220 | 100% | De Luzzzzz as usual. More than usual intermittency this week, pattern suggests cell tower issues. Vocan T/RH still wonky.
2020-12-11 | 1 | 220 | 99.5% | Thankfully intermittency was minor during RFW/PSPS this week. Except for De Luz, getting worse. Harrison Park was intermttent, then OOC on 12/10. External issues occurred post-activation: StormGeo dropped all stations from website for a couple hours on 12/9; VZ data network for So Cal went down 2:30-3:30 am on 12/9.
2020-12-18 | 0 | 220 | 100% | De Luz sleeping in as usual. Volcan T/RH still not fixed. 211 on 30 sec. 8 new stations now on SCADA. 4 new sites not in GIS yet: BUB, SOS, CVY, OLD; I've asked Jamie to look into this.
2020-12-25 | 0 | 220 | 100% | De Luz sleeping in as usual. Volcan T/RH still not fixed. 211 on 30 sec. 8 new stations now on SCADA. 4 new sites not in GIS yet: BUB, SOS, CVY, OLD; I've asked Jamie to look into this.
2021-01-01 | 2 | 220 | 99% | De Luz mostly OOC, waking up for brief intervals, cell & SCADA. Volcan dropped cell comm 07:40 12/31, appears to be in SCADA, still needs T/RH fix. Some others w/minor intermittency.
2021-01-08 | 0 | 220 | 100% | Boulevard West and Potrero have been out of cell comm since the wee hours of 1/8. They are in SCADA. Volcan T/RH remains down.
2021-01-15 | 0 | 220 | 100% | Volcan Mt. 5154; Bad T/RH sensor since 9/14/20, Kearny crew will roll up there at earliest opportunity but conditions continue to interfere. Boulevard West 1907 and Potrero 1933 OOC cellular on 1/8/21, were fixed on 1/12/21. De Luz has improved comms after Dennis Lundy diagnosed battery issue at RR site and Doug went up there and fixed it yesterday. He identified RF antenna issue at De Luz Creek which will require bucket truck.
2021-01-22 | 1 | 220 | 99.5% | Potrero intermittent then ooc at 00:40 on 1/21; it's in SCADA. Poomacha & Narrows Sub severely intermittent this week. Poomacha out at 06:10 on 1/22, SCADA OOC. Volcan T/RH still bad.
2021-01-29 | 1 | 220 | 99.5% | Potrero remains OOC but is showing up in SPARC. Volcan T/RH still out. De Luz back to daily intermittency. Poomacha and Harmony Grove occasionally intermittent this week.
2021-02-05 | 2 | 220 | 99% | De Luz back to nightly snooze all week (in SCADA). De Luz Rd out cold on 2/1. Potrero remains down (in SCADA). Volcan T/RH still bad. A battery issue identified by Dennis at Mt Laguna solved by setting LoggerNet data pull to hourly; will need new battery.
2021-02-12 | 4 | 220 | 98% | De Luz back to nightly snooze all week (in SCADA). De Luz Rd out cold on 2/1. Potrero, ooc for 20 days, woke up for 12 hours on 2/11 but now back out (in SCADA). Volcan T/RH still bad and wind went down at 01:00 on 2/12. Cell and logger issues identified by Dennis at Laguna; may need to swap modem to VZ and needs new logger, maybe battery. OMB ooc on 2/9.
2021-02-19 | 2 | 220 | 99% | De Luz nightly snooze all week (in SCADA). De Luz Rd out cold since 2/1. Potrero intermittent. BOB out 11:20 on 2/18. Volcan came back to normal reads on 2/16; miracle or Kim made it up there, don't know which. CLN, HAG, LAG, POM, MTL intermittent.
2021-02-26 | 3 | 220 | 98.5% | De Luz Rd 4834 remains OOC since 2/1 (no SCADA). Bob Owens Canyon 4841 OOC since 11:20 on 2/18 (no SCADA). Potrero 1933 dropped cell com at 22:10 on 2/20. Usual cellular intermittency at 11 chronic sites, though 8 of these have SCADA comm.
2021-03-05 | 3 | 220 | 98.5% | Usual intermittency. Requested Kearny roll on these: De Luz Rd 4834 remains OOC since 2/1 (no SCADA). Bob Owens Canyon 4841 OOC since 11:20 on 2/18 (no SCADA). Potrero 1933 dropped cell com at 22:10 on 2/20. Chronic cell problems here, gone through 5 modems in 6 years. May need solution other than modem swaps. Antenna? Repeaters? Seems to be doing ok in SCADA
2021-03-12 | 2 | 220 | 99% | POT & BOB came back, either miracle or someone got to them. But lost EUC and DLR still out. Twin Oaks bad T/RH and needs all upgrades. 6 potential sites selected for NDVI cams.
2021-03-19 | 2 | 220 | 99% | Twin Oaks came back to normal on 3/14, no word on upgrades being done. POT went dark again on 3/14, EUC ooc on 3/8, De Luz Rd since 2/1. Multiple requests to roll have been made.
2021-03-26 | 3 | 220 | 98.5% | TWO back to bad reads, will up priority. POT went dark again on 3/14, woke 3/19, out 3/20, EUC & DLR still out. Multiple requests to roll have been made. 12 sites ID'd for NDVI cams and/or fuel sticks. TNT and ROV subject to TL6926/683 W2S transfer.
2021-04-02 | 3 | 220 | 98.5% | TWO fixed, POT still OOC though Carlos went there and claimed it was ok. EUC & DLR still down. Up to 4 NDVI cams and/or fuel sites to be installed in May. TNT and ROV pending TL6926/683 W2S transfer. Usual intermittancy, 6 sites bad, 5 more occasional.
2021-04-09 | 5 | 220 | 98% | EUC, DLR, POT, BOB, CMC OOC. POT & CMC in SCADA Comm. SCADA Access form submitted this morning. ROV transfer should happen very soon, CB notified. No word on TNT. Rainbow Conservation Camp SCADA installed this week.
2021-04-16 | 4 | 220 | 98% | DLR, DLZ, EUC, POT, BOB OOC. BOB & POT awake briefly. Usual intermittency at ESC, MTL MLG, WWY. ROV transfer to Z416170 s/b issued to construction by 4/22/21. Nothing on TNT yet. RCC still not showing up in SPARC.
2021-04-23 | 5 | 220 | 98% | DLR, DLZ, EUC, POT, BOB OOC. BOB & POT awake briefly, though POT went 10 hours. Usual intermittency at ESC, MTL MLG, WWY. ROV transfer to Z416170 s/b issued to construction by 4/22/21. Nothing on TNT yet. RCC still not showing up in SPARC. 3 NDVI sites approved; GUR, YSA, WAR, BMR pending.
2021-04-30 | 4 | 220 | 98% | DLR, EUC, POT joined by Rancho Heights, OOC on 4/23. Intermittency at ESC, MTL, MLG, POM, SWR. BOB woke up on 4/29 and still live. 3 more new stations in SCADA, 23 un-confirmed.
2021-05-07 | 3 | 220 | 98.5% | EUC, POT and RHS still OOC. Usual suspects intermittent. Dennis fixed De Luz & De Luz Rd and got De Luz and NDC on 30 sec reads. NDVI cam & Fuel sensor installed at Santa Ysabel North. Plan to install cam at Guejito Ranch today. Tried to access SYR but couldn't find route in. NDVI cam and Fuel sensor installed at Santa Ysabel Ranch. Cam installed at Warners along with new battery and logger.
2021-05-14 | 5 | 220 | 98% | BOB, POT, EUC, RHS OOC and we lost De Luz again on 5/8. Warner's rebuild/upgrade completed on 5/13. Crestwood upgraded 5/13 also. Usual intermittency.
2021-05-21 | 6 | 220 | 97% | EUC, RHS, BOB, DLZ, POT, Volcan OOC. 97%. Sad. At least upgrades are picking up.
2021-05-28 | 5 | 220 | 98% | (On vacation this week) EUC, RHS, BOB, DLZ, POT remain ooc. Volcan came back in by itself. 3 Upgrades completed, total of 10.
2021-06-04 | 5 | 220 | 98% | POT finally fixed along w/rebuild/upgrade, cell comm seems stable. BOB, DLZ, EUC, RHS still ooc. Cameron Corners dropped out 6/2, has done so before and come back on its own, monitoring. Warners about to go out with low battery, camera issue? Needs larger solar panel. 13 rebuild/upgrades done to date.
2021-06-11 | 4 | 220 | 98% | BOB, DLZ, EUC still ooc. Cameron Corners dropped out 6/2. Rancho Heights woke up on its own, apparently. Warners still limping along with low battery, camera issue? Needs larger solar panel. 13 rebuild/upgrades done to date (none this week).
2021-06-18 | 2 | 220 | 99% | BOB came back in on its own, as did Cameron Corners. DLZ & EUC remain OOC. WAR still alive with low battery. 1 upgrade, Poomacha, bringing total to 14.
2021-06-25 | 4 | 220 | 98% | BOB ooc again on 6/21. Cameron Corners dropped out again 6/24. DLZ & EUC still OOC. WAR was visited/fixed but still a bit intermittent. Upgrades at 19 with 2 more scheduled today. Asked CB to please prioritize 14 stations at or past 10 years.
2021-07-01 | 1 | 220 | 99.5% | Even chronic sleepers awake most of the week. As I write this, just DLZ ooc, in SCADA, on shedule for July 8. Lighter than usual intermittency. WMP Rebuild/upgrades at 29 with 2-3 more possible today.
2021-07-09 | 2 | 220 | 99% | De Luz got fixed on 7/8 but we lost East Warners and Del Mar Heights. They're in SCADA. Usual intermittency, with a couple odd ones, Chollas Lake, Olivenhain. Rebuild/Upgrades at 32. 14 remain tbd.
2021-07-16 | 3 | 220 | 98.5% | East Warners & Del Mar Heights remain OOC, in SCADA. Lost Chollas Lake 7/9. San Clemente Ridge bad T/RH. 39 Rebuild/Upgrades as of this morning, 7 remaining will have to wait for CH200 delivery. 17 of 30 new (2020) sites now in SCADA/SPARC. 214 stations (all possible) on 30 sec reads.
723/21 | 3 | 220 | 98.5% | East Warners, Del Mar Heights & Chollas Lake remain OOC, in SCADA. SCR bad T/RH. No movement on rebuild/upgrades, one or two may happen today. Truck problems and sick call-ins derailed Kearny crew schedule this week.
2021-07-30 | 5 | 220 | 98% | East Warners, Del Mar Heights & Chollas Lake remain OOC, in SCADA. Julian dropped upon calibration/template upload. BOB OOC again. SCR bad T/RH. No movement on rebuild/upgrades, stands at 39.
2021-08-06 | 4 | 220 | 98% | East Warners, Del Mar Heights & Chollas Lake remain OOC, in SCADA. BOB OOC again. SCR bad T/RH. 41 Rebuild/Upgrades completed, 5 remain tbd. Hideaway Lake T/RH went wonky for just one read on 8/6, will monitor
2021-08-13 | 4 | 220 | 98% | East Warners, Del Mar Heights & Chollas Lake remain OOC, in SCADA. BOB OOC since 7/25. SCR bad T/RH. Sherilton Valley intermittency getting worse. 41 Rebuild/Upgrades completed, 5 remain tbd.
2021-08-20 | 3 | 220 | 98.5% | EWN and SCR fixed this week. Del Mar Heights & Chollas Lake remain OOC, in SCADA. BOB OOC since 7/25. 41 Rebuild/Upgrades completed, 5 remain tbd. Calibrations wrapping up rapidly.
2021-08-27 | 1 | 220 | 99.5% | Del Mar Heights and BOB fixed this week. Chollas remains OOC (cell). No change in Rebuild/upgrade count. Kearny calibration records don't match mine and Dennis'… we show 32 tbd, they say 8. Caballo Park job sent to Kearny this week.
2021-09-03 | 1 | 220 | 99.55% | Chollas fixed over the weekend but BOB dropped out again. Requested visit to Sherilton Valley fto address chronic intermittency. No Rebuild/Upgrade work done, 5 remain. Calibrations at 18 tbd by my count. Confirmed Kearny has Caballo Park job.
2021-09-10 | 1 | 220 | 99.55% | BOB OOC 9/2/21. SHV sleepy as ever. 1 more Rebuild, 4 to go. About 14 calibrations left if they complete a couple scheduled today. Verified Caballo Park job rec'd by Chris.
2021-09-17 | 0 | 220 | 100% | SHV and CLN chronic, getting worse. BOB fixed on 9/15, swapped in ATT and SCADA installed. 4 rebuilds tbd. 6 calibrations tbd, 3 with access issues (2 on CPen and RSF) and 3 pending rebuild/upgrades. RSF will require relo, house built beside it. I'm showing 10 new stations still need SCADA radios installed, but no way to verify.
2021-10-01 | 2 | 221 | 99% | Caballo Park Station added on 9/27/21. Not added to dashboard at this time but is up in MesoWest. Volcan received upgrades on 9/27/21 (some had not been done on recorded date) but dropped cell comm on 10/1; it is in SCADA. Sherilton Valley ooc at 11:40 on 10/1.
2021-10-08 | 2 | 221 | 99% | Volcan OOC cellular most of the time. Crestline and SHV very bad. Crew visits requested.
2021-10-15 | 1 | 221 | 99.5% | Volcan unresolved, Brice didn't bring spare modem. Dye Mountain rebuild/upgrade incomplete, Brice didn't bring spare sensors, broke the T/RH upon installing new logger. SOB bad T/RH to be fixed by Kim on Saturday. Poomacha showed bad wind reads in SPARC then weno OOC in SCADA. Usual chronic intermittency. RSF needs field trip to relo.
2021-10-22 | 0 | 221 | 100% | Volcan fixed w/smashed cable connector found and replaced. Everything else resolved as well, just the usual suspects intermittent now. Mataguay low voltage alert, likely cause bad T/RH sensor shorting out according to Dennis. RSF trip still to be planned. All WMP work & calibrations complete.
2021-10-29 | 0 | 221 | 100% | Crestline visited and small antenna tried but intermittency persists, probably due to nearby cell towers. Sherilton Valley really bad as well as Buffalo Bump which is slated for work. Harmony Grove got new modem but now has bad wind, T/RH reads. I thought calibrations were done but told CPEN sites still need OS/progamming updates.
2021-11-05 | 2 | 221 | 99% | BUB OOC solid on 10/30, came back in for a few hours mid-day 11/4. It needs batteries, charge regulators, solar panel. CPEN on schedule 11/10. Potrero OOC 23:50 on 11/4. Oddly Sheril is awake so far this morning.
2021-11-12 | 2 | 221 | 99% | BUB in and out, on schedule next week. POT came back on its own. Sheril sleepy as usual. San Pasqual RAWS OOC on 11/9, FTS notified.
2021-11-19 | 2 | 221 | 99% | OMB went out 11/9. BUB limping along, usual access cut off, crew will have to try again. SHV and Lilac lagging this a.m. Raul Serrano got San Pasqual RAWS back in with a reboot; FTS recommends new logger. Need to check SCADA comm (32 stations not showing up).
2021-11-26 | 2 | 221 | 99% | OMB still OOC; CMC out 11/23 (both in SCADA); SHV lagging as usual. BUB fixed on 11/19. Dennis finished changing PW to WxSt@t1on except for OMB, Sherilton Valley and West Wynola.
2021-12-03 | 2 | 221 | 99% | OMB fixed 12/2, WW noted change but no notice of new #s, don't know if PW updated. CMC remains OOC/cell, in SCADA. SHV etc. usual intermittency. Sky Valley & Rancho Heights, both ATT_16 dropped cell comm and came back around the same time, likely carrier/cell tower activity.
2021-12-10 | 0 | 221 | 100% | CMC and Alpine fixed 12/7. Crest wind reads remain off. Dennis was able to update PW on OMB, SHV and WWY which completes that task for all installed modems. Pine Valley lagging and wind reads stuck in SPARC, SCADA ticket requested. SHV was better but lagging again this a.m., back to sleep at 7:30.
2021-12-17 | 0 | 221 | 100% | Crest wind reads remain off. Crestline, Sherilton Valley and West Wynola consistently inconsistent, but are in SCADA. Hopefully a SCADA ticket was issued for Pine Valley, wind reads still stuck.
2021-12-23 | 0 | 221 | 100% | Crestline, Sherilton Valley and West Wynola severely intermittent. Crest wind reads still out
2021-12-30 | 1 | 221 | 99.5% | Sherilton Valley & Mt. Laguna out. No SCADA at Mt. Laguna. Some low battery reads due to long rainy spell. Crest got fixed. Mt. Laguna out solid 12/31.
2022-01-07 | 0 | 221 | 100% | Sherilton Valley & Mt. Laguna sleeping in as usual. Judging from email between Jamie and Roberta, just 4-5 more stations to be brought into SCADA comm.
2022-01-14 | 0 | 221 | 100% | SHV, Mt Laguna severely intermittent. Discovered Volcan wind reads zero since 12/29 storm; on schedule today 1/14. Valley Center ooc at 23:00 1/13 w/low battery reads, monitoring.
2022-01-21 | 0 | 221 | 100% | Vocan was scheduled but not visited, reads still 0. Valley Center back in but voltage not recovering, will require visit. Same with Santa Ysabel North. SHV intermittency really bad.
2022-01-28 | 0 | 221 | 100% | Volcan fixed this week, just in time for Santa Ana. VC voltage now holding steady, can be addressed on calibration. YSN back in but brain fried. Hoping Tony & crew get up there next week, barring wind. SHV asleed half the time as usual.
2022-02-04 | 1 | 221 | 99.5% | YSN, WAR fixed and calibrated. SHV bad cell as usual, in SCADA. Jamul dropped cell comm 2/2, SCADA lagging. GUR cam installed; WRB and MTL got fuel sticks and BMR cam installed.
2022-02-11 | 1 | 221 | 99.5% | Jamul cell comm still down, requested visit. Carveacre bad T/RH sensor, visit requested. Requested STV get comms upgrade during calibration.
2022-02-18 | 1 | 221 | 99.5% | Jamul cell comm still down, requested visit. Carveacre bad T/RH sensor, visit requested. Requested STV get comms upgrade during calibration.
2022-02-25 | 3 | 221 | 98.5% | Jamul still down, North Descanso OOC/in SCADA, White Star OOC/no SCADA, Carveacre bad T/RH, Sherilton Valley mostly asleep; Twin Oaks went OOC 2/24 but came back in on its own. Multiple requests sent to Kearny. Got SCADA screens access restored this week.
2022-03-04 | 2 | 221 | 99% | Jamul still down, North Descanso OOC/in SCADA, White Star back in on its own, Carveacre bad T/RH, Sherilton Valley mostly asleep. School House Canyon OOC 00:10 this morning, maybe weather related, monitoring. Calibrations under way in earnest, but weather (wind) stalling trouble work.
2022-03-11 | 4 | 221 | 98% | No opportunity for crews to troubleshoot this week although calibrations are being done. Counting SHV OOC as it's barely in comm. Jamul, NDC, School House Canyon OOC. Carveacre bad T/RH. Usual intermittency but Peutz Valley has joined the pack of slackers.
2022-03-18 | 2 | 221 | 99% | JAM, NDC still OOC, Carveacre bad T/RH. SHV back to sleep as usual. Subbu & Kyle asked for master list so hopefully will have newer stations in SPARC, PowerBI soon.
2022-03-25 | 3 | 221 | 98.5% | JAM, NDC still OOC, Carveacre bad T/RH. SHV back to sleep as usual. White Star OOC again, this time for 5 days.
2022-04-01 | 2 | 221 | 99% | White Star fixed, swapped VZ for ATT. NDC visited but not resolved, issue w/reapeater. Needs call w/WW while on site. SHV out solid now, will need visit.
2022-04-08 | 0 | 221 | 100% | A new ATT tower did the trick for SHV and NDC. NDC no longer on RR. We are solid!
2022-04-15 | 0 | 221 | 100% | Just De Luz lagging a bit.
2022-04-22 | 0 | 221 | 100% | BUB lagging. Volcan Mountain 5154 Broken Anemometer; Opposite wind direction reads noted on 4/18. Inspection on 4/19 revealed it snapped in half, but wind gusting too strong to fix. New meter to be installed temporarily at earliest opportunity. Heavy duty model ordered. Plan is to install it on subsequent visit to turn the cross arm at an angle to reduce icing.
2022-04-29 | 0 | 221 | 100% | La Posta lagging. Volcan still spinning upside down. Brice keeps swapping out anemometers that fail directional reads, 8 within the last month or two. Unacceptable. Tony requested they be sent to WW for analysis.
2022-05-06 | 1 | 221 | 99.5% | Pala RAWS ooc, FTS notified. Brief intermittency with 5-6 sites. Volcan still needs wind fix. At least 10 anemometers have been replaced due to failing calibration; Chris/Brice think it's worn out directional potentiometer. Sending them to WW for diagnostics.
2022-05-13 | 0 | 221 | 100% | Pala RAWS still out, Kearny will send crew. Usual minor intermittency. Volcan heavy duty anemometer arrived, job can proceed. Failed wind meters on the way to WW. NDVI issues mostly resolved except wiring fix for Guejito and LiFeP04 battery recommended for Warners. Requested Kearny resume installs.
2022-05-27 | 0 | 221 | 100% | Still no Pala fix. Volcan fixed. Very minor intermittency. 17-19 SCADA sites ooc at weekly check.
2022-06-03 | 0 | 221 | 100% | Pala still down. Very minor intermittency. Jamie following up w/Roberta about RTU stats.
2022-06-10 | 2 | 221 | 99% | Peutz Valley & Lake Cuyamaca only sporadically in comm all week, likely ATT issue. Both are in SCADA comm. Pala remains down.
2022-06-17 | 1 | 221 | 99.5% | Lake Cuyamaca fixed, Peutz still out. Pala RAWS fixed but without recommended firmware update.
2022-06-24 | 1 | 221 | 99.5% | Brice checked on Peutz; ATT & VZ both bad. Chris B said he'd ask Mike Sanderson to do a desktop survey to see if RRs would work. Meanwhile it has good SCADA comm.
2022-07-01 | 0 | 221 | 100% | 100% only possible because Peutz happened to be awake, a rare occurance these days. Brice has been very proactive with SCADA issues, restored comms to 4 sites this week. Lack of comm for newer sites still a mystery. Just one calibration done this week---hope that picks up again soon.
2022-07-08 | 1 | 221 | 99.5% | Hellhole Canyon OOC/cell on 7/7; in SCADA. Brice had IMT 4807 and HOS 5166 back in SCADA as of 7/6. Rainbow Valley, Peutz Valley and Laguna intermittent. Chollas Lake backwards wind reads noted as of 7/1.
2022-07-15 | 1 | 220 | 99.5% | HHC RSF by contract crew doing UG. Brice found Chollas anemometer was installed backwards, fixed. Peutz the only one asleep this a.m.
2022-07-22 | 2 | 220 | 99% | More than usual intermittency, perhaps due to overcast. HHC to be reinstalled by Sept 1. Equipment not yet located. Possible theft. Anderson Valley OOC/cell w/low battery. Peutz out solid as of 7/18. 11 sites in SCADA FAIL state; 8 OFF
2022-07-29 | 2 | 220 | 99% | Slight intermittency, usual suspects. Killed HHC cell account. AVY came back w/voltage up to 11+, requested new battery. Reiterated req for Peutz survey. Finally got job packet for RSF Relo. Requested Kearny do that and N. Escondido install as well as 3 NDVI/Fuels sites. SCADA: 12 FAIL/8 OFF (2020 sites).
2022-08-05 | 2 | 220 | 99% | HHC re-install confirmed in the works. Usual intermittency. AVY now at 12V+. Again requested Peutz survey. NOE & RSF good to go, confirmed by Matt Newbill. SCADA; 6 sites in OFF, BOB was restored w/corrected IP.
2022-08-12 | 2 | 221 | 99% | NOE installed 8/6; RSF Relo same day but with new kit, SCADA still in comm at old site. 13 SCADA in FAIL/INIT state, NO active stations in OFF state. AVY now out solid, new battery requested. Still waiting for survey at Peutz Valley. Borrego went out solid for a few days but mysteriously came back on its own.
2022-08-19 | 1 | 221 | 99.5% | AVY & CWD back in comm. HHC re-install should happen next week or so. All but 4 Apollo stations now in SCADA, final radio installs pending. BUB cronically intermittent and DDS has joined the club. RSF will get SCADA soon, alerted Kearny and EDOT to conflict with old site still active.
2022-08-26 | 2 | 221 | 99% | Note HHC not counted. It should be put back up soon. BUB getting worse. PVC OOC since 8/18 and not in SCADA. and PTZ remains OOC/cell, in SCADA. Poomacha officially unreachable.
2022-09-02 | 4 | 221 | 98% | HHC still down. SHV severely intermittent, counted as OOC today. PTZ still OOC. Brice reported fixind AVY but was actually at PVC. He has apparently forgotton the need to call WW while on site. He's supposed to fix AVY w/new battery today.
2022-09-09 | 4 | 221 | 98% | Hurrican Kay day! HHC was to be reinstalled this weekend but weather will likely delay. Brice swapped ATT for VZ at SHV, effectively killing cell comm. AVY checked by telecomm tech, found loose wire. Not fixed. PTZ still OOC. Del Dios South badly intermittent. Los Coyotes dropped cell for unknown reason 9/2. ATT tower issue? None of these can do 30 sec reads at present.
2022-09-16 | 4 | 222 | 98% | HHC re-installed, in comm 9/15/22. Los Coyotes OOC/cell (ATT) on 9/2, in SCADA. OMB dropped cell (VZ) 9/14, in SCADA. SHV & PTZ remain OOC/cell, in SCADA. I have lost ability to activate SIMs/modems successfully, now working with Mike Sanderson and Juan Vargas to hand off this task. Kearny has 1 spare ATT modem left.
9/22/22 (early issuance) | 3 | 222 | 98.5% | Los Coyotes OOC/cell (ATT) on 9/2, in SCADA. OMB fixed 9/16. SHV & PTZ remain OOC/cell, in SCADA. Solved VZ issues w/Mike Sanderson, he and Juan Vargas now set up in B2B. ATT provisioning fix still pending. SCADA comm looking great, 3 newer stations left to bring in. Bad news on NDVI cams, only 2 operating normally. 3 others stopped recording images months ago.
2022-09-30 | 3 | 222 | 98.5% | Los Coyotes OOC/cell (ATT) on 9/2, in SCADA. SHV & PTZ remain OOC/cell, in SCADA. ATT provisioning fix still pending, Juan apparently not available this week. SCADA comm looking great, 3 stations OOC. However, there may be a couple more OOC---they appear in SPARC but I notice the reads don't match WW or other dashboards.
2022-10-07 | 2 | 222 | 99% | Los Coyotes fixed, SHV & PTZ remain OOC/cell, in SCADA. ATT provisioning fix still pending, Juan not answering messaging/emails. SCADA comm looking great, 1 2020 station left, WIN. However, several in FAIL state that show up in PowerBI, but T/RH reads are way off MesoWest. 2 new camera/fuels installs: SOS cam & fuel, Highland Valley cam only. Marc identified ongoing problem, logger issue, will address w/Campbell Scientific.
2022-10-14 | 3 | 222 | 98.5% | SHV & PTZ remain OOC/cell, in SCADA. ATT provisioning fix still pending, Juan not answering messaging/emails/calls. SCADA comm looking great, 1 2020 station left, WIN. Iron Mt. Trail camera installed. MVN ooc as of 23:50 10/13, monitoring. Calibrations complete w2 excepitons/access issues AMO & POM. All SCADA-enabled stations now in SPARC-EOC.
2022-10-21 | 2 | 222 | 99% | SHV & PTZ remain OOC/cell, in SCADA. Mike Sanderson has site sheets, will survey when he has time. He came by and provisioned 6 ATT modems this morning. 8 NDVI cams installed, 3 w/Fuels.
2022-10-28 | 2 | 222 | 99% | PTZ & SHV remain ooc/cell, in SCADA, Kearny work req standing. Also requesting last NDVI install at Mission Trails and 3 fuels sensor sites though WMP goal has been met w/9 cams, 5 fuels (4 co-located).
2022-11-04 | 2 | 222 | 99% | (Ditto above, no change). PTZ & SHV remain ooc/cell, in SCADA, Kearny work req standing. Also requesting last NDVI install at Mission Trails and 3 fuels sensor sites though WMP goal has been met w/9 cams, 5 fuels (4 co-located).
2022-11-11 | 3 | 222 | 98.5% | PTZ & SHV remain ooc/cell, in SCADA, Kearny work req standing. Also requesting last NDVI install at Mission Trails and 3 fuels sensor sites though WMP goal has been met w/9 cams, 5 fuels (4 co-located). Anderson Valley OOC cell/SCADA, visit delayed by this week's rainstorm. Escondiod North finally added to internal dashboard.
2022-11-18 | 2 | 222 | 99% | PTZ & SHV remain ooc/cell, in SCADA, Kearny work req standing. MTL cam will have to wait for ethernet cable order. AVY fixed 11/15, new solar panel & battery. Just 2 '20 installs remain to be brought into SCADA comm, PVC and WIN.
2022-11-22 | 3 (+1 RAWS) | 222 | 99% | Early issuance due to holiday & 11/24 moderate Santa Ana. Mission Valley RAWS OOC 11/21 7:50. Monitoring. PTZ & SHV remain ooc/cell, in SCADA
2022-12-02 | 3 | 222 | 98.6% | MV RAWS still out, Kearny will get to it. PTZ & SHV no change. Living Coast OOC/cell 11/29, monitoring, will req crew if still out next week. All are in SCADA. MTL work still pending cable, to ship 12/29.
2022-12-09 | 4 | 222 | 98.2% | Rob fixed MV RAWS. Jamie put in telecomm survey reqs for PTZ & SHV, opened tickets for SCADA issues. DJZ, LCM OOC/cell, in SCADA. Santa Ysabel North intermittent/low voltage, bad temp reads. Crew visits requested.
2022-12-16 | 3 | 222 | 98.6% | PTZ, SHV remain ooc/cell. YSA fixed by Brice but may still need work. Sunshine Summit 5133 down on 12/14 for W2S. Will likely be down for a few weeks.
12/20/2022 (Early issuance due to holiday) | 2 | 222 | 99% | PTZ, SHV remain ooc/cell. YSA fixed by Brice but may still need work. Sunshine Summit 5133 down on 12/14 for W2S. Will likely be down for a few weeks. Otay Mtn down overnight but Madison was able to reach it and re-sync, got it back in. Signal weak lately, may join the ranks of chronic sleepers.
2022-12-30 | 2 | 222 | 99% | SSS still down. PTZ, SHV remain ooc/cell.
2023-01-06 | 3 | 222 | 98.6% | Cell problems at COY, LCM, De Luz Creek. Pine Valley Creek ooc at 22:50 1/5. SCADA comm a mess. All likely storm-related. SSS still down. PTZ, SHV remain ooc/cell.
2023-01-13 | 4 | 222 | 98% | SCADA comm still a mess. SSS still down. PTZ, SHV remain ooc/cell. Barrett RAWS has been ooc since 12/20. Rob Latting will take a look when he gets a chance. More rain tk, not much work likely to get done till things dry out. Calibrations have commenced.
2023-01-20 | 4 | 222 | 98% | SS still down. PTZ, SHV remain ooc/cell. Fallbrook went ooc/cell 1/13 at 12:00, in SCADA. Brice actually fixed Barrett RAWS on 1/19.
2023-01-27 | 3 (+1 sat comm) | 222 | 98% | SSS still down. PTZ, SHV remain ooc/cell. Mt Springs Grade RAWS now OOC. NDVI cams at BMR and MVN having issues. (MVN fixed 1/25) SSS not re-installed yet.
2023-02-03 | 3 (+1 sat comm) | 222 | 98% | SSS will remain down pending new pole selection. PTZ, SHV remain ooc/cell; Dave Walton submitted ticket 1/30; RITM0449059/ SCTASK0458467. Mt Springs Grade RAWS fixed on 1/27 but out again today. NDVI cams at BMR and IMT having issues. (MVN fixed 1/25)
2023-02-10 | 3 (+1 sat comm) | 222 | 98% | SSS will remain down pending new pole selection. PTZ, SHV remain ooc/cell; Dave Walton submitted ticket 1/30; RITM0449059/ SCTASK0458467, then performed survey and sent results to Kearny. Mt Springs Grade RAWS fixed on 1/27 but out again soon after, remains down. NDVI cams at BMR and IMT having issues along w/bad T/RH.
2023-02-17 | 2 (+1 sat comm) Wiscarver not yet at 24 hrs | 221* | 98% | *SSS will remain down pending job written for new pole. New Poomacha site chosen, hope it will keep in comm until new site installed. PTZ, SHV remain ooc/cell; Mt Springs Grade RAWSremains down. De Luz Creek and Wisecarver severely intermittent. NDVI cams at BMR and IMT having issues along w/bad T/RH.
2023-02-24 | 2 (+1 sat comm) | 221 | 98% | *SSS will remain down pending job written for new pole. New Poomacha site chosen, hope it will keep in comm until new site installed. PTZ, SHV remain ooc/cell; Mt Springs Grade RAWSremains down. NDVI cams all have same issue according to Brice. He fixed T/RH at BMR. Harrison Park wind reads are backwards. East Warners barely spinning, likely broken prop. Only 13 SCADA sites OOC, odd to see improved performance considering epic winter storm.
2023-03-03 | 2 (+1 sat comm) | 221 | 98% | SSS job submitted to Karen Williams, RA Planner. LaJolla Tribe asked to meet about new sites, but now not responding to emails. Requested work; East Warners, Harrison Park wind meters. NDVI stuff on hold for now, awaiting firmware fix from WW. Begging for cellular solution at PTZ & SHV (which is now OOC/SCADA.
2023-03-10 | 2 (+1 sat comm) | 222 | 98.5% | No change in status for PTZ, SHV. Surprise: SSS re-installed so paperwork will have to catch up. Finally pulled into La Jolla Tribal Council meeting; they recommed P61777 near a home that had roof blown off. Now Volcan showing backward reads too---so much for HD wind meter. EWR & HRP wind issues also still out. TNSC1 remains OOC long term.
2023-03-17 | 2 (+1 sat comm) | 222 | 98.5% | No change: PTZ, SHV, TNSC1. Volcan, EWR & HRP work requested. NDVI work still pending issue resolution from WW. Calibration Training took place this week but only 1 classroom day, weather cancelled field work.
2023-03-24 | 2 (+1 sat comm) | 222 | 98.5% | No change: PTZ, SHV, TNSC1. Volcan, EWR & HRP work requested. NDVI work still pending issue resolution from WW. Weather has delayed work for weeks---another storm next week.
2023-03-31 | 3 (+1 sat comm) | 222 | 98% | No change: PTZ, SHV, TNSC1. Volcan, EWR & HRP work requested. NDVI work still pending issue resolution from WW. Anderson Valley OOC/cell, Tony entered APN wrong during firmware update. Needs manual re-entry.
2023-04-07 | 7 (+1 sat comm) | 222 | 96% | IMT, WST, EWR lagging badly then OOC this morning. Cell tower issue? WW did report timer issue at WST but brought it back in yesterday afternoon. Along with usual suspects. PTZ, SHV, TNSC1 ooc long term. AVY still out. Drying out now so hopefully work can commence next week.
2023-04-14 | 3 (+1 sat comm) | 222 | 98% | 4 stations timer issue: WW implemented temporary clock offset fix, cause tbd. PTZ, SHV, TNSC1 remain ooc long term. AVY still out. Calibrations/fixes resumed, Brice replace wind at EWR. Still waiting camera issues resolution from WW.
2023-04-21 | 3 (+1 sat comm) | 222 | 98% | PTZ & SHV SCADA comm only, no cellular fix in sight. Brice resumed work this week, implemented fixes at AVY and IMT except for physical issue, telecomm equipment blocking wind meter rotation. MVN got it's fuel stick and camera fix, but now OOC/cell this morning.
2023-04-28 | 11 + 1 sat comm | 222 | 95% | PTZ & SHV SCADA comm only. Some kind of major cellular glitch this morning. OOC solid: BVD, GVY, HRP (these 2 visited by Brice this week). OOC since midnight: WCV, TLK, BOC, CWD. DLC ooc since 4am but that's usual chronic behaviour. WW identified "clock inconsistency" and promised fix in about an hour, which fixed some. Still OOC and may need visit: WCV, BOC, HRP (showing up in WW dashboard but not in MesoWest). Now almost all "West" stations lagging.
5/4/23 (early issuance) | 10 + 1 sat comm | 222 | 95% | ATT/RV50 sites dropping like flies. 3 OOC Solid 5-6 days: Boulder Creek 1965 (in SCADA), La Posta 5121 (in SCADA), West Alpine 1906 (OOC SCADA). 5 OOC since midnight: Barona Mesa 5149, Crestline 5155, West Santa Ysabel 5136, West Potrero 1972, Country Estates 1995 (all are in SCADA). 5 OOC since early a.m., these are known severely chronic sites: Wisecarver 5138, Buffalo Bump 4832, Turner Lake 1991, Rancho Heights 1981 (all are in SCADA)
2023-05-12 | 8 | 222 | 96% | TNSC1 finally back in upon annual maintenance this week. PTZ/SHV SCADA only. Between WW firmware update knocking out modems and possible ATT glitch and/or RV50 failures, 6 sites out solid (La Posta, West Alpine, Barona Mesa, Borrego, Wisecarver (back in at 10:00 this a.m), Boulder Creek. 4 more severely intermittent but not yet out for over 12 hours. WW to check w/Sierra Wireless.
2023-05-19 | 11 | 222 | 95% | No repair work or calibrations reported this week. LPT, WAL, BMA, BOC remain OOC solid. TLK, WCV only briefly awake. DLC getting worse. PTZ & SHV SCADA only. VCM reads seem normal today but no word that it was worked on.
2023-05-26 | 6 | 222 | 97% | LPT, WAL, BMA, BOC out solid. PTZ/SHV SCADA only.
Note on B40: McCrindle, Beth: Previously had eliminated known issues from count, to reflect stations that should be working are working. But I'm adjusting to a pure count now with goal of finally addressing long term issues this year and reaching a true 100% status.